## Global Inputs
Please close all other excel spreadsheets (including reopening this one) before running any macros contained in it
Topology change # | Description | Uptake year
0 | BAU
1 | MWTS-TGN/Fulham | 2028
2
3
4
EAR Loop | MWTS-E |  | PoE Weighting
Discount rate | 5.56% |  | P50 | 70%
Asset life | 45 | Years | P10 | 30%
First year of analysis | 2025 | Year
Line Segments for analysis (include new lines as well) | Length (km)
MWTS-SLE | 67.29
MWTS-TGN No.1 | 19.12
MWTS-TGN No.2 | 18.25
MWTS-MFA | 69.12
TGN-MFA | 46.57
TGN-SLE | 51.5
TGN-WISS | 27.5
WISS-SLE | 27
WISS-MFA | 19.07
ZSS connected to Loop
bdl
cnr
mfa
nla
sle
tgn
Ave no. of outages per year | 1
Ave. no. of outages per km line length per year | 0.036834
Ave. outage duration (hr) | 1
Ave. voltage collapse duration (hr) | 1
Sensitivities | Base | Low | High
Demand Forecasts | 100% | 90% | 110%
Failure Rate | 100% | 50% | 150%
Project Details | 5
Option 1: Do Nothing
Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC
Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC
Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC
Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS
Option 6:
Option 7:
Option 8:
|  | Summer | Winter
Gross Vs Net Load for LDC | Gross Load | 1.33 | 1.13
|  | Summer | Winter
Gross Load |  | 1.33 | 1.13
Net Load |  | 1 | 1

## VCR Calculation
| 1 |  |  |  | Sensitivity value | 1
| AER Rates (2024) |  |  |  |  | Values used in analysis
Commercial | 34.39 |  |  |  |  | 34.39
Farms | 22.25 |  |  |  |  | 22.25
Industrial | 33.49 |  |  |  |  | 33.49
Residential | 49.23 |  |  |  |  | 49.23
Customer consumption data (kWh) by ZSS
ZSS | bdl | cnr | mfa | nla | sle | tgn | 0 | 0 | 0 | 0 | 0 | 0 | EAR Loop
COMMERCIAL | 98092994.73 | 3286459.51 | 29396861.67 | 6169925.1 | 40624414.99 | 67013687.18 | [6 empty] | 244584343.18
FARM | 13601018.89 | 296168.14 | 39655627.3 | 3596991.02 | 12427542.72 | 11755715.82 | [6 empty] | 81333063.89
INDUSTRIAL | 13348904.31 | 703601.11 | 8981335.08 | 2186479.19 | 13728067.27 | 13620730.97 | [6 empty] | 52569117.93
LIGHT | 778879.99 | 0 | 787800.53 | 5187.52 | 0 | 1065802.23 | [6 empty] | 2637670.27
RESIDENTIAL | 105304587.71 | 4431296.7 | 33848726.33 | 17156032.74 | 45674977.99 | 77974991.78 | [6 empty] | 284390613.25
Grand Total | 231126385.63 | 8717525.46 | 112670350.91 | 29114615.57 | 112455002.97 | 171430927.98 | 0 | 0 | 0 | 0 | 0 | 0 | 665514808.52
%Utilisation by segment
Commercial | 42.44% | 37.7% | 26.09% | 21.19% | 36.13% | 39.09% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 36.75%
Farms | 5.885% | 3.397% | 35.2% | 12.35% | 11.05% | 6.857% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 12.22%
Industrial | 5.776% | 8.071% | 7.971% | 7.51% | 12.21% | 7.945% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 7.899%
Residential | 45.9% | 50.83% | 30.74% | 58.94% | 40.62% | 46.11% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 43.13%
VCR by segment | EAR Loop
Commercial | 12.6387
Farms | 2.7192
Industrial | 2.6454
Residential | 21.2323
Loop VCR | 39.2356

## Output for AusNet NPV Model
$k to $M | 0.001 | [8 empty] | $M to MWh | 25.4871
|  | Base Case Demand | [9 empty] | Base Case Demand
|  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 1.1137 | 1.1137 | 1.1137 | 1.1137 | 1.1137 |  |  |  | Total EUE (MWh) | FY25 | 28.3854 | 28.3854 | 28.3854 | 28.3854 | 28.3854 | 0 | 0 | 0 | Options sheet name: | Global Inputs
| FY26 | 2.6361 | 2.6361 | 2.6361 | 2.6361 | 2.6361 |  |  |  |  | FY26 | 67.1867 | 67.1867 | 67.1867 | 67.1867 | 67.1867 | 0 | 0 | 0 | VCR sheet name: | VCR Calculation
| FY27 | 4.8351 | 4.8351 | 4.8351 | 4.8351 | 4.8351 |  |  |  |  | FY27 | 123.2314 | 123.2314 | 123.2314 | 123.2314 | 123.2314 | 0 | 0 | 0 | EUSE sheet name: | EUSE Calculator
| FY28 | 2.3613 | 0.037438 | 0.0060347 | 0.011211 | 0.01758 |  |  |  |  | FY28 | 60.1833 | 0.95418 | 0.15381 | 0.28574 | 0.44806 | 0 | 0 | 0 | File Prefix: | EAR_MWTS-E_OPT
| FY29 | 2.5897 | 0.05616 | 0.0079976 | 0.013463 | 0.022594 |  |  |  |  | FY29 | 66.0045 | 1.4313 | 0.20384 | 0.34312 | 0.57586 | 0 | 0 | 0 |  |  | File reference | EUE Range reference | Base EUE range ref | Low EUE range ref | High EUE range ref
| FY30 | 2.9899 | 0.087536 | 0.013061 | 0.019408 | 0.033687 |  |  |  |  | FY30 | 76.2043 | 2.231 | 0.33289 | 0.49465 | 0.85857 | 0 | 0 | 0 | 1 | Option1 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY31 | 4.739 | 0.15929 | 0.030296 | 0.039024 | 0.065859 |  |  |  |  | FY31 | 120.7824 | 4.0598 | 0.77216 | 0.99461 | 1.6785 | 0 | 0 | 0 | 2 | Option2 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY32 | 7.1467 | 0.24956 | 0.09615 | 0.092869 | 0.10345 |  |  |  |  | FY32 | 182.1473 | 6.3607 | 2.4506 | 2.367 | 2.6367 | 0 | 0 | 0 | 3 | Option3 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY33 | 11.4165 | 0.53594 | 0.43224 | 0.36202 | 0.16921 |  |  |  |  | FY33 | 290.973 | 13.6596 | 11.0165 | 9.2269 | 4.3127 | 0 | 0 | 0 | 4 | Option4 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY34 | 12.1547 | 0.61292 | 0.53044 | 0.4436 | 0.18013 |  |  |  |  | FY34 | 309.7877 | 15.6214 | 13.5194 | 11.3061 | 4.591 | 0 | 0 | 0 | 5 | Option5 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY35 | 21.27 | 1.6853 | 1.7172 | 1.4872 | 0.24965 |  |  |  |  | FY35 | 542.11 | 42.9527 | 43.7675 | 37.9048 | 6.3627 | 0 | 0 | 0 | 6 | Option6 filename: | EAR_SMTS_OPT6.xlsx | '[EAR_SMTS_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_SMTS_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_SMTS_OPT6.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_SMTS_OPT6.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY36 | 23.3412 | 1.3511 | 1.3408 | 1.1652 | 0.24546 |  |  |  |  | FY36 | 594.9001 | 34.4347 | 34.1733 | 29.6984 | 6.256 | 0 | 0 | 0 | 7 | Option7 filename: | EAR_MWTS-E_OPT7.xlsx | '[EAR_MWTS-E_OPT7.xlsx]EUSE Calculator'!$F$18:$T$18
| FY37 | 28.4421 | 2.5671 | 2.9132 | 2.4614 | 0.31 |  |  |  |  | FY37 | 724.9067 | 65.4276 | 74.2494 | 62.7331 | 7.901 | 0 | 0 | 0 | 8 | Option8 filename: | EAR_MWTS-E_OPT8.xlsx | '[EAR_MWTS-E_OPT8.xlsx]EUSE Calculator'!$F$18:$T$18
| FY38 | 53.1535 | 7.3917 | 7.8574 | 7.0261 | 0.50155 |  |  |  |  | FY38 | 1354.7267 | 188.3918 | 200.2617 | 179.0744 | 12.7831 | 0 | 0 | 0
| FY39 | 43.3219 | 5.0403 | 5.603 | 4.8938 | 0.44973 |  |  |  |  | FY39 | 1104.149 | 128.4617 | 142.8044 | 124.7289 | 11.4622 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | Low Case Demand | [9 empty] | Low Case Demand
|  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 0.035548 | 0.035548 | 0.035548 | 0.035548 | 0.035548 |  |  |  | Total EUE (MWh) | FY25 | 0.90603 | 0.90603 | 0.90603 | 0.90603 | 0.90603 | 0 | 0 | 0
| FY26 | 0.26077 | 0.26077 | 0.26077 | 0.26077 | 0.26077 |  |  |  |  | FY26 | 6.6462 | 6.6462 | 6.6462 | 6.6462 | 6.6462 | 0 | 0 | 0
| FY27 | 0.65041 | 0.65041 | 0.65041 | 0.65041 | 0.65041 |  |  |  |  | FY27 | 16.577 | 16.577 | 16.577 | 16.577 | 16.577 | 0 | 0 | 0
| FY28 | 0.24823 | 0.0053674 | 0.00067765 | 0.0023404 | 0.0038113 |  |  |  |  | FY28 | 6.3268 | 0.1368 | 0.017271 | 0.059651 | 0.097139 | 0 | 0 | 0
| FY29 | 0.31943 | 0.0085961 | 0.00076837 | 0.0024977 | 0.0041704 |  |  |  |  | FY29 | 8.1414 | 0.21909 | 0.019584 | 0.063658 | 0.10629 | 0 | 0 | 0
| FY30 | 0.43666 | 0.015415 | 0.0010647 | 0.003048 | 0.00544 |  |  |  |  | FY30 | 11.1291 | 0.39288 | 0.027136 | 0.077685 | 0.13865 | 0 | 0 | 0
| FY31 | 0.78759 | 0.035401 | 0.0026152 | 0.005606 | 0.010746 |  |  |  |  | FY31 | 20.0734 | 0.90226 | 0.066654 | 0.14288 | 0.27389 | 0 | 0 | 0
| FY32 | 1.1507 | 0.059663 | 0.0054919 | 0.009606 | 0.018623 |  |  |  |  | FY32 | 29.3278 | 1.5206 | 0.13997 | 0.24483 | 0.47465 | 0 | 0 | 0
| FY33 | 1.7022 | 0.10327 | 0.013141 | 0.018085 | 0.034773 |  |  |  |  | FY33 | 43.3852 | 2.6321 | 0.33493 | 0.46093 | 0.88627 | 0 | 0 | 0
| FY34 | 1.6556 | 0.11059 | 0.014399 | 0.019704 | 0.037739 |  |  |  |  | FY34 | 42.1962 | 2.8186 | 0.36698 | 0.5022 | 0.96186 | 0 | 0 | 0
| FY35 | 2.3474 | 0.15638 | 0.02983 | 0.034607 | 0.059864 |  |  |  |  | FY35 | 59.8281 | 3.9858 | 0.76028 | 0.88204 | 1.5258 | 0 | 0 | 0
| FY36 | 2.8002 | 0.15174 | 0.026036 | 0.034027 | 0.059666 |  |  |  |  | FY36 | 71.3694 | 3.8675 | 0.66359 | 0.86724 | 1.5207 | 0 | 0 | 0
| FY37 | 3.1587 | 0.19725 | 0.04812 | 0.050465 | 0.078054 |  |  |  |  | FY37 | 80.5067 | 5.0274 | 1.2264 | 1.2862 | 1.9894 | 0 | 0 | 0
| FY38 | 5.2105 | 0.35444 | 0.20199 | 0.18266 | 0.11978 |  |  |  |  | FY38 | 132.8009 | 9.0337 | 5.1481 | 4.6556 | 3.0527 | 0 | 0 | 0
| FY39 | 4.4838 | 0.27377 | 0.11855 | 0.11202 | 0.10317 |  |  |  |  | FY39 | 114.2787 | 6.9777 | 3.0215 | 2.8551 | 2.6295 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | High Case Demand | [9 empty] | High Case Demand
|  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 5.8608 | 5.8608 | 5.8608 | 5.8608 | 5.8608 |  |  |  | Total EUE (MWh) | FY25 | 149.3743 | 149.3743 | 149.3743 | 149.3743 | 149.3743 | 0 | 0 | 0
| FY26 | 13.0978 | 13.0978 | 13.0978 | 13.0978 | 13.0978 |  |  |  |  | FY26 | 333.8236 | 333.8236 | 333.8236 | 333.8236 | 333.8236 | 0 | 0 | 0
| FY27 | 21.8339 | 21.8339 | 21.8339 | 21.8339 | 21.8339 |  |  |  |  | FY27 | 556.4826 | 556.4826 | 556.4826 | 556.4826 | 556.4826 | 0 | 0 | 0
| FY28 | 11.2255 | 0.1463 | 0.10202 | 0.082816 | 0.072356 |  |  |  |  | FY28 | 286.1053 | 3.7287 | 2.6001 | 2.1107 | 1.8441 | 0 | 0 | 0
| FY29 | 12.0422 | 0.20804 | 0.14566 | 0.12033 | 0.10331 |  |  |  |  | FY29 | 306.9216 | 5.3023 | 3.7124 | 3.067 | 2.6331 | 0 | 0 | 0
| FY30 | 14.598 | 0.36802 | 0.30173 | 0.25955 | 0.16568 |  |  |  |  | FY30 | 372.0607 | 9.3799 | 7.6903 | 6.6151 | 4.2226 | 0 | 0 | 0
| FY31 | 25.0662 | 1.2411 | 1.368 | 1.1697 | 0.39463 |  |  |  |  | FY31 | 638.8633 | 31.6326 | 34.8671 | 29.8121 | 10.0579 | 0 | 0 | 0
| FY32 | 40.4461 | 3.2549 | 3.8397 | 3.2945 | 0.66972 |  |  |  |  | FY32 | 1030.8529 | 82.959 | 97.862 | 83.9669 | 17.0693 | 0 | 0 | 0
| FY33 | 73.085 | 10.2324 | 11.3575 | 10.1335 | 1.1925 |  |  |  |  | FY33 | 1862.7224 | 260.7931 | 289.4697 | 258.2737 | 30.3935 | 0 | 0 | 0
| FY34 | 79.2349 | 11.5757 | 12.7949 | 11.4052 | 1.1551 |  |  |  |  | FY34 | 2019.4659 | 295.0307 | 326.1041 | 290.6858 | 29.44 | 0 | 0 | 0
| FY35 | 130.2164 | 26.7759 | 27.7689 | 25.4558 | 2.2125 |  |  |  |  | FY35 | 3318.8337 | 682.4401 | 707.7473 | 648.7946 | 56.389 | 0 | 0 | 0
| FY36 | 129.9448 | 23.2252 | 24.8881 | 22.6298 | 2.2736 |  |  |  |  | FY36 | 3311.912 | 591.9412 | 634.3257 | 576.7666 | 57.9462 | 0 | 0 | 0
| FY37 | 171.1314 | 39.6929 | 40.5508 | 37.5908 | 3.248 |  |  |  |  | FY37 | 4361.6375 | 1011.6551 | 1033.5214 | 958.0799 | 82.781 | 0 | 0 | 0
| FY38 | 273.2963 | 78.1336 | 76.3955 | 72.152 | 6.8496 |  |  |  |  | FY38 | 6965.5223 | 1991.3962 | 1947.0988 | 1838.9439 | 174.5771 | 0 | 0 | 0
| FY39 | 231.7687 | 60.865 | 60.7558 | 57.0528 | 5.2956 |  |  |  |  | FY39 | 5907.1059 | 1551.2716 | 1548.488 | 1454.1099 | 134.969 | 0 | 0 | 0
| Residual | [9 empty] | Residual

## Output for AusNet NPV Model_PoF
$k to $M | 0.001 | [8 empty] | $M to MWh | 25.4871
|  | Base Case Failure Rate | [9 empty] | Base Case Failure Rate
|  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 1.1137 | 1.1137 | 1.1137 | 1.1137 | 1.1137 |  |  |  | Total EUE (MWh) | FY25 | 28.3854 | 28.3854 | 28.3854 | 28.3854 | 28.3854 | 0 | 0 | 0 | Options sheet name: | Global Inputs
| FY26 | 2.6361 | 2.6361 | 2.6361 | 2.6361 | 2.6361 |  |  |  |  | FY26 | 67.1867 | 67.1867 | 67.1867 | 67.1867 | 67.1867 | 0 | 0 | 0 | VCR sheet name: | VCR Calculation
| FY27 | 4.8351 | 4.8351 | 4.8351 | 4.8351 | 4.8351 |  |  |  |  | FY27 | 123.2314 | 123.2314 | 123.2314 | 123.2314 | 123.2314 | 0 | 0 | 0 | EUSE sheet name (Base PoF): | EUSE Calculator_PoF
| FY28 | 2.3613 | 0.037438 | 0.0060347 | 0.011211 | 0.01758 |  |  |  |  | FY28 | 60.1833 | 0.95418 | 0.15381 | 0.28574 | 0.44806 | 0 | 0 | 0 | File Prefix: | EAR_MWTS-E_OPT
| FY29 | 2.5897 | 0.05616 | 0.0079976 | 0.013463 | 0.022594 |  |  |  |  | FY29 | 66.0045 | 1.4313 | 0.20384 | 0.34312 | 0.57586 | 0 | 0 | 0 |  |  | File reference | EUE Range reference | Base EUE range ref | Low EUE range ref | High EUE range ref
| FY30 | 2.9899 | 0.087536 | 0.013061 | 0.019408 | 0.033687 |  |  |  |  | FY30 | 76.2043 | 2.231 | 0.33289 | 0.49465 | 0.85857 | 0 | 0 | 0 | 1 | Option1 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT1.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY31 | 4.739 | 0.15929 | 0.030296 | 0.039024 | 0.065859 |  |  |  |  | FY31 | 120.7824 | 4.0598 | 0.77216 | 0.99461 | 1.6785 | 0 | 0 | 0 | 2 | Option2 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT2.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY32 | 7.1467 | 0.24956 | 0.09615 | 0.092869 | 0.10345 |  |  |  |  | FY32 | 182.1473 | 6.3607 | 2.4506 | 2.367 | 2.6367 | 0 | 0 | 0 | 3 | Option3 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT3.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY33 | 11.4165 | 0.53594 | 0.43224 | 0.36202 | 0.16921 |  |  |  |  | FY33 | 290.973 | 13.6596 | 11.0165 | 9.2269 | 4.3127 | 0 | 0 | 0 | 4 | Option4 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT4.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY34 | 12.1547 | 0.61292 | 0.53044 | 0.4436 | 0.18013 |  |  |  |  | FY34 | 309.7877 | 15.6214 | 13.5194 | 11.3061 | 4.591 | 0 | 0 | 0 | 5 | Option5 filename: | EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment East Gippsland 66kV Loop (MWTS-TGN-MFA lines)_OPT5.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY35 | 21.27 | 1.6853 | 1.7172 | 1.4872 | 0.24965 |  |  |  |  | FY35 | 542.11 | 42.9527 | 43.7675 | 37.9048 | 6.3627 | 0 | 0 | 0 | 6 | Option6 filename: | EAR_SMTS_OPT6.xlsx | '[EAR_SMTS_OPT6.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_SMTS_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_SMTS_OPT6.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_SMTS_OPT6.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY36 | 23.3412 | 1.3511 | 1.3408 | 1.1652 | 0.24546 |  |  |  |  | FY36 | 594.9001 | 34.4347 | 34.1733 | 29.6984 | 6.256 | 0 | 0 | 0 | 7 | Option7 filename: | EAR_MWTS-E_OPT7.xlsx | '[EAR_MWTS-E_OPT7.xlsx]EUSE Calculator_PoF'!$F$18:$T$18
| FY37 | 28.4421 | 2.5671 | 2.9132 | 2.4614 | 0.31 |  |  |  |  | FY37 | 724.9067 | 65.4276 | 74.2494 | 62.7331 | 7.901 | 0 | 0 | 0 | 8 | Option8 filename: | EAR_MWTS-E_OPT8.xlsx | '[EAR_MWTS-E_OPT8.xlsx]EUSE Calculator_PoF'!$F$18:$T$18
| FY38 | 53.1535 | 7.3917 | 7.8574 | 7.0261 | 0.50155 |  |  |  |  | FY38 | 1354.7267 | 188.3918 | 200.2617 | 179.0744 | 12.7831 | 0 | 0 | 0
| FY39 | 43.3219 | 5.0403 | 5.603 | 4.8938 | 0.44973 |  |  |  |  | FY39 | 1104.149 | 128.4617 | 142.8044 | 124.7289 | 11.4622 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | Low Case Failure Rate | [9 empty] | Low Case Failure Rate
|  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 1.0585 | 1.0585 | 1.0585 | 1.0585 | 1.0585 |  |  |  | Total EUE (MWh) | FY25 | 26.9779 | 26.9779 | 26.9779 | 26.9779 | 26.9779 | 0 | 0 | 0
| FY26 | 2.5254 | 2.5254 | 2.5254 | 2.5254 | 2.5254 |  |  |  |  | FY26 | 64.3652 | 64.3652 | 64.3652 | 64.3652 | 64.3652 | 0 | 0 | 0
| FY27 | 4.6632 | 4.6632 | 4.6632 | 4.6632 | 4.6632 |  |  |  |  | FY27 | 118.8522 | 118.8522 | 118.8522 | 118.8522 | 118.8522 | 0 | 0 | 0
| FY28 | 2.1035 | 0.018719 | 0.0030174 | 0.0056057 | 0.0087898 |  |  |  |  | FY28 | 53.6123 | 0.47709 | 0.076904 | 0.14287 | 0.22403 | 0 | 0 | 0
| FY29 | 2.2678 | 0.02808 | 0.0039988 | 0.0067313 | 0.011297 |  |  |  |  | FY29 | 57.8004 | 0.71567 | 0.10192 | 0.17156 | 0.28793 | 0 | 0 | 0
| FY30 | 2.5783 | 0.043768 | 0.0065305 | 0.009704 | 0.016843 |  |  |  |  | FY30 | 65.714 | 1.1155 | 0.16644 | 0.24733 | 0.42929 | 0 | 0 | 0
| FY31 | 4.15 | 0.079645 | 0.015152 | 0.019512 | 0.032929 |  |  |  |  | FY31 | 105.7707 | 2.0299 | 0.38619 | 0.49731 | 0.83927 | 0 | 0 | 0
| FY32 | 6.4045 | 0.13384 | 0.069306 | 0.060825 | 0.051726 |  |  |  |  | FY32 | 163.2322 | 3.4111 | 1.7664 | 1.5502 | 1.3183 | 0 | 0 | 0
| FY33 | 10.4631 | 0.36189 | 0.38325 | 0.3058 | 0.084606 |  |  |  |  | FY33 | 266.6746 | 9.2234 | 9.7678 | 7.7941 | 2.1564 | 0 | 0 | 0
| FY34 | 11.1717 | 0.42975 | 0.47757 | 0.38324 | 0.090066 |  |  |  |  | FY34 | 284.7343 | 10.9531 | 12.172 | 9.7676 | 2.2955 | 0 | 0 | 0
| FY35 | 20.1112 | 1.4493 | 1.6379 | 1.3978 | 0.12482 |  |  |  |  | FY35 | 512.5762 | 36.9392 | 41.7465 | 35.6269 | 3.1814 | 0 | 0 | 0
| FY36 | 22.1651 | 1.1202 | 1.2632 | 1.0777 | 0.12273 |  |  |  |  | FY36 | 564.9227 | 28.5507 | 32.1964 | 27.4662 | 3.128 | 0 | 0 | 0
| FY37 | 27.141 | 2.2857 | 2.8116 | 2.3475 | 0.15589 |  |  |  |  | FY37 | 691.7436 | 58.2551 | 71.6582 | 59.83 | 3.9731 | 0 | 0 | 0
| FY38 | 51.6182 | 7.0335 | 7.7083 | 6.8612 | 0.29192 |  |  |  |  | FY38 | 1315.5962 | 179.264 | 196.4608 | 174.873 | 7.4403 | 0 | 0 | 0
| FY39 | 41.8648 | 4.7117 | 5.4729 | 4.7492 | 0.26155 |  |  |  |  | FY39 | 1067.0115 | 120.0868 | 139.4872 | 121.043 | 6.666 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | High Case Failure Rate | [9 empty] | High Case Failure Rate
|  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Augment MWTS-TGN with 19/4.75 AAC + Augment TGN-MFA with 19/4.75 AAC | Option 3: Augment MWTS-TGN with 19/4.75 AAC + New TGN-SLE 66kV line with 19/4.75 AAC | Option 4: Augment MWTS-TGN with 19/4.75 AAC + New Switching Station at Winnindoo (WISS) + Augment TGN-WISS with 19/4.75 AAC + New line WISS-SLE with 19/4.75 AAC | Option 5: Augment MWTS-TGN with 19/4.75 AAC + construct 30MW/150MWh BESS at BDSS | Option 6: | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 1.1689 | 1.1689 | 1.1689 | 1.1689 | 1.1689 |  |  |  | Total EUE (MWh) | FY25 | 29.7929 | 29.7929 | 29.7929 | 29.7929 | 29.7929 | 0 | 0 | 0
| FY26 | 2.7468 | 2.7468 | 2.7468 | 2.7468 | 2.7468 |  |  |  |  | FY26 | 70.0083 | 70.0083 | 70.0083 | 70.0083 | 70.0083 | 0 | 0 | 0
| FY27 | 5.0069 | 5.0069 | 5.0069 | 5.0069 | 5.0069 |  |  |  |  | FY27 | 127.6106 | 127.6106 | 127.6106 | 127.6106 | 127.6106 | 0 | 0 | 0
| FY28 | 2.6191 | 0.056157 | 0.0090521 | 0.016817 | 0.02637 |  |  |  |  | FY28 | 66.7543 | 1.4313 | 0.23071 | 0.42862 | 0.67208 | 0 | 0 | 0
| FY29 | 2.9116 | 0.08424 | 0.011996 | 0.020194 | 0.033891 |  |  |  |  | FY29 | 74.2086 | 2.147 | 0.30575 | 0.51468 | 0.86378 | 0 | 0 | 0
| FY30 | 3.4015 | 0.1313 | 0.019592 | 0.029112 | 0.05053 |  |  |  |  | FY30 | 86.6946 | 3.3466 | 0.49933 | 0.74198 | 1.2879 | 0 | 0 | 0
| FY31 | 5.328 | 0.23894 | 0.04544 | 0.058536 | 0.098788 |  |  |  |  | FY31 | 135.7941 | 6.0898 | 1.1581 | 1.4919 | 2.5178 | 0 | 0 | 0
| FY32 | 7.8888 | 0.36529 | 0.12299 | 0.12491 | 0.15518 |  |  |  |  | FY32 | 201.0624 | 9.3102 | 3.1348 | 3.1837 | 3.955 | 0 | 0 | 0
| FY33 | 12.3699 | 0.71 | 0.48123 | 0.41824 | 0.25382 |  |  |  |  | FY33 | 315.2714 | 18.0958 | 12.2651 | 10.6598 | 6.4691 | 0 | 0 | 0
| FY34 | 13.1377 | 0.79608 | 0.58331 | 0.50396 | 0.2702 |  |  |  |  | FY34 | 334.841 | 20.2898 | 14.8668 | 12.8445 | 6.8866 | 0 | 0 | 0
| FY35 | 22.4288 | 1.9212 | 1.7965 | 1.5766 | 0.37447 |  |  |  |  | FY35 | 571.6438 | 48.9663 | 45.7885 | 40.1826 | 9.5441 | 0 | 0 | 0
| FY36 | 24.5174 | 1.5819 | 1.4184 | 1.2528 | 0.36819 |  |  |  |  | FY36 | 624.8775 | 40.3186 | 36.1501 | 31.9307 | 9.384 | 0 | 0 | 0
| FY37 | 29.7433 | 2.8485 | 3.0149 | 2.5753 | 0.46411 |  |  |  |  | FY37 | 758.0698 | 72.6001 | 76.8406 | 65.6363 | 11.8289 | 0 | 0 | 0
| FY38 | 54.6888 | 7.7498 | 8.0065 | 7.1909 | 0.71118 |  |  |  |  | FY38 | 1393.8572 | 197.5196 | 204.0627 | 183.2758 | 18.1259 | 0 | 0 | 0
| FY39 | 44.779 | 5.3689 | 5.7332 | 5.0384 | 0.63791 |  |  |  |  | FY39 | 1141.2866 | 136.8366 | 146.1217 | 128.4147 | 16.2585 | 0 | 0 | 0
| Residual | [9 empty] | Residual