## Global Inputs
Please close all other excel spreadsheets (including reopening this one) before running any macros contained in it
Topology change # | Description | Uptake year
0 | BAU
1 | Post-BVE | 2027
2 | Post-WOL | 2028
3
4
EAR Loop | SMTS |  | PoE Weighting
Discount rate | 5.56% |  | P50 | 70%
Asset life | 45 | Years | P10 | 30%
First year of analysis | 2025 | Year
Line Segments for analysis (include new lines as well) | Length (km)
KMS-BVE | 13.273
DRN-KLO | 23.95
SMTS-BVE | 44.967
SMTS-DRN 1 | 7.75
SMTS-DRN 2 | 7.75
SMTS-KMS | 58.24
SMTS-WOL | 11.65
WLT-BUS | 47.17
BVT-BUS | 46.52
WLT-BVT | 72.02
KMS-WOL | 35.89
KLO-WOL | 13.85
ZSS connected to Loop
drn
klk
klo
kms
mdi
ruba
smr
bve
wlt
Ave no. of outages per year | 1
Ave. no. of outages per km line length per year | 0.062828
Ave. outage duration (hr) | 1
Ave. voltage collapse duration (hr) | 1
Sensitivities | Base | Low | High
Demand Forecasts | 100% | 90% | 110%
Failure Rate | 100% | 50% | 150%
Project Details | 6
Option 1: Do Nothing
Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor
Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor
Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor
Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor
Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor
Option 7:
Option 8:
|  | Summer | Winter
Gross Vs Net Load for LDC | Gross Load | 1.33 | 1.13
|  | Summer | Winter
Gross Load |  | 1.33 | 1.13
Net Load |  | 1 | 1

## VCR Calculation
| 1 |  |  |  | Sensitivity value | 1
| AER Rates (2024) |  |  |  |  | Values used in analysis
Commercial | 34.39 |  |  |  |  | 34.39
Agricultural | 22.25 |  |  |  |  | 22.25
Industrial | 33.49 |  |  |  |  | 33.49
Residential | 49.23 |  |  |  |  | 49.23
Customer consumption data (kWh) by ZSS | [7 empty] | Assumed as KLO | Assumed as EPG
ZSS | drn | klk | klo | kms | mdi | ruba | smr | bve | wlt | 0 | 0 | 0 | EAR Loop | epg
COMMERCIAL | 50857813.2378 | 4511737.2575 | 39497133.0224 | 20193836.4322 | 200221.43 | 14722134.2734 | 49198773.4269 | 39497133.0224 | 20193836.4322 |  |  |  | 238872618.5347 | 20193836.4322
Agricultural | 16976721.4575 | 2922299.1532 | 876026.299 | 1845616.8665 | 153288.2952 | 7526475.5671 | 11483701.5568 | 876026.299 | 777639.91 |  |  |  | 43437795.4043 | 777639.91
INDUSTRIAL | 7976446.4466 | 101186.97 | 1076076.6106 | 4730506.41 | 16.0426 | 1216874.5499 | 46376919.8957 | 1076076.6106 | 14221065.1 |  |  |  | 76775168.6361 | 14221065.1
LIGHT | 659832.35 | 0 | 5259379.5 | 547479.19 | 0 | 247422.69 | 147474.96 | 5259379.5 | 0 |  |  |  | 12120968.19 | 0
RESIDENTIAL | 147184205.708 | 16157381.1115 | 75660655.1717 | 33788154.3753 | 176577.17 | 23148949.6778 | 51497167.0633 | 75660655.1717 | 113320328.64 |  |  |  | 536594074.0893 | 113320328.64
Grand Total | 223655019.1999 | 23692604.4922 | 122369270.6038 | 61105593.2739 | 530102.9378 | 46861856.7582 | 158704036.9026 | 122369270.6038 | 148512870.0822 | 0 | 0 | 0 | 907800624.8544 | 148512870.0822
%Utilisation by segment
Commercial | 22.74% | 19.04% | 32.28% | 33.05% | 37.77% | 31.42% | 31% | 32.28% | 13.6% | #DIV/0! | #DIV/0! | #DIV/0! | 26.31%
Agricultural | 7.591% | 12.33% | 0.7159% | 3.02% | 28.92% | 16.06% | 7.236% | 0.7159% | 0.5236% | #DIV/0! | #DIV/0! | #DIV/0! | 4.785%
Industrial | 3.566% | 0.4271% | 0.8794% | 7.742% | 0.003026% | 2.597% | 29.22% | 0.8794% | 9.576% | #DIV/0! | #DIV/0! | #DIV/0! | 8.457%
Residential | 66.1% | 68.2% | 66.13% | 56.19% | 33.31% | 49.93% | 32.54% | 66.13% | 76.3% | #DIV/0! | #DIV/0! | #DIV/0! | 60.44%
VCR by segment | EAR Loop
Commercial | 9.0492
Agricultural | 1.0647
Industrial | 2.8323
Residential | 29.7568
Loop VCR | 42.7029

## Output for AusNet NPV Model
$k to $M | 0.001 | [8 empty] | $M to MWh | 23.4176
|  | Base Case Demand | [9 empty] | Base Case Demand
|  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Options sheet name: | Global Inputs
| FY26 | 1.282e-05 | 1.282e-05 | 1.282e-05 | 1.282e-05 | 1.282e-05 | 1.282e-05 |  |  |  | FY26 | 0.00030021 | 0.00030021 | 0.00030021 | 0.00030021 | 0.00030021 | 0.00030021 | 0 | 0 | VCR sheet name: | VCR Calculation
| FY27 | 0.018527 | 3.4821e-06 | 4.9163e-06 | 2.5234e-06 | 0.07484 | 4.4389e-06 |  |  |  | FY27 | 0.43385 | 8.1542e-05 | 0.00011513 | 5.9093e-05 | 1.7526 | 0.00010395 | 0 | 0 | EUSE sheet name: | EUSE Calculator
| FY28 | 2.6758 | 0.014926 | 0.014932 | 2.4168e-06 | 0.078833 | 2.1806e-05 |  |  |  | FY28 | 62.6616 | 0.34952 | 0.34968 | 5.6595e-05 | 1.8461 | 0.00051065 | 0 | 0 | File Prefix: | EAR_SMTS_OPT
| FY29 | 9.9153 | 0.031325 | 0.031399 | 0.00026334 | 0.23298 | 0.00050734 |  |  |  | FY29 | 232.1922 | 0.73356 | 0.7353 | 0.0061667 | 5.4559 | 0.011881 | 0 | 0 |  |  | File reference | EUE Range reference | Base EUE range ref | Low EUE range ref | High EUE range ref
| FY30 | 22.6836 | 0.049245 | 0.049312 | 0.0012549 | 0.89483 | 0.0017872 |  |  |  | FY30 | 531.1952 | 1.1532 | 1.1548 | 0.029387 | 20.9548 | 0.041852 | 0 | 0 | 1 | Option1 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY31 | 45.7879 | 0.0828 | 0.082279 | 0.0036341 | 3.387 | 0.0048552 |  |  |  | FY31 | 1072.2427 | 1.939 | 1.9268 | 0.085101 | 79.3145 | 0.1137 | 0 | 0 | 2 | Option2 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY32 | 85.8533 | 0.17148 | 0.16946 | 0.009702 | 8.9885 | 0.02277 |  |  |  | FY32 | 2010.478 | 4.0156 | 3.9684 | 0.2272 | 210.4892 | 0.53321 | 0 | 0 | 3 | Option3 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY33 | 148.8037 | 0.41488 | 0.48423 | 0.06701 | 23.7673 | 0.38949 |  |  |  | FY33 | 3484.6236 | 9.7155 | 11.3394 | 1.5692 | 556.5735 | 9.121 | 0 | 0 | 4 | Option4 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY34 | 238.3427 | 1.0535 | 1.6319 | 0.44627 | 48.4899 | 2.4259 |  |  |  | FY34 | 5581.4121 | 24.6696 | 38.2158 | 10.4506 | 1135.5167 | 56.8088 | 0 | 0 | 5 | Option5 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY35 | 422.5048 | 3.7893 | 5.4523 | 2.809 | 101.8713 | 7.9164 |  |  |  | FY35 | 9894.0439 | 88.7359 | 127.6806 | 65.7794 | 2385.5802 | 185.3823 | 0 | 0 | 6 | Option6 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY36 | 722.3466 | 9.1347 | 15.3281 | 7.7487 | 205.1978 | 26.023 |  |  |  | FY36 | 16915.6145 | 213.9122 | 358.9475 | 181.4551 | 4805.2378 | 609.397 | 0 | 0 | 7 | Option7 filename: | EAR_SMTS_OPT7.xlsx | '[EAR_SMTS_OPT7.xlsx]EUSE Calculator'!$F$18:$T$18
| FY37 | 1152.7553 | 20.2703 | 38.8356 | 18.4027 | 372.9668 | 69.5954 |  |  |  | FY37 | 26994.7483 | 474.6819 | 909.4353 | 430.9471 | 8733.9837 | 1629.7565 | 0 | 0 | 8 | Option8 filename: | EAR_SMTS_OPT8.xlsx | '[EAR_SMTS_OPT8.xlsx]EUSE Calculator'!$F$18:$T$18
| FY38 | 2103.7027 | 53.0737 | 150.18 | 49.8915 | 807.9913 | 244.2519 |  |  |  | FY38 | 49263.6416 | 1242.8592 | 3516.8522 | 1168.3389 | 18921.2058 | 5719.7891 | 0 | 0
| FY39 | 3262.0447 | 129.8672 | 375.3872 | 123.9827 | 1385.4121 | 544.9388 |  |  |  | FY39 | 76389.2177 | 3041.1774 | 8790.6633 | 2903.3769 | 32443.0085 | 12761.1522 | 0 | 0
| Residual | [9 empty] | Residual
|  | Low Case Demand | [9 empty] | Low Case Demand
|  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | FY26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY27 | 0.0053465 | 0 | 0 | 0 | 0.023265 | 0 |  |  |  | FY27 | 0.1252 | 0 | 0 | 0 | 0.54481 | 0 | 0 | 0
| FY28 | 0.11397 | 0.0036995 | 0.0036995 | 0 | 0.036023 | 0 |  |  |  | FY28 | 2.669 | 0.086633 | 0.086633 | 0 | 0.84357 | 0 | 0 | 0
| FY29 | 1.518 | 0.010926 | 0.010926 | 0 | 0.065431 | 3.7409e-06 |  |  |  | FY29 | 35.5489 | 0.25587 | 0.25587 | 0 | 1.5322 | 8.7602e-05 | 0 | 0
| FY30 | 4.1967 | 0.019611 | 0.019619 | 3.0354e-05 | 0.10048 | 6.2088e-05 |  |  |  | FY30 | 98.2764 | 0.45925 | 0.45943 | 0.00071083 | 2.3529 | 0.001454 | 0 | 0
| FY31 | 10.3393 | 0.032519 | 0.032517 | 0.00028253 | 0.26153 | 0.0005355 |  |  |  | FY31 | 242.121 | 0.76153 | 0.76148 | 0.0066163 | 6.1245 | 0.01254 | 0 | 0
| FY32 | 25.7837 | 0.058864 | 0.058341 | 0.0014846 | 1.1895 | 0.0021083 |  |  |  | FY32 | 603.7911 | 1.3785 | 1.3662 | 0.034766 | 27.8551 | 0.049371 | 0 | 0
| FY33 | 55.0028 | 0.12397 | 0.12188 | 0.0046919 | 4.598 | 0.0076259 |  |  |  | FY33 | 1288.0338 | 2.9032 | 2.854 | 0.10987 | 107.6752 | 0.17858 | 0 | 0
| FY34 | 92.4995 | 0.23954 | 0.23675 | 0.011541 | 10.6801 | 0.070205 |  |  |  | FY34 | 2166.116 | 5.6095 | 5.5442 | 0.27026 | 250.1024 | 1.644 | 0 | 0
| FY35 | 156.9305 | 0.52025 | 0.5923 | 0.092772 | 25.2668 | 0.52998 |  |  |  | FY35 | 3674.9341 | 12.183 | 13.8701 | 2.1725 | 591.6884 | 12.4108 | 0 | 0
| FY36 | 263.6241 | 1.2649 | 1.9377 | 0.58153 | 54.4383 | 2.8606 |  |  |  | FY36 | 6173.4396 | 29.622 | 45.3755 | 13.618 | 1274.8142 | 66.9889 | 0 | 0
| FY37 | 429.2522 | 3.8801 | 5.5043 | 2.8871 | 104.2384 | 7.9101 |  |  |  | FY37 | 10052.0504 | 90.8624 | 128.8985 | 67.6095 | 2441.0113 | 185.2362 | 0 | 0
| FY38 | 828.8842 | 9.9311 | 18.6136 | 8.3907 | 239.6203 | 32.9734 |  |  |  | FY38 | 19410.4692 | 232.5616 | 435.8853 | 196.4892 | 5611.3296 | 772.1574 | 0 | 0
| FY39 | 1380.86 | 22.0143 | 62.0812 | 19.7614 | 472.1124 | 108.2051 |  |  |  | FY39 | 32336.4103 | 515.5223 | 1453.7916 | 462.7647 | 11055.7343 | 2533.9023 | 0 | 0
| Residual | [9 empty] | Residual
|  | High Case Demand | [9 empty] | High Case Demand
|  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 2.5821e-05 | 2.5821e-05 | 2.5821e-05 | 2.5821e-05 | 2.5821e-05 | 2.5821e-05 |  |  | Total EUE (MWh) | FY25 | 0.00060467 | 0.00060467 | 0.00060467 | 0.00060467 | 0.00060467 | 0.00060467 | 0 | 0
| FY26 | 0.00050838 | 0.00050838 | 0.00050838 | 0.00050838 | 0.00050838 | 0.00050838 |  |  |  | FY26 | 0.011905 | 0.011905 | 0.011905 | 0.011905 | 0.011905 | 0.011905 | 0 | 0
| FY27 | 0.067266 | 0.0002734 | 0.00027444 | 0.00012031 | 0.16042 | 0.00055604 |  |  |  | FY27 | 1.5752 | 0.0064024 | 0.0064267 | 0.0028174 | 3.7566 | 0.013021 | 0 | 0
| FY28 | 13.0552 | 0.036114 | 0.036228 | 0.00048744 | 0.29472 | 0.00081771 |  |  |  | FY28 | 305.7221 | 0.8457 | 0.84838 | 0.011415 | 6.9017 | 0.019149 | 0 | 0
| FY29 | 39.2072 | 0.06777 | 0.067869 | 0.0029523 | 2.6422 | 0.0039202 |  |  |  | FY29 | 918.1372 | 1.587 | 1.5893 | 0.069136 | 61.8746 | 0.091801 | 0 | 0
| FY30 | 71.1766 | 0.11118 | 0.11089 | 0.0070395 | 6.6184 | 0.0095161 |  |  |  | FY30 | 1666.7831 | 2.6035 | 2.5968 | 0.16485 | 154.9876 | 0.22285 | 0 | 0
| FY31 | 117.0832 | 0.21066 | 0.23695 | 0.016913 | 15.8089 | 0.14811 |  |  |  | FY31 | 2741.807 | 4.9331 | 5.5487 | 0.39606 | 370.2057 | 3.4685 | 0 | 0
| FY32 | 192.7087 | 0.58954 | 0.7987 | 0.1836 | 37.7784 | 1.2707 |  |  |  | FY32 | 4512.7719 | 13.8056 | 18.7035 | 4.2994 | 884.6779 | 29.7564 | 0 | 0
| FY33 | 338.4205 | 2.6191 | 3.8421 | 1.842 | 81.9459 | 5.5864 |  |  |  | FY33 | 7924.9911 | 61.3335 | 89.9727 | 43.1363 | 1918.9752 | 130.8206 | 0 | 0
| FY34 | 578.843 | 7.0667 | 10.1391 | 5.8711 | 156.8796 | 16.2692 |  |  |  | FY34 | 13555.1058 | 165.4848 | 237.4338 | 137.4862 | 3673.7425 | 380.9843 | 0 | 0
| FY35 | 1039.2093 | 16.5483 | 32.1122 | 14.7986 | 328.0638 | 57.3155 |  |  |  | FY35 | 24335.7755 | 387.521 | 751.9898 | 346.5483 | 7682.4637 | 1342.1903 | 0 | 0
| FY36 | 1696.3908 | 39.6657 | 97.933 | 37.0515 | 616.9942 | 162.4086 |  |  |  | FY36 | 39725.3794 | 928.8749 | 2293.3539 | 867.6567 | 14448.5153 | 3803.2172 | 0 | 0
| FY37 | 2570.8313 | 85.3698 | 223.2202 | 81.4216 | 1032.6663 | 343.653 |  |  |  | FY37 | 60202.667 | 1999.155 | 5227.2778 | 1906.6965 | 24182.5535 | 8047.5249 | 0 | 0
| FY38 | 4361.8044 | 232.4026 | 627.9408 | 223.5555 | 1940.0468 | 855.5336 |  |  |  | FY38 | 102142.9369 | 5442.3079 | 14704.8576 | 5235.1313 | 45431.2165 | 20034.5323 | 0 | 0
| FY39 | 6419.1331 | 507.7179 | 1237.2629 | 492.6277 | 2988.4568 | 1514.175 |  |  |  | FY39 | 150320.6114 | 11889.5286 | 28973.7118 | 11536.1517 | 69982.4475 | 35458.3248 | 0 | 0
| Residual | [9 empty] | Residual

## Output for AusNet NPV Model_PoF
$k to $M | 0.001 | [8 empty] | $M to MWh | 23.4176
|  | Base Case Failure Rate | [9 empty] | Base Case Failure Rate
|  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Options sheet name: | Global Inputs
| FY26 | 1.282e-05 | 1.282e-05 | 1.282e-05 | 1.282e-05 | 1.282e-05 | 1.282e-05 |  |  |  | FY26 | 0.00030021 | 0.00030021 | 0.00030021 | 0.00030021 | 0.00030021 | 0.00030021 | 0 | 0 | VCR sheet name: | VCR Calculation
| FY27 | 0.018527 | 3.4821e-06 | 4.9163e-06 | 2.5234e-06 | 0.07484 | 4.4389e-06 |  |  |  | FY27 | 0.43385 | 8.1542e-05 | 0.00011513 | 5.9093e-05 | 1.7526 | 0.00010395 | 0 | 0 | EUSE sheet name (Base PoF): | EUSE Calculator_PoF
| FY28 | 2.6758 | 0.014926 | 0.014932 | 2.4168e-06 | 0.078833 | 2.1806e-05 |  |  |  | FY28 | 62.6616 | 0.34952 | 0.34968 | 5.6595e-05 | 1.8461 | 0.00051065 | 0 | 0 | File Prefix: | EAR_SMTS_OPT
| FY29 | 9.9153 | 0.031325 | 0.031399 | 0.00026334 | 0.23298 | 0.00050734 |  |  |  | FY29 | 232.1922 | 0.73356 | 0.7353 | 0.0061667 | 5.4559 | 0.011881 | 0 | 0 |  |  | File reference | EUE Range reference | Base EUE range ref | Low EUE range ref | High EUE range ref
| FY30 | 22.6836 | 0.049245 | 0.049312 | 0.0012549 | 0.89483 | 0.0017872 |  |  |  | FY30 | 531.1952 | 1.1532 | 1.1548 | 0.029387 | 20.9548 | 0.041852 | 0 | 0 | 1 | Option1 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY31 | 45.7879 | 0.0828 | 0.082279 | 0.0036341 | 3.387 | 0.0048552 |  |  |  | FY31 | 1072.2427 | 1.939 | 1.9268 | 0.085101 | 79.3145 | 0.1137 | 0 | 0 | 2 | Option2 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY32 | 85.8533 | 0.17148 | 0.16946 | 0.009702 | 8.9885 | 0.02277 |  |  |  | FY32 | 2010.478 | 4.0156 | 3.9684 | 0.2272 | 210.4892 | 0.53321 | 0 | 0 | 3 | Option3 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY33 | 148.8037 | 0.41488 | 0.48423 | 0.06701 | 23.7673 | 0.38949 |  |  |  | FY33 | 3484.6236 | 9.7155 | 11.3394 | 1.5692 | 556.5735 | 9.121 | 0 | 0 | 4 | Option4 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY34 | 238.3427 | 1.0535 | 1.6319 | 0.44627 | 48.4899 | 2.4259 |  |  |  | FY34 | 5581.4121 | 24.6696 | 38.2158 | 10.4506 | 1135.5167 | 56.8088 | 0 | 0 | 5 | Option5 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY35 | 422.5048 | 3.7893 | 5.4523 | 2.809 | 101.8713 | 7.9164 |  |  |  | FY35 | 9894.0439 | 88.7359 | 127.6806 | 65.7794 | 2385.5802 | 185.3823 | 0 | 0 | 6 | Option6 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY36 | 722.3466 | 9.1347 | 15.3281 | 7.7487 | 205.1978 | 26.023 |  |  |  | FY36 | 16915.6145 | 213.9122 | 358.9475 | 181.4551 | 4805.2378 | 609.397 | 0 | 0 | 7 | Option7 filename: | EAR_SMTS_OPT7.xlsx | '[EAR_SMTS_OPT7.xlsx]EUSE Calculator_PoF'!$F$18:$T$18
| FY37 | 1152.7553 | 20.2703 | 38.8356 | 18.4027 | 372.9668 | 69.5954 |  |  |  | FY37 | 26994.7483 | 474.6819 | 909.4353 | 430.9471 | 8733.9837 | 1629.7565 | 0 | 0 | 8 | Option8 filename: | EAR_SMTS_OPT8.xlsx | '[EAR_SMTS_OPT8.xlsx]EUSE Calculator_PoF'!$F$18:$T$18
| FY38 | 2103.7027 | 53.0737 | 150.18 | 49.8915 | 807.9913 | 244.2519 |  |  |  | FY38 | 49263.6416 | 1242.8592 | 3516.8522 | 1168.3389 | 18921.2058 | 5719.7891 | 0 | 0
| FY39 | 3262.0447 | 129.8672 | 375.3872 | 123.9827 | 1385.4121 | 544.9388 |  |  |  | FY39 | 76389.2177 | 3041.1774 | 8790.6633 | 2903.3769 | 32443.0085 | 12761.1522 | 0 | 0
| Residual | [9 empty] | Residual
|  | Low Case Failure Rate | [9 empty] | Low Case Failure Rate
|  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 6.41e-06 | 6.41e-06 | 6.41e-06 | 6.41e-06 | 6.41e-06 | 6.41e-06 |  |  |  | FY26 | 0.00015011 | 0.00015011 | 0.00015011 | 0.00015011 | 0.00015011 | 0.00015011 | 0 | 0
| FY27 | 0.0092634 | 1.741e-06 | 2.4581e-06 | 1.2617e-06 | 0.03742 | 2.2194e-06 |  |  |  | FY27 | 0.21693 | 4.0771e-05 | 5.7564e-05 | 2.9546e-05 | 0.87628 | 5.1974e-05 | 0 | 0
| FY28 | 2.635 | 0.0074628 | 0.0074662 | 1.2084e-06 | 0.039417 | 1.0903e-05 |  |  |  | FY28 | 61.7049 | 0.17476 | 0.17484 | 2.8298e-05 | 0.92304 | 0.00025532 | 0 | 0
| FY29 | 9.8369 | 0.015663 | 0.0157 | 0.00013167 | 0.1598 | 0.00025367 |  |  |  | FY29 | 230.3564 | 0.36678 | 0.36765 | 0.0030833 | 3.7421 | 0.0059403 | 0 | 0
| FY30 | 22.5567 | 0.024623 | 0.024656 | 0.00062745 | 0.77468 | 0.0008936 |  |  |  | FY30 | 528.2234 | 0.5766 | 0.57739 | 0.014693 | 18.1412 | 0.020926 | 0 | 0
| FY31 | 45.5689 | 0.0414 | 0.041139 | 0.001817 | 3.1774 | 0.0024276 |  |  |  | FY31 | 1067.113 | 0.96949 | 0.96338 | 0.042551 | 74.4081 | 0.056848 | 0 | 0
| FY32 | 85.4396 | 0.085739 | 0.084731 | 0.004851 | 8.6063 | 0.014955 |  |  |  | FY32 | 2000.7885 | 2.0078 | 1.9842 | 0.1136 | 201.5378 | 0.35021 | 0 | 0
| FY33 | 148.0303 | 0.22721 | 0.29643 | 0.053271 | 23.0945 | 0.36127 |  |  |  | FY33 | 3466.5116 | 5.3206 | 6.9416 | 1.2475 | 540.8186 | 8.46 | 0 | 0
| FY34 | 237.0951 | 0.71576 | 1.2871 | 0.41216 | 47.4442 | 2.3538 |  |  |  | FY34 | 5552.1945 | 16.7613 | 30.1407 | 9.6518 | 1111.0295 | 55.1193 | 0 | 0
| FY35 | 420.5452 | 3.2083 | 4.8457 | 2.7181 | 100.2599 | 7.751 |  |  |  | FY35 | 9848.153 | 75.1301 | 113.4747 | 63.6518 | 2347.8459 | 181.5096 | 0 | 0
| FY36 | 719.547 | 8.2442 | 14.3823 | 7.5507 | 202.9124 | 25.7205 |  |  |  | FY36 | 16850.0537 | 193.0585 | 336.7984 | 176.8187 | 4751.72 | 602.3121 | 0 | 0
| FY37 | 1148.9474 | 18.9892 | 37.4582 | 18.0433 | 369.8733 | 69.1111 |  |  |  | FY37 | 26905.5751 | 444.6814 | 877.1811 | 422.531 | 8661.5396 | 1618.4141 | 0 | 0
| FY38 | 2098.1195 | 51.0236 | 147.9415 | 49.1381 | 803.5098 | 243.3838 |  |  |  | FY38 | 49132.8956 | 1194.8487 | 3464.4325 | 1150.6957 | 18816.2611 | 5699.4611 | 0 | 0
| FY39 | 3254.6843 | 126.9871 | 372.2206 | 122.7519 | 1379.5489 | 543.6229 |  |  |  | FY39 | 76216.8548 | 2973.7307 | 8716.5093 | 2874.5537 | 32305.7072 | 12730.3369 | 0 | 0
| Residual | [9 empty] | Residual
|  | High Case Failure Rate | [9 empty] | High Case Failure Rate
|  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8: |  |  | Option 1: Do Nothing | Option 2: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 3: Reconductor SMTS-BVE Line with 19/4.75 AAC Conductor | Option 4: Reconductor SMTS-BVE and BVE-KMS Line with 37/3.75 AAC Conductor | Option 5: Reconductor BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 6: Reconductor SMTS-BVE and BVE-BVE-Tee Line with 37/3.75 AAC Conductor | Option 7: | Option 8:
Cost of EUE ($M) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 1.923e-05 | 1.923e-05 | 1.923e-05 | 1.923e-05 | 1.923e-05 | 1.923e-05 |  |  |  | FY26 | 0.00045032 | 0.00045032 | 0.00045032 | 0.00045032 | 0.00045032 | 0.00045032 | 0 | 0
| FY27 | 0.02779 | 5.2231e-06 | 7.3744e-06 | 3.7852e-06 | 0.11226 | 6.6583e-06 |  |  |  | FY27 | 0.65078 | 0.00012231 | 0.00017269 | 8.8639e-05 | 2.6289 | 0.00015592 | 0 | 0
| FY28 | 2.7167 | 0.022388 | 0.022398 | 3.6252e-06 | 0.11825 | 3.2709e-05 |  |  |  | FY28 | 63.6183 | 0.52428 | 0.52452 | 8.4893e-05 | 2.7691 | 0.00076597 | 0 | 0
| FY29 | 9.9937 | 0.046988 | 0.047099 | 0.000395 | 0.30617 | 0.00076101 |  |  |  | FY29 | 234.0281 | 1.1003 | 1.1029 | 0.00925 | 7.1697 | 0.017821 | 0 | 0
| FY30 | 22.8105 | 0.073868 | 0.073968 | 0.0018823 | 1.015 | 0.0026808 |  |  |  | FY30 | 534.1671 | 1.7298 | 1.7322 | 0.04408 | 23.7684 | 0.062778 | 0 | 0
| FY31 | 46.007 | 0.1242 | 0.12342 | 0.0054511 | 3.5965 | 0.0072827 |  |  |  | FY31 | 1077.3724 | 2.9085 | 2.8902 | 0.12765 | 84.2208 | 0.17054 | 0 | 0
| FY32 | 86.2671 | 0.25722 | 0.25419 | 0.014553 | 9.3708 | 0.030585 |  |  |  | FY32 | 2020.1675 | 6.0234 | 5.9526 | 0.3408 | 219.4406 | 0.71622 | 0 | 0
| FY33 | 149.5771 | 0.60255 | 0.67203 | 0.080749 | 24.4401 | 0.41772 |  |  |  | FY33 | 3502.7356 | 14.1104 | 15.7372 | 1.891 | 572.3284 | 9.7819 | 0 | 0
| FY34 | 239.5904 | 1.3912 | 1.9768 | 0.48038 | 49.5356 | 2.4981 |  |  |  | FY34 | 5610.6298 | 32.578 | 46.2909 | 11.2494 | 1160.004 | 58.4983 | 0 | 0
| FY35 | 424.4645 | 4.3703 | 6.059 | 2.8998 | 103.4827 | 8.0817 |  |  |  | FY35 | 9939.9349 | 102.3417 | 141.8865 | 67.907 | 2423.3145 | 189.255 | 0 | 0
| FY36 | 725.1462 | 10.0252 | 16.2739 | 7.9467 | 207.4832 | 26.3256 |  |  |  | FY36 | 16981.1753 | 234.7659 | 381.0965 | 186.0915 | 4858.7556 | 616.4819 | 0 | 0
| FY37 | 1156.5633 | 21.5514 | 40.2129 | 18.7621 | 376.0604 | 70.0798 |  |  |  | FY37 | 27083.9216 | 504.6824 | 941.6896 | 439.3632 | 8806.4278 | 1641.0989 | 0 | 0
| FY38 | 2109.2859 | 55.1239 | 152.4184 | 50.6449 | 812.4727 | 245.1199 |  |  |  | FY38 | 49394.3877 | 1290.8696 | 3569.272 | 1185.9821 | 19026.1506 | 5740.1171 | 0 | 0
| FY39 | 3269.4051 | 132.7474 | 378.5538 | 125.2136 | 1391.2752 | 546.2547 |  |  |  | FY39 | 76561.5807 | 3108.6241 | 8864.8174 | 2932.2 | 32580.3097 | 12791.9675 | 0 | 0
| Residual | [9 empty] | Residual