## Global Inputs
Please close all other excel spreadsheets (including reopening this one) before running any macros contained in it
Topology change # | Description | Uptake year
0 | BAU
1 | Post-BVE | 2027
2 | DRN 3rdTx year | 2028
3
4
EAR Loop | SMTS |  | PoE Weighting
Discount rate | 5.56% |  | P50 | 70%
Asset life | 45 | Years | P10 | 30%
First year of analysis | 2025 | Year
Line Segments for analysis (include new lines as well) | Length (km)
KMS-BVE | 13.273
DRN-KLO | 23.95
SMTS-BVE | 44.967
SMTS-DRN 1 | 7.75
SMTS-DRN 2 | 7.75
WLT-BUS | 47.17
ZSS connected to Loop
drn
klk
klo
kms
mdi
ruba
smr
bve
Ave no. of outages per year | 1
Ave. no. of outages per km line length per year | 0.062828
Ave. outage duration (hr) | 1
Ave. voltage collapse duration (hr) | 1
Sensitivities | Base | Low | High
Demand Forecasts | 100% | 90% | 110%
Failure Rate | 100% | 50% | 150%
Project Details | 2
Option 0: Do Nothing
Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor
Option 2:
Option 3:
Option 4:
Option 5:
Option 6:
Option 7:
|  | Summer | Winter
Gross Vs Net Load for LDC | Gross Load | 1.33 | 1.13
|  | Summer | Winter
Gross Load |  | 1.33 | 1.13
Net Load |  | 1 | 1

## VCR Calculation
| 1 |  |  |  | Sensitivity value | 1
| AER Rates (2024) |  |  |  |  | Values used in analysis
Commercial | 34.39 |  |  |  |  | 34.39
Agricultural | 22.25 |  |  |  |  | 22.25
Industrial | 33.49 |  |  |  |  | 33.49
Residential | 49.23 |  |  |  |  | 49.23
Customer consumption data (kWh) by ZSS | [7 empty] | Assumed as KLO | Assumed as EPG
ZSS | drn | klk | klo | kms | mdi | ruba | smr | bve | 0 | 0 | 0 | 0 | EAR Loop | epg
COMMERCIAL | 50857813.2378 | 4511737.2575 | 39497133.0224 | 20193836.4322 | 200221.43 | 14722134.2734 | 49198773.4269 | 39497133.0224 |  |  |  |  | 218678782.1026 | 20193836.4322
Agricultural | 16976721.4575 | 2922299.1532 | 876026.299 | 1845616.8665 | 153288.2952 | 7526475.5671 | 11483701.5568 | 876026.299 |  |  |  |  | 42660155.4943 | 777639.91
INDUSTRIAL | 7976446.4466 | 101186.97 | 1076076.6106 | 4730506.41 | 16.0426 | 1216874.5499 | 46376919.8957 | 1076076.6106 |  |  |  |  | 62554103.5361 | 14221065.1
LIGHT | 659832.35 | 0 | 5259379.5 | 547479.19 | 0 | 247422.69 | 147474.96 | 5259379.5 |  |  |  |  | 12120968.19 | 0
RESIDENTIAL | 147184205.708 | 16157381.1115 | 75660655.1717 | 33788154.3753 | 176577.17 | 23148949.6778 | 51497167.0633 | 75660655.1717 |  |  |  |  | 423273745.4493 | 113320328.64
Grand Total | 223655019.1999 | 23692604.4922 | 122369270.6038 | 61105593.2739 | 530102.9378 | 46861856.7582 | 158704036.9026 | 122369270.6038 | 0 | 0 | 0 | 0 | 759287754.7722 | 148512870.0822
%Utilisation by segment
Commercial | 22.74% | 19.04% | 32.28% | 33.05% | 37.77% | 31.42% | 31% | 32.28% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 28.8%
Agricultural | 7.591% | 12.33% | 0.7159% | 3.02% | 28.92% | 16.06% | 7.236% | 0.7159% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 5.618%
Industrial | 3.566% | 0.4271% | 0.8794% | 7.742% | 0.003026% | 2.597% | 29.22% | 0.8794% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 8.239%
Residential | 66.1% | 68.2% | 66.13% | 56.19% | 33.31% | 49.93% | 32.54% | 66.13% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 57.34%
VCR by segment | EAR Loop
Commercial | 9.9045
Agricultural | 1.2501
Industrial | 2.7591
Residential | 28.2297
Loop VCR | 42.1434

## Output for AusNet NPV Model
$k to $M | 0.001 | [8 empty] | $M to MWh | 23.7285
|  | Base Case Demand | [9 empty] | Base Case Demand
|  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Options sheet name: | Global Inputs
| FY26 | 1.2652e-05 | 1.2652e-05 | [7 empty] | FY26 | 0.00030021 | 0.00030021 | 0 | 0 | 0 | 0 | 0 | 0 | VCR sheet name: | VCR Calculation
| FY27 | 0.0033766 | 1.9672e-05 | [7 empty] | FY27 | 0.080122 | 0.00046678 | 0 | 0 | 0 | 0 | 0 | 0 | EUSE sheet name: | EUSE Calculator
| FY28 | 0.038013 | 0.001423 | [7 empty] | FY28 | 0.90198 | 0.033766 | 0 | 0 | 0 | 0 | 0 | 0 | File Prefix: | EAR_SMTS_OPT
| FY29 | 0.76904 | 0.0051023 | [7 empty] | FY29 | 18.2481 | 0.12107 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | File reference | EUE Range reference | Base EUE range ref | Low EUE range ref | High EUE range ref
| FY30 | 2.8386 | 0.011137 | [7 empty] | FY30 | 67.3562 | 0.26427 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Option1 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY31 | 7.533 | 0.022619 | [7 empty] | FY31 | 178.7475 | 0.5367 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | Option2 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY32 | 19.5867 | 0.052281 | [7 empty] | FY32 | 464.7623 | 1.2405 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | Option3 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY33 | 45.1303 | 0.17594 | [7 empty] | FY33 | 1070.8743 | 4.1749 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | Option4 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY34 | 80.2238 | 0.66938 | [7 empty] | FY34 | 1903.5906 | 15.8833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | Option5 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY35 | 139.5181 | 3.1902 | [7 empty] | FY35 | 3310.5556 | 75.6998 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | Option6 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY36 | 236.8517 | 8.2804 | [7 empty] | FY36 | 5620.1361 | 196.4804 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | Option7 filename: | EAR_SMTS_OPT7.xlsx | '[EAR_SMTS_OPT7.xlsx]EUSE Calculator'!$F$18:$T$18
| FY37 | 386.9422 | 18.9576 | [7 empty] | FY37 | 9181.5603 | 449.8359 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | Option8 filename: | EAR_SMTS_OPT8.xlsx | '[EAR_SMTS_OPT8.xlsx]EUSE Calculator'!$F$18:$T$18
| FY38 | 786.0662 | 43.9651 | [7 empty] | FY38 | 18652.1758 | 1043.2271 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 1389.7422 | 90.849 | [7 empty] | FY39 | 32976.5052 | 2155.7122 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | Low Case Demand | [9 empty] | Low Case Demand
|  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 0 | 0 | [7 empty] | FY26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY27 | 0.0010167 | 0 | [7 empty] | FY27 | 0.024126 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY28 | 0.0030933 | 6.606e-05 | [7 empty] | FY28 | 0.073401 | 0.0015675 | 0 | 0 | 0 | 0 | 0 | 0
| FY29 | 0.0070951 | 0.00086805 | [7 empty] | FY29 | 0.16836 | 0.020598 | 0 | 0 | 0 | 0 | 0 | 0
| FY30 | 0.09849 | 0.0021765 | [7 empty] | FY30 | 2.337 | 0.051646 | 0 | 0 | 0 | 0 | 0 | 0
| FY31 | 0.81633 | 0.0053124 | [7 empty] | FY31 | 19.3703 | 0.12606 | 0 | 0 | 0 | 0 | 0 | 0
| FY32 | 3.3204 | 0.013044 | [7 empty] | FY32 | 78.7878 | 0.30951 | 0 | 0 | 0 | 0 | 0 | 0
| FY33 | 9.68 | 0.033379 | [7 empty] | FY33 | 229.6916 | 0.79202 | 0 | 0 | 0 | 0 | 0 | 0
| FY34 | 22.0697 | 0.074998 | [7 empty] | FY34 | 523.6801 | 1.7796 | 0 | 0 | 0 | 0 | 0 | 0
| FY35 | 47.1208 | 0.23075 | [7 empty] | FY35 | 1118.1067 | 5.4753 | 0 | 0 | 0 | 0 | 0 | 0
| FY36 | 86.1912 | 0.83633 | [7 empty] | FY36 | 2045.1877 | 19.8449 | 0 | 0 | 0 | 0 | 0 | 0
| FY37 | 144.0604 | 3.2721 | [7 empty] | FY37 | 3418.3375 | 77.6425 | 0 | 0 | 0 | 0 | 0 | 0
| FY38 | 260.4926 | 8.9235 | [7 empty] | FY38 | 6181.1002 | 211.7409 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 463.9637 | 18.9493 | [7 empty] | FY39 | 11009.1659 | 449.6382 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | High Case Demand | [9 empty] | High Case Demand
|  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 2.5483e-05 | 2.5483e-05 | [6 empty] | Total EUE (MWh) | FY25 | 0.00060467 | 0.00060467 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 0.00050171 | 0.00050171 | [7 empty] | FY26 | 0.011905 | 0.011905 | 0 | 0 | 0 | 0 | 0 | 0
| FY27 | 0.039434 | 0.00058358 | [7 empty] | FY27 | 0.93571 | 0.013848 | 0 | 0 | 0 | 0 | 0 | 0
| FY28 | 1.2764 | 0.0066373 | [7 empty] | FY28 | 30.2876 | 0.15749 | 0 | 0 | 0 | 0 | 0 | 0
| FY29 | 6.2149 | 0.018677 | [7 empty] | FY29 | 147.4692 | 0.44317 | 0 | 0 | 0 | 0 | 0 | 0
| FY30 | 14.5097 | 0.03443 | [7 empty] | FY30 | 344.2944 | 0.81696 | 0 | 0 | 0 | 0 | 0 | 0
| FY31 | 32.4413 | 0.069453 | [7 empty] | FY31 | 769.7847 | 1.648 | 0 | 0 | 0 | 0 | 0 | 0
| FY32 | 66.7857 | 0.31017 | [7 empty] | FY32 | 1584.7247 | 7.36 | 0 | 0 | 0 | 0 | 0 | 0
| FY33 | 121.1242 | 2.1518 | [7 empty] | FY33 | 2874.0968 | 51.0594 | 0 | 0 | 0 | 0 | 0 | 0
| FY34 | 195.0959 | 6.3358 | [7 empty] | FY34 | 4629.3351 | 150.3382 | 0 | 0 | 0 | 0 | 0 | 0
| FY35 | 344.8434 | 15.2935 | [7 empty] | FY35 | 8182.6197 | 362.8914 | 0 | 0 | 0 | 0 | 0 | 0
| FY36 | 613.2436 | 35.145 | [7 empty] | FY36 | 14551.3536 | 833.9379 | 0 | 0 | 0 | 0 | 0 | 0
| FY37 | 1018.4358 | 72.3423 | [7 empty] | FY37 | 24165.9599 | 1716.5738 | 0 | 0 | 0 | 0 | 0 | 0
| FY38 | 2029.1803 | 159.8187 | [7 empty] | FY38 | 48149.4154 | 3792.2592 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 3305.9326 | 331.9896 | [7 empty] | FY39 | 78444.8419 | 7877.618 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual

## Output for AusNet NPV Model_PoF
$k to $M | 0.001 | [8 empty] | $M to MWh | 23.7285
|  | Base Case Failure Rate | [9 empty] | Base Case Failure Rate
|  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Options sheet name: | Global Inputs
| FY26 | 1.2652e-05 | 1.2652e-05 | [7 empty] | FY26 | 0.00030021 | 0.00030021 | 0 | 0 | 0 | 0 | 0 | 0 | VCR sheet name: | VCR Calculation
| FY27 | 0.0033766 | 1.9672e-05 | [7 empty] | FY27 | 0.080122 | 0.00046678 | 0 | 0 | 0 | 0 | 0 | 0 | EUSE sheet name (Base PoF): | EUSE Calculator_PoF
| FY28 | 0.038013 | 0.001423 | [7 empty] | FY28 | 0.90198 | 0.033766 | 0 | 0 | 0 | 0 | 0 | 0 | File Prefix: | EAR_SMTS_OPT
| FY29 | 0.76904 | 0.0051023 | [7 empty] | FY29 | 18.2481 | 0.12107 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | File reference | EUE Range reference | Base EUE range ref | Low EUE range ref | High EUE range ref
| FY30 | 2.8386 | 0.011137 | [7 empty] | FY30 | 67.3562 | 0.26427 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Option1 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY31 | 7.533 | 0.022619 | [7 empty] | FY31 | 178.7475 | 0.5367 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | Option2 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY32 | 19.5867 | 0.052281 | [7 empty] | FY32 | 464.7623 | 1.2405 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | Option3 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT3.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY33 | 45.1303 | 0.17594 | [7 empty] | FY33 | 1070.8743 | 4.1749 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | Option4 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT4.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY34 | 80.2238 | 0.66938 | [7 empty] | FY34 | 1903.5906 | 15.8833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | Option5 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT5.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY35 | 139.5181 | 3.1902 | [7 empty] | FY35 | 3310.5556 | 75.6998 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | Option6 filename: | EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx | '[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-BVE-KMS 66kV Line_OPT6.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY36 | 236.8517 | 8.2804 | [7 empty] | FY36 | 5620.1361 | 196.4804 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | Option7 filename: | EAR_SMTS_OPT7.xlsx | '[EAR_SMTS_OPT7.xlsx]EUSE Calculator_PoF'!$F$18:$T$18
| FY37 | 386.9422 | 18.9576 | [7 empty] | FY37 | 9181.5603 | 449.8359 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | Option8 filename: | EAR_SMTS_OPT8.xlsx | '[EAR_SMTS_OPT8.xlsx]EUSE Calculator_PoF'!$F$18:$T$18
| FY38 | 786.0662 | 43.9651 | [7 empty] | FY38 | 18652.1758 | 1043.2271 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 1389.7422 | 90.849 | [7 empty] | FY39 | 32976.5052 | 2155.7122 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | Low Case Failure Rate | [9 empty] | Low Case Failure Rate
|  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 6.326e-06 | 6.326e-06 | [7 empty] | FY26 | 0.00015011 | 0.00015011 | 0 | 0 | 0 | 0 | 0 | 0
| FY27 | 0.0016883 | 9.8359e-06 | [7 empty] | FY27 | 0.040061 | 0.00023339 | 0 | 0 | 0 | 0 | 0 | 0
| FY28 | 0.033372 | 0.00071151 | [7 empty] | FY28 | 0.79188 | 0.016883 | 0 | 0 | 0 | 0 | 0 | 0
| FY29 | 0.75853 | 0.0025512 | [7 empty] | FY29 | 17.9987 | 0.060535 | 0 | 0 | 0 | 0 | 0 | 0
| FY30 | 2.8198 | 0.0055687 | [7 empty] | FY30 | 66.9091 | 0.13214 | 0 | 0 | 0 | 0 | 0 | 0
| FY31 | 7.4971 | 0.011309 | [7 empty] | FY31 | 177.8938 | 0.26835 | 0 | 0 | 0 | 0 | 0 | 0
| FY32 | 19.5086 | 0.02614 | [7 empty] | FY32 | 462.9091 | 0.62027 | 0 | 0 | 0 | 0 | 0 | 0
| FY33 | 44.9576 | 0.11027 | [7 empty] | FY33 | 1066.7758 | 2.6165 | 0 | 0 | 0 | 0 | 0 | 0
| FY34 | 79.905 | 0.53778 | [7 empty] | FY34 | 1896.0255 | 12.7607 | 0 | 0 | 0 | 0 | 0 | 0
| FY35 | 138.9472 | 2.9438 | [7 empty] | FY35 | 3297.0089 | 69.853 | 0 | 0 | 0 | 0 | 0 | 0
| FY36 | 235.9437 | 7.8778 | [7 empty] | FY36 | 5598.5921 | 186.9292 | 0 | 0 | 0 | 0 | 0 | 0
| FY37 | 385.6135 | 18.3561 | [7 empty] | FY37 | 9150.0331 | 435.5627 | 0 | 0 | 0 | 0 | 0 | 0
| FY38 | 783.8838 | 42.9357 | [7 empty] | FY38 | 18600.3914 | 1018.8012 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 1386.6566 | 89.3425 | [7 empty] | FY39 | 32903.2902 | 2119.9629 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | High Case Failure Rate | [9 empty] | High Case Failure Rate
|  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: Reconductor SMTS-BVE Line with 37/3.75 AAC Conductor | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 1.8978e-05 | 1.8978e-05 | [7 empty] | FY26 | 0.00045032 | 0.00045032 | 0 | 0 | 0 | 0 | 0 | 0
| FY27 | 0.0050649 | 2.9508e-05 | [7 empty] | FY27 | 0.12018 | 0.00070017 | 0 | 0 | 0 | 0 | 0 | 0
| FY28 | 0.042653 | 0.0021345 | [7 empty] | FY28 | 1.0121 | 0.050649 | 0 | 0 | 0 | 0 | 0 | 0
| FY29 | 0.77955 | 0.0076535 | [7 empty] | FY29 | 18.4975 | 0.18161 | 0 | 0 | 0 | 0 | 0 | 0
| FY30 | 2.8575 | 0.016706 | [7 empty] | FY30 | 67.8033 | 0.39641 | 0 | 0 | 0 | 0 | 0 | 0
| FY31 | 7.569 | 0.033928 | [7 empty] | FY31 | 179.6013 | 0.80506 | 0 | 0 | 0 | 0 | 0 | 0
| FY32 | 19.6648 | 0.078421 | [7 empty] | FY32 | 466.6155 | 1.8608 | 0 | 0 | 0 | 0 | 0 | 0
| FY33 | 45.303 | 0.24161 | [7 empty] | FY33 | 1074.9727 | 5.7332 | 0 | 0 | 0 | 0 | 0 | 0
| FY34 | 80.5426 | 0.80097 | [7 empty] | FY34 | 1911.1556 | 19.0059 | 0 | 0 | 0 | 0 | 0 | 0
| FY35 | 140.089 | 3.4367 | [7 empty] | FY35 | 3324.1023 | 81.5466 | 0 | 0 | 0 | 0 | 0 | 0
| FY36 | 237.7596 | 8.6829 | [7 empty] | FY36 | 5641.6801 | 206.0317 | 0 | 0 | 0 | 0 | 0 | 0
| FY37 | 388.2709 | 19.5591 | [7 empty] | FY37 | 9213.0875 | 464.1091 | 0 | 0 | 0 | 0 | 0 | 0
| FY38 | 788.2485 | 44.9945 | [7 empty] | FY38 | 18703.9601 | 1067.6531 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 1392.8277 | 92.3556 | [7 empty] | FY39 | 33049.7203 | 2191.4615 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual