## Global Inputs
Please close all other excel spreadsheets (including reopening this one) before running any macros contained in it
Topology change # | Description | Uptake year
0 | BAU
1 | KLO 3rdTx year | 2028
2 | WLT Load uptake year | 2029
3
4
EAR Loop | SMTS |  | PoE Weighting
Discount rate | 5.56% |  | P50 | 70%
Asset life | 45 | Years | P10 | 30%
First year of analysis | 2025 | Year
Line Segments for analysis (include new lines as well) | Length (km)
DRN-KLO | 23.95
SMTS-DRN 1 | 7.75
SMTS-DRN 2 | 7.75
SMTS-KMS | 58.24
SMTS-WOL | 11.65
KMS-WOL | 35.89
KLO-WOL | 13.85
ZSS connected to Loop
drn
klk
klo
kms
mdi
ruba
smr
wol
Ave no. of outages per year | 1
Ave. no. of outages per km line length per year | 0.062828
Ave. outage duration (hr) | 1
Ave. voltage collapse duration (hr) | 1
Sensitivities | Base | Low | High
Demand Forecasts | 100% | 90% | 110%
Failure Rate | 100% | 50% | 150%
Project Details | 2
Option 0: Do Nothing
Option 1: New SMTS-WLT Line UG_1600_AL_XLPE
Option 2:
Option 3:
Option 4:
Option 5:
Option 6:
Option 7:
|  | Summer | Winter
Gross Vs Net Load for LDC | Gross Load | 1.33 | 1.13
|  | Summer | Winter
Gross Load |  | 1.33 | 1.13
Net Load |  | 1 | 1

## VCR Calculation
| 1 |  |  |  | Sensitivity value | 1
| AER Rates (2024) |  |  |  |  | Values used in analysis
Commercial | 34.39 |  |  |  |  | 34.39
Agricultural | 22.25 |  |  |  |  | 22.25
Industrial | 33.49 |  |  |  |  | 33.49
Residential | 49.23 |  |  |  |  | 49.23
Customer consumption data (kWh) by ZSS | [7 empty] | Assumed as KLO | Assumed as EPG
ZSS | drn | klk | klo | kms | mdi | ruba | smr | wol | 0 | 0 | 0 | 0 | EAR Loop | epg
COMMERCIAL | 50857813.2378 | 4511737.2575 | 39497133.0224 | 20193836.4322 | 200221.43 | 14722134.2734 | 49198773.4269 | 20193836.4322 |  |  |  |  | 199375485.5123 | 20193836.4322
Agricultural | 16976721.4575 | 2922299.1532 | 876026.299 | 1845616.8665 | 153288.2952 | 7526475.5671 | 11483701.5568 | 777639.91 |  |  |  |  | 42561769.1053 | 777639.91
INDUSTRIAL | 7976446.4466 | 101186.97 | 1076076.6106 | 4730506.41 | 16.0426 | 1216874.5499 | 46376919.8957 | 14221065.1 |  |  |  |  | 75699092.0254 | 14221065.1
LIGHT | 659832.35 | 0 | 5259379.5 | 547479.19 | 0 | 247422.69 | 147474.96 | 0 |  |  |  |  | 6861588.69 | 0
RESIDENTIAL | 147184205.708 | 16157381.1115 | 75660655.1717 | 33788154.3753 | 176577.17 | 23148949.6778 | 51497167.0633 | 113320328.64 |  |  |  |  | 460933418.9176 | 113320328.64
Grand Total | 223655019.1999 | 23692604.4922 | 122369270.6038 | 61105593.2739 | 530102.9378 | 46861856.7582 | 158704036.9026 | 148512870.0822 | 0 | 0 | 0 | 0 | 785431354.2506 | 148512870.0822
%Utilisation by segment
Commercial | 22.74% | 19.04% | 32.28% | 33.05% | 37.77% | 31.42% | 31% | 13.6% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 25.38%
Agricultural | 7.591% | 12.33% | 0.7159% | 3.02% | 28.92% | 16.06% | 7.236% | 0.5236% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 5.419%
Industrial | 3.566% | 0.4271% | 0.8794% | 7.742% | 0.003026% | 2.597% | 29.22% | 9.576% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 9.638%
Residential | 66.1% | 68.2% | 66.13% | 56.19% | 33.31% | 49.93% | 32.54% | 76.3% | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 59.56%
VCR by segment | EAR Loop
Commercial | 8.7296
Agricultural | 1.2057
Industrial | 3.2277
Residential | 29.3209
Loop VCR | 42.484

## Output for AusNet NPV Model
$k to $M | 0.001 | [8 empty] | $M to MWh | 23.5383
|  | Base Case Demand | [9 empty] | Base Case Demand
|  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Options sheet name: | Global Inputs
| FY26 | 6.7558e-08 | 6.7558e-08 | [7 empty] | FY26 | 1.5902e-06 | 1.5902e-06 | 0 | 0 | 0 | 0 | 0 | 0 | VCR sheet name: | VCR Calculation
| FY27 | 1.0546e-05 | 1.0546e-05 | [7 empty] | FY27 | 0.00024824 | 0.00024824 | 0 | 0 | 0 | 0 | 0 | 0 | EUSE sheet name: | EUSE Calculator
| FY28 | 173.5646 | 0.0031306 | [7 empty] | FY28 | 4085.4146 | 0.07369 | 0 | 0 | 0 | 0 | 0 | 0 | File Prefix: | EAR_SMTS_OPT
| FY29 | 83.0813 | 0 | [7 empty] | FY29 | 1955.5929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | File reference | EUE Range reference | Base EUE range ref | Low EUE range ref | High EUE range ref
| FY30 | 143.7442 | 0 | [7 empty] | FY30 | 3383.4937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Option1 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY31 | 232.0161 | 2.9389e-05 | [7 empty] | FY31 | 5461.2642 | 0.00069177 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | Option2 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx]EUSE Calculator'!$F$18:$T$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx]EUSE Calculator'!$Y$18:$AM$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY32 | 363.1123 | 0.00037595 | [7 empty] | FY32 | 8547.0437 | 0.0088492 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | Option3 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY33 | 533.6604 | 0.0055786 | [7 empty] | FY33 | 12561.4563 | 0.13131 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | Option4 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY34 | 744.0212 | 0.026681 | [7 empty] | FY34 | 17512.9909 | 0.62803 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | Option5 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY35 | 1029.7202 | 0.091864 | [7 empty] | FY35 | 24237.858 | 2.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | Option6 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY36 | 1413.3292 | 0.22032 | [7 empty] | FY36 | 33267.3611 | 5.1859 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | Option7 filename: | EAR_SMTS_OPT7.xlsx | '[EAR_SMTS_OPT7.xlsx]EUSE Calculator'!$F$18:$T$18
| FY37 | 1871.5037 | 0.37757 | [7 empty] | FY37 | 44052.0084 | 8.8874 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | Option8 filename: | EAR_SMTS_OPT8.xlsx | '[EAR_SMTS_OPT8.xlsx]EUSE Calculator'!$F$18:$T$18
| FY38 | 2519.4471 | 0.84232 | [7 empty] | FY38 | 59303.4922 | 19.8268 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 3249.2163 | 1.3003 | [7 empty] | FY39 | 76481.0161 | 30.6073 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | Low Case Demand | [9 empty] | Low Case Demand
|  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 0 | 0 | [7 empty] | FY26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY27 | 0 | 0 | [7 empty] | FY27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY28 | 60.0605 | 0.00065926 | [7 empty] | FY28 | 1413.722 | 0.015518 | 0 | 0 | 0 | 0 | 0 | 0
| FY29 | 18.7487 | 0 | [7 empty] | FY29 | 441.3133 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY30 | 41.9896 | 0 | [7 empty] | FY30 | 988.3628 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY31 | 84.5794 | 0 | [7 empty] | FY31 | 1990.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY32 | 156.3401 | 0 | [7 empty] | FY32 | 3679.9793 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY33 | 255.7965 | 8.136e-05 | [7 empty] | FY33 | 6021.0132 | 0.0019151 | 0 | 0 | 0 | 0 | 0 | 0
| FY34 | 380.9036 | 0.0012878 | [7 empty] | FY34 | 8965.8212 | 0.030312 | 0 | 0 | 0 | 0 | 0 | 0
| FY35 | 553.2413 | 0.0098322 | [7 empty] | FY35 | 13022.3583 | 0.23143 | 0 | 0 | 0 | 0 | 0 | 0
| FY36 | 784.4698 | 0.038564 | [7 empty] | FY36 | 18465.0816 | 0.90772 | 0 | 0 | 0 | 0 | 0 | 0
| FY37 | 1060.9714 | 0.086627 | [7 empty] | FY37 | 24973.4592 | 2.0391 | 0 | 0 | 0 | 0 | 0 | 0
| FY38 | 1442.4297 | 0.28573 | [7 empty] | FY38 | 33952.3386 | 6.7255 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 1843.9866 | 0.52597 | [7 empty] | FY39 | 43404.3032 | 12.3805 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | High Case Demand | [9 empty] | High Case Demand
|  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 2.7927e-06 | 2.7927e-06 | [6 empty] | Total EUE (MWh) | FY25 | 6.5734e-05 | 6.5734e-05 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 7.6083e-05 | 7.6083e-05 | [7 empty] | FY26 | 0.0017909 | 0.0017909 | 0 | 0 | 0 | 0 | 0 | 0
| FY27 | 0.00026782 | 0.00026782 | [7 empty] | FY27 | 0.006304 | 0.006304 | 0 | 0 | 0 | 0 | 0 | 0
| FY28 | 353.2377 | 0.0089432 | [7 empty] | FY28 | 8314.6125 | 0.21051 | 0 | 0 | 0 | 0 | 0 | 0
| FY29 | 211.04 | 1.2379e-05 | [7 empty] | FY29 | 4967.523 | 0.00029139 | 0 | 0 | 0 | 0 | 0 | 0
| FY30 | 317.1658 | 0.00011683 | [7 empty] | FY30 | 7465.5428 | 0.0027501 | 0 | 0 | 0 | 0 | 0 | 0
| FY31 | 462.1443 | 0.0011141 | [7 empty] | FY31 | 10878.0892 | 0.026224 | 0 | 0 | 0 | 0 | 0 | 0
| FY32 | 673.6889 | 0.0085462 | [7 empty] | FY32 | 15857.4899 | 0.20116 | 0 | 0 | 0 | 0 | 0 | 0
| FY33 | 943.2626 | 0.05169 | [7 empty] | FY33 | 22202.7934 | 1.2167 | 0 | 0 | 0 | 0 | 0 | 0
| FY34 | 1273.7005 | 0.15147 | [7 empty] | FY34 | 29980.7387 | 3.5655 | 0 | 0 | 0 | 0 | 0 | 0
| FY35 | 1722.1364 | 0.34779 | [7 empty] | FY35 | 40536.1561 | 8.1863 | 0 | 0 | 0 | 0 | 0 | 0
| FY36 | 2340.4557 | 0.63632 | [7 empty] | FY36 | 55090.3401 | 14.978 | 0 | 0 | 0 | 0 | 0 | 0
| FY37 | 3119.8036 | 0.94414 | [7 empty] | FY37 | 73434.8613 | 22.2233 | 0 | 0 | 0 | 0 | 0 | 0
| FY38 | 4289.2948 | 1.7515 | [7 empty] | FY38 | 100962.6925 | 41.2265 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 5604.3106 | 2.9241 | [7 empty] | FY39 | 131915.9223 | 68.8292 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual

## Output for AusNet NPV Model_PoF
$k to $M | 0.001 | [8 empty] | $M to MWh | 23.5383
|  | Base Case Failure Rate | [9 empty] | Base Case Failure Rate
|  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Options sheet name: | Global Inputs
| FY26 | 6.7558e-08 | 6.7558e-08 | [7 empty] | FY26 | 1.5902e-06 | 1.5902e-06 | 0 | 0 | 0 | 0 | 0 | 0 | VCR sheet name: | VCR Calculation
| FY27 | 1.0546e-05 | 1.0546e-05 | [7 empty] | FY27 | 0.00024824 | 0.00024824 | 0 | 0 | 0 | 0 | 0 | 0 | EUSE sheet name (Base PoF): | EUSE Calculator_PoF
| FY28 | 173.5646 | 0.0031306 | [7 empty] | FY28 | 4085.4146 | 0.07369 | 0 | 0 | 0 | 0 | 0 | 0 | File Prefix: | EAR_SMTS_OPT
| FY29 | 83.0813 | 0 | [7 empty] | FY29 | 1955.5929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | File reference | EUE Range reference | Base EUE range ref | Low EUE range ref | High EUE range ref
| FY30 | 143.7442 | 0 | [7 empty] | FY30 | 3383.4937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Option1 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT1.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY31 | 232.0161 | 2.9389e-05 | [7 empty] | FY31 | 5461.2642 | 0.00069177 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | Option2 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$Y$18:$AM$18 | '[EAR_Augment SMTS-WLT 66kV Line_OPT2.xlsx]EUSE Calculator_PoF'!$AR$18:$BF$18
| FY32 | 363.1123 | 0.00037595 | [7 empty] | FY32 | 8547.0437 | 0.0088492 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | Option3 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT3.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY33 | 533.6604 | 0.0055786 | [7 empty] | FY33 | 12561.4563 | 0.13131 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | Option4 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT4.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY34 | 744.0212 | 0.026681 | [7 empty] | FY34 | 17512.9909 | 0.62803 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | Option5 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT5.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY35 | 1029.7202 | 0.091864 | [7 empty] | FY35 | 24237.858 | 2.1623 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | Option6 filename: | EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx | '[EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx]EUSE Calculator_PoF'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx]EUSE Calculator'!$F$18:$T$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx]EUSE Calculator'!$Y$18:$AM$18 | 'C:\PSSE\EDPR\EAR_template\[EAR_Augment SMTS-WLT 66kV Line_OPT6.xlsx]EUSE Calculator'!$AR$18:$BF$18
| FY36 | 1413.3292 | 0.22032 | [7 empty] | FY36 | 33267.3611 | 5.1859 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | Option7 filename: | EAR_SMTS_OPT7.xlsx | '[EAR_SMTS_OPT7.xlsx]EUSE Calculator_PoF'!$F$18:$T$18
| FY37 | 1871.5037 | 0.37757 | [7 empty] | FY37 | 44052.0084 | 8.8874 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | Option8 filename: | EAR_SMTS_OPT8.xlsx | '[EAR_SMTS_OPT8.xlsx]EUSE Calculator_PoF'!$F$18:$T$18
| FY38 | 2519.4471 | 0.84232 | [7 empty] | FY38 | 59303.4922 | 19.8268 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 3249.2163 | 1.3003 | [7 empty] | FY39 | 76481.0161 | 30.6073 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | Low Case Failure Rate | [9 empty] | Low Case Failure Rate
|  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 3.3779e-08 | 3.3779e-08 | [7 empty] | FY26 | 7.9511e-07 | 7.9511e-07 | 0 | 0 | 0 | 0 | 0 | 0
| FY27 | 5.2731e-06 | 5.2731e-06 | [7 empty] | FY27 | 0.00012412 | 0.00012412 | 0 | 0 | 0 | 0 | 0 | 0
| FY28 | 173.4983 | 0.0015653 | [7 empty] | FY28 | 4083.8546 | 0.036845 | 0 | 0 | 0 | 0 | 0 | 0
| FY29 | 82.9744 | 0 | [7 empty] | FY29 | 1953.0761 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY30 | 143.5876 | 0 | [7 empty] | FY30 | 3379.8071 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY31 | 231.791 | 1.4695e-05 | [7 empty] | FY31 | 5455.9664 | 0.00034589 | 0 | 0 | 0 | 0 | 0 | 0
| FY32 | 362.7866 | 0.00018798 | [7 empty] | FY32 | 8539.3775 | 0.0044246 | 0 | 0 | 0 | 0 | 0 | 0
| FY33 | 533.195 | 0.0027893 | [7 empty] | FY33 | 12550.5018 | 0.065655 | 0 | 0 | 0 | 0 | 0 | 0
| FY34 | 743.3522 | 0.013341 | [7 empty] | FY34 | 17497.2433 | 0.31402 | 0 | 0 | 0 | 0 | 0 | 0
| FY35 | 1028.7107 | 0.045932 | [7 empty] | FY35 | 24214.0979 | 1.0812 | 0 | 0 | 0 | 0 | 0 | 0
| FY36 | 1411.7922 | 0.11016 | [7 empty] | FY36 | 33231.1832 | 2.593 | 0 | 0 | 0 | 0 | 0 | 0
| FY37 | 1869.3365 | 0.18879 | [7 empty] | FY37 | 44000.9952 | 4.4437 | 0 | 0 | 0 | 0 | 0 | 0
| FY38 | 2516.0029 | 0.42116 | [7 empty] | FY38 | 59222.4209 | 9.9134 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 3244.5128 | 0.65016 | [7 empty] | FY39 | 76370.3026 | 15.3037 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual
|  | High Case Failure Rate | [9 empty] | High Case Failure Rate
|  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7: |  |  | Option 0: Do Nothing | Option 1: New SMTS-WLT Line UG_1600_AL_XLPE | Option 2: | Option 3: | Option 4: | Option 5: | Option 6: | Option 7:
Cost of EUE ($M) | FY25 | 0 | 0 | [6 empty] | Total EUE (MWh) | FY25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY26 | 1.0134e-07 | 1.0134e-07 | [7 empty] | FY26 | 2.3853e-06 | 2.3853e-06 | 0 | 0 | 0 | 0 | 0 | 0
| FY27 | 1.5819e-05 | 1.5819e-05 | [7 empty] | FY27 | 0.00037236 | 0.00037236 | 0 | 0 | 0 | 0 | 0 | 0
| FY28 | 173.6309 | 0.004696 | [7 empty] | FY28 | 4086.9747 | 0.11053 | 0 | 0 | 0 | 0 | 0 | 0
| FY29 | 83.1883 | 0 | [7 empty] | FY29 | 1958.1098 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY30 | 143.9008 | 0 | [7 empty] | FY30 | 3387.1803 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FY31 | 232.2412 | 4.4084e-05 | [7 empty] | FY31 | 5466.562 | 0.0010377 | 0 | 0 | 0 | 0 | 0 | 0
| FY32 | 363.4379 | 0.00056393 | [7 empty] | FY32 | 8554.7099 | 0.013274 | 0 | 0 | 0 | 0 | 0 | 0
| FY33 | 534.1258 | 0.0083679 | [7 empty] | FY33 | 12572.4108 | 0.19697 | 0 | 0 | 0 | 0 | 0 | 0
| FY34 | 744.6902 | 0.040022 | [7 empty] | FY34 | 17528.7385 | 0.94205 | 0 | 0 | 0 | 0 | 0 | 0
| FY35 | 1030.7296 | 0.1378 | [7 empty] | FY35 | 24261.6181 | 3.2435 | 0 | 0 | 0 | 0 | 0 | 0
| FY36 | 1414.8662 | 0.33048 | [7 empty] | FY36 | 33303.539 | 7.7789 | 0 | 0 | 0 | 0 | 0 | 0
| FY37 | 1873.6709 | 0.56636 | [7 empty] | FY37 | 44103.0217 | 13.3311 | 0 | 0 | 0 | 0 | 0 | 0
| FY38 | 2522.8913 | 1.2635 | [7 empty] | FY38 | 59384.5635 | 29.7402 | 0 | 0 | 0 | 0 | 0 | 0
| FY39 | 3253.9199 | 1.9505 | [7 empty] | FY39 | 76591.7295 | 45.911 | 0 | 0 | 0 | 0 | 0 | 0
| Residual | [9 empty] | Residual