## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 162349945.5089 | 67.2% | 33.0819
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 70185987.1383 | 29.05% | 9.9906
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 3438927.3871 | 1.423% | 0.4767
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 5622421.9462 | 2.327% | 0.5178
[5 empty] | 241597281.9805 |  | 44.0669
Customer No. and Vol per Feeder | [6 empty] | 44066.9381 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 70185987.1383 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 6.016 | E@R MWh | 6.016
RESIDENTL | 162349945.5089 | [14 empty] | cost of EUE ($) | 265107.9226 | cost of EUE ($M) | 0.26511
FARM | 5622421.9462
INDUSTRIAL | 3438927.3871
Forecast (FCT)
Forecast | 2031
Summer POE50 | 135.5707
Summer POE10 | 155.7974
Winter POE50 | 117.8415
Winter POE10 | 123.5192
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 16.69 |  | Summer POE50 | 117.214 |  |  | 100% | 0 | 117.214 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 137.4407 |  |  | 99% | 0 | 116.0419 | 99% |  | 99% | 0 | 99% | 0
Embedded Generation |  |  | Winter POE50 | 99.4848 |  |  | 98% | 0.37816 | 114.8697 | 98% |  | 98% | 9.929 | 98% | 26.7951
|  |  | Winter POE10 | 105.1625 |  |  | 97% | 0.75633 | 113.6976 | 97% |  | 97% | 9.4857 | 97% | 26.3519
Year | 2031 | [5 empty] | 95% | 1.1345 | 111.3533 | 95% |  | 95% | 8.8209 | 95% | 25.687
Capacity | 0 | [5 empty] | 90% | 4.538 | 105.4926 | 90% |  | 90% | 65.4249 | 90% | 217.2201
[7 empty] | 85% | 7.9414 | 99.6319 | 85% |  | 85% | 45.4782 | 85% | 197.2733
Demand Mangement | [6 empty] | 80% | 11.7231 | 93.7712 | 80% |  | 80% | 28.3682 | 80% | 197.0295
[7 empty] | 75% | 17.7737 | 87.9105 | 75% |  | 75% | 10.7866 | 75% | 279.7863
Year | 2031 | [5 empty] | 70% | 35.1693 | 82.0498 | 70% |  | 70% |  | 70% | 702.4354
Capacity | 1.6667 | [5 empty] | 65% | 59.3718 | 76.1891 | 65% |  | 65% |  | 65% | 835.4577
[7 empty] | 60% | 156.9382 | 70.3284 | 60% |  | 60% |  | 60% | 2796.1316
LDC | [6 empty] | 55% | 363.794 | 64.4677 | 55% |  | 55% |  | 55% | 4715.9123
[7 empty] | 50% | 771.4551 | 58.607 | 50% |  | 50% |  | 50% | 6904.7022
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 1255.5054 | 52.7463 | 45% |  | 45% |  | 45% | 5361.6593
100% | 0% | 0 |  |  |  |  | 40% | 2059.1045 | 46.8856 | 40% |  | 40% |  | 40% | 4191.5383
99% | 0% | 0 |  |  |  |  | 35% | 3060.4836 | 41.0249 | 35% |  | 35% |  | 35% | 446.2949
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3366.0403 | 35.1642 | 30% |  | 30% |  | 30%
97% | 0.01722% | 0.75633 |  |  |  |  | 25% | 3686.3454 | 29.3035 | 25% |  | 25% |  | 25%
95% | 0.02583% | 1.1345 |  |  |  |  | 20% | 4028.5841 | 23.4428 | 20% |  | 20% |  | 20%
90% | 0.1033% | 4.538 |  |  |  |  | 15% | 4345.1076 | 17.5821 | 15% |  | 15% |  | 15%
85% | 0.1808% | 7.9414 |  |  |  |  | 10% | 4381.0332 | 11.7214 | 10% |  | 10% |  | 10%
80% | 0.2669% | 11.7231 |  |  |  |  | 5% | 4391.6218 | 5.8607 | 5% |  | 5% |  | 5%
75% | 0.4047% | 17.7737 |  |  |  |  | 9.992e-14% | 4391.6218 | 1.1712e-13 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
70% | 0.8008% | 35.1693 | [7 empty] | Total E@R | 0 | Total E@R | 178.2936 | Total E@R | 26924.275
65% | 1.352% | 59.3718 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.4217 | Total WE@R | 0.072489
60% | 3.573% | 156.9382 |  |  |  |  | MD Weighted LDC
55% | 8.283% | 363.794
50% | 17.57% | 771.4551 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 28.59% | 1255.5054 |  |  |  |  | 100% | 0 | 137.4407 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 46.88% | 2059.1045 |  |  |  |  | 99% | 0.37816 | 136.0663
35% | 69.68% | 3060.4836 |  |  |  |  | 98% | 1.1345 | 134.6919 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 76.64% | 3366.0403 |  |  |  |  | 97% | 2.269 | 133.3175 | 100% |  | 100% |  | 100%
25% | 83.93% | 3686.3454 |  |  |  |  | 95% | 4.538 | 130.5687 | 99% | 2.1947 | 99% | 17.983 | 99% | 34.8492
20% | 91.73% | 4028.5841 |  |  |  |  | 90% | 7.9414 | 123.6966 | 98% | 3.3498 | 98% | 34.9266 | 98% | 68.6588
15% | 98.93% | 4345.1076 |  |  |  |  | 85% | 14.3702 | 116.8246 | 97% | 3.4655 | 97% | 50.8306 | 97% | 101.429
10% | 99.75% | 4381.0332 |  |  |  |  | 80% | 19.6645 | 109.9526 | 95% | 2.3133 | 95% | 96.9834 | 95% | 198.1802
5% | 99.99% | 4391.6218 |  |  |  |  | 75% | 25.7152 | 103.0805 | 90% |  | 90% | 129.1029 | 90% | 280.8981
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 34.7911 | 96.2085 | 85% |  | 85% | 199.6822 | 85% | 486.4063
[7 empty] | 65% | 46.136 | 89.3364 | 80% |  | 80% | 128.0615 | 80% | 364.1873
[7 empty] | 60% | 76.7673 | 82.4644 | 75% |  | 75% | 104.7759 | 75% | 374.634
[7 empty] | 55% | 106.2642 | 75.5924 | 70% |  | 70% | 94.7937 | 70% | 499.5807
LDC | [6 empty] | 50% | 178.4935 | 68.7203 | 65% |  | 65% | 40.5294 | 65% | 546.5132
[7 empty] | 45% | 367.9538 | 61.8483 | 60% |  | 60% | 0.041494 | 60% | 1265.0862
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 741.202 | 54.9763 | 55% |  | 55% |  | 55% | 1015.528
100% | 0% | 0 |  |  |  |  | 35% | 1167.7713 | 48.1042 | 50% |  | 50% |  | 50% | 1990.3789
99% | 0.00861% | 0.37816 |  |  |  |  | 30% | 2002.3799 | 41.2322 | 45% |  | 45% |  | 45% | 3918.8591
98% | 0.02583% | 1.1345 |  |  |  |  | 25% | 3173.5547 | 34.3602 | 40% |  | 40% |  | 40% | 5155.4129
97% | 0.05166% | 2.269 |  |  |  |  | 20% | 3477.5988 | 27.4881 | 35% |  | 35% |  | 35% | 2960.5014
95% | 0.1033% | 4.538 |  |  |  |  | 15% | 3788.4498 | 20.6161 | 30% |  | 30% |  | 30% | 745.6853
90% | 0.1808% | 7.9414 |  |  |  |  | 10% | 4317.5016 | 13.7441 | 25% |  | 25% |  | 25%
85% | 0.3272% | 14.3702 |  |  |  |  | 5% | 4391.6218 | 6.872 | 20% |  | 20% |  | 20%
80% | 0.4477% | 19.6645 |  |  |  |  | 9.992e-14% | 4391.6218 | 1.3733e-13 | 15% |  | 15% |  | 15%
75% | 0.5855% | 25.7152 | [7 empty] | 10% |  | 10% |  | 10%
70% | 0.7921% | 34.7911 | [7 empty] | 5% |  | 5% |  | 5%
65% | 1.05% | 46.136 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
60% | 1.748% | 76.7673 | [7 empty] | Total E@R | 11.3233 | Total E@R | 897.7107 | Total E@R | 20006.7886
55% | 2.419% | 106.2642 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 4.5065 | Total WE@R | 0.90997 | Total WE@R | 0.023085
50% | 4.064% | 178.4935
45% | 8.378% | 367.9538 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 16.88% | 741.202 |  |  |  |  | 100% | 0 | 99.4848
35% | 26.59% | 1167.7713 |  |  |  |  | 99% | 0.5944 | 98.4899 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 45.59% | 2002.3799 |  |  |  |  | 98% | 0.8916 | 97.4951
25% | 72.26% | 3173.5547 |  |  |  |  | 97% | 1.486 | 96.5003 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 79.18% | 3477.5988 |  |  |  |  | 95% | 2.3776 | 94.5106 | 100% |  | 100% |  | 100%
15% | 86.26% | 3788.4498 |  |  |  |  | 90% | 3.2692 | 89.5363 | 99% |  | 99% | 0.70577 | 99% | 29.7718
10% | 98.3% | 4317.5016 |  |  |  |  | 85% | 13.9683 | 84.5621 | 98% |  | 98% | 0.071104 | 98% | 14.5902
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 41.3106 | 79.5878 | 97% |  | 97% |  | 97% | 28.5891
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 126.3094 | 74.6136 | 95% |  | 95% |  | 95% | 41.5532
[7 empty] | 70% | 323.9464 | 69.6394 | 90% |  | 90% |  | 90% | 38.4487
[7 empty] | 65% | 549.5201 | 64.6651 | 85% |  | 85% |  | 85% | 408.1639
[7 empty] | 60% | 799.4641 | 59.6909 | 80% |  | 80% |  | 80% | 907.0785
LDC | [6 empty] | 55% | 1116.2777 | 54.7166 | 75% |  | 75% |  | 75% | 2397.0265
[7 empty] | 50% | 1494.9086 | 49.7424 | 70% |  | 70% |  | 70% | 4590.4118
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 2004.0097 | 44.7682 | 65% |  | 65% |  | 65% | 4117.2244
100% | 0% | 0 |  |  |  |  | 40% | 2877.179 | 39.7939 | 60% |  | 60% |  | 60% | 3318.7553
99% | 0.01353% | 0.5944 |  |  |  |  | 35% | 3454.933 | 34.8197 | 55% |  | 55% |  | 55% | 2630.7435
98% | 0.0203% | 0.8916 |  |  |  |  | 30% | 3663.5664 | 29.8454 | 50% |  | 50% |  | 50% | 1260.6583
97% | 0.03383% | 1.486 |  |  |  |  | 25% | 3862.6894 | 24.8712 | 45% |  | 45% |  | 45% | 36.3146
95% | 0.05413% | 2.3776 |  |  |  |  | 20% | 4122.7381 | 19.897 | 40% |  | 40% |  | 40%
90% | 0.07443% | 3.2692 |  |  |  |  | 15% | 4372.3849 | 14.9227 | 35% |  | 35% |  | 35%
85% | 0.318% | 13.9683 |  |  |  |  | 10% | 4374.4653 | 9.9485 | 30% |  | 30% |  | 30%
80% | 0.9406% | 41.3106 |  |  |  |  | 5% | 4374.7625 | 4.9742 | 25% |  | 25% |  | 25%
75% | 2.876% | 126.3094 |  |  |  |  | 9.992e-14% | 4375.9513 | 9.9405e-14 | 20% |  | 20% |  | 20%
70% | 7.376% | 323.9464 | [7 empty] | 15% |  | 15% |  | 15%
65% | 12.51% | 549.5201 | [7 empty] | 10% |  | 10% |  | 10%
60% | 18.2% | 799.4641 | [7 empty] | 5% |  | 5% |  | 5%
55% | 25.42% | 1116.2777 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 34.04% | 1494.9086 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 0.77687 | Total E@R | 19819.3296
45% | 45.63% | 2004.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.0015612 | Total WE@R | 0.045336
40% | 65.51% | 2877.179 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 78.66% | 3454.933 |  |  |  |  | 100% | 0 | 105.1625 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 83.41% | 3663.5664 |  |  |  |  | 99% | 0.5944 | 104.1109
25% | 87.95% | 3862.6894 |  |  |  |  | 98% | 0.8916 | 103.0593 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 93.87% | 4122.7381 |  |  |  |  | 97% | 1.486 | 102.0076 | 100% |  | 100% |  | 100%
15% | 99.55% | 4372.3849 |  |  |  |  | 95% | 2.3776 | 99.9044 | 99% |  | 99% | 4.0637 | 99% | 33.1297
10% | 99.6% | 4374.4653 |  |  |  |  | 90% | 3.2692 | 94.6463 | 98% |  | 98% | 1.7193 | 98% | 16.2523
5% | 99.61% | 4374.7625 |  |  |  |  | 85% | 13.9683 | 89.3881 | 97% |  | 97% | 2.8135 | 97% | 31.8796
9.992e-14% | 99.63% | 4375.9513 |  |  |  |  | 80% | 41.3106 | 84.13 | 95% |  | 95% | 2.8139 | 95% | 46.4129
[7 empty] | 75% | 126.3094 | 78.8719 | 90% |  | 90% | 0.37545 | 90% | 43.1312
[7 empty] | 70% | 323.9464 | 73.6138 | 85% |  | 85% |  | 85% | 461.3172
[7 empty] | 65% | 549.5201 | 68.3556 | 80% |  | 80% |  | 80% | 1035.1526
LDC | [6 empty] | 60% | 799.4641 | 63.0975 | 75% |  | 75% |  | 75% | 2771.0402
[7 empty] | 55% | 1116.2777 | 57.8394 | 70% |  | 70% |  | 70% | 5403.9526
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 1494.9086 | 52.5813 | 65% |  | 65% |  | 65% | 4981.7249
100% | 0% | 0 |  |  |  |  | 45% | 2004.0097 | 47.3231 | 60% |  | 60% |  | 60% | 4205.6983
99% | 0.01353% | 0.5944 |  |  |  |  | 40% | 2877.179 | 42.065 | 55% |  | 55% |  | 55% | 3665.0394
98% | 0.0203% | 0.8916 |  |  |  |  | 35% | 3454.933 | 36.8069 | 50% |  | 50% |  | 50% | 2389.2801
97% | 0.03383% | 1.486 |  |  |  |  | 30% | 3663.5664 | 31.5488 | 45% |  | 45% |  | 45% | 656.0457
95% | 0.05413% | 2.3776 |  |  |  |  | 25% | 3862.6894 | 26.2906 | 40% |  | 40% |  | 40%
90% | 0.07443% | 3.2692 |  |  |  |  | 20% | 4122.7381 | 21.0325 | 35% |  | 35% |  | 35%
85% | 0.318% | 13.9683 |  |  |  |  | 15% | 4372.3849 | 15.7744 | 30% |  | 30% |  | 30%
80% | 0.9406% | 41.3106 |  |  |  |  | 10% | 4374.4653 | 10.5163 | 25% |  | 25% |  | 25%
75% | 2.876% | 126.3094 |  |  |  |  | 5% | 4374.7625 | 5.2581 | 20% |  | 20% |  | 20%
70% | 7.376% | 323.9464 |  |  |  |  | 9.992e-14% | 4375.9513 | 1.0508e-13 | 15% |  | 15% |  | 15%
65% | 12.51% | 549.5201 | [7 empty] | 10% |  | 10% |  | 10%
60% | 18.2% | 799.4641 | [7 empty] | 5% |  | 5% |  | 5%
55% | 25.42% | 1116.2777 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 34.04% | 1494.9086 | [7 empty] | Total E@R | 0 | Total E@R | 11.7859 | Total E@R | 25740.0567
45% | 45.63% | 2004.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.01015 | Total WE@R | 0.025234
40% | 65.51% | 2877.179
35% | 78.66% | 3454.933
30% | 83.41% | 3663.5664
25% | 87.95% | 3862.6894
20% | 93.87% | 4122.7381
15% | 99.55% | 4372.3849
10% | 99.6% | 4374.4653
5% | 99.61% | 4374.7625
9.992e-14% | 99.63% | 4375.9513
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 130.95 |  |  | Year | 2031
SCR (N-1) | 89.2 |  |  | SCR (N) | 130.95
SCR (N-2) | 44.6 |  |  | SCR (N-1) | 89.2
WCR (N) | 142.95 |  |  | SCR (N-2) | 44.6
WCR (N-1) | 97.8 |  |  | WCR (N) | 142.95
WCR (N-2) | 48.9 |  |  | WCR (N-1) | 97.8
|  |  |  | WCR (N-2) | 48.9
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.0091026 | 0.0065832 | 0.011955 | 0.018873 | 0.02847 | 0.046528 | 0.26511 | 1.1074 | 2.6178 | 4.4532 | 6.9476 | 12.9693 | 17.3791 | 24.7523 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318
Total EUE (MWh) | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744
Residual Values
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0091026 | 0.0065832 | 0.011955 | 0.0050107 | 0.0084908 | 0.015956 | 0.0271 | 0.047528 | 0.38877 | 1.1562 | 2.2863 | 4.936 | 7.4932 | 11.59 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014 | 16.9014
Total EUE (MWh) | 0.20656 | 0.14939 | 0.27129 | 0.11371 | 0.19268 | 0.36207 | 0.61497 | 1.0785 | 8.8223 | 26.2367 | 51.882 | 112.0107 | 170.0411 | 263.0088 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0091026 | 0.0065832 | 0.011955 | 0.018873 | 0.02847 | 0.046528 | 0.26511 | 1.1074 | 2.6178 | 4.4532 | 6.9476 | 12.9693 | 17.3791 | 24.7523 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318
Total EUE (MWh) | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0091026 | 0.0065832 | 0.011955 | 0.0026922 | 0.005107 | 0.010453 | 0.018597 | 0.03486 | 0.091804 | 0.56921 | 1.3794 | 3.3924 | 5.4629 | 8.6248 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566 | 12.9566
Total EUE (MWh) | 0.20656 | 0.14939 | 0.27129 | 0.061093 | 0.11589 | 0.2372 | 0.42202 | 0.79108 | 2.0833 | 12.917 | 31.3035 | 76.9837 | 123.968 | 195.7195 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0091026 | 0.0065832 | 0.011955 | 0.018873 | 0.02847 | 0.046528 | 0.26511 | 1.1074 | 2.6178 | 4.4532 | 6.9476 | 12.9693 | 17.3791 | 24.7523 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318
Total EUE (MWh) | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0045662 | 0.0027415 | 0.0054826 | 0.0091917 | 0.01464 | 0.024739 | 0.038744 | 0.14572 | 0.84206 | 1.7952 | 3.1278 | 6.1406 | 8.8608 | 13.1724 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819 | 18.5819
Total EUE (MWh) | 0.10362 | 0.062212 | 0.12442 | 0.20859 | 0.33221 | 0.56139 | 0.87922 | 3.3069 | 19.1087 | 40.7389 | 70.978 | 139.3475 | 201.0749 | 298.9173 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0091026 | 0.0065832 | 0.011955 | 0.018873 | 0.02847 | 0.046528 | 0.26511 | 1.1074 | 2.6178 | 4.4532 | 6.9476 | 12.9693 | 17.3791 | 24.7523 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318
Total EUE (MWh) | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0091026 | 0.0065832 | 0.011955 | 0.018873 | 0.02847 | 0.046528 | 0.26511 | 1.1074 | 2.6178 | 4.4532 | 6.9476 | 12.9693 | 17.3791 | 24.7523 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318 | 34.0318
Total EUE (MWh) | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744

## Key Model Assumption & Inputs
Select ZSS & Region | CLN | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
High | 110% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1A New PHS ZSS + Four new feeders | 1A New PHS ZSS + Four new feeders
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Option 6 - Non Network | Non Network
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 |  | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | 6.8848 | 7.8511 | 8.1512 | 8.3996 | 8.6182 | 8.9724 | 9.2916 | 9.7408 | 10.2098 | 10.5907 | 10.9491 | 11.4893 | 11.8773 | 12.269 | 12.6854
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Transfers (MVA) Option 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Transfers (MVA) Option 4 |  |  |  | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Transfers (MVA) Option 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
CLN | N/A | DS-CLN-TRNFMR-XXXXXXXXXXXX | New CLN 3rd TX | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | CLN
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 89.7351 | 104.3341 | 108.3435 | 111.4611 | 115.2173 | 119.0984 | 123.2461 | 128.0275 | 133.6994 | 139.0092 | 144.6013 | 154.2938 | 157.43 | 163.5566 | 168.1999
Summer POE10 | 10 |  |  | 104.9463 | 119.6766 | 124.2514 | 128.0364 | 131.3686 | 136.7682 | 141.634 | 148.4809 | 155.6302 | 161.4365 | 166.8996 | 175.1342 | 181.0486 | 187.0195 | 193.3671
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 69.1182 | 84.5179 | 88.1502 | 92.8679 | 97.437 | 101.4753 | 107.1286 | 113.3315 | 119.6901 | 125.9989 | 131.579 | 137.6925 | 139.8743 | 147.8441 | 156.1056
Winter POE10 | 10 |  |  | 74.018 | 89.4372 | 93.2911 | 98.0701 | 102.5171 | 107.2692 | 112.2902 | 119.5588 | 125.8642 | 131.807 | 137.993 | 145.465 | 147.8036 | 155.8793 | 163.4009
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | CLN | 0 | 18 | 17.73 | 17.46 | 17.2 | 16.94 | 16.69 | 16.44 | 16.19 | 15.95 | 15.71 | 15.48 | 15.24 | 15.01 | 14.79
|  | PowerFactor | 1

## Load Duration Curves
Station
CLN
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.01353% | 0.5944 | 0.00861% | 0.37816 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.02583% | 1.1345 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.03383% | 1.486 | 0.05166% | 2.269 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.05413% | 2.3776 | 0.1033% | 4.538 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.07443% | 3.2692 | 0.1808% | 7.9414 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 0.318% | 13.9683 | 0.3272% | 14.3702 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 0.9406% | 41.3106 | 0.4477% | 19.6645 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 2.876% | 126.3094 | 0.5855% | 25.7152 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 7.376% | 323.9464 | 0.7921% | 34.7911 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 12.51% | 549.5201 | 1.05% | 46.136 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 18.2% | 799.4641 | 1.748% | 76.7673 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 25.42% | 1116.2777 | 2.419% | 106.2642 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 34.04% | 1494.9086 | 4.064% | 178.4935 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 45.63% | 2004.0097 | 8.378% | 367.9538 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 65.51% | 2877.179 | 16.88% | 741.202 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 78.66% | 3454.933 | 26.59% | 1167.7713 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 83.41% | 3663.5664 | 45.59% | 2002.3799 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 87.95% | 3862.6894 | 72.26% | 3173.5547 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 93.87% | 4122.7381 | 79.18% | 3477.5988 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.55% | 4372.3849 | 86.26% | 3788.4498 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.6% | 4374.4653 | 98.3% | 4317.5016 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.61% | 4374.7625 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.63% | 4375.9513 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.01353% | 0.5944 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.03383% | 1.486 | 0.01722% | 0.75633 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.05413% | 2.3776 | 0.02583% | 1.1345 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.07443% | 3.2692 | 0.1033% | 4.538 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 0.318% | 13.9683 | 0.1808% | 7.9414 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 0.9406% | 41.3106 | 0.2669% | 11.7231 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 2.876% | 126.3094 | 0.4047% | 17.7737 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 7.376% | 323.9464 | 0.8008% | 35.1693 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 12.51% | 549.5201 | 1.352% | 59.3718 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 18.2% | 799.4641 | 3.573% | 156.9382 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 25.42% | 1116.2777 | 8.283% | 363.794 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 34.04% | 1494.9086 | 17.57% | 771.4551 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 45.63% | 2004.0097 | 28.59% | 1255.5054 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 65.51% | 2877.179 | 46.88% | 2059.1045 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 78.66% | 3454.933 | 69.68% | 3060.4836 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 83.41% | 3663.5664 | 76.64% | 3366.0403 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 87.95% | 3862.6894 | 83.93% | 3686.3454 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 93.87% | 4122.7381 | 91.73% | 4028.5841 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.55% | 4372.3849 | 98.93% | 4345.1076 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.6% | 4374.4653 | 99.75% | 4381.0332 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.61% | 4374.7625 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.63% | 4375.9513 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 1 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 2 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 3 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 4 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 5 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 6 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 7 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 8 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 1 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 3 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 4 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 5 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 6 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 7 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 8 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 1 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 2 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 3 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 4 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 7 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 8 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 76.03 | 92.9697 | 96.9652 | 102.1547 | 107.1807 | 111.6228 | 117.8415 | 124.6646 | 131.6591 | 138.5988 | 144.7369 | 151.4618 | 153.8617 | 162.6285 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162 | 171.7162
Maximum Demand (MVA) - P10 | 81.4198 | 98.381 | 102.6202 | 107.8771 | 112.7688 | 117.9961 | 123.5192 | 131.5147 | 138.4506 | 144.9877 | 151.7923 | 160.0115 | 162.5839 | 171.4673 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741 | 179.741
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 18 | 17.73 | 17.46 | 17.2 | 16.94 | 16.69 | 16.44 | 16.19 | 15.95 | 15.71 | 15.48 | 15.24 | 15.01 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79
Demand management (MVA) | 0 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 98.7086 | 114.7675 | 119.1778 | 122.6072 | 126.739 | 131.0082 | 135.5707 | 140.8303 | 147.0694 | 152.9101 | 159.0614 | 169.7232 | 173.173 | 179.9123 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199 | 185.0199
Maximum Demand (MVA) - P10 | 115.4409 | 131.6443 | 136.6765 | 140.8401 | 144.5054 | 150.445 | 155.7974 | 163.329 | 171.1932 | 177.5801 | 183.5896 | 192.6476 | 199.1534 | 205.7214 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038 | 212.7038
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 18 | 17.73 | 17.46 | 17.2 | 16.94 | 16.69 | 16.44 | 16.19 | 15.95 | 15.71 | 15.48 | 15.24 | 15.01 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79
Demand management (MVA) | 0 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471
Option 2 - 1A New PHS ZSS + Four new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 76.03 | 73.303 | 77.5685 | 68.528 | 73.8141 | 78.5161 | 84.9848 | 92.0579 | 99.3024 | 106.4821 | 112.8603 | 119.8151 | 122.4551 | 131.4518 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 81.4198 | 78.7143 | 83.2235 | 74.2505 | 79.4022 | 84.8894 | 90.6625 | 98.908 | 106.0939 | 112.8711 | 119.9157 | 128.3648 | 131.1773 | 140.2906 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 98.7086 | 95.1008 | 99.7811 | 88.9805 | 93.3723 | 97.9015 | 102.714 | 108.2236 | 114.7127 | 120.7934 | 127.1847 | 138.0766 | 141.7664 | 148.7356 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 115.4409 | 111.9776 | 117.2799 | 107.2134 | 111.1388 | 117.3383 | 122.9407 | 130.7223 | 138.8365 | 145.4635 | 151.7129 | 161.001 | 167.7468 | 174.5447 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 76.03 | 73.303 | 77.5685 | 63.6947 | 68.9807 | 73.6828 | 80.1515 | 87.2246 | 94.4691 | 101.6488 | 108.0269 | 114.9818 | 117.6217 | 126.6185 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 81.4198 | 78.7143 | 83.2235 | 69.4171 | 74.5688 | 80.0561 | 85.8292 | 94.0747 | 101.2606 | 108.0377 | 115.0823 | 123.5315 | 126.3439 | 135.4573 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 98.7086 | 95.1008 | 99.7811 | 84.1472 | 88.539 | 93.0682 | 97.8807 | 103.3903 | 109.8794 | 115.9601 | 122.3514 | 133.2432 | 136.933 | 143.9023 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 115.4409 | 111.9776 | 117.2799 | 102.3801 | 106.3054 | 112.505 | 118.1074 | 125.889 | 134.0032 | 140.6301 | 146.8796 | 156.1676 | 162.9134 | 169.7114 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471
Option 6 - Non Network
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 6.8848 | 7.8511 | 8.1512 | 8.3996 | 8.6182 | 8.9724 | 9.2916 | 9.7408 | 10.2098 | 10.5907 | 10.9491 | 11.4893 | 11.8773 | 12.269 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 69.1452 | 65.4519 | 69.4173 | 74.6284 | 79.6959 | 84.0438 | 90.1932 | 96.8172 | 103.5926 | 110.3915 | 116.4112 | 122.8258 | 125.0778 | 133.6828 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 74.5351 | 70.8632 | 75.0723 | 80.3509 | 85.284 | 90.4171 | 95.8709 | 103.6672 | 110.3841 | 116.7804 | 123.4666 | 131.3755 | 133.8 | 142.5216 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 91.8238 | 87.2497 | 91.6299 | 95.081 | 99.2542 | 103.4291 | 107.9224 | 112.9828 | 119.0029 | 124.7027 | 130.7356 | 141.0873 | 144.3891 | 150.9666 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 108.5561 | 104.1265 | 109.1286 | 113.3138 | 117.0206 | 122.866 | 128.1491 | 135.4815 | 143.1267 | 149.3728 | 155.2639 | 164.0117 | 170.3695 | 176.7757 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 100% | 0 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
99% | 0.5944 | 75.2697 | 72.57 | 76.7928 | 82.1977 | 87.4309 | 92.086 | 98.4899 | 105.4924 | 112.6644 | 119.7723 | 126.0867 | 132.972 | 135.5855 | 144.4923 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 99% | 0.5944 | 80.6056 | 77.9271 | 82.3913 | 87.863 | 92.9632 | 98.3955 | 104.1109 | 112.2739 | 119.388 | 126.0974 | 133.0715 | 141.4362 | 144.2205 | 153.2427 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515
98% | 0.8916 | 74.5094 | 71.8369 | 76.0171 | 81.3674 | 86.5478 | 91.1558 | 97.4951 | 104.4268 | 111.5264 | 118.5625 | 124.8131 | 131.6288 | 134.216 | 143.0328 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 98% | 0.8916 | 79.7914 | 77.14 | 81.5591 | 86.9755 | 92.0241 | 97.4016 | 103.0593 | 111.1398 | 118.182 | 124.8237 | 131.7273 | 140.0075 | 142.7637 | 151.6948 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186
97% | 1.486 | 73.7491 | 71.1039 | 75.2415 | 80.5371 | 85.6646 | 90.2257 | 96.5003 | 103.3612 | 110.3883 | 117.3527 | 123.5395 | 130.2857 | 132.8464 | 141.5732 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 97% | 1.486 | 78.9772 | 76.3529 | 80.7268 | 86.0879 | 91.0851 | 96.4077 | 102.0076 | 110.0058 | 116.9761 | 123.5499 | 130.3832 | 138.5789 | 141.307 | 150.1469 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858
95% | 2.3776 | 72.2285 | 69.6379 | 73.6901 | 78.8766 | 83.8984 | 88.3653 | 94.5106 | 101.23 | 108.1123 | 114.933 | 120.9923 | 127.5994 | 130.1073 | 138.6542 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 95% | 2.3776 | 77.3488 | 74.7786 | 79.0624 | 84.3129 | 89.2071 | 94.42 | 99.9044 | 107.7376 | 114.5642 | 121.0025 | 127.6949 | 135.7216 | 138.3934 | 147.0511 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201
90% | 3.2692 | 68.427 | 65.9727 | 69.8117 | 74.7252 | 79.4827 | 83.7145 | 89.5363 | 95.9021 | 102.4222 | 108.8839 | 114.6242 | 120.8836 | 123.2596 | 131.3566 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 90% | 3.2692 | 73.2778 | 70.8429 | 74.9012 | 79.8754 | 84.512 | 89.4505 | 94.6463 | 102.0672 | 108.5345 | 114.634 | 120.9741 | 128.5784 | 131.1095 | 139.3116 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559
85% | 13.9683 | 64.6255 | 62.3076 | 65.9332 | 70.5738 | 75.067 | 79.0637 | 84.5621 | 90.5743 | 96.732 | 102.8348 | 108.2562 | 114.1679 | 116.4118 | 124.059 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 85% | 13.9683 | 69.2069 | 66.9071 | 70.74 | 75.4379 | 79.8168 | 84.481 | 89.3881 | 96.3968 | 102.5048 | 108.2654 | 114.2533 | 121.4351 | 123.8257 | 131.572 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917
80% | 41.3106 | 60.824 | 58.6424 | 62.0548 | 66.4224 | 70.6513 | 74.4129 | 79.5878 | 85.2464 | 91.0419 | 96.7857 | 101.8882 | 107.4521 | 109.5641 | 116.7614 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 80% | 41.3106 | 65.1359 | 62.9714 | 66.5788 | 71.0004 | 75.1217 | 79.5115 | 84.13 | 90.7264 | 96.4751 | 101.8969 | 107.5325 | 114.2919 | 116.5418 | 123.8325 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274
75% | 126.3094 | 57.0225 | 54.9773 | 58.1764 | 62.271 | 66.2356 | 69.7621 | 74.6136 | 79.9185 | 85.3518 | 90.7366 | 95.5202 | 100.7363 | 102.7163 | 109.4638 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 75% | 126.3094 | 61.0649 | 59.0357 | 62.4177 | 66.5628 | 70.4266 | 74.5421 | 78.8719 | 85.056 | 90.4454 | 95.5283 | 100.8117 | 107.1486 | 109.258 | 116.093 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632
70% | 323.9464 | 53.221 | 51.3121 | 54.298 | 58.1196 | 61.8198 | 65.1113 | 69.6394 | 74.5906 | 79.6617 | 84.6875 | 89.1522 | 94.0206 | 95.8685 | 102.1663 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 70% | 323.9464 | 56.9939 | 55.1 | 58.2565 | 62.1253 | 65.7315 | 69.5726 | 73.6138 | 79.3856 | 84.4157 | 89.1598 | 94.091 | 100.0054 | 101.9741 | 108.3534 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299
65% | 549.5201 | 49.4195 | 47.647 | 50.4195 | 53.9682 | 57.4041 | 60.4605 | 64.6651 | 69.2627 | 73.9716 | 78.6384 | 82.7842 | 87.3048 | 89.0208 | 94.8687 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 65% | 549.5201 | 52.9229 | 51.1643 | 54.0953 | 57.6878 | 61.0364 | 64.6031 | 68.3556 | 73.7152 | 78.386 | 82.7912 | 87.3702 | 92.8621 | 94.6902 | 100.6139 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348
60% | 799.4641 | 45.618 | 43.9818 | 46.5411 | 49.8168 | 52.9884 | 55.8097 | 59.6909 | 63.9348 | 68.2814 | 72.5893 | 76.4162 | 80.5891 | 82.173 | 87.5711 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 60% | 799.4641 | 48.8519 | 47.2286 | 49.9341 | 53.2503 | 56.3413 | 59.6337 | 63.0975 | 68.0448 | 72.3563 | 76.4226 | 80.6494 | 85.7189 | 87.4064 | 92.8744 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706
55% | 1116.2777 | 41.8165 | 40.3167 | 42.6627 | 45.6654 | 48.5727 | 51.1589 | 54.7166 | 58.6069 | 62.5913 | 66.5402 | 70.0481 | 73.8733 | 75.3253 | 80.2735 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 55% | 1116.2777 | 44.7809 | 43.2929 | 45.773 | 48.8128 | 51.6462 | 54.6642 | 57.8394 | 62.3744 | 66.3266 | 70.0541 | 73.9286 | 78.5757 | 80.1225 | 85.1348 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064
50% | 1494.9086 | 38.015 | 36.6515 | 38.7843 | 41.514 | 44.157 | 46.5081 | 49.7424 | 53.279 | 56.9012 | 60.4911 | 63.6801 | 67.1576 | 68.4775 | 72.9759 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 50% | 1494.9086 | 40.7099 | 39.3571 | 41.6118 | 44.3752 | 46.9511 | 49.6947 | 52.5813 | 56.704 | 60.297 | 63.6855 | 67.2078 | 71.4324 | 72.8386 | 77.3953 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422
45% | 2004.0097 | 34.2135 | 32.9864 | 34.9058 | 37.3626 | 39.7413 | 41.8573 | 44.7682 | 47.9511 | 51.2111 | 54.442 | 57.3121 | 60.4418 | 61.6298 | 65.6783 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 45% | 2004.0097 | 36.6389 | 35.4214 | 37.4506 | 39.9377 | 42.256 | 44.7252 | 47.3231 | 51.0336 | 54.2673 | 57.317 | 60.487 | 64.2892 | 65.5548 | 69.6558 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779
40% | 2877.179 | 30.412 | 29.3212 | 31.0274 | 33.2112 | 35.3256 | 37.2065 | 39.7939 | 42.6232 | 45.521 | 48.3929 | 50.9441 | 53.7261 | 54.782 | 58.3807 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 40% | 2877.179 | 32.5679 | 31.4857 | 33.2894 | 35.5002 | 37.5609 | 39.7558 | 42.065 | 45.3632 | 48.2376 | 50.9484 | 53.7663 | 57.1459 | 58.2709 | 61.9162 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137
35% | 3454.933 | 26.6105 | 25.6561 | 27.149 | 29.0598 | 30.9099 | 32.5556 | 34.8197 | 37.2953 | 39.8308 | 42.3438 | 44.5761 | 47.0103 | 47.9343 | 51.0831 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 35% | 3454.933 | 28.4969 | 27.55 | 29.1282 | 31.0627 | 32.8658 | 34.7863 | 36.8069 | 39.6928 | 42.2079 | 44.5799 | 47.0455 | 50.0027 | 50.987 | 54.1767 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495
30% | 3663.5664 | 22.809 | 21.9909 | 23.2706 | 24.9084 | 26.4942 | 27.9048 | 29.8454 | 31.9674 | 34.1407 | 36.2946 | 38.2081 | 40.2945 | 41.0865 | 43.7855 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 30% | 3663.5664 | 24.4259 | 23.6143 | 24.9671 | 26.6251 | 28.1707 | 29.8168 | 31.5488 | 34.0224 | 36.1782 | 38.2113 | 40.3247 | 42.8595 | 43.7032 | 46.4372 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853
25% | 3862.6894 | 19.0075 | 18.3258 | 19.3921 | 20.757 | 22.0785 | 23.254 | 24.8712 | 26.6395 | 28.4506 | 30.2455 | 31.8401 | 33.5788 | 34.2388 | 36.4879 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 25% | 3862.6894 | 20.355 | 19.6786 | 20.8059 | 22.1876 | 23.4755 | 24.8474 | 26.2906 | 28.352 | 30.1485 | 31.8428 | 33.6039 | 35.7162 | 36.4193 | 38.6977 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211
20% | 4122.7381 | 15.206 | 14.6606 | 15.5137 | 16.6056 | 17.6628 | 18.6032 | 19.897 | 21.3116 | 22.7605 | 24.1964 | 25.4721 | 26.863 | 27.391 | 29.1904 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 20% | 4122.7381 | 16.284 | 15.7429 | 16.6447 | 17.7501 | 18.7804 | 19.8779 | 21.0325 | 22.6816 | 24.1188 | 25.4742 | 26.8831 | 28.573 | 29.1355 | 30.9581 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569
15% | 4372.3849 | 11.4045 | 10.9955 | 11.6353 | 12.4542 | 13.2471 | 13.9524 | 14.9227 | 15.9837 | 17.0704 | 18.1473 | 19.104 | 20.1473 | 20.5433 | 21.8928 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 15% | 4372.3849 | 12.213 | 11.8071 | 12.4835 | 13.3126 | 14.0853 | 14.9084 | 15.7744 | 17.0112 | 18.0891 | 19.1057 | 20.1623 | 21.4297 | 21.8516 | 23.2186 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926
10% | 4374.4653 | 7.603 | 7.3303 | 7.7569 | 8.3028 | 8.8314 | 9.3016 | 9.9485 | 10.6558 | 11.3802 | 12.0982 | 12.736 | 13.4315 | 13.6955 | 14.5952 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 10% | 4374.4653 | 8.142 | 7.8714 | 8.3224 | 8.875 | 9.3902 | 9.9389 | 10.5163 | 11.3408 | 12.0594 | 12.7371 | 13.4416 | 14.2865 | 14.5677 | 15.4791 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284
5% | 4374.7625 | 3.8015 | 3.6652 | 3.8784 | 4.1514 | 4.4157 | 4.6508 | 4.9742 | 5.3279 | 5.6901 | 6.0491 | 6.368 | 6.7158 | 6.8478 | 7.2976 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 5% | 4374.7625 | 4.071 | 3.9357 | 4.1612 | 4.4375 | 4.6951 | 4.9695 | 5.2581 | 5.6704 | 6.0297 | 6.3686 | 6.7208 | 7.1432 | 7.2839 | 7.7395 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642
9.992e-14% | 4375.9513 | 7.5969e-14 | 7.3244e-14 | 7.7507e-14 | 8.2962e-14 | 8.8243e-14 | 9.2942e-14 | 9.9405e-14 | 1.0647e-13 | 1.1371e-13 | 1.2089e-13 | 1.2726e-13 | 1.3421e-13 | 1.3685e-13 | 1.4584e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 9.992e-14% | 4375.9513 | 8.1355e-14 | 7.8651e-14 | 8.3157e-14 | 8.868e-14 | 9.3827e-14 | 9.931e-14 | 1.0508e-13 | 1.1332e-13 | 1.205e-13 | 1.2727e-13 | 1.3431e-13 | 1.4275e-13 | 1.4556e-13 | 1.5467e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 100% | 0 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471
99% | 0 | 97.7215 | 94.1498 | 98.7833 | 102.4457 | 106.7936 | 111.2775 | 116.0419 | 121.4964 | 127.9206 | 133.9405 | 140.2679 | 151.0508 | 154.7037 | 161.6032 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 99% | 0.37816 | 114.2865 | 110.8579 | 116.1071 | 120.4963 | 124.3824 | 130.52 | 136.0663 | 143.7701 | 151.8031 | 158.3638 | 164.5508 | 173.746 | 180.4243 | 187.1543 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846
98% | 0.37816 | 96.7344 | 93.1988 | 97.7855 | 101.4109 | 105.7149 | 110.1535 | 114.8697 | 120.2691 | 126.6285 | 132.5876 | 138.851 | 149.525 | 153.1411 | 159.9709 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 98% | 1.1345 | 113.1321 | 109.7381 | 114.9343 | 119.2791 | 123.126 | 129.2016 | 134.6919 | 142.3179 | 150.2698 | 156.7642 | 162.8887 | 171.991 | 178.6018 | 185.2638 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222
97% | 0.75633 | 95.7473 | 92.2478 | 96.7877 | 100.3761 | 104.6362 | 109.0295 | 113.6976 | 119.0419 | 125.3363 | 131.2346 | 137.4342 | 147.9993 | 151.5784 | 158.3385 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 97% | 2.269 | 111.9777 | 108.6183 | 113.7615 | 118.062 | 121.8696 | 127.8832 | 133.3175 | 140.8656 | 148.7364 | 155.1646 | 161.2266 | 170.236 | 176.7794 | 183.3734 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597
95% | 1.1345 | 93.7731 | 90.3458 | 94.7921 | 98.3065 | 102.4787 | 106.7814 | 111.3533 | 116.5874 | 122.7521 | 128.5288 | 134.6005 | 144.9477 | 148.4531 | 155.0738 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 95% | 4.538 | 109.6689 | 106.3788 | 111.4159 | 115.6277 | 119.3568 | 125.2464 | 130.5687 | 137.9612 | 145.6697 | 151.9653 | 157.9023 | 166.7259 | 173.1344 | 179.5925 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347
90% | 4.538 | 88.8377 | 85.5907 | 89.803 | 93.1325 | 97.0851 | 101.1614 | 105.4926 | 110.4512 | 116.2914 | 121.7641 | 127.5162 | 137.3189 | 140.6397 | 146.912 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 90% | 7.9414 | 103.8968 | 100.7799 | 105.5519 | 109.5421 | 113.0749 | 118.6545 | 123.6966 | 130.7001 | 138.0029 | 143.9671 | 149.5917 | 157.9509 | 164.0221 | 170.1403 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224
85% | 7.9414 | 83.9023 | 80.8357 | 84.814 | 87.9585 | 91.6915 | 95.5413 | 99.6319 | 104.3151 | 109.8308 | 114.9994 | 120.432 | 129.6901 | 132.8264 | 138.7503 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 85% | 14.3702 | 98.1248 | 95.181 | 99.6879 | 103.4564 | 106.7929 | 112.0626 | 116.8246 | 123.439 | 130.336 | 135.969 | 141.281 | 149.1758 | 154.9097 | 160.688 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81
80% | 11.7231 | 78.9669 | 76.0807 | 79.8249 | 82.7844 | 86.2979 | 89.9212 | 93.7712 | 98.1789 | 103.3702 | 108.2347 | 113.3478 | 122.0613 | 125.0131 | 130.5885 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 80% | 19.6645 | 92.3527 | 89.5821 | 93.8239 | 97.3707 | 100.511 | 105.4707 | 109.9526 | 116.1778 | 122.6692 | 127.9708 | 132.9704 | 140.4008 | 145.7974 | 151.2358 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977
75% | 17.7737 | 74.0314 | 71.3256 | 74.8358 | 77.6104 | 80.9042 | 84.3011 | 87.9105 | 92.0427 | 96.9095 | 101.4701 | 106.2635 | 114.4324 | 117.1998 | 122.4267 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 75% | 25.7152 | 86.5807 | 83.9832 | 87.9599 | 91.285 | 94.2291 | 98.8788 | 103.0805 | 108.9167 | 115.0024 | 119.9726 | 124.6597 | 131.6257 | 136.6851 | 141.7836 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853
70% | 35.1693 | 69.096 | 66.5706 | 69.8468 | 72.4364 | 75.5106 | 78.6811 | 82.0498 | 85.9065 | 90.4489 | 94.7054 | 99.1793 | 106.8036 | 109.3865 | 114.2649 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 70% | 34.7911 | 80.8086 | 78.3843 | 82.0959 | 85.1994 | 87.9471 | 92.2868 | 96.2085 | 101.6556 | 107.3356 | 111.9744 | 116.3491 | 122.8507 | 127.5727 | 132.3313 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373
65% | 59.3718 | 64.1606 | 61.8155 | 64.8577 | 67.2623 | 70.117 | 73.061 | 76.1891 | 79.7703 | 83.9883 | 87.9407 | 92.0951 | 99.1748 | 101.5731 | 106.1031 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 65% | 46.136 | 75.0366 | 72.7855 | 76.2319 | 79.1137 | 81.6652 | 85.6949 | 89.3364 | 94.3945 | 99.6687 | 103.9763 | 108.0384 | 114.0756 | 118.4604 | 122.8791 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606
60% | 156.9382 | 59.2251 | 57.0605 | 59.8687 | 62.0883 | 64.7234 | 67.4409 | 70.3284 | 73.6342 | 77.5276 | 81.1761 | 85.0108 | 91.5459 | 93.7598 | 97.9414 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 60% | 76.7673 | 69.2645 | 67.1866 | 70.3679 | 73.028 | 75.3833 | 79.103 | 82.4644 | 87.1334 | 92.0019 | 95.9781 | 99.7278 | 105.3006 | 109.3481 | 113.4268 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483
55% | 363.794 | 54.2897 | 52.3055 | 54.8796 | 56.9143 | 59.3298 | 61.8208 | 64.4677 | 67.498 | 71.067 | 74.4114 | 77.9266 | 83.9171 | 85.9465 | 89.7796 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 55% | 106.2642 | 63.4925 | 61.5877 | 64.5039 | 66.9424 | 69.1013 | 72.5111 | 75.5924 | 79.8723 | 84.3351 | 87.9799 | 91.4171 | 96.5255 | 100.2357 | 103.9746 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359
50% | 771.4551 | 49.3543 | 47.5504 | 49.8906 | 51.7403 | 53.9362 | 56.2008 | 58.607 | 61.3618 | 64.6064 | 67.6467 | 70.8424 | 76.2883 | 78.1332 | 81.6178 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 50% | 178.4935 | 57.7205 | 55.9888 | 58.6399 | 60.8567 | 62.8194 | 65.9192 | 68.7203 | 72.6112 | 76.6683 | 79.9817 | 83.1065 | 87.7505 | 91.1234 | 94.5224 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235
45% | 1255.5054 | 44.4189 | 42.7954 | 44.9015 | 46.5662 | 48.5425 | 50.5807 | 52.7463 | 55.2256 | 58.1457 | 60.882 | 63.7581 | 68.6595 | 70.3199 | 73.456 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 45% | 367.9538 | 51.9484 | 50.3899 | 52.7759 | 54.771 | 56.5374 | 59.3273 | 61.8483 | 65.35 | 69.0014 | 71.9836 | 74.7958 | 78.9754 | 82.011 | 85.0701 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112
40% | 2059.1045 | 39.4834 | 38.0403 | 39.9125 | 41.3922 | 43.1489 | 44.9606 | 46.8856 | 49.0894 | 51.6851 | 54.1174 | 56.6739 | 61.0306 | 62.5066 | 65.2942 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 40% | 741.202 | 46.1764 | 44.7911 | 46.9119 | 48.6854 | 50.2555 | 52.7353 | 54.9763 | 58.0889 | 61.3346 | 63.9854 | 66.4852 | 70.2004 | 72.8987 | 75.6179 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988
35% | 3060.4836 | 34.548 | 33.2853 | 34.9234 | 36.2182 | 37.7553 | 39.3405 | 41.0249 | 42.9533 | 45.2244 | 47.3527 | 49.5897 | 53.4018 | 54.6932 | 57.1325 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 35% | 1167.7713 | 40.4043 | 39.1922 | 41.048 | 42.5997 | 43.9736 | 46.1434 | 48.1042 | 50.8278 | 53.6678 | 55.9872 | 58.1745 | 61.4253 | 63.7864 | 66.1657 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865
30% | 3366.0403 | 29.6126 | 28.5302 | 29.9343 | 31.0442 | 32.3617 | 33.7205 | 35.1642 | 36.8171 | 38.7638 | 40.588 | 42.5054 | 45.773 | 46.8799 | 48.9707 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 30% | 2002.3799 | 34.6323 | 33.5933 | 35.184 | 36.514 | 37.6916 | 39.5515 | 41.2322 | 43.5667 | 46.001 | 47.989 | 49.8639 | 52.6503 | 54.674 | 56.7134 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741
25% | 3686.3454 | 24.6771 | 23.7752 | 24.9453 | 25.8701 | 26.9681 | 28.1004 | 29.3035 | 30.6809 | 32.3032 | 33.8234 | 35.4212 | 38.1441 | 39.0666 | 40.8089 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 25% | 3173.5547 | 28.8602 | 27.9944 | 29.32 | 30.4283 | 31.4097 | 32.9596 | 34.3602 | 36.3056 | 38.3341 | 39.9909 | 41.5532 | 43.8752 | 45.5617 | 47.2612 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618
20% | 4028.5841 | 19.7417 | 19.0202 | 19.9562 | 20.6961 | 21.5745 | 22.4803 | 23.4428 | 24.5447 | 25.8425 | 27.0587 | 28.3369 | 30.5153 | 31.2533 | 32.6471 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 20% | 3477.5988 | 23.0882 | 22.3955 | 23.456 | 24.3427 | 25.1278 | 26.3677 | 27.4881 | 29.0445 | 30.6673 | 31.9927 | 33.2426 | 35.1002 | 36.4494 | 37.8089 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494
15% | 4345.1076 | 14.8063 | 14.2651 | 14.9672 | 15.5221 | 16.1808 | 16.8602 | 17.5821 | 18.4085 | 19.3819 | 20.294 | 21.2527 | 22.8865 | 23.44 | 24.4853 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 15% | 3788.4498 | 17.3161 | 16.7966 | 17.592 | 18.257 | 18.8458 | 19.7758 | 20.6161 | 21.7833 | 23.0005 | 23.9945 | 24.9319 | 26.3251 | 27.337 | 28.3567 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371
10% | 4381.0332 | 9.8709 | 9.5101 | 9.9781 | 10.3481 | 10.7872 | 11.2402 | 11.7214 | 12.2724 | 12.9213 | 13.5293 | 14.1685 | 15.2577 | 15.6266 | 16.3236 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 10% | 4317.5016 | 11.5441 | 11.1978 | 11.728 | 12.1713 | 12.5639 | 13.1838 | 13.7441 | 14.5222 | 15.3337 | 15.9963 | 16.6213 | 17.5501 | 18.2247 | 18.9045 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247
5% | 4391.6218 | 4.9354 | 4.755 | 4.9891 | 5.174 | 5.3936 | 5.6201 | 5.8607 | 6.1362 | 6.4606 | 6.7647 | 7.0842 | 7.6288 | 7.8133 | 8.1618 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 5% | 4391.6218 | 5.772 | 5.5989 | 5.864 | 6.0857 | 6.2819 | 6.5919 | 6.872 | 7.2611 | 7.6668 | 7.9982 | 8.3106 | 8.775 | 9.1123 | 9.4522 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124
9.992e-14% | 4391.6218 | 9.863e-14 | 9.5025e-14 | 9.9701e-14 | 1.034e-13 | 1.0779e-13 | 1.1231e-13 | 1.1712e-13 | 1.2263e-13 | 1.2911e-13 | 1.3519e-13 | 1.4157e-13 | 1.5245e-13 | 1.5614e-13 | 1.6311e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 9.992e-14% | 4391.6218 | 1.1535e-13 | 1.1189e-13 | 1.1719e-13 | 1.2162e-13 | 1.2554e-13 | 1.3173e-13 | 1.3733e-13 | 1.4511e-13 | 1.5321e-13 | 1.5984e-13 | 1.6608e-13 | 1.7536e-13 | 1.821e-13 | 1.8889e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 76.03 | 73.303 | 77.5685 | 68.528 | 73.8141 | 78.5161 | 84.9848 | 92.0579 | 99.3024 | 106.4821 | 112.8603 | 119.8151 | 122.4551 | 131.4518 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 140.7595 | 100% | 0 | 81.4198 | 78.7143 | 83.2235 | 74.2505 | 79.4022 | 84.8894 | 90.6625 | 98.908 | 106.0939 | 112.8711 | 119.9157 | 128.3648 | 131.1773 | 140.2906 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843 | 148.7843
99% | 0.5944 | 75.2697 | 72.57 | 76.7928 | 67.8427 | 73.0759 | 77.731 | 84.1349 | 91.1374 | 98.3094 | 105.4173 | 111.7317 | 118.617 | 121.2305 | 130.1373 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 139.3519 | 99% | 0.5944 | 80.6056 | 77.9271 | 82.3913 | 73.508 | 78.6082 | 84.0405 | 89.7559 | 97.9189 | 105.033 | 111.7424 | 118.7165 | 127.0812 | 129.8655 | 138.8877 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965 | 147.2965
98% | 0.8916 | 74.5094 | 71.8369 | 76.0171 | 67.1574 | 72.3378 | 76.9458 | 83.2851 | 90.2168 | 97.3164 | 104.3525 | 110.6031 | 117.4188 | 120.006 | 128.8228 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 137.9443 | 98% | 0.8916 | 79.7914 | 77.14 | 81.5591 | 72.7655 | 77.8141 | 83.1916 | 88.8493 | 96.9298 | 103.972 | 110.6137 | 117.5173 | 125.7975 | 128.5537 | 137.4848 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086 | 145.8086
97% | 1.486 | 73.7491 | 71.1039 | 75.2415 | 66.4721 | 71.5996 | 76.1607 | 82.4353 | 89.2962 | 96.3233 | 103.2877 | 109.4745 | 116.2207 | 118.7814 | 127.5082 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 136.5367 | 97% | 1.486 | 78.9772 | 76.3529 | 80.7268 | 72.0229 | 77.0201 | 82.3427 | 87.9426 | 95.9408 | 102.9111 | 109.4849 | 116.3182 | 124.5139 | 127.242 | 136.0819 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208 | 144.3208
95% | 2.3776 | 72.2285 | 69.6379 | 73.6901 | 65.1016 | 70.1234 | 74.5903 | 80.7356 | 87.455 | 94.3373 | 101.158 | 107.2173 | 113.8244 | 116.3323 | 124.8792 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 133.7215 | 95% | 2.3776 | 77.3488 | 74.7786 | 79.0624 | 70.5379 | 75.4321 | 80.645 | 86.1294 | 93.9626 | 100.7892 | 107.2275 | 113.9199 | 121.9466 | 124.6184 | 133.2761 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451 | 141.3451
90% | 3.2692 | 68.427 | 65.9727 | 69.8117 | 61.6752 | 66.4327 | 70.6645 | 76.4863 | 82.8521 | 89.3722 | 95.8339 | 101.5742 | 107.8336 | 110.2096 | 118.3066 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 126.6836 | 90% | 3.2692 | 73.2778 | 70.8429 | 74.9012 | 66.8254 | 71.462 | 76.4005 | 81.5963 | 89.0172 | 95.4845 | 101.584 | 107.9241 | 115.5284 | 118.0595 | 126.2616 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059 | 133.9059
85% | 13.9683 | 64.6255 | 62.3076 | 65.9332 | 58.2488 | 62.742 | 66.7387 | 72.2371 | 78.2493 | 84.407 | 90.5098 | 95.9312 | 101.8429 | 104.0868 | 111.734 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 119.6456 | 85% | 13.9683 | 69.2069 | 66.9071 | 70.74 | 63.1129 | 67.4918 | 72.156 | 77.0631 | 84.0718 | 90.1798 | 95.9404 | 101.9283 | 109.1101 | 111.5007 | 119.247 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667 | 126.4667
80% | 41.3106 | 60.824 | 58.6424 | 62.0548 | 54.8224 | 59.0513 | 62.8129 | 67.9878 | 73.6464 | 79.4419 | 85.1857 | 90.2882 | 95.8521 | 97.9641 | 105.1614 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 112.6076 | 80% | 41.3106 | 65.1359 | 62.9714 | 66.5788 | 59.4004 | 63.5217 | 67.9115 | 72.53 | 79.1264 | 84.8751 | 90.2969 | 95.9325 | 102.6919 | 104.9418 | 112.2325 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274 | 119.0274
75% | 126.3094 | 57.0225 | 54.9773 | 58.1764 | 51.396 | 55.3606 | 58.8871 | 63.7386 | 69.0435 | 74.4768 | 79.8616 | 84.6452 | 89.8613 | 91.8413 | 98.5888 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 105.5696 | 75% | 126.3094 | 61.0649 | 59.0357 | 62.4177 | 55.6878 | 59.5516 | 63.6671 | 67.9969 | 74.181 | 79.5704 | 84.6533 | 89.9367 | 96.2736 | 98.383 | 105.218 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882 | 111.5882
70% | 323.9464 | 53.221 | 51.3121 | 54.298 | 47.9696 | 51.6698 | 54.9613 | 59.4894 | 64.4406 | 69.5117 | 74.5375 | 79.0022 | 83.8706 | 85.7185 | 92.0163 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 98.5317 | 70% | 323.9464 | 56.9939 | 55.1 | 58.2565 | 51.9753 | 55.5815 | 59.4226 | 63.4638 | 69.2356 | 74.2657 | 79.0098 | 83.941 | 89.8554 | 91.8241 | 98.2034 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149 | 104.149
65% | 549.5201 | 49.4195 | 47.647 | 50.4195 | 44.5432 | 47.9791 | 51.0355 | 55.2401 | 59.8377 | 64.5466 | 69.2134 | 73.3592 | 77.8798 | 79.5958 | 85.4437 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 91.4937 | 65% | 549.5201 | 52.9229 | 51.1643 | 54.0953 | 48.2628 | 51.6114 | 55.1781 | 58.9306 | 64.2902 | 68.961 | 73.3662 | 77.9452 | 83.4371 | 85.2652 | 91.1889 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098 | 96.7098
60% | 799.4641 | 45.618 | 43.9818 | 46.5411 | 41.1168 | 44.2884 | 47.1097 | 50.9909 | 55.2348 | 59.5814 | 63.8893 | 67.7162 | 71.8891 | 73.473 | 78.8711 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 84.4557 | 60% | 799.4641 | 48.8519 | 47.2286 | 49.9341 | 44.5503 | 47.6413 | 50.9337 | 54.3975 | 59.3448 | 63.6563 | 67.7226 | 71.9494 | 77.0189 | 78.7064 | 84.1744 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706 | 89.2706
55% | 1116.2777 | 41.8165 | 40.3167 | 42.6627 | 37.6904 | 40.5977 | 43.1839 | 46.7416 | 50.6319 | 54.6163 | 58.5652 | 62.0731 | 65.8983 | 67.3503 | 72.2985 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 77.4177 | 55% | 1116.2777 | 44.7809 | 43.2929 | 45.773 | 40.8378 | 43.6712 | 46.6892 | 49.8644 | 54.3994 | 58.3516 | 62.0791 | 65.9536 | 70.6007 | 72.1475 | 77.1598 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314 | 81.8314
50% | 1494.9086 | 38.015 | 36.6515 | 38.7843 | 34.264 | 36.907 | 39.2581 | 42.4924 | 46.029 | 49.6512 | 53.2411 | 56.4301 | 59.9076 | 61.2275 | 65.7259 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 70.3798 | 50% | 1494.9086 | 40.7099 | 39.3571 | 41.6118 | 37.1252 | 39.7011 | 42.4447 | 45.3313 | 49.454 | 53.047 | 56.4355 | 59.9578 | 64.1824 | 65.5886 | 70.1453 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922 | 74.3922
45% | 2004.0097 | 34.2135 | 32.9864 | 34.9058 | 30.8376 | 33.2163 | 35.3323 | 38.2432 | 41.4261 | 44.6861 | 47.917 | 50.7871 | 53.9168 | 55.1048 | 59.1533 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 63.3418 | 45% | 2004.0097 | 36.6389 | 35.4214 | 37.4506 | 33.4127 | 35.731 | 38.2002 | 40.7981 | 44.5086 | 47.7423 | 50.792 | 53.962 | 57.7642 | 59.0298 | 63.1308 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529 | 66.9529
40% | 2877.179 | 30.412 | 29.3212 | 31.0274 | 27.4112 | 29.5256 | 31.4065 | 33.9939 | 36.8232 | 39.721 | 42.5929 | 45.1441 | 47.9261 | 48.982 | 52.5807 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 56.3038 | 40% | 2877.179 | 32.5679 | 31.4857 | 33.2894 | 29.7002 | 31.7609 | 33.9558 | 36.265 | 39.5632 | 42.4376 | 45.1484 | 47.9663 | 51.3459 | 52.4709 | 56.1162 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137 | 59.5137
35% | 3454.933 | 26.6105 | 25.6561 | 27.149 | 23.9848 | 25.8349 | 27.4806 | 29.7447 | 32.2203 | 34.7558 | 37.2688 | 39.5011 | 41.9353 | 42.8593 | 46.0081 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 49.2658 | 35% | 3454.933 | 28.4969 | 27.55 | 29.1282 | 25.9877 | 27.7908 | 29.7113 | 31.7319 | 34.6178 | 37.1329 | 39.5049 | 41.9705 | 44.9277 | 45.912 | 49.1017 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745 | 52.0745
30% | 3663.5664 | 22.809 | 21.9909 | 23.2706 | 20.5584 | 22.1442 | 23.5548 | 25.4954 | 27.6174 | 29.7907 | 31.9446 | 33.8581 | 35.9445 | 36.7365 | 39.4355 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 42.2279 | 30% | 3663.5664 | 24.4259 | 23.6143 | 24.9671 | 22.2751 | 23.8207 | 25.4668 | 27.1988 | 29.6724 | 31.8282 | 33.8613 | 35.9747 | 38.5095 | 39.3532 | 42.0872 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353 | 44.6353
25% | 3862.6894 | 19.0075 | 18.3258 | 19.3921 | 17.132 | 18.4535 | 19.629 | 21.2462 | 23.0145 | 24.8256 | 26.6205 | 28.2151 | 29.9538 | 30.6138 | 32.8629 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 35.1899 | 25% | 3862.6894 | 20.355 | 19.6786 | 20.8059 | 18.5626 | 19.8505 | 21.2224 | 22.6656 | 24.727 | 26.5235 | 28.2178 | 29.9789 | 32.0912 | 32.7943 | 35.0727 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961 | 37.1961
20% | 4122.7381 | 15.206 | 14.6606 | 15.5137 | 13.7056 | 14.7628 | 15.7032 | 16.997 | 18.4116 | 19.8605 | 21.2964 | 22.5721 | 23.963 | 24.491 | 26.2904 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 28.1519 | 20% | 4122.7381 | 16.284 | 15.7429 | 16.6447 | 14.8501 | 15.8804 | 16.9779 | 18.1325 | 19.7816 | 21.2188 | 22.5742 | 23.9831 | 25.673 | 26.2355 | 28.0581 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569 | 29.7569
15% | 4372.3849 | 11.4045 | 10.9955 | 11.6353 | 10.2792 | 11.0721 | 11.7774 | 12.7477 | 13.8087 | 14.8954 | 15.9723 | 16.929 | 17.9723 | 18.3683 | 19.7178 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 21.1139 | 15% | 4372.3849 | 12.213 | 11.8071 | 12.4835 | 11.1376 | 11.9103 | 12.7334 | 13.5994 | 14.8362 | 15.9141 | 16.9307 | 17.9873 | 19.2547 | 19.6766 | 21.0436 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176 | 22.3176
10% | 4374.4653 | 7.603 | 7.3303 | 7.7569 | 6.8528 | 7.3814 | 7.8516 | 8.4985 | 9.2058 | 9.9302 | 10.6482 | 11.286 | 11.9815 | 12.2455 | 13.1452 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 14.076 | 10% | 4374.4653 | 8.142 | 7.8714 | 8.3224 | 7.425 | 7.9402 | 8.4889 | 9.0663 | 9.8908 | 10.6094 | 11.2871 | 11.9916 | 12.8365 | 13.1177 | 14.0291 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784 | 14.8784
5% | 4374.7625 | 3.8015 | 3.6652 | 3.8784 | 3.4264 | 3.6907 | 3.9258 | 4.2492 | 4.6029 | 4.9651 | 5.3241 | 5.643 | 5.9908 | 6.1228 | 6.5726 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 7.038 | 5% | 4374.7625 | 4.071 | 3.9357 | 4.1612 | 3.7125 | 3.9701 | 4.2445 | 4.5331 | 4.9454 | 5.3047 | 5.6436 | 5.9958 | 6.4182 | 6.5589 | 7.0145 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392 | 7.4392
9.992e-14% | 4375.9513 | 7.5969e-14 | 7.3244e-14 | 7.7507e-14 | 6.8473e-14 | 7.3755e-14 | 7.8453e-14 | 8.4917e-14 | 9.1984e-14 | 9.9223e-14 | 1.064e-13 | 1.1277e-13 | 1.1972e-13 | 1.2236e-13 | 1.3135e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 1.4065e-13 | 9.992e-14% | 4375.9513 | 8.1355e-14 | 7.8651e-14 | 8.3157e-14 | 7.4191e-14 | 7.9339e-14 | 8.4822e-14 | 9.059e-14 | 9.8829e-14 | 1.0601e-13 | 1.1278e-13 | 1.1982e-13 | 1.2826e-13 | 1.3107e-13 | 1.4018e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13 | 1.4867e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 98.7086 | 95.1008 | 99.7811 | 88.9805 | 93.3723 | 97.9015 | 102.714 | 108.2236 | 114.7127 | 120.7934 | 127.1847 | 138.0766 | 141.7664 | 148.7356 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 154.0632 | 100% | 0 | 115.4409 | 111.9776 | 117.2799 | 107.2134 | 111.1388 | 117.3383 | 122.9407 | 130.7223 | 138.8365 | 145.4635 | 151.7129 | 161.001 | 167.7468 | 174.5447 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471 | 181.7471
99% | 0 | 97.7215 | 94.1498 | 98.7833 | 88.0907 | 92.4386 | 96.9225 | 101.6869 | 107.1414 | 113.5656 | 119.5855 | 125.9129 | 136.6958 | 140.3487 | 147.2482 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 152.5226 | 99% | 0.37816 | 114.2865 | 110.8579 | 116.1071 | 106.1413 | 110.0274 | 116.165 | 121.7113 | 129.4151 | 137.4481 | 144.0088 | 150.1958 | 159.391 | 166.0693 | 172.7993 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296 | 179.9296
98% | 0.37816 | 96.7344 | 93.1988 | 97.7855 | 87.2009 | 91.5049 | 95.9435 | 100.6597 | 106.0591 | 112.4185 | 118.3776 | 124.641 | 135.315 | 138.9311 | 145.7609 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 150.9819 | 98% | 1.1345 | 113.1321 | 109.7381 | 114.9343 | 105.0691 | 108.916 | 114.9916 | 120.4819 | 128.1079 | 136.0598 | 142.5542 | 148.6787 | 157.781 | 164.3918 | 171.0538 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122 | 178.1122
97% | 0.75633 | 95.7473 | 92.2478 | 96.7877 | 86.3111 | 90.5712 | 94.9645 | 99.6326 | 104.9769 | 111.2713 | 117.1696 | 123.3692 | 133.9343 | 137.5134 | 144.2735 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 149.4413 | 97% | 2.269 | 111.9777 | 108.6183 | 113.7615 | 103.997 | 107.8046 | 113.8182 | 119.2525 | 126.8006 | 134.6714 | 141.0996 | 147.1616 | 156.171 | 162.7144 | 169.3084 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947 | 176.2947
95% | 1.1345 | 93.7731 | 90.3458 | 94.7921 | 84.5315 | 88.7037 | 93.0064 | 97.5783 | 102.8124 | 108.9771 | 114.7538 | 120.8255 | 131.1727 | 134.6781 | 141.2988 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 146.36 | 95% | 4.538 | 109.6689 | 106.3788 | 111.4159 | 101.8527 | 105.5818 | 111.4714 | 116.7937 | 124.1862 | 131.8947 | 138.1903 | 144.1273 | 152.9509 | 159.3594 | 165.8175 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597 | 172.6597
90% | 4.538 | 88.8377 | 85.5907 | 89.803 | 80.0825 | 84.0351 | 88.1114 | 92.4426 | 97.4012 | 103.2414 | 108.7141 | 114.4662 | 124.2689 | 127.5897 | 133.862 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 138.6569 | 90% | 7.9414 | 103.8968 | 100.7799 | 105.5519 | 96.4921 | 100.0249 | 105.6045 | 110.6466 | 117.6501 | 124.9529 | 130.9171 | 136.5417 | 144.9009 | 150.9721 | 157.0903 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724 | 163.5724
85% | 7.9414 | 83.9023 | 80.8357 | 84.814 | 75.6335 | 79.3665 | 83.2163 | 87.3069 | 91.9901 | 97.5058 | 102.6744 | 108.107 | 117.3651 | 120.5014 | 126.4253 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 130.9537 | 85% | 14.3702 | 98.1248 | 95.181 | 99.6879 | 91.1314 | 94.4679 | 99.7376 | 104.4996 | 111.114 | 118.011 | 123.644 | 128.956 | 136.8508 | 142.5847 | 148.363 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485 | 154.485
80% | 11.7231 | 78.9669 | 76.0807 | 79.8249 | 71.1844 | 74.6979 | 78.3212 | 82.1712 | 86.5789 | 91.7702 | 96.6347 | 101.7478 | 110.4613 | 113.4131 | 118.9885 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 123.2506 | 80% | 19.6645 | 92.3527 | 89.5821 | 93.8239 | 85.7707 | 88.911 | 93.8707 | 98.3526 | 104.5778 | 111.0692 | 116.3708 | 121.3704 | 128.8008 | 134.1974 | 139.6358 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977 | 145.3977
75% | 17.7737 | 74.0314 | 71.3256 | 74.8358 | 66.7354 | 70.0292 | 73.4261 | 77.0355 | 81.1677 | 86.0345 | 90.5951 | 95.3885 | 103.5574 | 106.3248 | 111.5517 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 115.5474 | 75% | 25.7152 | 86.5807 | 83.9832 | 87.9599 | 80.41 | 83.3541 | 88.0038 | 92.2055 | 98.0417 | 104.1274 | 109.0976 | 113.7847 | 120.7507 | 125.8101 | 130.9086 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103 | 136.3103
70% | 35.1693 | 69.096 | 66.5706 | 69.8468 | 62.2864 | 65.3606 | 68.5311 | 71.8998 | 75.7565 | 80.2989 | 84.5554 | 89.0293 | 96.6536 | 99.2365 | 104.1149 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 107.8442 | 70% | 34.7911 | 80.8086 | 78.3843 | 82.0959 | 75.0494 | 77.7971 | 82.1368 | 86.0585 | 91.5056 | 97.1856 | 101.8244 | 106.1991 | 112.7007 | 117.4227 | 122.1813 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223 | 127.223
65% | 59.3718 | 64.1606 | 61.8155 | 64.8577 | 57.8373 | 60.692 | 63.636 | 66.7641 | 70.3453 | 74.5633 | 78.5157 | 82.6701 | 89.7498 | 92.1481 | 96.6781 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 100.1411 | 65% | 46.136 | 75.0366 | 72.7855 | 76.2319 | 69.6887 | 72.2402 | 76.2699 | 79.9114 | 84.9695 | 90.2437 | 94.5513 | 98.6134 | 104.6506 | 109.0354 | 113.4541 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356 | 118.1356
60% | 156.9382 | 59.2251 | 57.0605 | 59.8687 | 53.3883 | 56.0234 | 58.7409 | 61.6284 | 64.9342 | 68.8276 | 72.4761 | 76.3108 | 82.8459 | 85.0598 | 89.2414 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 92.4379 | 60% | 76.7673 | 69.2645 | 67.1866 | 70.3679 | 64.328 | 66.6833 | 70.403 | 73.7644 | 78.4334 | 83.3019 | 87.2781 | 91.0278 | 96.6006 | 100.6481 | 104.7268 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483 | 109.0483
55% | 363.794 | 54.2897 | 52.3055 | 54.8796 | 48.9393 | 51.3548 | 53.8458 | 56.4927 | 59.523 | 63.092 | 66.4364 | 69.9516 | 75.9421 | 77.9715 | 81.8046 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 84.7348 | 55% | 106.2642 | 63.4925 | 61.5877 | 64.5039 | 58.9674 | 61.1263 | 64.5361 | 67.6174 | 71.8973 | 76.3601 | 80.0049 | 83.4421 | 88.5505 | 92.2607 | 95.9996 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609 | 99.9609
50% | 771.4551 | 49.3543 | 47.5504 | 49.8906 | 44.4903 | 46.6862 | 48.9508 | 51.357 | 54.1118 | 57.3564 | 60.3967 | 63.5924 | 69.0383 | 70.8832 | 74.3678 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 77.0316 | 50% | 178.4935 | 57.7205 | 55.9888 | 58.6399 | 53.6067 | 55.5694 | 58.6692 | 61.4703 | 65.3612 | 69.4183 | 72.7317 | 75.8565 | 80.5005 | 83.8734 | 87.2724 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735 | 90.8735
45% | 1255.5054 | 44.4189 | 42.7954 | 44.9015 | 40.0412 | 42.0175 | 44.0557 | 46.2213 | 48.7006 | 51.6207 | 54.357 | 57.2331 | 62.1345 | 63.7949 | 66.931 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 69.3284 | 45% | 367.9538 | 51.9484 | 50.3899 | 52.7759 | 48.246 | 50.0124 | 52.8023 | 55.3233 | 58.825 | 62.4764 | 65.4586 | 68.2708 | 72.4504 | 75.486 | 78.5451 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862 | 81.7862
40% | 2059.1045 | 39.4834 | 38.0403 | 39.9125 | 35.5922 | 37.3489 | 39.1606 | 41.0856 | 43.2894 | 45.8851 | 48.3174 | 50.8739 | 55.2306 | 56.7066 | 59.4942 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 61.6253 | 40% | 741.202 | 46.1764 | 44.7911 | 46.9119 | 42.8854 | 44.4555 | 46.9353 | 49.1763 | 52.2889 | 55.5346 | 58.1854 | 60.6852 | 64.4004 | 67.0987 | 69.8179 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988 | 72.6988
35% | 3060.4836 | 34.548 | 33.2853 | 34.9234 | 31.1432 | 32.6803 | 34.2655 | 35.9499 | 37.8783 | 40.1494 | 42.2777 | 44.5147 | 48.3268 | 49.6182 | 52.0575 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 53.9221 | 35% | 1167.7713 | 40.4043 | 39.1922 | 41.048 | 37.5247 | 38.8986 | 41.0684 | 43.0292 | 45.7528 | 48.5928 | 50.9122 | 53.0995 | 56.3503 | 58.7114 | 61.0907 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115 | 63.6115
30% | 3366.0403 | 29.6126 | 28.5302 | 29.9343 | 26.6942 | 28.0117 | 29.3705 | 30.8142 | 32.4671 | 34.4138 | 36.238 | 38.1554 | 41.423 | 42.5299 | 44.6207 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 46.219 | 30% | 2002.3799 | 34.6323 | 33.5933 | 35.184 | 32.164 | 33.3416 | 35.2015 | 36.8822 | 39.2167 | 41.651 | 43.639 | 45.5139 | 48.3003 | 50.324 | 52.3634 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241 | 54.5241
25% | 3686.3454 | 24.6771 | 23.7752 | 24.9453 | 22.2451 | 23.3431 | 24.4754 | 25.6785 | 27.0559 | 28.6782 | 30.1984 | 31.7962 | 34.5191 | 35.4416 | 37.1839 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 38.5158 | 25% | 3173.5547 | 28.8602 | 27.9944 | 29.32 | 26.8033 | 27.7847 | 29.3346 | 30.7352 | 32.6806 | 34.7091 | 36.3659 | 37.9282 | 40.2502 | 41.9367 | 43.6362 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368 | 45.4368
20% | 4028.5841 | 19.7417 | 19.0202 | 19.9562 | 17.7961 | 18.6745 | 19.5803 | 20.5428 | 21.6447 | 22.9425 | 24.1587 | 25.4369 | 27.6153 | 28.3533 | 29.7471 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 30.8126 | 20% | 3477.5988 | 23.0882 | 22.3955 | 23.456 | 21.4427 | 22.2278 | 23.4677 | 24.5881 | 26.1445 | 27.7673 | 29.0927 | 30.3426 | 32.2002 | 33.5494 | 34.9089 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494 | 36.3494
15% | 4345.1076 | 14.8063 | 14.2651 | 14.9672 | 13.3471 | 14.0058 | 14.6852 | 15.4071 | 16.2335 | 17.2069 | 18.119 | 19.0777 | 20.7115 | 21.265 | 22.3103 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 23.1095 | 15% | 3788.4498 | 17.3161 | 16.7966 | 17.592 | 16.082 | 16.6708 | 17.6008 | 18.4411 | 19.6083 | 20.8255 | 21.8195 | 22.7569 | 24.1501 | 25.162 | 26.1817 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621 | 27.2621
10% | 4381.0332 | 9.8709 | 9.5101 | 9.9781 | 8.8981 | 9.3372 | 9.7902 | 10.2714 | 10.8224 | 11.4713 | 12.0793 | 12.7185 | 13.8077 | 14.1766 | 14.8736 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 15.4063 | 10% | 4317.5016 | 11.5441 | 11.1978 | 11.728 | 10.7213 | 11.1139 | 11.7338 | 12.2941 | 13.0722 | 13.8837 | 14.5463 | 15.1713 | 16.1001 | 16.7747 | 17.4545 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747 | 18.1747
5% | 4391.6218 | 4.9354 | 4.755 | 4.9891 | 4.449 | 4.6686 | 4.8951 | 5.1357 | 5.4112 | 5.7356 | 6.0397 | 6.3592 | 6.9038 | 7.0883 | 7.4368 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 7.7032 | 5% | 4391.6218 | 5.772 | 5.5989 | 5.864 | 5.3607 | 5.5569 | 5.8669 | 6.147 | 6.5361 | 6.9418 | 7.2732 | 7.5856 | 8.05 | 8.3873 | 8.7272 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874 | 9.0874
9.992e-14% | 4391.6218 | 9.863e-14 | 9.5025e-14 | 9.9701e-14 | 8.8909e-14 | 9.3298e-14 | 9.7823e-14 | 1.0263e-13 | 1.0814e-13 | 1.1462e-13 | 1.207e-13 | 1.2708e-13 | 1.3797e-13 | 1.4165e-13 | 1.4862e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 1.5394e-13 | 9.992e-14% | 4391.6218 | 1.1535e-13 | 1.1189e-13 | 1.1719e-13 | 1.0713e-13 | 1.1105e-13 | 1.1724e-13 | 1.2284e-13 | 1.3062e-13 | 1.3873e-13 | 1.4535e-13 | 1.5159e-13 | 1.6087e-13 | 1.6761e-13 | 1.7441e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13 | 1.816e-13
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 100% | 0 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
99% | 0.5944 | 75.2697 | 72.57 | 76.7928 | 82.1977 | 87.4309 | 92.086 | 98.4899 | 105.4924 | 112.6644 | 119.7723 | 126.0867 | 132.972 | 135.5855 | 144.4923 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 99% | 0.5944 | 80.6056 | 77.9271 | 82.3913 | 87.863 | 92.9632 | 98.3955 | 104.1109 | 112.2739 | 119.388 | 126.0974 | 133.0715 | 141.4362 | 144.2205 | 153.2427 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515
98% | 0.8916 | 74.5094 | 71.8369 | 76.0171 | 81.3674 | 86.5478 | 91.1558 | 97.4951 | 104.4268 | 111.5264 | 118.5625 | 124.8131 | 131.6288 | 134.216 | 143.0328 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 98% | 0.8916 | 79.7914 | 77.14 | 81.5591 | 86.9755 | 92.0241 | 97.4016 | 103.0593 | 111.1398 | 118.182 | 124.8237 | 131.7273 | 140.0075 | 142.7637 | 151.6948 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186
97% | 1.486 | 73.7491 | 71.1039 | 75.2415 | 80.5371 | 85.6646 | 90.2257 | 96.5003 | 103.3612 | 110.3883 | 117.3527 | 123.5395 | 130.2857 | 132.8464 | 141.5732 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 97% | 1.486 | 78.9772 | 76.3529 | 80.7268 | 86.0879 | 91.0851 | 96.4077 | 102.0076 | 110.0058 | 116.9761 | 123.5499 | 130.3832 | 138.5789 | 141.307 | 150.1469 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858
95% | 2.3776 | 72.2285 | 69.6379 | 73.6901 | 78.8766 | 83.8984 | 88.3653 | 94.5106 | 101.23 | 108.1123 | 114.933 | 120.9923 | 127.5994 | 130.1073 | 138.6542 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 95% | 2.3776 | 77.3488 | 74.7786 | 79.0624 | 84.3129 | 89.2071 | 94.42 | 99.9044 | 107.7376 | 114.5642 | 121.0025 | 127.6949 | 135.7216 | 138.3934 | 147.0511 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201
90% | 3.2692 | 68.427 | 65.9727 | 69.8117 | 74.7252 | 79.4827 | 83.7145 | 89.5363 | 95.9021 | 102.4222 | 108.8839 | 114.6242 | 120.8836 | 123.2596 | 131.3566 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 90% | 3.2692 | 73.2778 | 70.8429 | 74.9012 | 79.8754 | 84.512 | 89.4505 | 94.6463 | 102.0672 | 108.5345 | 114.634 | 120.9741 | 128.5784 | 131.1095 | 139.3116 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559
85% | 13.9683 | 64.6255 | 62.3076 | 65.9332 | 70.5738 | 75.067 | 79.0637 | 84.5621 | 90.5743 | 96.732 | 102.8348 | 108.2562 | 114.1679 | 116.4118 | 124.059 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 85% | 13.9683 | 69.2069 | 66.9071 | 70.74 | 75.4379 | 79.8168 | 84.481 | 89.3881 | 96.3968 | 102.5048 | 108.2654 | 114.2533 | 121.4351 | 123.8257 | 131.572 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917
80% | 41.3106 | 60.824 | 58.6424 | 62.0548 | 66.4224 | 70.6513 | 74.4129 | 79.5878 | 85.2464 | 91.0419 | 96.7857 | 101.8882 | 107.4521 | 109.5641 | 116.7614 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 80% | 41.3106 | 65.1359 | 62.9714 | 66.5788 | 71.0004 | 75.1217 | 79.5115 | 84.13 | 90.7264 | 96.4751 | 101.8969 | 107.5325 | 114.2919 | 116.5418 | 123.8325 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274
75% | 126.3094 | 57.0225 | 54.9773 | 58.1764 | 62.271 | 66.2356 | 69.7621 | 74.6136 | 79.9185 | 85.3518 | 90.7366 | 95.5202 | 100.7363 | 102.7163 | 109.4638 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 75% | 126.3094 | 61.0649 | 59.0357 | 62.4177 | 66.5628 | 70.4266 | 74.5421 | 78.8719 | 85.056 | 90.4454 | 95.5283 | 100.8117 | 107.1486 | 109.258 | 116.093 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632
70% | 323.9464 | 53.221 | 51.3121 | 54.298 | 58.1196 | 61.8198 | 65.1113 | 69.6394 | 74.5906 | 79.6617 | 84.6875 | 89.1522 | 94.0206 | 95.8685 | 102.1663 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 70% | 323.9464 | 56.9939 | 55.1 | 58.2565 | 62.1253 | 65.7315 | 69.5726 | 73.6138 | 79.3856 | 84.4157 | 89.1598 | 94.091 | 100.0054 | 101.9741 | 108.3534 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299
65% | 549.5201 | 49.4195 | 47.647 | 50.4195 | 53.9682 | 57.4041 | 60.4605 | 64.6651 | 69.2627 | 73.9716 | 78.6384 | 82.7842 | 87.3048 | 89.0208 | 94.8687 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 65% | 549.5201 | 52.9229 | 51.1643 | 54.0953 | 57.6878 | 61.0364 | 64.6031 | 68.3556 | 73.7152 | 78.386 | 82.7912 | 87.3702 | 92.8621 | 94.6902 | 100.6139 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348
60% | 799.4641 | 45.618 | 43.9818 | 46.5411 | 49.8168 | 52.9884 | 55.8097 | 59.6909 | 63.9348 | 68.2814 | 72.5893 | 76.4162 | 80.5891 | 82.173 | 87.5711 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 60% | 799.4641 | 48.8519 | 47.2286 | 49.9341 | 53.2503 | 56.3413 | 59.6337 | 63.0975 | 68.0448 | 72.3563 | 76.4226 | 80.6494 | 85.7189 | 87.4064 | 92.8744 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706
55% | 1116.2777 | 41.8165 | 40.3167 | 42.6627 | 45.6654 | 48.5727 | 51.1589 | 54.7166 | 58.6069 | 62.5913 | 66.5402 | 70.0481 | 73.8733 | 75.3253 | 80.2735 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 55% | 1116.2777 | 44.7809 | 43.2929 | 45.773 | 48.8128 | 51.6462 | 54.6642 | 57.8394 | 62.3744 | 66.3266 | 70.0541 | 73.9286 | 78.5757 | 80.1225 | 85.1348 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064
50% | 1494.9086 | 38.015 | 36.6515 | 38.7843 | 41.514 | 44.157 | 46.5081 | 49.7424 | 53.279 | 56.9012 | 60.4911 | 63.6801 | 67.1576 | 68.4775 | 72.9759 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 50% | 1494.9086 | 40.7099 | 39.3571 | 41.6118 | 44.3752 | 46.9511 | 49.6947 | 52.5813 | 56.704 | 60.297 | 63.6855 | 67.2078 | 71.4324 | 72.8386 | 77.3953 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422
45% | 2004.0097 | 34.2135 | 32.9864 | 34.9058 | 37.3626 | 39.7413 | 41.8573 | 44.7682 | 47.9511 | 51.2111 | 54.442 | 57.3121 | 60.4418 | 61.6298 | 65.6783 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 45% | 2004.0097 | 36.6389 | 35.4214 | 37.4506 | 39.9377 | 42.256 | 44.7252 | 47.3231 | 51.0336 | 54.2673 | 57.317 | 60.487 | 64.2892 | 65.5548 | 69.6558 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779
40% | 2877.179 | 30.412 | 29.3212 | 31.0274 | 33.2112 | 35.3256 | 37.2065 | 39.7939 | 42.6232 | 45.521 | 48.3929 | 50.9441 | 53.7261 | 54.782 | 58.3807 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 40% | 2877.179 | 32.5679 | 31.4857 | 33.2894 | 35.5002 | 37.5609 | 39.7558 | 42.065 | 45.3632 | 48.2376 | 50.9484 | 53.7663 | 57.1459 | 58.2709 | 61.9162 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137
35% | 3454.933 | 26.6105 | 25.6561 | 27.149 | 29.0598 | 30.9099 | 32.5556 | 34.8197 | 37.2953 | 39.8308 | 42.3438 | 44.5761 | 47.0103 | 47.9343 | 51.0831 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 35% | 3454.933 | 28.4969 | 27.55 | 29.1282 | 31.0627 | 32.8658 | 34.7863 | 36.8069 | 39.6928 | 42.2079 | 44.5799 | 47.0455 | 50.0027 | 50.987 | 54.1767 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495
30% | 3663.5664 | 22.809 | 21.9909 | 23.2706 | 24.9084 | 26.4942 | 27.9048 | 29.8454 | 31.9674 | 34.1407 | 36.2946 | 38.2081 | 40.2945 | 41.0865 | 43.7855 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 30% | 3663.5664 | 24.4259 | 23.6143 | 24.9671 | 26.6251 | 28.1707 | 29.8168 | 31.5488 | 34.0224 | 36.1782 | 38.2113 | 40.3247 | 42.8595 | 43.7032 | 46.4372 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853
25% | 3862.6894 | 19.0075 | 18.3258 | 19.3921 | 20.757 | 22.0785 | 23.254 | 24.8712 | 26.6395 | 28.4506 | 30.2455 | 31.8401 | 33.5788 | 34.2388 | 36.4879 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 25% | 3862.6894 | 20.355 | 19.6786 | 20.8059 | 22.1876 | 23.4755 | 24.8474 | 26.2906 | 28.352 | 30.1485 | 31.8428 | 33.6039 | 35.7162 | 36.4193 | 38.6977 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211
20% | 4122.7381 | 15.206 | 14.6606 | 15.5137 | 16.6056 | 17.6628 | 18.6032 | 19.897 | 21.3116 | 22.7605 | 24.1964 | 25.4721 | 26.863 | 27.391 | 29.1904 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 20% | 4122.7381 | 16.284 | 15.7429 | 16.6447 | 17.7501 | 18.7804 | 19.8779 | 21.0325 | 22.6816 | 24.1188 | 25.4742 | 26.8831 | 28.573 | 29.1355 | 30.9581 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569
15% | 4372.3849 | 11.4045 | 10.9955 | 11.6353 | 12.4542 | 13.2471 | 13.9524 | 14.9227 | 15.9837 | 17.0704 | 18.1473 | 19.104 | 20.1473 | 20.5433 | 21.8928 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 15% | 4372.3849 | 12.213 | 11.8071 | 12.4835 | 13.3126 | 14.0853 | 14.9084 | 15.7744 | 17.0112 | 18.0891 | 19.1057 | 20.1623 | 21.4297 | 21.8516 | 23.2186 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926
10% | 4374.4653 | 7.603 | 7.3303 | 7.7569 | 8.3028 | 8.8314 | 9.3016 | 9.9485 | 10.6558 | 11.3802 | 12.0982 | 12.736 | 13.4315 | 13.6955 | 14.5952 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 10% | 4374.4653 | 8.142 | 7.8714 | 8.3224 | 8.875 | 9.3902 | 9.9389 | 10.5163 | 11.3408 | 12.0594 | 12.7371 | 13.4416 | 14.2865 | 14.5677 | 15.4791 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284
5% | 4374.7625 | 3.8015 | 3.6652 | 3.8784 | 4.1514 | 4.4157 | 4.6508 | 4.9742 | 5.3279 | 5.6901 | 6.0491 | 6.368 | 6.7158 | 6.8478 | 7.2976 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 5% | 4374.7625 | 4.071 | 3.9357 | 4.1612 | 4.4375 | 4.6951 | 4.9695 | 5.2581 | 5.6704 | 6.0297 | 6.3686 | 6.7208 | 7.1432 | 7.2839 | 7.7395 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642
9.992e-14% | 4375.9513 | 7.5969e-14 | 7.3244e-14 | 7.7507e-14 | 8.2962e-14 | 8.8243e-14 | 9.2942e-14 | 9.9405e-14 | 1.0647e-13 | 1.1371e-13 | 1.2089e-13 | 1.2726e-13 | 1.3421e-13 | 1.3685e-13 | 1.4584e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 9.992e-14% | 4375.9513 | 8.1355e-14 | 7.8651e-14 | 8.3157e-14 | 8.868e-14 | 9.3827e-14 | 9.931e-14 | 1.0508e-13 | 1.1332e-13 | 1.205e-13 | 1.2727e-13 | 1.3431e-13 | 1.4275e-13 | 1.4556e-13 | 1.5467e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 100% | 0 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471
99% | 0 | 97.7215 | 94.1498 | 98.7833 | 102.4457 | 106.7936 | 111.2775 | 116.0419 | 121.4964 | 127.9206 | 133.9405 | 140.2679 | 151.0508 | 154.7037 | 161.6032 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 99% | 0.37816 | 114.2865 | 110.8579 | 116.1071 | 120.4963 | 124.3824 | 130.52 | 136.0663 | 143.7701 | 151.8031 | 158.3638 | 164.5508 | 173.746 | 180.4243 | 187.1543 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846
98% | 0.37816 | 96.7344 | 93.1988 | 97.7855 | 101.4109 | 105.7149 | 110.1535 | 114.8697 | 120.2691 | 126.6285 | 132.5876 | 138.851 | 149.525 | 153.1411 | 159.9709 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 98% | 1.1345 | 113.1321 | 109.7381 | 114.9343 | 119.2791 | 123.126 | 129.2016 | 134.6919 | 142.3179 | 150.2698 | 156.7642 | 162.8887 | 171.991 | 178.6018 | 185.2638 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222
97% | 0.75633 | 95.7473 | 92.2478 | 96.7877 | 100.3761 | 104.6362 | 109.0295 | 113.6976 | 119.0419 | 125.3363 | 131.2346 | 137.4342 | 147.9993 | 151.5784 | 158.3385 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 97% | 2.269 | 111.9777 | 108.6183 | 113.7615 | 118.062 | 121.8696 | 127.8832 | 133.3175 | 140.8656 | 148.7364 | 155.1646 | 161.2266 | 170.236 | 176.7794 | 183.3734 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597
95% | 1.1345 | 93.7731 | 90.3458 | 94.7921 | 98.3065 | 102.4787 | 106.7814 | 111.3533 | 116.5874 | 122.7521 | 128.5288 | 134.6005 | 144.9477 | 148.4531 | 155.0738 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 95% | 4.538 | 109.6689 | 106.3788 | 111.4159 | 115.6277 | 119.3568 | 125.2464 | 130.5687 | 137.9612 | 145.6697 | 151.9653 | 157.9023 | 166.7259 | 173.1344 | 179.5925 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347
90% | 4.538 | 88.8377 | 85.5907 | 89.803 | 93.1325 | 97.0851 | 101.1614 | 105.4926 | 110.4512 | 116.2914 | 121.7641 | 127.5162 | 137.3189 | 140.6397 | 146.912 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 90% | 7.9414 | 103.8968 | 100.7799 | 105.5519 | 109.5421 | 113.0749 | 118.6545 | 123.6966 | 130.7001 | 138.0029 | 143.9671 | 149.5917 | 157.9509 | 164.0221 | 170.1403 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224
85% | 7.9414 | 83.9023 | 80.8357 | 84.814 | 87.9585 | 91.6915 | 95.5413 | 99.6319 | 104.3151 | 109.8308 | 114.9994 | 120.432 | 129.6901 | 132.8264 | 138.7503 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 85% | 14.3702 | 98.1248 | 95.181 | 99.6879 | 103.4564 | 106.7929 | 112.0626 | 116.8246 | 123.439 | 130.336 | 135.969 | 141.281 | 149.1758 | 154.9097 | 160.688 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81
80% | 11.7231 | 78.9669 | 76.0807 | 79.8249 | 82.7844 | 86.2979 | 89.9212 | 93.7712 | 98.1789 | 103.3702 | 108.2347 | 113.3478 | 122.0613 | 125.0131 | 130.5885 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 80% | 19.6645 | 92.3527 | 89.5821 | 93.8239 | 97.3707 | 100.511 | 105.4707 | 109.9526 | 116.1778 | 122.6692 | 127.9708 | 132.9704 | 140.4008 | 145.7974 | 151.2358 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977
75% | 17.7737 | 74.0314 | 71.3256 | 74.8358 | 77.6104 | 80.9042 | 84.3011 | 87.9105 | 92.0427 | 96.9095 | 101.4701 | 106.2635 | 114.4324 | 117.1998 | 122.4267 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 75% | 25.7152 | 86.5807 | 83.9832 | 87.9599 | 91.285 | 94.2291 | 98.8788 | 103.0805 | 108.9167 | 115.0024 | 119.9726 | 124.6597 | 131.6257 | 136.6851 | 141.7836 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853
70% | 35.1693 | 69.096 | 66.5706 | 69.8468 | 72.4364 | 75.5106 | 78.6811 | 82.0498 | 85.9065 | 90.4489 | 94.7054 | 99.1793 | 106.8036 | 109.3865 | 114.2649 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 70% | 34.7911 | 80.8086 | 78.3843 | 82.0959 | 85.1994 | 87.9471 | 92.2868 | 96.2085 | 101.6556 | 107.3356 | 111.9744 | 116.3491 | 122.8507 | 127.5727 | 132.3313 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373
65% | 59.3718 | 64.1606 | 61.8155 | 64.8577 | 67.2623 | 70.117 | 73.061 | 76.1891 | 79.7703 | 83.9883 | 87.9407 | 92.0951 | 99.1748 | 101.5731 | 106.1031 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 65% | 46.136 | 75.0366 | 72.7855 | 76.2319 | 79.1137 | 81.6652 | 85.6949 | 89.3364 | 94.3945 | 99.6687 | 103.9763 | 108.0384 | 114.0756 | 118.4604 | 122.8791 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606
60% | 156.9382 | 59.2251 | 57.0605 | 59.8687 | 62.0883 | 64.7234 | 67.4409 | 70.3284 | 73.6342 | 77.5276 | 81.1761 | 85.0108 | 91.5459 | 93.7598 | 97.9414 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 60% | 76.7673 | 69.2645 | 67.1866 | 70.3679 | 73.028 | 75.3833 | 79.103 | 82.4644 | 87.1334 | 92.0019 | 95.9781 | 99.7278 | 105.3006 | 109.3481 | 113.4268 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483
55% | 363.794 | 54.2897 | 52.3055 | 54.8796 | 56.9143 | 59.3298 | 61.8208 | 64.4677 | 67.498 | 71.067 | 74.4114 | 77.9266 | 83.9171 | 85.9465 | 89.7796 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 55% | 106.2642 | 63.4925 | 61.5877 | 64.5039 | 66.9424 | 69.1013 | 72.5111 | 75.5924 | 79.8723 | 84.3351 | 87.9799 | 91.4171 | 96.5255 | 100.2357 | 103.9746 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359
50% | 771.4551 | 49.3543 | 47.5504 | 49.8906 | 51.7403 | 53.9362 | 56.2008 | 58.607 | 61.3618 | 64.6064 | 67.6467 | 70.8424 | 76.2883 | 78.1332 | 81.6178 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 50% | 178.4935 | 57.7205 | 55.9888 | 58.6399 | 60.8567 | 62.8194 | 65.9192 | 68.7203 | 72.6112 | 76.6683 | 79.9817 | 83.1065 | 87.7505 | 91.1234 | 94.5224 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235
45% | 1255.5054 | 44.4189 | 42.7954 | 44.9015 | 46.5662 | 48.5425 | 50.5807 | 52.7463 | 55.2256 | 58.1457 | 60.882 | 63.7581 | 68.6595 | 70.3199 | 73.456 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 45% | 367.9538 | 51.9484 | 50.3899 | 52.7759 | 54.771 | 56.5374 | 59.3273 | 61.8483 | 65.35 | 69.0014 | 71.9836 | 74.7958 | 78.9754 | 82.011 | 85.0701 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112
40% | 2059.1045 | 39.4834 | 38.0403 | 39.9125 | 41.3922 | 43.1489 | 44.9606 | 46.8856 | 49.0894 | 51.6851 | 54.1174 | 56.6739 | 61.0306 | 62.5066 | 65.2942 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 40% | 741.202 | 46.1764 | 44.7911 | 46.9119 | 48.6854 | 50.2555 | 52.7353 | 54.9763 | 58.0889 | 61.3346 | 63.9854 | 66.4852 | 70.2004 | 72.8987 | 75.6179 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988
35% | 3060.4836 | 34.548 | 33.2853 | 34.9234 | 36.2182 | 37.7553 | 39.3405 | 41.0249 | 42.9533 | 45.2244 | 47.3527 | 49.5897 | 53.4018 | 54.6932 | 57.1325 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 35% | 1167.7713 | 40.4043 | 39.1922 | 41.048 | 42.5997 | 43.9736 | 46.1434 | 48.1042 | 50.8278 | 53.6678 | 55.9872 | 58.1745 | 61.4253 | 63.7864 | 66.1657 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865
30% | 3366.0403 | 29.6126 | 28.5302 | 29.9343 | 31.0442 | 32.3617 | 33.7205 | 35.1642 | 36.8171 | 38.7638 | 40.588 | 42.5054 | 45.773 | 46.8799 | 48.9707 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 30% | 2002.3799 | 34.6323 | 33.5933 | 35.184 | 36.514 | 37.6916 | 39.5515 | 41.2322 | 43.5667 | 46.001 | 47.989 | 49.8639 | 52.6503 | 54.674 | 56.7134 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741
25% | 3686.3454 | 24.6771 | 23.7752 | 24.9453 | 25.8701 | 26.9681 | 28.1004 | 29.3035 | 30.6809 | 32.3032 | 33.8234 | 35.4212 | 38.1441 | 39.0666 | 40.8089 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 25% | 3173.5547 | 28.8602 | 27.9944 | 29.32 | 30.4283 | 31.4097 | 32.9596 | 34.3602 | 36.3056 | 38.3341 | 39.9909 | 41.5532 | 43.8752 | 45.5617 | 47.2612 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618
20% | 4028.5841 | 19.7417 | 19.0202 | 19.9562 | 20.6961 | 21.5745 | 22.4803 | 23.4428 | 24.5447 | 25.8425 | 27.0587 | 28.3369 | 30.5153 | 31.2533 | 32.6471 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 20% | 3477.5988 | 23.0882 | 22.3955 | 23.456 | 24.3427 | 25.1278 | 26.3677 | 27.4881 | 29.0445 | 30.6673 | 31.9927 | 33.2426 | 35.1002 | 36.4494 | 37.8089 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494
15% | 4345.1076 | 14.8063 | 14.2651 | 14.9672 | 15.5221 | 16.1808 | 16.8602 | 17.5821 | 18.4085 | 19.3819 | 20.294 | 21.2527 | 22.8865 | 23.44 | 24.4853 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 15% | 3788.4498 | 17.3161 | 16.7966 | 17.592 | 18.257 | 18.8458 | 19.7758 | 20.6161 | 21.7833 | 23.0005 | 23.9945 | 24.9319 | 26.3251 | 27.337 | 28.3567 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371
10% | 4381.0332 | 9.8709 | 9.5101 | 9.9781 | 10.3481 | 10.7872 | 11.2402 | 11.7214 | 12.2724 | 12.9213 | 13.5293 | 14.1685 | 15.2577 | 15.6266 | 16.3236 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 10% | 4317.5016 | 11.5441 | 11.1978 | 11.728 | 12.1713 | 12.5639 | 13.1838 | 13.7441 | 14.5222 | 15.3337 | 15.9963 | 16.6213 | 17.5501 | 18.2247 | 18.9045 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247
5% | 4391.6218 | 4.9354 | 4.755 | 4.9891 | 5.174 | 5.3936 | 5.6201 | 5.8607 | 6.1362 | 6.4606 | 6.7647 | 7.0842 | 7.6288 | 7.8133 | 8.1618 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 5% | 4391.6218 | 5.772 | 5.5989 | 5.864 | 6.0857 | 6.2819 | 6.5919 | 6.872 | 7.2611 | 7.6668 | 7.9982 | 8.3106 | 8.775 | 9.1123 | 9.4522 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124
9.992e-14% | 4391.6218 | 9.863e-14 | 9.5025e-14 | 9.9701e-14 | 1.034e-13 | 1.0779e-13 | 1.1231e-13 | 1.1712e-13 | 1.2263e-13 | 1.2911e-13 | 1.3519e-13 | 1.4157e-13 | 1.5245e-13 | 1.5614e-13 | 1.6311e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 9.992e-14% | 4391.6218 | 1.1535e-13 | 1.1189e-13 | 1.1719e-13 | 1.2162e-13 | 1.2554e-13 | 1.3173e-13 | 1.3733e-13 | 1.4511e-13 | 1.5321e-13 | 1.5984e-13 | 1.6608e-13 | 1.7536e-13 | 1.821e-13 | 1.8889e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 76.03 | 73.303 | 77.5685 | 63.6947 | 68.9807 | 73.6828 | 80.1515 | 87.2246 | 94.4691 | 101.6488 | 108.0269 | 114.9818 | 117.6217 | 126.6185 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 135.9262 | 100% | 0 | 81.4198 | 78.7143 | 83.2235 | 69.4171 | 74.5688 | 80.0561 | 85.8292 | 94.0747 | 101.2606 | 108.0377 | 115.0823 | 123.5315 | 126.3439 | 135.4573 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951 | 143.951
99% | 0.5944 | 75.2697 | 72.57 | 76.7928 | 63.0577 | 68.2909 | 72.946 | 79.3499 | 86.3524 | 93.5244 | 100.6323 | 106.9467 | 113.832 | 116.4455 | 125.3523 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 134.5669 | 99% | 0.5944 | 80.6056 | 77.9271 | 82.3913 | 68.723 | 73.8232 | 79.2555 | 84.9709 | 93.1339 | 100.248 | 106.9574 | 113.9315 | 122.2962 | 125.0805 | 134.1027 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115 | 142.5115
98% | 0.8916 | 74.5094 | 71.8369 | 76.0171 | 62.4208 | 67.6011 | 72.2091 | 78.5484 | 85.4801 | 92.5797 | 99.6158 | 105.8664 | 112.6822 | 115.2693 | 124.0861 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 133.2076 | 98% | 0.8916 | 79.7914 | 77.14 | 81.5591 | 68.0288 | 73.0775 | 78.455 | 84.1126 | 92.1932 | 99.2354 | 105.877 | 112.7807 | 121.0609 | 123.8171 | 132.7481 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072 | 141.072
97% | 1.486 | 73.7491 | 71.1039 | 75.2415 | 61.7838 | 66.9113 | 71.4723 | 77.7469 | 84.6079 | 91.635 | 98.5994 | 104.7861 | 111.5323 | 114.0931 | 122.8199 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 131.8484 | 97% | 1.486 | 78.9772 | 76.3529 | 80.7268 | 67.3346 | 72.3318 | 77.6544 | 83.2543 | 91.2524 | 98.2228 | 104.7966 | 111.6298 | 119.8256 | 122.5536 | 131.3936 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324 | 139.6324
95% | 2.3776 | 72.2285 | 69.6379 | 73.6901 | 60.5099 | 65.5317 | 69.9987 | 76.1439 | 82.8634 | 89.7456 | 96.5664 | 102.6256 | 109.2327 | 111.7407 | 120.2875 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 129.1299 | 95% | 2.3776 | 77.3488 | 74.7786 | 79.0624 | 65.9463 | 70.8404 | 76.0533 | 81.5377 | 89.3709 | 96.1975 | 102.6359 | 109.3282 | 117.3549 | 120.0267 | 128.6844 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534 | 136.7534
90% | 3.2692 | 68.427 | 65.9727 | 69.8117 | 57.3252 | 62.0827 | 66.3145 | 72.1363 | 78.5021 | 85.0222 | 91.4839 | 97.2242 | 103.4836 | 105.8596 | 113.9566 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 122.3336 | 90% | 3.2692 | 73.2778 | 70.8429 | 74.9012 | 62.4754 | 67.112 | 72.0505 | 77.2463 | 84.6672 | 91.1345 | 97.234 | 103.5741 | 111.1784 | 113.7095 | 121.9116 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559 | 129.5559
85% | 13.9683 | 64.6255 | 62.3076 | 65.9332 | 54.1405 | 58.6336 | 62.6304 | 68.1287 | 74.1409 | 80.2987 | 86.4015 | 91.8229 | 97.7345 | 99.9785 | 107.6257 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 115.5372 | 85% | 13.9683 | 69.2069 | 66.9071 | 70.74 | 59.0046 | 63.3835 | 68.0477 | 72.9548 | 79.9635 | 86.0715 | 91.8321 | 97.82 | 105.0018 | 107.3923 | 115.1387 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583 | 122.3583
80% | 41.3106 | 60.824 | 58.6424 | 62.0548 | 50.9557 | 55.1846 | 58.9462 | 64.1212 | 69.7797 | 75.5753 | 81.3191 | 86.4215 | 91.9854 | 94.0974 | 101.2948 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 108.7409 | 80% | 41.3106 | 65.1359 | 62.9714 | 66.5788 | 55.5337 | 59.6551 | 64.0449 | 68.6633 | 75.2597 | 81.0085 | 86.4302 | 92.0659 | 98.8252 | 101.0752 | 108.3658 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608 | 115.1608
75% | 126.3094 | 57.0225 | 54.9773 | 58.1764 | 47.771 | 51.7356 | 55.2621 | 60.1136 | 65.4185 | 70.8518 | 76.2366 | 81.0202 | 86.2363 | 88.2163 | 94.9638 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 101.9446 | 75% | 126.3094 | 61.0649 | 59.0357 | 62.4177 | 52.0628 | 55.9266 | 60.0421 | 64.3719 | 70.556 | 75.9454 | 81.0283 | 86.3117 | 92.6486 | 94.758 | 101.593 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632 | 107.9632
70% | 323.9464 | 53.221 | 51.3121 | 54.298 | 44.5863 | 48.2865 | 51.578 | 56.106 | 61.0572 | 66.1284 | 71.1542 | 75.6189 | 80.4873 | 82.3352 | 88.6329 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 95.1483 | 70% | 323.9464 | 56.9939 | 55.1 | 58.2565 | 48.592 | 52.1982 | 56.0393 | 60.0804 | 65.8523 | 70.8824 | 75.6264 | 80.5576 | 86.4721 | 88.4408 | 94.8201 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657 | 100.7657
65% | 549.5201 | 49.4195 | 47.647 | 50.4195 | 41.4015 | 44.8375 | 47.8938 | 52.0985 | 56.696 | 61.4049 | 66.0717 | 70.2175 | 74.7382 | 76.4541 | 82.302 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 88.352 | 65% | 549.5201 | 52.9229 | 51.1643 | 54.0953 | 45.1211 | 48.4697 | 52.0365 | 55.789 | 61.1485 | 65.8194 | 70.2245 | 74.8035 | 80.2955 | 82.1236 | 88.0472 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681 | 93.5681
60% | 799.4641 | 45.618 | 43.9818 | 46.5411 | 38.2168 | 41.3884 | 44.2097 | 48.0909 | 52.3348 | 56.6814 | 60.9893 | 64.8162 | 68.9891 | 70.573 | 75.9711 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 81.5557 | 60% | 799.4641 | 48.8519 | 47.2286 | 49.9341 | 41.6503 | 44.7413 | 48.0337 | 51.4975 | 56.4448 | 60.7563 | 64.8226 | 69.0494 | 74.1189 | 75.8064 | 81.2744 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706 | 86.3706
55% | 1116.2777 | 41.8165 | 40.3167 | 42.6627 | 35.0321 | 37.9394 | 40.5255 | 44.0833 | 47.9735 | 51.958 | 55.9068 | 59.4148 | 63.24 | 64.692 | 69.6402 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 74.7594 | 55% | 1116.2777 | 44.7809 | 43.2929 | 45.773 | 38.1794 | 41.0129 | 44.0309 | 47.206 | 51.7411 | 55.6933 | 59.4208 | 63.2953 | 67.9423 | 69.4892 | 74.5015 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173 | 79.173
50% | 1494.9086 | 38.015 | 36.6515 | 38.7843 | 31.8473 | 34.4904 | 36.8414 | 40.0757 | 43.6123 | 47.2345 | 50.8244 | 54.0135 | 57.4909 | 58.8109 | 63.3092 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 67.9631 | 50% | 1494.9086 | 40.7099 | 39.3571 | 41.6118 | 34.7086 | 37.2844 | 40.028 | 42.9146 | 47.0373 | 50.6303 | 54.0189 | 57.5412 | 61.7658 | 63.172 | 67.7286 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755 | 71.9755
45% | 2004.0097 | 34.2135 | 32.9864 | 34.9058 | 28.6626 | 31.0413 | 33.1573 | 36.0682 | 39.2511 | 42.5111 | 45.742 | 48.6121 | 51.7418 | 52.9298 | 56.9783 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 61.1668 | 45% | 2004.0097 | 36.6389 | 35.4214 | 37.4506 | 31.2377 | 33.556 | 36.0252 | 38.6231 | 42.3336 | 45.5673 | 48.617 | 51.787 | 55.5892 | 56.8548 | 60.9558 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779 | 64.7779
40% | 2877.179 | 30.412 | 29.3212 | 31.0274 | 25.4779 | 27.5923 | 29.4731 | 32.0606 | 34.8898 | 37.7876 | 40.6595 | 43.2108 | 45.9927 | 47.0487 | 50.6474 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 54.3705 | 40% | 2877.179 | 32.5679 | 31.4857 | 33.2894 | 27.7669 | 29.8275 | 32.0224 | 34.3317 | 37.6299 | 40.5042 | 43.2151 | 46.0329 | 49.4126 | 50.5376 | 54.1829 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804 | 57.5804
35% | 3454.933 | 26.6105 | 25.6561 | 27.149 | 22.2931 | 24.1433 | 25.789 | 28.053 | 30.5286 | 33.0642 | 35.5771 | 37.8094 | 40.2436 | 41.1676 | 44.3165 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 47.5742 | 35% | 3454.933 | 28.4969 | 27.55 | 29.1282 | 24.296 | 26.0991 | 28.0196 | 30.0402 | 32.9261 | 35.4412 | 37.8132 | 40.2788 | 43.236 | 44.2204 | 47.41 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828 | 50.3828
30% | 3663.5664 | 22.809 | 21.9909 | 23.2706 | 19.1084 | 20.6942 | 22.1048 | 24.0454 | 26.1674 | 28.3407 | 30.4946 | 32.4081 | 34.4945 | 35.2865 | 37.9855 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 40.7779 | 30% | 3663.5664 | 24.4259 | 23.6143 | 24.9671 | 20.8251 | 22.3707 | 24.0168 | 25.7488 | 28.2224 | 30.3782 | 32.4113 | 34.5247 | 37.0595 | 37.9032 | 40.6372 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853 | 43.1853
25% | 3862.6894 | 19.0075 | 18.3258 | 19.3921 | 15.9237 | 17.2452 | 18.4207 | 20.0379 | 21.8062 | 23.6173 | 25.4122 | 27.0067 | 28.7454 | 29.4054 | 31.6546 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 33.9815 | 25% | 3862.6894 | 20.355 | 19.6786 | 20.8059 | 17.3543 | 18.6422 | 20.014 | 21.4573 | 23.5187 | 25.3151 | 27.0094 | 28.7706 | 30.8829 | 31.586 | 33.8643 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877 | 35.9877
20% | 4122.7381 | 15.206 | 14.6606 | 15.5137 | 12.7389 | 13.7961 | 14.7366 | 16.0303 | 17.4449 | 18.8938 | 20.3298 | 21.6054 | 22.9964 | 23.5243 | 25.3237 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 27.1852 | 20% | 4122.7381 | 16.284 | 15.7429 | 16.6447 | 13.8834 | 14.9138 | 16.0112 | 17.1658 | 18.8149 | 20.2521 | 21.6075 | 23.0165 | 24.7063 | 25.2688 | 27.0915 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902 | 28.7902
15% | 4372.3849 | 11.4045 | 10.9955 | 11.6353 | 9.5542 | 10.3471 | 11.0524 | 12.0227 | 13.0837 | 14.1704 | 15.2473 | 16.204 | 17.2473 | 17.6433 | 18.9928 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 20.3889 | 15% | 4372.3849 | 12.213 | 11.8071 | 12.4835 | 10.4126 | 11.1853 | 12.0084 | 12.8744 | 14.1112 | 15.1891 | 16.2057 | 17.2623 | 18.5297 | 18.9516 | 20.3186 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926 | 21.5926
10% | 4374.4653 | 7.603 | 7.3303 | 7.7569 | 6.3695 | 6.8981 | 7.3683 | 8.0151 | 8.7225 | 9.4469 | 10.1649 | 10.8027 | 11.4982 | 11.7622 | 12.6618 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 13.5926 | 10% | 4374.4653 | 8.142 | 7.8714 | 8.3224 | 6.9417 | 7.4569 | 8.0056 | 8.5829 | 9.4075 | 10.1261 | 10.8038 | 11.5082 | 12.3532 | 12.6344 | 13.5457 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951 | 14.3951
5% | 4374.7625 | 3.8015 | 3.6652 | 3.8784 | 3.1847 | 3.449 | 3.6841 | 4.0076 | 4.3612 | 4.7235 | 5.0824 | 5.4013 | 5.7491 | 5.8811 | 6.3309 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 6.7963 | 5% | 4374.7625 | 4.071 | 3.9357 | 4.1612 | 3.4709 | 3.7284 | 4.0028 | 4.2915 | 4.7037 | 5.063 | 5.4019 | 5.7541 | 6.1766 | 6.3172 | 6.7729 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975 | 7.1975
9.992e-14% | 4375.9513 | 7.5969e-14 | 7.3244e-14 | 7.7507e-14 | 6.3644e-14 | 6.8926e-14 | 7.3624e-14 | 8.0087e-14 | 8.7155e-14 | 9.4394e-14 | 1.0157e-13 | 1.0794e-13 | 1.1489e-13 | 1.1753e-13 | 1.2652e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 1.3582e-13 | 9.992e-14% | 4375.9513 | 8.1355e-14 | 7.8651e-14 | 8.3157e-14 | 6.9362e-14 | 7.4509e-14 | 7.9992e-14 | 8.5761e-14 | 9.3999e-14 | 1.0118e-13 | 1.0795e-13 | 1.1499e-13 | 1.2343e-13 | 1.2624e-13 | 1.3535e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13 | 1.4384e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 98.7086 | 95.1008 | 99.7811 | 84.1472 | 88.539 | 93.0682 | 97.8807 | 103.3903 | 109.8794 | 115.9601 | 122.3514 | 133.2432 | 136.933 | 143.9023 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 149.2299 | 100% | 0 | 115.4409 | 111.9776 | 117.2799 | 102.3801 | 106.3054 | 112.505 | 118.1074 | 125.889 | 134.0032 | 140.6301 | 146.8796 | 156.1676 | 162.9134 | 169.7114 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138 | 176.9138
99% | 0 | 97.7215 | 94.1498 | 98.7833 | 83.3057 | 87.6536 | 92.1375 | 96.9019 | 102.3564 | 108.7806 | 114.8005 | 121.1279 | 131.9108 | 135.5637 | 142.4632 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 147.7376 | 99% | 0.37816 | 114.2865 | 110.8579 | 116.1071 | 101.3563 | 105.2424 | 111.38 | 116.9263 | 124.6301 | 132.6631 | 139.2238 | 145.4108 | 154.606 | 161.2843 | 168.0143 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446 | 175.1446
98% | 0.37816 | 96.7344 | 93.1988 | 97.7855 | 82.4643 | 86.7682 | 91.2068 | 95.9231 | 101.3225 | 107.6818 | 113.6409 | 119.9044 | 130.5784 | 134.1944 | 141.0242 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 146.2453 | 98% | 1.1345 | 113.1321 | 109.7381 | 114.9343 | 100.3325 | 104.1793 | 110.2549 | 115.7452 | 123.3712 | 131.3231 | 137.8175 | 143.942 | 153.0443 | 159.6552 | 166.3172 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755 | 173.3755
97% | 0.75633 | 95.7473 | 92.2478 | 96.7877 | 81.6228 | 85.8828 | 90.2761 | 94.9443 | 100.2886 | 106.583 | 112.4813 | 118.6808 | 129.2459 | 132.8251 | 139.5852 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 144.753 | 97% | 2.269 | 111.9777 | 108.6183 | 113.7615 | 99.3087 | 103.1163 | 109.1299 | 114.5641 | 122.1123 | 129.9831 | 136.4112 | 142.4732 | 151.4826 | 158.026 | 164.6201 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064 | 171.6064
95% | 1.1345 | 93.7731 | 90.3458 | 94.7921 | 79.9398 | 84.112 | 88.4148 | 92.9866 | 98.2208 | 104.3854 | 110.1621 | 116.2338 | 126.5811 | 130.0864 | 136.7071 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 141.7684 | 95% | 4.538 | 109.6689 | 106.3788 | 111.4159 | 97.2611 | 100.9902 | 106.8798 | 112.202 | 119.5945 | 127.303 | 133.5986 | 139.5356 | 148.3593 | 154.7678 | 161.2258 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681 | 168.0681
90% | 4.538 | 88.8377 | 85.5907 | 89.803 | 75.7325 | 79.6851 | 83.7614 | 88.0926 | 93.0512 | 98.8914 | 104.3641 | 110.1162 | 119.9189 | 123.2397 | 129.512 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 134.3069 | 90% | 7.9414 | 103.8968 | 100.7799 | 105.5519 | 92.1421 | 95.6749 | 101.2545 | 106.2966 | 113.3001 | 120.6029 | 126.5671 | 132.1917 | 140.5509 | 146.6221 | 152.7403 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224 | 159.2224
85% | 7.9414 | 83.9023 | 80.8357 | 84.814 | 71.5251 | 75.2581 | 79.108 | 83.1986 | 87.8817 | 93.3975 | 98.5661 | 103.9987 | 113.2567 | 116.3931 | 122.3169 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 126.8454 | 85% | 14.3702 | 98.1248 | 95.181 | 99.6879 | 87.0231 | 90.3596 | 95.6293 | 100.3913 | 107.0056 | 113.9027 | 119.5356 | 124.8477 | 132.7425 | 138.4764 | 144.2547 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767 | 150.3767
80% | 11.7231 | 78.9669 | 76.0807 | 79.8249 | 67.3178 | 70.8312 | 74.4545 | 78.3045 | 82.7122 | 87.9035 | 92.7681 | 97.8811 | 106.5946 | 109.5464 | 115.1218 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 119.3839 | 80% | 19.6645 | 92.3527 | 89.5821 | 93.8239 | 81.904 | 85.0443 | 90.004 | 94.4859 | 100.7112 | 107.2025 | 112.5041 | 117.5037 | 124.9341 | 130.3307 | 135.7691 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531 | 141.531
75% | 17.7737 | 74.0314 | 71.3256 | 74.8358 | 63.1104 | 66.4042 | 69.8011 | 73.4105 | 77.5427 | 82.4095 | 86.9701 | 91.7635 | 99.9324 | 102.6998 | 107.9267 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 111.9224 | 75% | 25.7152 | 86.5807 | 83.9832 | 87.9599 | 76.785 | 79.7291 | 84.3788 | 88.5805 | 94.4167 | 100.5024 | 105.4726 | 110.1597 | 117.1257 | 122.1851 | 127.2836 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853 | 132.6853
70% | 35.1693 | 69.096 | 66.5706 | 69.8468 | 58.903 | 61.9773 | 65.1477 | 68.5165 | 72.3732 | 76.9156 | 81.1721 | 85.646 | 93.2703 | 95.8531 | 100.7316 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 104.4609 | 70% | 34.7911 | 80.8086 | 78.3843 | 82.0959 | 71.666 | 74.4138 | 78.7535 | 82.6751 | 88.1223 | 93.8022 | 98.4411 | 102.8157 | 109.3174 | 114.0394 | 118.798 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396 | 123.8396
65% | 59.3718 | 64.1606 | 61.8155 | 64.8577 | 54.6957 | 57.5503 | 60.4943 | 63.6224 | 67.2037 | 71.4216 | 75.3741 | 79.5284 | 86.6081 | 89.0065 | 93.5365 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 96.9994 | 65% | 46.136 | 75.0366 | 72.7855 | 76.2319 | 66.547 | 69.0985 | 73.1283 | 76.7698 | 81.8278 | 87.1021 | 91.4096 | 95.4717 | 101.509 | 105.8937 | 110.3124 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939 | 114.9939
60% | 156.9382 | 59.2251 | 57.0605 | 59.8687 | 50.4883 | 53.1234 | 55.8409 | 58.7284 | 62.0342 | 65.9276 | 69.5761 | 73.4108 | 79.9459 | 82.1598 | 86.3414 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 89.5379 | 60% | 76.7673 | 69.2645 | 67.1866 | 70.3679 | 61.428 | 63.7833 | 67.503 | 70.8644 | 75.5334 | 80.4019 | 84.3781 | 88.1278 | 93.7006 | 97.7481 | 101.8268 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483 | 106.1483
55% | 363.794 | 54.2897 | 52.3055 | 54.8796 | 46.281 | 48.6964 | 51.1875 | 53.8344 | 56.8647 | 60.4337 | 63.7781 | 67.2933 | 73.2838 | 75.3132 | 79.1462 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 82.0764 | 55% | 106.2642 | 63.4925 | 61.5877 | 64.5039 | 56.309 | 58.468 | 61.8778 | 64.959 | 69.2389 | 73.7017 | 77.3466 | 80.7838 | 85.8922 | 89.6024 | 93.3413 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026 | 97.3026
50% | 771.4551 | 49.3543 | 47.5504 | 49.8906 | 42.0736 | 44.2695 | 46.5341 | 48.9403 | 51.6951 | 54.9397 | 57.98 | 61.1757 | 66.6216 | 68.4665 | 71.9511 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 74.6149 | 50% | 178.4935 | 57.7205 | 55.9888 | 58.6399 | 51.19 | 53.1527 | 56.2525 | 59.0537 | 62.9445 | 67.0016 | 70.3151 | 73.4398 | 78.0838 | 81.4567 | 84.8557 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569 | 88.4569
45% | 1255.5054 | 44.4189 | 42.7954 | 44.9015 | 37.8662 | 39.8425 | 41.8807 | 44.0463 | 46.5256 | 49.4457 | 52.182 | 55.0581 | 59.9595 | 61.6199 | 64.756 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 67.1534 | 45% | 367.9538 | 51.9484 | 50.3899 | 52.7759 | 46.071 | 47.8374 | 50.6273 | 53.1483 | 56.65 | 60.3014 | 63.2836 | 66.0958 | 70.2754 | 73.311 | 76.3701 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112 | 79.6112
40% | 2059.1045 | 39.4834 | 38.0403 | 39.9125 | 33.6589 | 35.4156 | 37.2273 | 39.1523 | 41.3561 | 43.9517 | 46.384 | 48.9406 | 53.2973 | 54.7732 | 57.5609 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 59.6919 | 40% | 741.202 | 46.1764 | 44.7911 | 46.9119 | 40.952 | 42.5222 | 45.002 | 47.2429 | 50.3556 | 53.6013 | 56.2521 | 58.7518 | 62.4671 | 65.1654 | 67.8846 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655 | 70.7655
35% | 3060.4836 | 34.548 | 33.2853 | 34.9234 | 29.4515 | 30.9886 | 32.5739 | 34.2582 | 36.1866 | 38.4578 | 40.586 | 42.823 | 46.6351 | 47.9266 | 50.3658 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 52.2305 | 35% | 1167.7713 | 40.4043 | 39.1922 | 41.048 | 35.833 | 37.2069 | 39.3768 | 41.3376 | 44.0611 | 46.9011 | 49.2205 | 51.4079 | 54.6587 | 57.0197 | 59.399 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198 | 61.9198
30% | 3366.0403 | 29.6126 | 28.5302 | 29.9343 | 25.2442 | 26.5617 | 27.9205 | 29.3642 | 31.0171 | 32.9638 | 34.788 | 36.7054 | 39.973 | 41.0799 | 43.1707 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 44.769 | 30% | 2002.3799 | 34.6323 | 33.5933 | 35.184 | 30.714 | 31.8916 | 33.7515 | 35.4322 | 37.7667 | 40.201 | 42.189 | 44.0639 | 46.8503 | 48.874 | 50.9134 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741 | 53.0741
25% | 3686.3454 | 24.6771 | 23.7752 | 24.9453 | 21.0368 | 22.1347 | 23.267 | 24.4702 | 25.8476 | 27.4698 | 28.99 | 30.5878 | 33.3108 | 34.2333 | 35.9756 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 37.3075 | 25% | 3173.5547 | 28.8602 | 27.9944 | 29.32 | 25.595 | 26.5764 | 28.1263 | 29.5268 | 31.4722 | 33.5008 | 35.1575 | 36.7199 | 39.0419 | 40.7284 | 42.4279 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284 | 44.2284
20% | 4028.5841 | 19.7417 | 19.0202 | 19.9562 | 16.8294 | 17.7078 | 18.6136 | 19.5761 | 20.6781 | 21.9759 | 23.192 | 24.4703 | 26.6486 | 27.3866 | 28.7805 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 29.846 | 20% | 3477.5988 | 23.0882 | 22.3955 | 23.456 | 20.476 | 21.2611 | 22.501 | 23.6215 | 25.1778 | 26.8006 | 28.126 | 29.3759 | 31.2335 | 32.5827 | 33.9423 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828 | 35.3828
15% | 4345.1076 | 14.8063 | 14.2651 | 14.9672 | 12.6221 | 13.2808 | 13.9602 | 14.6821 | 15.5085 | 16.4819 | 17.394 | 18.3527 | 19.9865 | 20.54 | 21.5853 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 22.3845 | 15% | 3788.4498 | 17.3161 | 16.7966 | 17.592 | 15.357 | 15.9458 | 16.8758 | 17.7161 | 18.8833 | 20.1005 | 21.0945 | 22.0319 | 23.4251 | 24.437 | 25.4567 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371 | 26.5371
10% | 4381.0332 | 9.8709 | 9.5101 | 9.9781 | 8.4147 | 8.8539 | 9.3068 | 9.7881 | 10.339 | 10.9879 | 11.596 | 12.2351 | 13.3243 | 13.6933 | 14.3902 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 14.923 | 10% | 4317.5016 | 11.5441 | 11.1978 | 11.728 | 10.238 | 10.6305 | 11.2505 | 11.8107 | 12.5889 | 13.4003 | 14.063 | 14.688 | 15.6168 | 16.2913 | 16.9711 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914 | 17.6914
5% | 4391.6218 | 4.9354 | 4.755 | 4.9891 | 4.2074 | 4.4269 | 4.6534 | 4.894 | 5.1695 | 5.494 | 5.798 | 6.1176 | 6.6622 | 6.8467 | 7.1951 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 7.4615 | 5% | 4391.6218 | 5.772 | 5.5989 | 5.864 | 5.119 | 5.3153 | 5.6253 | 5.9054 | 6.2944 | 6.7002 | 7.0315 | 7.344 | 7.8084 | 8.1457 | 8.4856 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457 | 8.8457
9.992e-14% | 4391.6218 | 9.863e-14 | 9.5025e-14 | 9.9701e-14 | 8.408e-14 | 8.8468e-14 | 9.2994e-14 | 9.7802e-14 | 1.0331e-13 | 1.0979e-13 | 1.1587e-13 | 1.2225e-13 | 1.3314e-13 | 1.3682e-13 | 1.4379e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 1.4911e-13 | 9.992e-14% | 4391.6218 | 1.1535e-13 | 1.1189e-13 | 1.1719e-13 | 1.023e-13 | 1.0622e-13 | 1.1242e-13 | 1.1801e-13 | 1.2579e-13 | 1.339e-13 | 1.4052e-13 | 1.4676e-13 | 1.5604e-13 | 1.6278e-13 | 1.6958e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 100% | 0 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
99% | 0.5944 | 75.2697 | 72.57 | 76.7928 | 82.1977 | 87.4309 | 92.086 | 98.4899 | 105.4924 | 112.6644 | 119.7723 | 126.0867 | 132.972 | 135.5855 | 144.4923 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 99% | 0.5944 | 80.6056 | 77.9271 | 82.3913 | 87.863 | 92.9632 | 98.3955 | 104.1109 | 112.2739 | 119.388 | 126.0974 | 133.0715 | 141.4362 | 144.2205 | 153.2427 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515
98% | 0.8916 | 74.5094 | 71.8369 | 76.0171 | 81.3674 | 86.5478 | 91.1558 | 97.4951 | 104.4268 | 111.5264 | 118.5625 | 124.8131 | 131.6288 | 134.216 | 143.0328 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 98% | 0.8916 | 79.7914 | 77.14 | 81.5591 | 86.9755 | 92.0241 | 97.4016 | 103.0593 | 111.1398 | 118.182 | 124.8237 | 131.7273 | 140.0075 | 142.7637 | 151.6948 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186
97% | 1.486 | 73.7491 | 71.1039 | 75.2415 | 80.5371 | 85.6646 | 90.2257 | 96.5003 | 103.3612 | 110.3883 | 117.3527 | 123.5395 | 130.2857 | 132.8464 | 141.5732 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 97% | 1.486 | 78.9772 | 76.3529 | 80.7268 | 86.0879 | 91.0851 | 96.4077 | 102.0076 | 110.0058 | 116.9761 | 123.5499 | 130.3832 | 138.5789 | 141.307 | 150.1469 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858
95% | 2.3776 | 72.2285 | 69.6379 | 73.6901 | 78.8766 | 83.8984 | 88.3653 | 94.5106 | 101.23 | 108.1123 | 114.933 | 120.9923 | 127.5994 | 130.1073 | 138.6542 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 95% | 2.3776 | 77.3488 | 74.7786 | 79.0624 | 84.3129 | 89.2071 | 94.42 | 99.9044 | 107.7376 | 114.5642 | 121.0025 | 127.6949 | 135.7216 | 138.3934 | 147.0511 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201
90% | 3.2692 | 68.427 | 65.9727 | 69.8117 | 74.7252 | 79.4827 | 83.7145 | 89.5363 | 95.9021 | 102.4222 | 108.8839 | 114.6242 | 120.8836 | 123.2596 | 131.3566 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 90% | 3.2692 | 73.2778 | 70.8429 | 74.9012 | 79.8754 | 84.512 | 89.4505 | 94.6463 | 102.0672 | 108.5345 | 114.634 | 120.9741 | 128.5784 | 131.1095 | 139.3116 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559
85% | 13.9683 | 64.6255 | 62.3076 | 65.9332 | 70.5738 | 75.067 | 79.0637 | 84.5621 | 90.5743 | 96.732 | 102.8348 | 108.2562 | 114.1679 | 116.4118 | 124.059 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 85% | 13.9683 | 69.2069 | 66.9071 | 70.74 | 75.4379 | 79.8168 | 84.481 | 89.3881 | 96.3968 | 102.5048 | 108.2654 | 114.2533 | 121.4351 | 123.8257 | 131.572 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917
80% | 41.3106 | 60.824 | 58.6424 | 62.0548 | 66.4224 | 70.6513 | 74.4129 | 79.5878 | 85.2464 | 91.0419 | 96.7857 | 101.8882 | 107.4521 | 109.5641 | 116.7614 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 80% | 41.3106 | 65.1359 | 62.9714 | 66.5788 | 71.0004 | 75.1217 | 79.5115 | 84.13 | 90.7264 | 96.4751 | 101.8969 | 107.5325 | 114.2919 | 116.5418 | 123.8325 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274
75% | 126.3094 | 57.0225 | 54.9773 | 58.1764 | 62.271 | 66.2356 | 69.7621 | 74.6136 | 79.9185 | 85.3518 | 90.7366 | 95.5202 | 100.7363 | 102.7163 | 109.4638 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 75% | 126.3094 | 61.0649 | 59.0357 | 62.4177 | 66.5628 | 70.4266 | 74.5421 | 78.8719 | 85.056 | 90.4454 | 95.5283 | 100.8117 | 107.1486 | 109.258 | 116.093 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632
70% | 323.9464 | 53.221 | 51.3121 | 54.298 | 58.1196 | 61.8198 | 65.1113 | 69.6394 | 74.5906 | 79.6617 | 84.6875 | 89.1522 | 94.0206 | 95.8685 | 102.1663 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 70% | 323.9464 | 56.9939 | 55.1 | 58.2565 | 62.1253 | 65.7315 | 69.5726 | 73.6138 | 79.3856 | 84.4157 | 89.1598 | 94.091 | 100.0054 | 101.9741 | 108.3534 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299
65% | 549.5201 | 49.4195 | 47.647 | 50.4195 | 53.9682 | 57.4041 | 60.4605 | 64.6651 | 69.2627 | 73.9716 | 78.6384 | 82.7842 | 87.3048 | 89.0208 | 94.8687 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 65% | 549.5201 | 52.9229 | 51.1643 | 54.0953 | 57.6878 | 61.0364 | 64.6031 | 68.3556 | 73.7152 | 78.386 | 82.7912 | 87.3702 | 92.8621 | 94.6902 | 100.6139 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348
60% | 799.4641 | 45.618 | 43.9818 | 46.5411 | 49.8168 | 52.9884 | 55.8097 | 59.6909 | 63.9348 | 68.2814 | 72.5893 | 76.4162 | 80.5891 | 82.173 | 87.5711 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 60% | 799.4641 | 48.8519 | 47.2286 | 49.9341 | 53.2503 | 56.3413 | 59.6337 | 63.0975 | 68.0448 | 72.3563 | 76.4226 | 80.6494 | 85.7189 | 87.4064 | 92.8744 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706
55% | 1116.2777 | 41.8165 | 40.3167 | 42.6627 | 45.6654 | 48.5727 | 51.1589 | 54.7166 | 58.6069 | 62.5913 | 66.5402 | 70.0481 | 73.8733 | 75.3253 | 80.2735 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 55% | 1116.2777 | 44.7809 | 43.2929 | 45.773 | 48.8128 | 51.6462 | 54.6642 | 57.8394 | 62.3744 | 66.3266 | 70.0541 | 73.9286 | 78.5757 | 80.1225 | 85.1348 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064
50% | 1494.9086 | 38.015 | 36.6515 | 38.7843 | 41.514 | 44.157 | 46.5081 | 49.7424 | 53.279 | 56.9012 | 60.4911 | 63.6801 | 67.1576 | 68.4775 | 72.9759 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 50% | 1494.9086 | 40.7099 | 39.3571 | 41.6118 | 44.3752 | 46.9511 | 49.6947 | 52.5813 | 56.704 | 60.297 | 63.6855 | 67.2078 | 71.4324 | 72.8386 | 77.3953 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422
45% | 2004.0097 | 34.2135 | 32.9864 | 34.9058 | 37.3626 | 39.7413 | 41.8573 | 44.7682 | 47.9511 | 51.2111 | 54.442 | 57.3121 | 60.4418 | 61.6298 | 65.6783 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 45% | 2004.0097 | 36.6389 | 35.4214 | 37.4506 | 39.9377 | 42.256 | 44.7252 | 47.3231 | 51.0336 | 54.2673 | 57.317 | 60.487 | 64.2892 | 65.5548 | 69.6558 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779
40% | 2877.179 | 30.412 | 29.3212 | 31.0274 | 33.2112 | 35.3256 | 37.2065 | 39.7939 | 42.6232 | 45.521 | 48.3929 | 50.9441 | 53.7261 | 54.782 | 58.3807 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 40% | 2877.179 | 32.5679 | 31.4857 | 33.2894 | 35.5002 | 37.5609 | 39.7558 | 42.065 | 45.3632 | 48.2376 | 50.9484 | 53.7663 | 57.1459 | 58.2709 | 61.9162 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137
35% | 3454.933 | 26.6105 | 25.6561 | 27.149 | 29.0598 | 30.9099 | 32.5556 | 34.8197 | 37.2953 | 39.8308 | 42.3438 | 44.5761 | 47.0103 | 47.9343 | 51.0831 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 35% | 3454.933 | 28.4969 | 27.55 | 29.1282 | 31.0627 | 32.8658 | 34.7863 | 36.8069 | 39.6928 | 42.2079 | 44.5799 | 47.0455 | 50.0027 | 50.987 | 54.1767 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495
30% | 3663.5664 | 22.809 | 21.9909 | 23.2706 | 24.9084 | 26.4942 | 27.9048 | 29.8454 | 31.9674 | 34.1407 | 36.2946 | 38.2081 | 40.2945 | 41.0865 | 43.7855 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 30% | 3663.5664 | 24.4259 | 23.6143 | 24.9671 | 26.6251 | 28.1707 | 29.8168 | 31.5488 | 34.0224 | 36.1782 | 38.2113 | 40.3247 | 42.8595 | 43.7032 | 46.4372 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853
25% | 3862.6894 | 19.0075 | 18.3258 | 19.3921 | 20.757 | 22.0785 | 23.254 | 24.8712 | 26.6395 | 28.4506 | 30.2455 | 31.8401 | 33.5788 | 34.2388 | 36.4879 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 25% | 3862.6894 | 20.355 | 19.6786 | 20.8059 | 22.1876 | 23.4755 | 24.8474 | 26.2906 | 28.352 | 30.1485 | 31.8428 | 33.6039 | 35.7162 | 36.4193 | 38.6977 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211
20% | 4122.7381 | 15.206 | 14.6606 | 15.5137 | 16.6056 | 17.6628 | 18.6032 | 19.897 | 21.3116 | 22.7605 | 24.1964 | 25.4721 | 26.863 | 27.391 | 29.1904 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 20% | 4122.7381 | 16.284 | 15.7429 | 16.6447 | 17.7501 | 18.7804 | 19.8779 | 21.0325 | 22.6816 | 24.1188 | 25.4742 | 26.8831 | 28.573 | 29.1355 | 30.9581 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569
15% | 4372.3849 | 11.4045 | 10.9955 | 11.6353 | 12.4542 | 13.2471 | 13.9524 | 14.9227 | 15.9837 | 17.0704 | 18.1473 | 19.104 | 20.1473 | 20.5433 | 21.8928 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 15% | 4372.3849 | 12.213 | 11.8071 | 12.4835 | 13.3126 | 14.0853 | 14.9084 | 15.7744 | 17.0112 | 18.0891 | 19.1057 | 20.1623 | 21.4297 | 21.8516 | 23.2186 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926
10% | 4374.4653 | 7.603 | 7.3303 | 7.7569 | 8.3028 | 8.8314 | 9.3016 | 9.9485 | 10.6558 | 11.3802 | 12.0982 | 12.736 | 13.4315 | 13.6955 | 14.5952 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 10% | 4374.4653 | 8.142 | 7.8714 | 8.3224 | 8.875 | 9.3902 | 9.9389 | 10.5163 | 11.3408 | 12.0594 | 12.7371 | 13.4416 | 14.2865 | 14.5677 | 15.4791 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284
5% | 4374.7625 | 3.8015 | 3.6652 | 3.8784 | 4.1514 | 4.4157 | 4.6508 | 4.9742 | 5.3279 | 5.6901 | 6.0491 | 6.368 | 6.7158 | 6.8478 | 7.2976 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 5% | 4374.7625 | 4.071 | 3.9357 | 4.1612 | 4.4375 | 4.6951 | 4.9695 | 5.2581 | 5.6704 | 6.0297 | 6.3686 | 6.7208 | 7.1432 | 7.2839 | 7.7395 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642
9.992e-14% | 4375.9513 | 7.5969e-14 | 7.3244e-14 | 7.7507e-14 | 8.2962e-14 | 8.8243e-14 | 9.2942e-14 | 9.9405e-14 | 1.0647e-13 | 1.1371e-13 | 1.2089e-13 | 1.2726e-13 | 1.3421e-13 | 1.3685e-13 | 1.4584e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 9.992e-14% | 4375.9513 | 8.1355e-14 | 7.8651e-14 | 8.3157e-14 | 8.868e-14 | 9.3827e-14 | 9.931e-14 | 1.0508e-13 | 1.1332e-13 | 1.205e-13 | 1.2727e-13 | 1.3431e-13 | 1.4275e-13 | 1.4556e-13 | 1.5467e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 100% | 0 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471
99% | 0 | 97.7215 | 94.1498 | 98.7833 | 102.4457 | 106.7936 | 111.2775 | 116.0419 | 121.4964 | 127.9206 | 133.9405 | 140.2679 | 151.0508 | 154.7037 | 161.6032 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 99% | 0.37816 | 114.2865 | 110.8579 | 116.1071 | 120.4963 | 124.3824 | 130.52 | 136.0663 | 143.7701 | 151.8031 | 158.3638 | 164.5508 | 173.746 | 180.4243 | 187.1543 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846
98% | 0.37816 | 96.7344 | 93.1988 | 97.7855 | 101.4109 | 105.7149 | 110.1535 | 114.8697 | 120.2691 | 126.6285 | 132.5876 | 138.851 | 149.525 | 153.1411 | 159.9709 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 98% | 1.1345 | 113.1321 | 109.7381 | 114.9343 | 119.2791 | 123.126 | 129.2016 | 134.6919 | 142.3179 | 150.2698 | 156.7642 | 162.8887 | 171.991 | 178.6018 | 185.2638 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222
97% | 0.75633 | 95.7473 | 92.2478 | 96.7877 | 100.3761 | 104.6362 | 109.0295 | 113.6976 | 119.0419 | 125.3363 | 131.2346 | 137.4342 | 147.9993 | 151.5784 | 158.3385 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 97% | 2.269 | 111.9777 | 108.6183 | 113.7615 | 118.062 | 121.8696 | 127.8832 | 133.3175 | 140.8656 | 148.7364 | 155.1646 | 161.2266 | 170.236 | 176.7794 | 183.3734 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597
95% | 1.1345 | 93.7731 | 90.3458 | 94.7921 | 98.3065 | 102.4787 | 106.7814 | 111.3533 | 116.5874 | 122.7521 | 128.5288 | 134.6005 | 144.9477 | 148.4531 | 155.0738 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 95% | 4.538 | 109.6689 | 106.3788 | 111.4159 | 115.6277 | 119.3568 | 125.2464 | 130.5687 | 137.9612 | 145.6697 | 151.9653 | 157.9023 | 166.7259 | 173.1344 | 179.5925 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347
90% | 4.538 | 88.8377 | 85.5907 | 89.803 | 93.1325 | 97.0851 | 101.1614 | 105.4926 | 110.4512 | 116.2914 | 121.7641 | 127.5162 | 137.3189 | 140.6397 | 146.912 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 90% | 7.9414 | 103.8968 | 100.7799 | 105.5519 | 109.5421 | 113.0749 | 118.6545 | 123.6966 | 130.7001 | 138.0029 | 143.9671 | 149.5917 | 157.9509 | 164.0221 | 170.1403 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224
85% | 7.9414 | 83.9023 | 80.8357 | 84.814 | 87.9585 | 91.6915 | 95.5413 | 99.6319 | 104.3151 | 109.8308 | 114.9994 | 120.432 | 129.6901 | 132.8264 | 138.7503 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 85% | 14.3702 | 98.1248 | 95.181 | 99.6879 | 103.4564 | 106.7929 | 112.0626 | 116.8246 | 123.439 | 130.336 | 135.969 | 141.281 | 149.1758 | 154.9097 | 160.688 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81
80% | 11.7231 | 78.9669 | 76.0807 | 79.8249 | 82.7844 | 86.2979 | 89.9212 | 93.7712 | 98.1789 | 103.3702 | 108.2347 | 113.3478 | 122.0613 | 125.0131 | 130.5885 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 80% | 19.6645 | 92.3527 | 89.5821 | 93.8239 | 97.3707 | 100.511 | 105.4707 | 109.9526 | 116.1778 | 122.6692 | 127.9708 | 132.9704 | 140.4008 | 145.7974 | 151.2358 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977
75% | 17.7737 | 74.0314 | 71.3256 | 74.8358 | 77.6104 | 80.9042 | 84.3011 | 87.9105 | 92.0427 | 96.9095 | 101.4701 | 106.2635 | 114.4324 | 117.1998 | 122.4267 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 75% | 25.7152 | 86.5807 | 83.9832 | 87.9599 | 91.285 | 94.2291 | 98.8788 | 103.0805 | 108.9167 | 115.0024 | 119.9726 | 124.6597 | 131.6257 | 136.6851 | 141.7836 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853
70% | 35.1693 | 69.096 | 66.5706 | 69.8468 | 72.4364 | 75.5106 | 78.6811 | 82.0498 | 85.9065 | 90.4489 | 94.7054 | 99.1793 | 106.8036 | 109.3865 | 114.2649 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 70% | 34.7911 | 80.8086 | 78.3843 | 82.0959 | 85.1994 | 87.9471 | 92.2868 | 96.2085 | 101.6556 | 107.3356 | 111.9744 | 116.3491 | 122.8507 | 127.5727 | 132.3313 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373
65% | 59.3718 | 64.1606 | 61.8155 | 64.8577 | 67.2623 | 70.117 | 73.061 | 76.1891 | 79.7703 | 83.9883 | 87.9407 | 92.0951 | 99.1748 | 101.5731 | 106.1031 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 65% | 46.136 | 75.0366 | 72.7855 | 76.2319 | 79.1137 | 81.6652 | 85.6949 | 89.3364 | 94.3945 | 99.6687 | 103.9763 | 108.0384 | 114.0756 | 118.4604 | 122.8791 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606
60% | 156.9382 | 59.2251 | 57.0605 | 59.8687 | 62.0883 | 64.7234 | 67.4409 | 70.3284 | 73.6342 | 77.5276 | 81.1761 | 85.0108 | 91.5459 | 93.7598 | 97.9414 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 60% | 76.7673 | 69.2645 | 67.1866 | 70.3679 | 73.028 | 75.3833 | 79.103 | 82.4644 | 87.1334 | 92.0019 | 95.9781 | 99.7278 | 105.3006 | 109.3481 | 113.4268 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483
55% | 363.794 | 54.2897 | 52.3055 | 54.8796 | 56.9143 | 59.3298 | 61.8208 | 64.4677 | 67.498 | 71.067 | 74.4114 | 77.9266 | 83.9171 | 85.9465 | 89.7796 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 55% | 106.2642 | 63.4925 | 61.5877 | 64.5039 | 66.9424 | 69.1013 | 72.5111 | 75.5924 | 79.8723 | 84.3351 | 87.9799 | 91.4171 | 96.5255 | 100.2357 | 103.9746 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359
50% | 771.4551 | 49.3543 | 47.5504 | 49.8906 | 51.7403 | 53.9362 | 56.2008 | 58.607 | 61.3618 | 64.6064 | 67.6467 | 70.8424 | 76.2883 | 78.1332 | 81.6178 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 50% | 178.4935 | 57.7205 | 55.9888 | 58.6399 | 60.8567 | 62.8194 | 65.9192 | 68.7203 | 72.6112 | 76.6683 | 79.9817 | 83.1065 | 87.7505 | 91.1234 | 94.5224 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235
45% | 1255.5054 | 44.4189 | 42.7954 | 44.9015 | 46.5662 | 48.5425 | 50.5807 | 52.7463 | 55.2256 | 58.1457 | 60.882 | 63.7581 | 68.6595 | 70.3199 | 73.456 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 45% | 367.9538 | 51.9484 | 50.3899 | 52.7759 | 54.771 | 56.5374 | 59.3273 | 61.8483 | 65.35 | 69.0014 | 71.9836 | 74.7958 | 78.9754 | 82.011 | 85.0701 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112
40% | 2059.1045 | 39.4834 | 38.0403 | 39.9125 | 41.3922 | 43.1489 | 44.9606 | 46.8856 | 49.0894 | 51.6851 | 54.1174 | 56.6739 | 61.0306 | 62.5066 | 65.2942 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 40% | 741.202 | 46.1764 | 44.7911 | 46.9119 | 48.6854 | 50.2555 | 52.7353 | 54.9763 | 58.0889 | 61.3346 | 63.9854 | 66.4852 | 70.2004 | 72.8987 | 75.6179 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988
35% | 3060.4836 | 34.548 | 33.2853 | 34.9234 | 36.2182 | 37.7553 | 39.3405 | 41.0249 | 42.9533 | 45.2244 | 47.3527 | 49.5897 | 53.4018 | 54.6932 | 57.1325 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 35% | 1167.7713 | 40.4043 | 39.1922 | 41.048 | 42.5997 | 43.9736 | 46.1434 | 48.1042 | 50.8278 | 53.6678 | 55.9872 | 58.1745 | 61.4253 | 63.7864 | 66.1657 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865
30% | 3366.0403 | 29.6126 | 28.5302 | 29.9343 | 31.0442 | 32.3617 | 33.7205 | 35.1642 | 36.8171 | 38.7638 | 40.588 | 42.5054 | 45.773 | 46.8799 | 48.9707 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 30% | 2002.3799 | 34.6323 | 33.5933 | 35.184 | 36.514 | 37.6916 | 39.5515 | 41.2322 | 43.5667 | 46.001 | 47.989 | 49.8639 | 52.6503 | 54.674 | 56.7134 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741
25% | 3686.3454 | 24.6771 | 23.7752 | 24.9453 | 25.8701 | 26.9681 | 28.1004 | 29.3035 | 30.6809 | 32.3032 | 33.8234 | 35.4212 | 38.1441 | 39.0666 | 40.8089 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 25% | 3173.5547 | 28.8602 | 27.9944 | 29.32 | 30.4283 | 31.4097 | 32.9596 | 34.3602 | 36.3056 | 38.3341 | 39.9909 | 41.5532 | 43.8752 | 45.5617 | 47.2612 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618
20% | 4028.5841 | 19.7417 | 19.0202 | 19.9562 | 20.6961 | 21.5745 | 22.4803 | 23.4428 | 24.5447 | 25.8425 | 27.0587 | 28.3369 | 30.5153 | 31.2533 | 32.6471 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 20% | 3477.5988 | 23.0882 | 22.3955 | 23.456 | 24.3427 | 25.1278 | 26.3677 | 27.4881 | 29.0445 | 30.6673 | 31.9927 | 33.2426 | 35.1002 | 36.4494 | 37.8089 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494
15% | 4345.1076 | 14.8063 | 14.2651 | 14.9672 | 15.5221 | 16.1808 | 16.8602 | 17.5821 | 18.4085 | 19.3819 | 20.294 | 21.2527 | 22.8865 | 23.44 | 24.4853 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 15% | 3788.4498 | 17.3161 | 16.7966 | 17.592 | 18.257 | 18.8458 | 19.7758 | 20.6161 | 21.7833 | 23.0005 | 23.9945 | 24.9319 | 26.3251 | 27.337 | 28.3567 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371
10% | 4381.0332 | 9.8709 | 9.5101 | 9.9781 | 10.3481 | 10.7872 | 11.2402 | 11.7214 | 12.2724 | 12.9213 | 13.5293 | 14.1685 | 15.2577 | 15.6266 | 16.3236 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 10% | 4317.5016 | 11.5441 | 11.1978 | 11.728 | 12.1713 | 12.5639 | 13.1838 | 13.7441 | 14.5222 | 15.3337 | 15.9963 | 16.6213 | 17.5501 | 18.2247 | 18.9045 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247
5% | 4391.6218 | 4.9354 | 4.755 | 4.9891 | 5.174 | 5.3936 | 5.6201 | 5.8607 | 6.1362 | 6.4606 | 6.7647 | 7.0842 | 7.6288 | 7.8133 | 8.1618 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 5% | 4391.6218 | 5.772 | 5.5989 | 5.864 | 6.0857 | 6.2819 | 6.5919 | 6.872 | 7.2611 | 7.6668 | 7.9982 | 8.3106 | 8.775 | 9.1123 | 9.4522 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124
9.992e-14% | 4391.6218 | 9.863e-14 | 9.5025e-14 | 9.9701e-14 | 1.034e-13 | 1.0779e-13 | 1.1231e-13 | 1.1712e-13 | 1.2263e-13 | 1.2911e-13 | 1.3519e-13 | 1.4157e-13 | 1.5245e-13 | 1.5614e-13 | 1.6311e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 9.992e-14% | 4391.6218 | 1.1535e-13 | 1.1189e-13 | 1.1719e-13 | 1.2162e-13 | 1.2554e-13 | 1.3173e-13 | 1.3733e-13 | 1.4511e-13 | 1.5321e-13 | 1.5984e-13 | 1.6608e-13 | 1.7536e-13 | 1.821e-13 | 1.8889e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 69.1452 | 65.4519 | 69.4173 | 74.6284 | 79.6959 | 84.0438 | 90.1932 | 96.8172 | 103.5926 | 110.3915 | 116.4112 | 122.8258 | 125.0778 | 133.6828 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 142.5741 | 100% | 0 | 74.5351 | 70.8632 | 75.0723 | 80.3509 | 85.284 | 90.4171 | 95.8709 | 103.6672 | 110.3841 | 116.7804 | 123.4666 | 131.3755 | 133.8 | 142.5216 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989 | 150.5989
99% | 0.5944 | 68.4538 | 64.7974 | 68.7231 | 73.8822 | 78.899 | 83.2033 | 89.2913 | 95.849 | 102.5567 | 109.2875 | 115.2471 | 121.5976 | 123.827 | 132.346 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 141.1483 | 99% | 0.5944 | 73.7897 | 70.1545 | 74.3216 | 79.5474 | 84.4312 | 89.5129 | 94.9122 | 102.6306 | 109.2803 | 115.6126 | 122.2319 | 130.0618 | 132.462 | 141.0964 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929 | 149.0929
98% | 0.8916 | 67.7623 | 64.1428 | 68.0289 | 73.1359 | 78.102 | 82.3629 | 88.3893 | 94.8808 | 101.5208 | 108.1836 | 114.083 | 120.3693 | 122.5762 | 131.0091 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 139.7226 | 98% | 0.8916 | 73.0444 | 69.4459 | 73.5709 | 78.7439 | 83.5783 | 88.6087 | 93.9535 | 101.5939 | 108.1764 | 114.4448 | 120.9972 | 128.748 | 131.124 | 139.6712 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869 | 147.5869
97% | 1.486 | 67.0709 | 63.4883 | 67.3348 | 72.3896 | 77.305 | 81.5224 | 87.4874 | 93.9127 | 100.4848 | 107.0797 | 112.9188 | 119.1411 | 121.3254 | 129.6723 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 138.2969 | 97% | 1.486 | 72.299 | 68.7373 | 72.8201 | 77.9404 | 82.7255 | 87.7045 | 92.9948 | 100.5572 | 107.0726 | 113.277 | 119.7626 | 127.4343 | 129.786 | 138.246 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809 | 146.0809
95% | 2.3776 | 65.688 | 62.1793 | 65.9464 | 70.897 | 75.7111 | 79.8416 | 85.6835 | 91.9763 | 98.413 | 104.8719 | 110.5906 | 116.6845 | 118.8239 | 126.9986 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 135.4454 | 95% | 2.3776 | 70.8083 | 67.32 | 71.3187 | 76.3334 | 81.0198 | 85.8962 | 91.0774 | 98.4839 | 104.8649 | 110.9414 | 117.2932 | 124.8068 | 127.11 | 135.3955 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689 | 143.0689
90% | 3.2692 | 62.2307 | 58.9067 | 62.4755 | 67.1656 | 71.7263 | 75.6394 | 81.1739 | 87.1355 | 93.2334 | 99.3523 | 104.7701 | 110.5432 | 112.57 | 120.3145 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 128.3167 | 90% | 3.2692 | 67.0815 | 63.7768 | 67.5651 | 72.3158 | 76.7556 | 81.3753 | 86.2838 | 93.3005 | 99.3457 | 105.1023 | 111.1199 | 118.238 | 120.42 | 128.2694 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539 | 135.539
85% | 13.9683 | 58.7735 | 55.6341 | 59.0047 | 63.4342 | 67.7415 | 71.4372 | 76.6642 | 82.2946 | 88.0537 | 93.8327 | 98.9495 | 104.402 | 106.3161 | 113.6304 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 121.188 | 85% | 13.9683 | 63.3548 | 60.2337 | 63.8115 | 68.2983 | 72.4914 | 76.8545 | 81.4903 | 88.1171 | 93.8265 | 99.2633 | 104.9466 | 111.6692 | 113.73 | 121.1434 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009 | 128.009
80% | 41.3106 | 55.3162 | 52.3615 | 55.5338 | 59.7027 | 63.7567 | 67.235 | 72.1546 | 77.4537 | 82.8741 | 88.3132 | 93.1289 | 98.2607 | 100.0622 | 106.9462 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 114.0593 | 80% | 41.3106 | 59.628 | 56.6905 | 60.0578 | 64.2807 | 68.2272 | 72.3336 | 76.6967 | 82.9338 | 88.3073 | 93.4243 | 98.7732 | 105.1004 | 107.04 | 114.0173 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791 | 120.4791
75% | 126.3094 | 51.8589 | 49.0889 | 52.063 | 55.9713 | 59.7719 | 63.0328 | 67.6449 | 72.6129 | 77.6945 | 82.7936 | 87.3084 | 92.1194 | 93.8083 | 100.2621 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 106.9306 | 75% | 126.3094 | 55.9013 | 53.1474 | 56.3042 | 60.2632 | 63.963 | 67.8128 | 71.9032 | 77.7504 | 82.7881 | 87.5853 | 92.5999 | 98.5317 | 100.35 | 106.8912 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492 | 112.9492
70% | 323.9464 | 48.4017 | 45.8163 | 48.5921 | 52.2399 | 55.7871 | 58.8306 | 63.1352 | 67.772 | 72.5148 | 77.274 | 81.4878 | 85.9781 | 87.5544 | 93.578 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 99.8019 | 70% | 323.9464 | 52.1745 | 49.6042 | 52.5506 | 56.2456 | 59.6988 | 63.2919 | 67.1096 | 72.5671 | 77.2689 | 81.7463 | 86.4266 | 91.9629 | 93.66 | 99.7651 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192 | 105.4192
65% | 549.5201 | 44.9444 | 42.5437 | 45.1212 | 48.5085 | 51.8023 | 54.6284 | 58.6256 | 62.9312 | 67.3352 | 71.7544 | 75.6673 | 79.8368 | 81.3006 | 86.8938 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 92.6732 | 65% | 549.5201 | 48.4478 | 46.0611 | 48.797 | 52.2281 | 55.4346 | 58.7711 | 62.3161 | 67.3837 | 71.7497 | 75.9073 | 80.2533 | 85.3941 | 86.97 | 92.639 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893 | 97.8893
60% | 799.4641 | 41.4871 | 39.2711 | 41.6504 | 44.7771 | 47.8176 | 50.4263 | 54.1159 | 58.0903 | 62.1556 | 66.2349 | 69.8467 | 73.6955 | 75.0467 | 80.2097 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 85.5444 | 60% | 799.4641 | 44.721 | 42.5179 | 45.0434 | 48.2105 | 51.1704 | 54.2502 | 57.5225 | 62.2003 | 66.2305 | 70.0682 | 74.0799 | 78.8253 | 80.28 | 85.513 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593 | 90.3593
55% | 1116.2777 | 38.0299 | 35.9985 | 38.1795 | 41.0456 | 43.8328 | 46.2241 | 49.6063 | 53.2494 | 56.9759 | 60.7153 | 64.0261 | 67.5542 | 68.7928 | 73.5255 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 78.4157 | 55% | 1116.2777 | 40.9943 | 38.9747 | 41.2898 | 44.193 | 46.9062 | 49.7294 | 52.729 | 57.017 | 60.7113 | 64.2292 | 67.9066 | 72.2565 | 73.59 | 78.3869 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294 | 82.8294
50% | 1494.9086 | 34.5726 | 32.7259 | 34.7086 | 37.3142 | 39.848 | 42.0219 | 45.0966 | 48.4086 | 51.7963 | 55.1957 | 58.2056 | 61.4129 | 62.5389 | 66.8414 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 71.287 | 50% | 1494.9086 | 37.2675 | 35.4316 | 37.5362 | 40.1755 | 42.642 | 45.2085 | 47.9355 | 51.8336 | 55.1921 | 58.3902 | 61.7333 | 65.6878 | 66.9 | 71.2608 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994 | 75.2994
45% | 2004.0097 | 31.1154 | 29.4533 | 31.2378 | 33.5828 | 35.8632 | 37.8197 | 40.5869 | 43.5677 | 46.6167 | 49.6762 | 52.385 | 55.2716 | 56.285 | 60.1573 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 64.1583 | 45% | 2004.0097 | 33.5408 | 31.8884 | 33.7825 | 36.1579 | 38.3778 | 40.6877 | 43.1419 | 46.6503 | 49.6729 | 52.5512 | 55.56 | 59.119 | 60.21 | 64.1347 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695 | 67.7695
40% | 2877.179 | 27.6581 | 26.1808 | 27.7669 | 29.8514 | 31.8784 | 33.6175 | 36.0773 | 38.7269 | 41.4371 | 44.1566 | 46.5645 | 49.1303 | 50.0311 | 53.4731 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 57.0296 | 40% | 2877.179 | 29.814 | 28.3453 | 30.0289 | 32.1404 | 34.1136 | 36.1668 | 38.3484 | 41.4669 | 44.1536 | 46.7122 | 49.3866 | 52.5502 | 53.52 | 57.0086 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396 | 60.2396
35% | 3454.933 | 24.2008 | 22.9082 | 24.296 | 26.12 | 27.8936 | 29.4153 | 31.5676 | 33.886 | 36.2574 | 38.637 | 40.7439 | 42.989 | 43.7772 | 46.789 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 49.9009 | 35% | 3454.933 | 26.0873 | 24.8021 | 26.2753 | 28.1228 | 29.8494 | 31.646 | 33.5548 | 36.2835 | 38.6344 | 40.8731 | 43.2133 | 45.9814 | 46.83 | 49.8826 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096 | 52.7096
30% | 3663.5664 | 20.7436 | 19.6356 | 20.8252 | 22.3885 | 23.9088 | 25.2131 | 27.058 | 29.0452 | 31.0778 | 33.1174 | 34.9234 | 36.8477 | 37.5233 | 40.1048 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 42.7722 | 30% | 3663.5664 | 22.3605 | 21.2589 | 22.5217 | 24.1053 | 25.5852 | 27.1251 | 28.7613 | 31.1002 | 33.1152 | 35.0341 | 37.04 | 39.4127 | 40.14 | 42.7565 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797 | 45.1797
25% | 3862.6894 | 17.2863 | 16.363 | 17.3543 | 18.6571 | 19.924 | 21.0109 | 22.5483 | 24.2043 | 25.8982 | 27.5979 | 29.1028 | 30.7065 | 31.2694 | 33.4207 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 35.6435 | 25% | 3862.6894 | 18.6338 | 17.7158 | 18.7681 | 20.0877 | 21.321 | 22.6043 | 23.9677 | 25.9168 | 27.596 | 29.1951 | 30.8666 | 32.8439 | 33.45 | 35.6304 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497 | 37.6497
20% | 4122.7381 | 13.829 | 13.0904 | 13.8835 | 14.9257 | 15.9392 | 16.8088 | 18.0386 | 19.3634 | 20.7185 | 22.0783 | 23.2822 | 24.5652 | 25.0156 | 26.7366 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 28.5148 | 20% | 4122.7381 | 14.907 | 14.1726 | 15.0145 | 16.0702 | 17.0568 | 18.0834 | 19.1742 | 20.7334 | 22.0768 | 23.3561 | 24.6933 | 26.2751 | 26.76 | 28.5043 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198 | 30.1198
15% | 4372.3849 | 10.3718 | 9.8178 | 10.4126 | 11.1943 | 11.9544 | 12.6066 | 13.529 | 14.5226 | 15.5389 | 16.5587 | 17.4617 | 18.4239 | 18.7617 | 20.0524 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 21.3861 | 15% | 4372.3849 | 11.1803 | 10.6295 | 11.2608 | 12.0526 | 12.7926 | 13.5626 | 14.3806 | 15.5501 | 16.5576 | 17.5171 | 18.52 | 19.7063 | 20.07 | 21.3782 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898 | 22.5898
10% | 4374.4653 | 6.9145 | 6.5452 | 6.9417 | 7.4628 | 7.9696 | 8.4044 | 9.0193 | 9.6817 | 10.3593 | 11.0391 | 11.6411 | 12.2826 | 12.5078 | 13.3683 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 14.2574 | 10% | 4374.4653 | 7.4535 | 7.0863 | 7.5072 | 8.0351 | 8.5284 | 9.0417 | 9.5871 | 10.3667 | 11.0384 | 11.678 | 12.3467 | 13.1376 | 13.38 | 14.2522 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599 | 15.0599
5% | 4374.7625 | 3.4573 | 3.2726 | 3.4709 | 3.7314 | 3.9848 | 4.2022 | 4.5097 | 4.8409 | 5.1796 | 5.5196 | 5.8206 | 6.1413 | 6.2539 | 6.6841 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 7.1287 | 5% | 4374.7625 | 3.7268 | 3.5432 | 3.7536 | 4.0175 | 4.2642 | 4.5209 | 4.7935 | 5.1834 | 5.5192 | 5.839 | 6.1733 | 6.5688 | 6.69 | 7.1261 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299 | 7.5299
9.992e-14% | 4375.9513 | 6.909e-14 | 6.54e-14 | 6.9362e-14 | 7.4569e-14 | 7.9632e-14 | 8.3977e-14 | 9.0121e-14 | 9.674e-14 | 1.0351e-13 | 1.103e-13 | 1.1632e-13 | 1.2273e-13 | 1.2498e-13 | 1.3358e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 1.4246e-13 | 9.992e-14% | 4375.9513 | 7.4475e-14 | 7.0807e-14 | 7.5012e-14 | 8.0287e-14 | 8.5216e-14 | 9.0345e-14 | 9.5794e-14 | 1.0358e-13 | 1.103e-13 | 1.1669e-13 | 1.2337e-13 | 1.3127e-13 | 1.3369e-13 | 1.4241e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13 | 1.5048e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 91.8238 | 87.2497 | 91.6299 | 95.081 | 99.2542 | 103.4291 | 107.9224 | 112.9828 | 119.0029 | 124.7027 | 130.7356 | 141.0873 | 144.3891 | 150.9666 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 155.8778 | 100% | 0 | 108.5561 | 104.1265 | 109.1286 | 113.3138 | 117.0206 | 122.866 | 128.1491 | 135.4815 | 143.1267 | 149.3728 | 155.2639 | 164.0117 | 170.3695 | 176.7757 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617 | 183.5617
99% | 0 | 90.9056 | 86.3772 | 90.7136 | 94.1302 | 98.2616 | 102.3948 | 106.8432 | 111.853 | 117.8129 | 123.4557 | 129.4283 | 139.6764 | 142.9452 | 149.4569 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 154.319 | 99% | 0.37816 | 107.4706 | 103.0852 | 108.0373 | 112.1807 | 115.8504 | 121.6373 | 126.8676 | 134.1267 | 141.6955 | 147.8791 | 153.7112 | 162.3716 | 168.6658 | 175.008 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261 | 181.7261
98% | 0.37816 | 89.9873 | 85.5047 | 89.7973 | 93.1794 | 97.2691 | 101.3606 | 105.764 | 110.7232 | 116.6229 | 122.2087 | 128.1209 | 138.2655 | 141.5013 | 147.9473 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 152.7602 | 98% | 1.1345 | 106.385 | 102.044 | 106.9461 | 111.0476 | 114.6802 | 120.4086 | 125.5861 | 132.7719 | 140.2642 | 146.3853 | 152.1586 | 160.7314 | 166.9621 | 173.2402 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904 | 179.8904
97% | 0.75633 | 89.0691 | 84.6322 | 88.881 | 92.2286 | 96.2765 | 100.3263 | 104.6848 | 109.5934 | 115.4328 | 120.9617 | 126.8136 | 136.8546 | 140.0574 | 146.4376 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 151.2014 | 97% | 2.269 | 105.2994 | 101.0027 | 105.8548 | 109.9144 | 113.51 | 119.18 | 124.3046 | 131.4171 | 138.8329 | 144.8916 | 150.6059 | 159.0913 | 165.2584 | 171.4725 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548 | 178.0548
95% | 1.1345 | 87.2326 | 82.8872 | 87.0484 | 90.3269 | 94.2915 | 98.2577 | 102.5263 | 107.3337 | 113.0528 | 118.4676 | 124.1988 | 134.0329 | 137.1696 | 143.4183 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 148.0839 | 95% | 4.538 | 103.1283 | 98.9202 | 103.6722 | 107.6481 | 111.1696 | 116.7227 | 121.7416 | 128.7075 | 135.9704 | 141.9041 | 147.5007 | 155.8111 | 161.851 | 167.937 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836 | 174.3836
90% | 4.538 | 82.6414 | 78.5247 | 82.4669 | 85.5729 | 89.3288 | 93.0862 | 97.1302 | 101.6846 | 107.1026 | 112.2325 | 117.6621 | 126.9785 | 129.9502 | 135.8699 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 140.29 | 90% | 7.9414 | 97.7005 | 93.7139 | 98.2158 | 101.9825 | 105.3185 | 110.5794 | 115.3342 | 121.9334 | 128.8141 | 134.4355 | 139.7375 | 147.6105 | 153.3325 | 159.0982 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055 | 165.2055
85% | 7.9414 | 78.0502 | 74.1622 | 77.8854 | 80.8188 | 84.366 | 87.9148 | 91.7341 | 96.0354 | 101.1525 | 105.9973 | 111.1253 | 119.9242 | 122.7307 | 128.3216 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 132.4961 | 85% | 14.3702 | 92.2727 | 88.5075 | 92.7593 | 96.3168 | 99.4675 | 104.4361 | 108.9267 | 115.1593 | 121.6577 | 126.9669 | 131.9743 | 139.4099 | 144.814 | 150.2594 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274 | 156.0274
80% | 11.7231 | 73.459 | 69.7998 | 73.3039 | 76.0648 | 79.4033 | 82.7433 | 86.3379 | 90.3863 | 95.2023 | 99.7622 | 104.5885 | 112.8698 | 115.5113 | 120.7733 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 124.7022 | 80% | 19.6645 | 86.8449 | 83.3012 | 87.3029 | 90.6511 | 93.6165 | 98.2928 | 102.5193 | 108.3852 | 114.5014 | 119.4982 | 124.2111 | 131.2093 | 136.2956 | 141.4206 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493 | 146.8493
75% | 17.7737 | 68.8678 | 65.4373 | 68.7224 | 71.3107 | 74.4406 | 77.5719 | 80.9418 | 84.7371 | 89.2522 | 93.5271 | 98.0517 | 105.8154 | 108.2918 | 113.2249 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 116.9083 | 75% | 25.7152 | 81.4171 | 78.0949 | 81.8465 | 84.9854 | 87.7655 | 92.1495 | 96.1118 | 101.6112 | 107.345 | 112.0296 | 116.4479 | 123.0088 | 127.7771 | 132.5818 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713 | 137.6713
70% | 35.1693 | 64.2767 | 61.0748 | 64.1409 | 66.5567 | 69.4779 | 72.4004 | 75.5457 | 79.088 | 83.302 | 87.2919 | 91.5149 | 98.7611 | 101.0724 | 105.6766 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 109.1144 | 70% | 34.7911 | 75.9893 | 72.8886 | 76.39 | 79.3197 | 81.9144 | 86.0062 | 89.7044 | 94.8371 | 100.1887 | 104.5609 | 108.6847 | 114.8082 | 119.2586 | 123.743 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932 | 128.4932
65% | 59.3718 | 59.6855 | 56.7123 | 59.5594 | 61.8026 | 64.5152 | 67.2289 | 70.1496 | 73.4388 | 77.3519 | 81.0568 | 84.9782 | 91.7067 | 93.8529 | 98.1283 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 101.3206 | 65% | 46.136 | 70.5615 | 67.6822 | 70.9336 | 73.654 | 76.0634 | 79.8629 | 83.2969 | 88.063 | 93.0324 | 97.0923 | 100.9215 | 106.6076 | 110.7401 | 114.9042 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151 | 119.3151
60% | 156.9382 | 55.0943 | 52.3498 | 54.9779 | 57.0486 | 59.5525 | 62.0575 | 64.7535 | 67.7897 | 71.4018 | 74.8216 | 78.4414 | 84.6524 | 86.6334 | 90.58 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 93.5267 | 60% | 76.7673 | 65.1337 | 62.4759 | 65.4772 | 67.9883 | 70.2124 | 73.7196 | 76.8895 | 81.2889 | 85.876 | 89.6237 | 93.1583 | 98.407 | 102.2217 | 106.0654 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137 | 110.137
55% | 363.794 | 50.5031 | 47.9873 | 50.3964 | 52.2945 | 54.5898 | 56.886 | 59.3573 | 62.1406 | 65.4516 | 68.5865 | 71.9046 | 77.598 | 79.414 | 83.0316 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 85.7328 | 55% | 106.2642 | 59.7059 | 57.2696 | 60.0207 | 62.3226 | 64.3613 | 67.5763 | 70.482 | 74.5148 | 78.7197 | 82.155 | 85.3951 | 90.2064 | 93.7032 | 97.2267 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589 | 100.9589
50% | 771.4551 | 45.9119 | 43.6248 | 45.8149 | 47.5405 | 49.6271 | 51.7146 | 53.9612 | 56.4914 | 59.5015 | 62.3514 | 65.3678 | 70.5436 | 72.1945 | 75.4833 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 77.9389 | 50% | 178.4935 | 54.2781 | 52.0633 | 54.5643 | 56.6569 | 58.5103 | 61.433 | 64.0746 | 67.7408 | 71.5634 | 74.6864 | 77.6319 | 82.0058 | 85.1847 | 88.3879 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808 | 91.7808
45% | 1255.5054 | 41.3207 | 39.2624 | 41.2334 | 42.7864 | 44.6644 | 46.5431 | 48.5651 | 50.8423 | 53.5513 | 56.1162 | 58.831 | 63.4893 | 64.9751 | 67.935 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 70.145 | 45% | 367.9538 | 48.8503 | 46.8569 | 49.1079 | 50.9912 | 52.6593 | 55.2897 | 57.6671 | 60.9667 | 64.407 | 67.2178 | 69.8687 | 73.8053 | 76.6663 | 79.5491 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028 | 82.6028
40% | 2059.1045 | 36.7295 | 34.8999 | 36.652 | 38.0324 | 39.7017 | 41.3717 | 43.169 | 45.1931 | 47.6012 | 49.8811 | 52.2943 | 56.4349 | 57.7556 | 60.3866 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 62.3511 | 40% | 741.202 | 43.4225 | 41.6506 | 43.6515 | 45.3255 | 46.8082 | 49.1464 | 51.2596 | 54.1926 | 57.2507 | 59.7491 | 62.1055 | 65.6047 | 68.1478 | 70.7103 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247 | 73.4247
35% | 3060.4836 | 32.1383 | 30.5374 | 32.0705 | 33.2783 | 34.739 | 36.2002 | 37.7728 | 39.544 | 41.651 | 43.646 | 45.7575 | 49.3805 | 50.5362 | 52.8383 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 54.5572 | 35% | 1167.7713 | 37.9946 | 36.4443 | 38.195 | 39.6598 | 40.9572 | 43.0031 | 44.8522 | 47.4185 | 50.0944 | 52.2805 | 54.3423 | 57.4041 | 59.6293 | 61.8715 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466 | 64.2466
30% | 3366.0403 | 27.5471 | 26.1749 | 27.489 | 28.5243 | 29.7763 | 31.0287 | 32.3767 | 33.8949 | 35.7009 | 37.4108 | 39.2207 | 42.3262 | 43.3167 | 45.29 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 46.7633 | 30% | 2002.3799 | 32.5668 | 31.238 | 32.7386 | 33.9942 | 35.1062 | 36.8598 | 38.4447 | 40.6445 | 42.938 | 44.8118 | 46.5792 | 49.2035 | 51.1108 | 53.0327 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685 | 55.0685
25% | 3686.3454 | 22.9559 | 21.8124 | 22.9075 | 23.7702 | 24.8135 | 25.8573 | 26.9806 | 28.2457 | 29.7507 | 31.1757 | 32.6839 | 35.2718 | 36.0973 | 37.7416 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 25% | 3173.5547 | 27.139 | 26.0316 | 27.2822 | 28.3285 | 29.2552 | 30.7165 | 32.0373 | 33.8704 | 35.7817 | 37.3432 | 38.816 | 41.0029 | 42.5924 | 44.1939 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904 | 45.8904
20% | 4028.5841 | 18.3648 | 17.4499 | 18.326 | 19.0162 | 19.8508 | 20.6858 | 21.5845 | 22.5966 | 23.8006 | 24.9405 | 26.1471 | 28.2175 | 28.8778 | 30.1933 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 31.1756 | 20% | 3477.5988 | 21.7112 | 20.8253 | 21.8257 | 22.6628 | 23.4041 | 24.5732 | 25.6298 | 27.0963 | 28.6253 | 29.8746 | 31.0528 | 32.8023 | 34.0739 | 35.3551 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123 | 36.7123
15% | 4345.1076 | 13.7736 | 13.0875 | 13.7445 | 14.2621 | 14.8881 | 15.5144 | 16.1884 | 16.9474 | 17.8504 | 18.7054 | 19.6103 | 21.1631 | 21.6584 | 22.645 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 23.3817 | 15% | 3788.4498 | 16.2834 | 15.619 | 16.3693 | 16.9971 | 17.5531 | 18.4299 | 19.2224 | 20.3222 | 21.469 | 22.4059 | 23.2896 | 24.6018 | 25.5554 | 26.5164 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343 | 27.5343
10% | 4381.0332 | 9.1824 | 8.725 | 9.163 | 9.5081 | 9.9254 | 10.3429 | 10.7922 | 11.2983 | 11.9003 | 12.4703 | 13.0736 | 14.1087 | 14.4389 | 15.0967 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 15.5878 | 10% | 4317.5016 | 10.8556 | 10.4127 | 10.9129 | 11.3314 | 11.7021 | 12.2866 | 12.8149 | 13.5482 | 14.3127 | 14.9373 | 15.5264 | 16.4012 | 17.0369 | 17.6776 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562 | 18.3562
5% | 4391.6218 | 4.5912 | 4.3625 | 4.5815 | 4.754 | 4.9627 | 5.1715 | 5.3961 | 5.6491 | 5.9501 | 6.2351 | 6.5368 | 7.0544 | 7.2195 | 7.5483 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 7.7939 | 5% | 4391.6218 | 5.4278 | 5.2063 | 5.4564 | 5.6657 | 5.851 | 6.1433 | 6.4075 | 6.7741 | 7.1563 | 7.4686 | 7.7632 | 8.2006 | 8.5185 | 8.8388 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781 | 9.1781
9.992e-14% | 4391.6218 | 9.175e-14 | 8.718e-14 | 9.1557e-14 | 9.5005e-14 | 9.9175e-14 | 1.0335e-13 | 1.0784e-13 | 1.1289e-13 | 1.1891e-13 | 1.246e-13 | 1.3063e-13 | 1.4097e-13 | 1.4427e-13 | 1.5085e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 1.5575e-13 | 9.992e-14% | 4391.6218 | 1.0847e-13 | 1.0404e-13 | 1.0904e-13 | 1.1322e-13 | 1.1693e-13 | 1.2277e-13 | 1.2805e-13 | 1.3537e-13 | 1.4301e-13 | 1.4925e-13 | 1.5514e-13 | 1.6388e-13 | 1.7023e-13 | 1.7663e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13 | 1.8341e-13
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 100% | 0 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
99% | 0.5944 | 75.2697 | 72.57 | 76.7928 | 82.1977 | 87.4309 | 92.086 | 98.4899 | 105.4924 | 112.6644 | 119.7723 | 126.0867 | 132.972 | 135.5855 | 144.4923 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 99% | 0.5944 | 80.6056 | 77.9271 | 82.3913 | 87.863 | 92.9632 | 98.3955 | 104.1109 | 112.2739 | 119.388 | 126.0974 | 133.0715 | 141.4362 | 144.2205 | 153.2427 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515
98% | 0.8916 | 74.5094 | 71.8369 | 76.0171 | 81.3674 | 86.5478 | 91.1558 | 97.4951 | 104.4268 | 111.5264 | 118.5625 | 124.8131 | 131.6288 | 134.216 | 143.0328 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 98% | 0.8916 | 79.7914 | 77.14 | 81.5591 | 86.9755 | 92.0241 | 97.4016 | 103.0593 | 111.1398 | 118.182 | 124.8237 | 131.7273 | 140.0075 | 142.7637 | 151.6948 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186
97% | 1.486 | 73.7491 | 71.1039 | 75.2415 | 80.5371 | 85.6646 | 90.2257 | 96.5003 | 103.3612 | 110.3883 | 117.3527 | 123.5395 | 130.2857 | 132.8464 | 141.5732 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 97% | 1.486 | 78.9772 | 76.3529 | 80.7268 | 86.0879 | 91.0851 | 96.4077 | 102.0076 | 110.0058 | 116.9761 | 123.5499 | 130.3832 | 138.5789 | 141.307 | 150.1469 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858
95% | 2.3776 | 72.2285 | 69.6379 | 73.6901 | 78.8766 | 83.8984 | 88.3653 | 94.5106 | 101.23 | 108.1123 | 114.933 | 120.9923 | 127.5994 | 130.1073 | 138.6542 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 95% | 2.3776 | 77.3488 | 74.7786 | 79.0624 | 84.3129 | 89.2071 | 94.42 | 99.9044 | 107.7376 | 114.5642 | 121.0025 | 127.6949 | 135.7216 | 138.3934 | 147.0511 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201
90% | 3.2692 | 68.427 | 65.9727 | 69.8117 | 74.7252 | 79.4827 | 83.7145 | 89.5363 | 95.9021 | 102.4222 | 108.8839 | 114.6242 | 120.8836 | 123.2596 | 131.3566 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 90% | 3.2692 | 73.2778 | 70.8429 | 74.9012 | 79.8754 | 84.512 | 89.4505 | 94.6463 | 102.0672 | 108.5345 | 114.634 | 120.9741 | 128.5784 | 131.1095 | 139.3116 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559
85% | 13.9683 | 64.6255 | 62.3076 | 65.9332 | 70.5738 | 75.067 | 79.0637 | 84.5621 | 90.5743 | 96.732 | 102.8348 | 108.2562 | 114.1679 | 116.4118 | 124.059 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 85% | 13.9683 | 69.2069 | 66.9071 | 70.74 | 75.4379 | 79.8168 | 84.481 | 89.3881 | 96.3968 | 102.5048 | 108.2654 | 114.2533 | 121.4351 | 123.8257 | 131.572 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917
80% | 41.3106 | 60.824 | 58.6424 | 62.0548 | 66.4224 | 70.6513 | 74.4129 | 79.5878 | 85.2464 | 91.0419 | 96.7857 | 101.8882 | 107.4521 | 109.5641 | 116.7614 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 80% | 41.3106 | 65.1359 | 62.9714 | 66.5788 | 71.0004 | 75.1217 | 79.5115 | 84.13 | 90.7264 | 96.4751 | 101.8969 | 107.5325 | 114.2919 | 116.5418 | 123.8325 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274
75% | 126.3094 | 57.0225 | 54.9773 | 58.1764 | 62.271 | 66.2356 | 69.7621 | 74.6136 | 79.9185 | 85.3518 | 90.7366 | 95.5202 | 100.7363 | 102.7163 | 109.4638 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 75% | 126.3094 | 61.0649 | 59.0357 | 62.4177 | 66.5628 | 70.4266 | 74.5421 | 78.8719 | 85.056 | 90.4454 | 95.5283 | 100.8117 | 107.1486 | 109.258 | 116.093 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632
70% | 323.9464 | 53.221 | 51.3121 | 54.298 | 58.1196 | 61.8198 | 65.1113 | 69.6394 | 74.5906 | 79.6617 | 84.6875 | 89.1522 | 94.0206 | 95.8685 | 102.1663 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 70% | 323.9464 | 56.9939 | 55.1 | 58.2565 | 62.1253 | 65.7315 | 69.5726 | 73.6138 | 79.3856 | 84.4157 | 89.1598 | 94.091 | 100.0054 | 101.9741 | 108.3534 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299
65% | 549.5201 | 49.4195 | 47.647 | 50.4195 | 53.9682 | 57.4041 | 60.4605 | 64.6651 | 69.2627 | 73.9716 | 78.6384 | 82.7842 | 87.3048 | 89.0208 | 94.8687 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 65% | 549.5201 | 52.9229 | 51.1643 | 54.0953 | 57.6878 | 61.0364 | 64.6031 | 68.3556 | 73.7152 | 78.386 | 82.7912 | 87.3702 | 92.8621 | 94.6902 | 100.6139 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348
60% | 799.4641 | 45.618 | 43.9818 | 46.5411 | 49.8168 | 52.9884 | 55.8097 | 59.6909 | 63.9348 | 68.2814 | 72.5893 | 76.4162 | 80.5891 | 82.173 | 87.5711 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 60% | 799.4641 | 48.8519 | 47.2286 | 49.9341 | 53.2503 | 56.3413 | 59.6337 | 63.0975 | 68.0448 | 72.3563 | 76.4226 | 80.6494 | 85.7189 | 87.4064 | 92.8744 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706
55% | 1116.2777 | 41.8165 | 40.3167 | 42.6627 | 45.6654 | 48.5727 | 51.1589 | 54.7166 | 58.6069 | 62.5913 | 66.5402 | 70.0481 | 73.8733 | 75.3253 | 80.2735 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 55% | 1116.2777 | 44.7809 | 43.2929 | 45.773 | 48.8128 | 51.6462 | 54.6642 | 57.8394 | 62.3744 | 66.3266 | 70.0541 | 73.9286 | 78.5757 | 80.1225 | 85.1348 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064
50% | 1494.9086 | 38.015 | 36.6515 | 38.7843 | 41.514 | 44.157 | 46.5081 | 49.7424 | 53.279 | 56.9012 | 60.4911 | 63.6801 | 67.1576 | 68.4775 | 72.9759 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 50% | 1494.9086 | 40.7099 | 39.3571 | 41.6118 | 44.3752 | 46.9511 | 49.6947 | 52.5813 | 56.704 | 60.297 | 63.6855 | 67.2078 | 71.4324 | 72.8386 | 77.3953 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422
45% | 2004.0097 | 34.2135 | 32.9864 | 34.9058 | 37.3626 | 39.7413 | 41.8573 | 44.7682 | 47.9511 | 51.2111 | 54.442 | 57.3121 | 60.4418 | 61.6298 | 65.6783 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 45% | 2004.0097 | 36.6389 | 35.4214 | 37.4506 | 39.9377 | 42.256 | 44.7252 | 47.3231 | 51.0336 | 54.2673 | 57.317 | 60.487 | 64.2892 | 65.5548 | 69.6558 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779
40% | 2877.179 | 30.412 | 29.3212 | 31.0274 | 33.2112 | 35.3256 | 37.2065 | 39.7939 | 42.6232 | 45.521 | 48.3929 | 50.9441 | 53.7261 | 54.782 | 58.3807 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 40% | 2877.179 | 32.5679 | 31.4857 | 33.2894 | 35.5002 | 37.5609 | 39.7558 | 42.065 | 45.3632 | 48.2376 | 50.9484 | 53.7663 | 57.1459 | 58.2709 | 61.9162 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137
35% | 3454.933 | 26.6105 | 25.6561 | 27.149 | 29.0598 | 30.9099 | 32.5556 | 34.8197 | 37.2953 | 39.8308 | 42.3438 | 44.5761 | 47.0103 | 47.9343 | 51.0831 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 35% | 3454.933 | 28.4969 | 27.55 | 29.1282 | 31.0627 | 32.8658 | 34.7863 | 36.8069 | 39.6928 | 42.2079 | 44.5799 | 47.0455 | 50.0027 | 50.987 | 54.1767 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495
30% | 3663.5664 | 22.809 | 21.9909 | 23.2706 | 24.9084 | 26.4942 | 27.9048 | 29.8454 | 31.9674 | 34.1407 | 36.2946 | 38.2081 | 40.2945 | 41.0865 | 43.7855 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 30% | 3663.5664 | 24.4259 | 23.6143 | 24.9671 | 26.6251 | 28.1707 | 29.8168 | 31.5488 | 34.0224 | 36.1782 | 38.2113 | 40.3247 | 42.8595 | 43.7032 | 46.4372 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853
25% | 3862.6894 | 19.0075 | 18.3258 | 19.3921 | 20.757 | 22.0785 | 23.254 | 24.8712 | 26.6395 | 28.4506 | 30.2455 | 31.8401 | 33.5788 | 34.2388 | 36.4879 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 25% | 3862.6894 | 20.355 | 19.6786 | 20.8059 | 22.1876 | 23.4755 | 24.8474 | 26.2906 | 28.352 | 30.1485 | 31.8428 | 33.6039 | 35.7162 | 36.4193 | 38.6977 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211
20% | 4122.7381 | 15.206 | 14.6606 | 15.5137 | 16.6056 | 17.6628 | 18.6032 | 19.897 | 21.3116 | 22.7605 | 24.1964 | 25.4721 | 26.863 | 27.391 | 29.1904 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 20% | 4122.7381 | 16.284 | 15.7429 | 16.6447 | 17.7501 | 18.7804 | 19.8779 | 21.0325 | 22.6816 | 24.1188 | 25.4742 | 26.8831 | 28.573 | 29.1355 | 30.9581 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569
15% | 4372.3849 | 11.4045 | 10.9955 | 11.6353 | 12.4542 | 13.2471 | 13.9524 | 14.9227 | 15.9837 | 17.0704 | 18.1473 | 19.104 | 20.1473 | 20.5433 | 21.8928 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 15% | 4372.3849 | 12.213 | 11.8071 | 12.4835 | 13.3126 | 14.0853 | 14.9084 | 15.7744 | 17.0112 | 18.0891 | 19.1057 | 20.1623 | 21.4297 | 21.8516 | 23.2186 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926
10% | 4374.4653 | 7.603 | 7.3303 | 7.7569 | 8.3028 | 8.8314 | 9.3016 | 9.9485 | 10.6558 | 11.3802 | 12.0982 | 12.736 | 13.4315 | 13.6955 | 14.5952 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 10% | 4374.4653 | 8.142 | 7.8714 | 8.3224 | 8.875 | 9.3902 | 9.9389 | 10.5163 | 11.3408 | 12.0594 | 12.7371 | 13.4416 | 14.2865 | 14.5677 | 15.4791 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284
5% | 4374.7625 | 3.8015 | 3.6652 | 3.8784 | 4.1514 | 4.4157 | 4.6508 | 4.9742 | 5.3279 | 5.6901 | 6.0491 | 6.368 | 6.7158 | 6.8478 | 7.2976 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 5% | 4374.7625 | 4.071 | 3.9357 | 4.1612 | 4.4375 | 4.6951 | 4.9695 | 5.2581 | 5.6704 | 6.0297 | 6.3686 | 6.7208 | 7.1432 | 7.2839 | 7.7395 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642
9.992e-14% | 4375.9513 | 7.5969e-14 | 7.3244e-14 | 7.7507e-14 | 8.2962e-14 | 8.8243e-14 | 9.2942e-14 | 9.9405e-14 | 1.0647e-13 | 1.1371e-13 | 1.2089e-13 | 1.2726e-13 | 1.3421e-13 | 1.3685e-13 | 1.4584e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 9.992e-14% | 4375.9513 | 8.1355e-14 | 7.8651e-14 | 8.3157e-14 | 8.868e-14 | 9.3827e-14 | 9.931e-14 | 1.0508e-13 | 1.1332e-13 | 1.205e-13 | 1.2727e-13 | 1.3431e-13 | 1.4275e-13 | 1.4556e-13 | 1.5467e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 100% | 0 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471
99% | 0 | 97.7215 | 94.1498 | 98.7833 | 102.4457 | 106.7936 | 111.2775 | 116.0419 | 121.4964 | 127.9206 | 133.9405 | 140.2679 | 151.0508 | 154.7037 | 161.6032 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 99% | 0.37816 | 114.2865 | 110.8579 | 116.1071 | 120.4963 | 124.3824 | 130.52 | 136.0663 | 143.7701 | 151.8031 | 158.3638 | 164.5508 | 173.746 | 180.4243 | 187.1543 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846
98% | 0.37816 | 96.7344 | 93.1988 | 97.7855 | 101.4109 | 105.7149 | 110.1535 | 114.8697 | 120.2691 | 126.6285 | 132.5876 | 138.851 | 149.525 | 153.1411 | 159.9709 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 98% | 1.1345 | 113.1321 | 109.7381 | 114.9343 | 119.2791 | 123.126 | 129.2016 | 134.6919 | 142.3179 | 150.2698 | 156.7642 | 162.8887 | 171.991 | 178.6018 | 185.2638 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222
97% | 0.75633 | 95.7473 | 92.2478 | 96.7877 | 100.3761 | 104.6362 | 109.0295 | 113.6976 | 119.0419 | 125.3363 | 131.2346 | 137.4342 | 147.9993 | 151.5784 | 158.3385 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 97% | 2.269 | 111.9777 | 108.6183 | 113.7615 | 118.062 | 121.8696 | 127.8832 | 133.3175 | 140.8656 | 148.7364 | 155.1646 | 161.2266 | 170.236 | 176.7794 | 183.3734 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597
95% | 1.1345 | 93.7731 | 90.3458 | 94.7921 | 98.3065 | 102.4787 | 106.7814 | 111.3533 | 116.5874 | 122.7521 | 128.5288 | 134.6005 | 144.9477 | 148.4531 | 155.0738 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 95% | 4.538 | 109.6689 | 106.3788 | 111.4159 | 115.6277 | 119.3568 | 125.2464 | 130.5687 | 137.9612 | 145.6697 | 151.9653 | 157.9023 | 166.7259 | 173.1344 | 179.5925 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347
90% | 4.538 | 88.8377 | 85.5907 | 89.803 | 93.1325 | 97.0851 | 101.1614 | 105.4926 | 110.4512 | 116.2914 | 121.7641 | 127.5162 | 137.3189 | 140.6397 | 146.912 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 90% | 7.9414 | 103.8968 | 100.7799 | 105.5519 | 109.5421 | 113.0749 | 118.6545 | 123.6966 | 130.7001 | 138.0029 | 143.9671 | 149.5917 | 157.9509 | 164.0221 | 170.1403 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224
85% | 7.9414 | 83.9023 | 80.8357 | 84.814 | 87.9585 | 91.6915 | 95.5413 | 99.6319 | 104.3151 | 109.8308 | 114.9994 | 120.432 | 129.6901 | 132.8264 | 138.7503 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 85% | 14.3702 | 98.1248 | 95.181 | 99.6879 | 103.4564 | 106.7929 | 112.0626 | 116.8246 | 123.439 | 130.336 | 135.969 | 141.281 | 149.1758 | 154.9097 | 160.688 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81
80% | 11.7231 | 78.9669 | 76.0807 | 79.8249 | 82.7844 | 86.2979 | 89.9212 | 93.7712 | 98.1789 | 103.3702 | 108.2347 | 113.3478 | 122.0613 | 125.0131 | 130.5885 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 80% | 19.6645 | 92.3527 | 89.5821 | 93.8239 | 97.3707 | 100.511 | 105.4707 | 109.9526 | 116.1778 | 122.6692 | 127.9708 | 132.9704 | 140.4008 | 145.7974 | 151.2358 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977
75% | 17.7737 | 74.0314 | 71.3256 | 74.8358 | 77.6104 | 80.9042 | 84.3011 | 87.9105 | 92.0427 | 96.9095 | 101.4701 | 106.2635 | 114.4324 | 117.1998 | 122.4267 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 75% | 25.7152 | 86.5807 | 83.9832 | 87.9599 | 91.285 | 94.2291 | 98.8788 | 103.0805 | 108.9167 | 115.0024 | 119.9726 | 124.6597 | 131.6257 | 136.6851 | 141.7836 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853
70% | 35.1693 | 69.096 | 66.5706 | 69.8468 | 72.4364 | 75.5106 | 78.6811 | 82.0498 | 85.9065 | 90.4489 | 94.7054 | 99.1793 | 106.8036 | 109.3865 | 114.2649 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 70% | 34.7911 | 80.8086 | 78.3843 | 82.0959 | 85.1994 | 87.9471 | 92.2868 | 96.2085 | 101.6556 | 107.3356 | 111.9744 | 116.3491 | 122.8507 | 127.5727 | 132.3313 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373
65% | 59.3718 | 64.1606 | 61.8155 | 64.8577 | 67.2623 | 70.117 | 73.061 | 76.1891 | 79.7703 | 83.9883 | 87.9407 | 92.0951 | 99.1748 | 101.5731 | 106.1031 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 65% | 46.136 | 75.0366 | 72.7855 | 76.2319 | 79.1137 | 81.6652 | 85.6949 | 89.3364 | 94.3945 | 99.6687 | 103.9763 | 108.0384 | 114.0756 | 118.4604 | 122.8791 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606
60% | 156.9382 | 59.2251 | 57.0605 | 59.8687 | 62.0883 | 64.7234 | 67.4409 | 70.3284 | 73.6342 | 77.5276 | 81.1761 | 85.0108 | 91.5459 | 93.7598 | 97.9414 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 60% | 76.7673 | 69.2645 | 67.1866 | 70.3679 | 73.028 | 75.3833 | 79.103 | 82.4644 | 87.1334 | 92.0019 | 95.9781 | 99.7278 | 105.3006 | 109.3481 | 113.4268 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483
55% | 363.794 | 54.2897 | 52.3055 | 54.8796 | 56.9143 | 59.3298 | 61.8208 | 64.4677 | 67.498 | 71.067 | 74.4114 | 77.9266 | 83.9171 | 85.9465 | 89.7796 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 55% | 106.2642 | 63.4925 | 61.5877 | 64.5039 | 66.9424 | 69.1013 | 72.5111 | 75.5924 | 79.8723 | 84.3351 | 87.9799 | 91.4171 | 96.5255 | 100.2357 | 103.9746 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359
50% | 771.4551 | 49.3543 | 47.5504 | 49.8906 | 51.7403 | 53.9362 | 56.2008 | 58.607 | 61.3618 | 64.6064 | 67.6467 | 70.8424 | 76.2883 | 78.1332 | 81.6178 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 50% | 178.4935 | 57.7205 | 55.9888 | 58.6399 | 60.8567 | 62.8194 | 65.9192 | 68.7203 | 72.6112 | 76.6683 | 79.9817 | 83.1065 | 87.7505 | 91.1234 | 94.5224 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235
45% | 1255.5054 | 44.4189 | 42.7954 | 44.9015 | 46.5662 | 48.5425 | 50.5807 | 52.7463 | 55.2256 | 58.1457 | 60.882 | 63.7581 | 68.6595 | 70.3199 | 73.456 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 45% | 367.9538 | 51.9484 | 50.3899 | 52.7759 | 54.771 | 56.5374 | 59.3273 | 61.8483 | 65.35 | 69.0014 | 71.9836 | 74.7958 | 78.9754 | 82.011 | 85.0701 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112
40% | 2059.1045 | 39.4834 | 38.0403 | 39.9125 | 41.3922 | 43.1489 | 44.9606 | 46.8856 | 49.0894 | 51.6851 | 54.1174 | 56.6739 | 61.0306 | 62.5066 | 65.2942 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 40% | 741.202 | 46.1764 | 44.7911 | 46.9119 | 48.6854 | 50.2555 | 52.7353 | 54.9763 | 58.0889 | 61.3346 | 63.9854 | 66.4852 | 70.2004 | 72.8987 | 75.6179 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988
35% | 3060.4836 | 34.548 | 33.2853 | 34.9234 | 36.2182 | 37.7553 | 39.3405 | 41.0249 | 42.9533 | 45.2244 | 47.3527 | 49.5897 | 53.4018 | 54.6932 | 57.1325 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 35% | 1167.7713 | 40.4043 | 39.1922 | 41.048 | 42.5997 | 43.9736 | 46.1434 | 48.1042 | 50.8278 | 53.6678 | 55.9872 | 58.1745 | 61.4253 | 63.7864 | 66.1657 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865
30% | 3366.0403 | 29.6126 | 28.5302 | 29.9343 | 31.0442 | 32.3617 | 33.7205 | 35.1642 | 36.8171 | 38.7638 | 40.588 | 42.5054 | 45.773 | 46.8799 | 48.9707 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 30% | 2002.3799 | 34.6323 | 33.5933 | 35.184 | 36.514 | 37.6916 | 39.5515 | 41.2322 | 43.5667 | 46.001 | 47.989 | 49.8639 | 52.6503 | 54.674 | 56.7134 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741
25% | 3686.3454 | 24.6771 | 23.7752 | 24.9453 | 25.8701 | 26.9681 | 28.1004 | 29.3035 | 30.6809 | 32.3032 | 33.8234 | 35.4212 | 38.1441 | 39.0666 | 40.8089 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 25% | 3173.5547 | 28.8602 | 27.9944 | 29.32 | 30.4283 | 31.4097 | 32.9596 | 34.3602 | 36.3056 | 38.3341 | 39.9909 | 41.5532 | 43.8752 | 45.5617 | 47.2612 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618
20% | 4028.5841 | 19.7417 | 19.0202 | 19.9562 | 20.6961 | 21.5745 | 22.4803 | 23.4428 | 24.5447 | 25.8425 | 27.0587 | 28.3369 | 30.5153 | 31.2533 | 32.6471 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 20% | 3477.5988 | 23.0882 | 22.3955 | 23.456 | 24.3427 | 25.1278 | 26.3677 | 27.4881 | 29.0445 | 30.6673 | 31.9927 | 33.2426 | 35.1002 | 36.4494 | 37.8089 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494
15% | 4345.1076 | 14.8063 | 14.2651 | 14.9672 | 15.5221 | 16.1808 | 16.8602 | 17.5821 | 18.4085 | 19.3819 | 20.294 | 21.2527 | 22.8865 | 23.44 | 24.4853 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 15% | 3788.4498 | 17.3161 | 16.7966 | 17.592 | 18.257 | 18.8458 | 19.7758 | 20.6161 | 21.7833 | 23.0005 | 23.9945 | 24.9319 | 26.3251 | 27.337 | 28.3567 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371
10% | 4381.0332 | 9.8709 | 9.5101 | 9.9781 | 10.3481 | 10.7872 | 11.2402 | 11.7214 | 12.2724 | 12.9213 | 13.5293 | 14.1685 | 15.2577 | 15.6266 | 16.3236 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 10% | 4317.5016 | 11.5441 | 11.1978 | 11.728 | 12.1713 | 12.5639 | 13.1838 | 13.7441 | 14.5222 | 15.3337 | 15.9963 | 16.6213 | 17.5501 | 18.2247 | 18.9045 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247
5% | 4391.6218 | 4.9354 | 4.755 | 4.9891 | 5.174 | 5.3936 | 5.6201 | 5.8607 | 6.1362 | 6.4606 | 6.7647 | 7.0842 | 7.6288 | 7.8133 | 8.1618 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 5% | 4391.6218 | 5.772 | 5.5989 | 5.864 | 6.0857 | 6.2819 | 6.5919 | 6.872 | 7.2611 | 7.6668 | 7.9982 | 8.3106 | 8.775 | 9.1123 | 9.4522 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124
9.992e-14% | 4391.6218 | 9.863e-14 | 9.5025e-14 | 9.9701e-14 | 1.034e-13 | 1.0779e-13 | 1.1231e-13 | 1.1712e-13 | 1.2263e-13 | 1.2911e-13 | 1.3519e-13 | 1.4157e-13 | 1.5245e-13 | 1.5614e-13 | 1.6311e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 9.992e-14% | 4391.6218 | 1.1535e-13 | 1.1189e-13 | 1.1719e-13 | 1.2162e-13 | 1.2554e-13 | 1.3173e-13 | 1.3733e-13 | 1.4511e-13 | 1.5321e-13 | 1.5984e-13 | 1.6608e-13 | 1.7536e-13 | 1.821e-13 | 1.8889e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 76.03 | 73.303 | 77.5685 | 83.028 | 88.3141 | 93.0161 | 99.4848 | 106.5579 | 113.8024 | 120.9821 | 127.3603 | 134.3151 | 136.9551 | 145.9518 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 155.2595 | 100% | 0 | 81.4198 | 78.7143 | 83.2235 | 88.7505 | 93.9022 | 99.3894 | 105.1625 | 113.408 | 120.5939 | 127.3711 | 134.4157 | 142.8648 | 145.6773 | 154.7906 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843 | 163.2843
99% | 0.5944 | 75.2697 | 72.57 | 76.7928 | 82.1977 | 87.4309 | 92.086 | 98.4899 | 105.4924 | 112.6644 | 119.7723 | 126.0867 | 132.972 | 135.5855 | 144.4923 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 153.7069 | 99% | 0.5944 | 80.6056 | 77.9271 | 82.3913 | 87.863 | 92.9632 | 98.3955 | 104.1109 | 112.2739 | 119.388 | 126.0974 | 133.0715 | 141.4362 | 144.2205 | 153.2427 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515 | 161.6515
98% | 0.8916 | 74.5094 | 71.8369 | 76.0171 | 81.3674 | 86.5478 | 91.1558 | 97.4951 | 104.4268 | 111.5264 | 118.5625 | 124.8131 | 131.6288 | 134.216 | 143.0328 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 152.1543 | 98% | 0.8916 | 79.7914 | 77.14 | 81.5591 | 86.9755 | 92.0241 | 97.4016 | 103.0593 | 111.1398 | 118.182 | 124.8237 | 131.7273 | 140.0075 | 142.7637 | 151.6948 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186 | 160.0186
97% | 1.486 | 73.7491 | 71.1039 | 75.2415 | 80.5371 | 85.6646 | 90.2257 | 96.5003 | 103.3612 | 110.3883 | 117.3527 | 123.5395 | 130.2857 | 132.8464 | 141.5732 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 150.6017 | 97% | 1.486 | 78.9772 | 76.3529 | 80.7268 | 86.0879 | 91.0851 | 96.4077 | 102.0076 | 110.0058 | 116.9761 | 123.5499 | 130.3832 | 138.5789 | 141.307 | 150.1469 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858 | 158.3858
95% | 2.3776 | 72.2285 | 69.6379 | 73.6901 | 78.8766 | 83.8984 | 88.3653 | 94.5106 | 101.23 | 108.1123 | 114.933 | 120.9923 | 127.5994 | 130.1073 | 138.6542 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 147.4965 | 95% | 2.3776 | 77.3488 | 74.7786 | 79.0624 | 84.3129 | 89.2071 | 94.42 | 99.9044 | 107.7376 | 114.5642 | 121.0025 | 127.6949 | 135.7216 | 138.3934 | 147.0511 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201 | 155.1201
90% | 3.2692 | 68.427 | 65.9727 | 69.8117 | 74.7252 | 79.4827 | 83.7145 | 89.5363 | 95.9021 | 102.4222 | 108.8839 | 114.6242 | 120.8836 | 123.2596 | 131.3566 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 139.7336 | 90% | 3.2692 | 73.2778 | 70.8429 | 74.9012 | 79.8754 | 84.512 | 89.4505 | 94.6463 | 102.0672 | 108.5345 | 114.634 | 120.9741 | 128.5784 | 131.1095 | 139.3116 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559 | 146.9559
85% | 13.9683 | 64.6255 | 62.3076 | 65.9332 | 70.5738 | 75.067 | 79.0637 | 84.5621 | 90.5743 | 96.732 | 102.8348 | 108.2562 | 114.1679 | 116.4118 | 124.059 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 131.9706 | 85% | 13.9683 | 69.2069 | 66.9071 | 70.74 | 75.4379 | 79.8168 | 84.481 | 89.3881 | 96.3968 | 102.5048 | 108.2654 | 114.2533 | 121.4351 | 123.8257 | 131.572 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917 | 138.7917
80% | 41.3106 | 60.824 | 58.6424 | 62.0548 | 66.4224 | 70.6513 | 74.4129 | 79.5878 | 85.2464 | 91.0419 | 96.7857 | 101.8882 | 107.4521 | 109.5641 | 116.7614 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 124.2076 | 80% | 41.3106 | 65.1359 | 62.9714 | 66.5788 | 71.0004 | 75.1217 | 79.5115 | 84.13 | 90.7264 | 96.4751 | 101.8969 | 107.5325 | 114.2919 | 116.5418 | 123.8325 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274 | 130.6274
75% | 126.3094 | 57.0225 | 54.9773 | 58.1764 | 62.271 | 66.2356 | 69.7621 | 74.6136 | 79.9185 | 85.3518 | 90.7366 | 95.5202 | 100.7363 | 102.7163 | 109.4638 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 116.4446 | 75% | 126.3094 | 61.0649 | 59.0357 | 62.4177 | 66.5628 | 70.4266 | 74.5421 | 78.8719 | 85.056 | 90.4454 | 95.5283 | 100.8117 | 107.1486 | 109.258 | 116.093 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632 | 122.4632
70% | 323.9464 | 53.221 | 51.3121 | 54.298 | 58.1196 | 61.8198 | 65.1113 | 69.6394 | 74.5906 | 79.6617 | 84.6875 | 89.1522 | 94.0206 | 95.8685 | 102.1663 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 108.6817 | 70% | 323.9464 | 56.9939 | 55.1 | 58.2565 | 62.1253 | 65.7315 | 69.5726 | 73.6138 | 79.3856 | 84.4157 | 89.1598 | 94.091 | 100.0054 | 101.9741 | 108.3534 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299 | 114.299
65% | 549.5201 | 49.4195 | 47.647 | 50.4195 | 53.9682 | 57.4041 | 60.4605 | 64.6651 | 69.2627 | 73.9716 | 78.6384 | 82.7842 | 87.3048 | 89.0208 | 94.8687 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 100.9187 | 65% | 549.5201 | 52.9229 | 51.1643 | 54.0953 | 57.6878 | 61.0364 | 64.6031 | 68.3556 | 73.7152 | 78.386 | 82.7912 | 87.3702 | 92.8621 | 94.6902 | 100.6139 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348 | 106.1348
60% | 799.4641 | 45.618 | 43.9818 | 46.5411 | 49.8168 | 52.9884 | 55.8097 | 59.6909 | 63.9348 | 68.2814 | 72.5893 | 76.4162 | 80.5891 | 82.173 | 87.5711 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 93.1557 | 60% | 799.4641 | 48.8519 | 47.2286 | 49.9341 | 53.2503 | 56.3413 | 59.6337 | 63.0975 | 68.0448 | 72.3563 | 76.4226 | 80.6494 | 85.7189 | 87.4064 | 92.8744 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706 | 97.9706
55% | 1116.2777 | 41.8165 | 40.3167 | 42.6627 | 45.6654 | 48.5727 | 51.1589 | 54.7166 | 58.6069 | 62.5913 | 66.5402 | 70.0481 | 73.8733 | 75.3253 | 80.2735 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 85.3927 | 55% | 1116.2777 | 44.7809 | 43.2929 | 45.773 | 48.8128 | 51.6462 | 54.6642 | 57.8394 | 62.3744 | 66.3266 | 70.0541 | 73.9286 | 78.5757 | 80.1225 | 85.1348 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064 | 89.8064
50% | 1494.9086 | 38.015 | 36.6515 | 38.7843 | 41.514 | 44.157 | 46.5081 | 49.7424 | 53.279 | 56.9012 | 60.4911 | 63.6801 | 67.1576 | 68.4775 | 72.9759 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 77.6298 | 50% | 1494.9086 | 40.7099 | 39.3571 | 41.6118 | 44.3752 | 46.9511 | 49.6947 | 52.5813 | 56.704 | 60.297 | 63.6855 | 67.2078 | 71.4324 | 72.8386 | 77.3953 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422 | 81.6422
45% | 2004.0097 | 34.2135 | 32.9864 | 34.9058 | 37.3626 | 39.7413 | 41.8573 | 44.7682 | 47.9511 | 51.2111 | 54.442 | 57.3121 | 60.4418 | 61.6298 | 65.6783 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 69.8668 | 45% | 2004.0097 | 36.6389 | 35.4214 | 37.4506 | 39.9377 | 42.256 | 44.7252 | 47.3231 | 51.0336 | 54.2673 | 57.317 | 60.487 | 64.2892 | 65.5548 | 69.6558 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779 | 73.4779
40% | 2877.179 | 30.412 | 29.3212 | 31.0274 | 33.2112 | 35.3256 | 37.2065 | 39.7939 | 42.6232 | 45.521 | 48.3929 | 50.9441 | 53.7261 | 54.782 | 58.3807 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 62.1038 | 40% | 2877.179 | 32.5679 | 31.4857 | 33.2894 | 35.5002 | 37.5609 | 39.7558 | 42.065 | 45.3632 | 48.2376 | 50.9484 | 53.7663 | 57.1459 | 58.2709 | 61.9162 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137 | 65.3137
35% | 3454.933 | 26.6105 | 25.6561 | 27.149 | 29.0598 | 30.9099 | 32.5556 | 34.8197 | 37.2953 | 39.8308 | 42.3438 | 44.5761 | 47.0103 | 47.9343 | 51.0831 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 54.3408 | 35% | 3454.933 | 28.4969 | 27.55 | 29.1282 | 31.0627 | 32.8658 | 34.7863 | 36.8069 | 39.6928 | 42.2079 | 44.5799 | 47.0455 | 50.0027 | 50.987 | 54.1767 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495 | 57.1495
30% | 3663.5664 | 22.809 | 21.9909 | 23.2706 | 24.9084 | 26.4942 | 27.9048 | 29.8454 | 31.9674 | 34.1407 | 36.2946 | 38.2081 | 40.2945 | 41.0865 | 43.7855 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 46.5779 | 30% | 3663.5664 | 24.4259 | 23.6143 | 24.9671 | 26.6251 | 28.1707 | 29.8168 | 31.5488 | 34.0224 | 36.1782 | 38.2113 | 40.3247 | 42.8595 | 43.7032 | 46.4372 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853 | 48.9853
25% | 3862.6894 | 19.0075 | 18.3258 | 19.3921 | 20.757 | 22.0785 | 23.254 | 24.8712 | 26.6395 | 28.4506 | 30.2455 | 31.8401 | 33.5788 | 34.2388 | 36.4879 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 38.8149 | 25% | 3862.6894 | 20.355 | 19.6786 | 20.8059 | 22.1876 | 23.4755 | 24.8474 | 26.2906 | 28.352 | 30.1485 | 31.8428 | 33.6039 | 35.7162 | 36.4193 | 38.6977 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211 | 40.8211
20% | 4122.7381 | 15.206 | 14.6606 | 15.5137 | 16.6056 | 17.6628 | 18.6032 | 19.897 | 21.3116 | 22.7605 | 24.1964 | 25.4721 | 26.863 | 27.391 | 29.1904 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 31.0519 | 20% | 4122.7381 | 16.284 | 15.7429 | 16.6447 | 17.7501 | 18.7804 | 19.8779 | 21.0325 | 22.6816 | 24.1188 | 25.4742 | 26.8831 | 28.573 | 29.1355 | 30.9581 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569 | 32.6569
15% | 4372.3849 | 11.4045 | 10.9955 | 11.6353 | 12.4542 | 13.2471 | 13.9524 | 14.9227 | 15.9837 | 17.0704 | 18.1473 | 19.104 | 20.1473 | 20.5433 | 21.8928 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 23.2889 | 15% | 4372.3849 | 12.213 | 11.8071 | 12.4835 | 13.3126 | 14.0853 | 14.9084 | 15.7744 | 17.0112 | 18.0891 | 19.1057 | 20.1623 | 21.4297 | 21.8516 | 23.2186 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926 | 24.4926
10% | 4374.4653 | 7.603 | 7.3303 | 7.7569 | 8.3028 | 8.8314 | 9.3016 | 9.9485 | 10.6558 | 11.3802 | 12.0982 | 12.736 | 13.4315 | 13.6955 | 14.5952 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 15.526 | 10% | 4374.4653 | 8.142 | 7.8714 | 8.3224 | 8.875 | 9.3902 | 9.9389 | 10.5163 | 11.3408 | 12.0594 | 12.7371 | 13.4416 | 14.2865 | 14.5677 | 15.4791 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284 | 16.3284
5% | 4374.7625 | 3.8015 | 3.6652 | 3.8784 | 4.1514 | 4.4157 | 4.6508 | 4.9742 | 5.3279 | 5.6901 | 6.0491 | 6.368 | 6.7158 | 6.8478 | 7.2976 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 7.763 | 5% | 4374.7625 | 4.071 | 3.9357 | 4.1612 | 4.4375 | 4.6951 | 4.9695 | 5.2581 | 5.6704 | 6.0297 | 6.3686 | 6.7208 | 7.1432 | 7.2839 | 7.7395 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642 | 8.1642
9.992e-14% | 4375.9513 | 7.5969e-14 | 7.3244e-14 | 7.7507e-14 | 8.2962e-14 | 8.8243e-14 | 9.2942e-14 | 9.9405e-14 | 1.0647e-13 | 1.1371e-13 | 1.2089e-13 | 1.2726e-13 | 1.3421e-13 | 1.3685e-13 | 1.4584e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 1.5514e-13 | 9.992e-14% | 4375.9513 | 8.1355e-14 | 7.8651e-14 | 8.3157e-14 | 8.868e-14 | 9.3827e-14 | 9.931e-14 | 1.0508e-13 | 1.1332e-13 | 1.205e-13 | 1.2727e-13 | 1.3431e-13 | 1.4275e-13 | 1.4556e-13 | 1.5467e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13 | 1.6315e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 98.7086 | 95.1008 | 99.7811 | 103.4805 | 107.8723 | 112.4015 | 117.214 | 122.7236 | 129.2127 | 135.2934 | 141.6847 | 152.5766 | 156.2664 | 163.2356 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 168.5632 | 100% | 0 | 115.4409 | 111.9776 | 117.2799 | 121.7134 | 125.6388 | 131.8383 | 137.4407 | 145.2223 | 153.3365 | 159.9635 | 166.2129 | 175.501 | 182.2468 | 189.0447 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471 | 196.2471
99% | 0 | 97.7215 | 94.1498 | 98.7833 | 102.4457 | 106.7936 | 111.2775 | 116.0419 | 121.4964 | 127.9206 | 133.9405 | 140.2679 | 151.0508 | 154.7037 | 161.6032 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 166.8776 | 99% | 0.37816 | 114.2865 | 110.8579 | 116.1071 | 120.4963 | 124.3824 | 130.52 | 136.0663 | 143.7701 | 151.8031 | 158.3638 | 164.5508 | 173.746 | 180.4243 | 187.1543 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846 | 194.2846
98% | 0.37816 | 96.7344 | 93.1988 | 97.7855 | 101.4109 | 105.7149 | 110.1535 | 114.8697 | 120.2691 | 126.6285 | 132.5876 | 138.851 | 149.525 | 153.1411 | 159.9709 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 165.1919 | 98% | 1.1345 | 113.1321 | 109.7381 | 114.9343 | 119.2791 | 123.126 | 129.2016 | 134.6919 | 142.3179 | 150.2698 | 156.7642 | 162.8887 | 171.991 | 178.6018 | 185.2638 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222 | 192.3222
97% | 0.75633 | 95.7473 | 92.2478 | 96.7877 | 100.3761 | 104.6362 | 109.0295 | 113.6976 | 119.0419 | 125.3363 | 131.2346 | 137.4342 | 147.9993 | 151.5784 | 158.3385 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 163.5063 | 97% | 2.269 | 111.9777 | 108.6183 | 113.7615 | 118.062 | 121.8696 | 127.8832 | 133.3175 | 140.8656 | 148.7364 | 155.1646 | 161.2266 | 170.236 | 176.7794 | 183.3734 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597 | 190.3597
95% | 1.1345 | 93.7731 | 90.3458 | 94.7921 | 98.3065 | 102.4787 | 106.7814 | 111.3533 | 116.5874 | 122.7521 | 128.5288 | 134.6005 | 144.9477 | 148.4531 | 155.0738 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 160.135 | 95% | 4.538 | 109.6689 | 106.3788 | 111.4159 | 115.6277 | 119.3568 | 125.2464 | 130.5687 | 137.9612 | 145.6697 | 151.9653 | 157.9023 | 166.7259 | 173.1344 | 179.5925 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347 | 186.4347
90% | 4.538 | 88.8377 | 85.5907 | 89.803 | 93.1325 | 97.0851 | 101.1614 | 105.4926 | 110.4512 | 116.2914 | 121.7641 | 127.5162 | 137.3189 | 140.6397 | 146.912 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 151.7069 | 90% | 7.9414 | 103.8968 | 100.7799 | 105.5519 | 109.5421 | 113.0749 | 118.6545 | 123.6966 | 130.7001 | 138.0029 | 143.9671 | 149.5917 | 157.9509 | 164.0221 | 170.1403 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224 | 176.6224
85% | 7.9414 | 83.9023 | 80.8357 | 84.814 | 87.9585 | 91.6915 | 95.5413 | 99.6319 | 104.3151 | 109.8308 | 114.9994 | 120.432 | 129.6901 | 132.8264 | 138.7503 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 143.2787 | 85% | 14.3702 | 98.1248 | 95.181 | 99.6879 | 103.4564 | 106.7929 | 112.0626 | 116.8246 | 123.439 | 130.336 | 135.969 | 141.281 | 149.1758 | 154.9097 | 160.688 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81 | 166.81
80% | 11.7231 | 78.9669 | 76.0807 | 79.8249 | 82.7844 | 86.2979 | 89.9212 | 93.7712 | 98.1789 | 103.3702 | 108.2347 | 113.3478 | 122.0613 | 125.0131 | 130.5885 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 134.8506 | 80% | 19.6645 | 92.3527 | 89.5821 | 93.8239 | 97.3707 | 100.511 | 105.4707 | 109.9526 | 116.1778 | 122.6692 | 127.9708 | 132.9704 | 140.4008 | 145.7974 | 151.2358 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977 | 156.9977
75% | 17.7737 | 74.0314 | 71.3256 | 74.8358 | 77.6104 | 80.9042 | 84.3011 | 87.9105 | 92.0427 | 96.9095 | 101.4701 | 106.2635 | 114.4324 | 117.1998 | 122.4267 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 126.4224 | 75% | 25.7152 | 86.5807 | 83.9832 | 87.9599 | 91.285 | 94.2291 | 98.8788 | 103.0805 | 108.9167 | 115.0024 | 119.9726 | 124.6597 | 131.6257 | 136.6851 | 141.7836 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853 | 147.1853
70% | 35.1693 | 69.096 | 66.5706 | 69.8468 | 72.4364 | 75.5106 | 78.6811 | 82.0498 | 85.9065 | 90.4489 | 94.7054 | 99.1793 | 106.8036 | 109.3865 | 114.2649 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 117.9942 | 70% | 34.7911 | 80.8086 | 78.3843 | 82.0959 | 85.1994 | 87.9471 | 92.2868 | 96.2085 | 101.6556 | 107.3356 | 111.9744 | 116.3491 | 122.8507 | 127.5727 | 132.3313 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373 | 137.373
65% | 59.3718 | 64.1606 | 61.8155 | 64.8577 | 67.2623 | 70.117 | 73.061 | 76.1891 | 79.7703 | 83.9883 | 87.9407 | 92.0951 | 99.1748 | 101.5731 | 106.1031 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 109.5661 | 65% | 46.136 | 75.0366 | 72.7855 | 76.2319 | 79.1137 | 81.6652 | 85.6949 | 89.3364 | 94.3945 | 99.6687 | 103.9763 | 108.0384 | 114.0756 | 118.4604 | 122.8791 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606 | 127.5606
60% | 156.9382 | 59.2251 | 57.0605 | 59.8687 | 62.0883 | 64.7234 | 67.4409 | 70.3284 | 73.6342 | 77.5276 | 81.1761 | 85.0108 | 91.5459 | 93.7598 | 97.9414 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 101.1379 | 60% | 76.7673 | 69.2645 | 67.1866 | 70.3679 | 73.028 | 75.3833 | 79.103 | 82.4644 | 87.1334 | 92.0019 | 95.9781 | 99.7278 | 105.3006 | 109.3481 | 113.4268 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483 | 117.7483
55% | 363.794 | 54.2897 | 52.3055 | 54.8796 | 56.9143 | 59.3298 | 61.8208 | 64.4677 | 67.498 | 71.067 | 74.4114 | 77.9266 | 83.9171 | 85.9465 | 89.7796 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 92.7098 | 55% | 106.2642 | 63.4925 | 61.5877 | 64.5039 | 66.9424 | 69.1013 | 72.5111 | 75.5924 | 79.8723 | 84.3351 | 87.9799 | 91.4171 | 96.5255 | 100.2357 | 103.9746 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359 | 107.9359
50% | 771.4551 | 49.3543 | 47.5504 | 49.8906 | 51.7403 | 53.9362 | 56.2008 | 58.607 | 61.3618 | 64.6064 | 67.6467 | 70.8424 | 76.2883 | 78.1332 | 81.6178 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 84.2816 | 50% | 178.4935 | 57.7205 | 55.9888 | 58.6399 | 60.8567 | 62.8194 | 65.9192 | 68.7203 | 72.6112 | 76.6683 | 79.9817 | 83.1065 | 87.7505 | 91.1234 | 94.5224 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235 | 98.1235
45% | 1255.5054 | 44.4189 | 42.7954 | 44.9015 | 46.5662 | 48.5425 | 50.5807 | 52.7463 | 55.2256 | 58.1457 | 60.882 | 63.7581 | 68.6595 | 70.3199 | 73.456 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 75.8534 | 45% | 367.9538 | 51.9484 | 50.3899 | 52.7759 | 54.771 | 56.5374 | 59.3273 | 61.8483 | 65.35 | 69.0014 | 71.9836 | 74.7958 | 78.9754 | 82.011 | 85.0701 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112 | 88.3112
40% | 2059.1045 | 39.4834 | 38.0403 | 39.9125 | 41.3922 | 43.1489 | 44.9606 | 46.8856 | 49.0894 | 51.6851 | 54.1174 | 56.6739 | 61.0306 | 62.5066 | 65.2942 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 67.4253 | 40% | 741.202 | 46.1764 | 44.7911 | 46.9119 | 48.6854 | 50.2555 | 52.7353 | 54.9763 | 58.0889 | 61.3346 | 63.9854 | 66.4852 | 70.2004 | 72.8987 | 75.6179 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988 | 78.4988
35% | 3060.4836 | 34.548 | 33.2853 | 34.9234 | 36.2182 | 37.7553 | 39.3405 | 41.0249 | 42.9533 | 45.2244 | 47.3527 | 49.5897 | 53.4018 | 54.6932 | 57.1325 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 58.9971 | 35% | 1167.7713 | 40.4043 | 39.1922 | 41.048 | 42.5997 | 43.9736 | 46.1434 | 48.1042 | 50.8278 | 53.6678 | 55.9872 | 58.1745 | 61.4253 | 63.7864 | 66.1657 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865 | 68.6865
30% | 3366.0403 | 29.6126 | 28.5302 | 29.9343 | 31.0442 | 32.3617 | 33.7205 | 35.1642 | 36.8171 | 38.7638 | 40.588 | 42.5054 | 45.773 | 46.8799 | 48.9707 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 50.569 | 30% | 2002.3799 | 34.6323 | 33.5933 | 35.184 | 36.514 | 37.6916 | 39.5515 | 41.2322 | 43.5667 | 46.001 | 47.989 | 49.8639 | 52.6503 | 54.674 | 56.7134 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741 | 58.8741
25% | 3686.3454 | 24.6771 | 23.7752 | 24.9453 | 25.8701 | 26.9681 | 28.1004 | 29.3035 | 30.6809 | 32.3032 | 33.8234 | 35.4212 | 38.1441 | 39.0666 | 40.8089 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 42.1408 | 25% | 3173.5547 | 28.8602 | 27.9944 | 29.32 | 30.4283 | 31.4097 | 32.9596 | 34.3602 | 36.3056 | 38.3341 | 39.9909 | 41.5532 | 43.8752 | 45.5617 | 47.2612 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618 | 49.0618
20% | 4028.5841 | 19.7417 | 19.0202 | 19.9562 | 20.6961 | 21.5745 | 22.4803 | 23.4428 | 24.5447 | 25.8425 | 27.0587 | 28.3369 | 30.5153 | 31.2533 | 32.6471 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 33.7126 | 20% | 3477.5988 | 23.0882 | 22.3955 | 23.456 | 24.3427 | 25.1278 | 26.3677 | 27.4881 | 29.0445 | 30.6673 | 31.9927 | 33.2426 | 35.1002 | 36.4494 | 37.8089 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494 | 39.2494
15% | 4345.1076 | 14.8063 | 14.2651 | 14.9672 | 15.5221 | 16.1808 | 16.8602 | 17.5821 | 18.4085 | 19.3819 | 20.294 | 21.2527 | 22.8865 | 23.44 | 24.4853 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 25.2845 | 15% | 3788.4498 | 17.3161 | 16.7966 | 17.592 | 18.257 | 18.8458 | 19.7758 | 20.6161 | 21.7833 | 23.0005 | 23.9945 | 24.9319 | 26.3251 | 27.337 | 28.3567 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371 | 29.4371
10% | 4381.0332 | 9.8709 | 9.5101 | 9.9781 | 10.3481 | 10.7872 | 11.2402 | 11.7214 | 12.2724 | 12.9213 | 13.5293 | 14.1685 | 15.2577 | 15.6266 | 16.3236 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 16.8563 | 10% | 4317.5016 | 11.5441 | 11.1978 | 11.728 | 12.1713 | 12.5639 | 13.1838 | 13.7441 | 14.5222 | 15.3337 | 15.9963 | 16.6213 | 17.5501 | 18.2247 | 18.9045 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247 | 19.6247
5% | 4391.6218 | 4.9354 | 4.755 | 4.9891 | 5.174 | 5.3936 | 5.6201 | 5.8607 | 6.1362 | 6.4606 | 6.7647 | 7.0842 | 7.6288 | 7.8133 | 8.1618 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 8.4282 | 5% | 4391.6218 | 5.772 | 5.5989 | 5.864 | 6.0857 | 6.2819 | 6.5919 | 6.872 | 7.2611 | 7.6668 | 7.9982 | 8.3106 | 8.775 | 9.1123 | 9.4522 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124 | 9.8124
9.992e-14% | 4391.6218 | 9.863e-14 | 9.5025e-14 | 9.9701e-14 | 1.034e-13 | 1.0779e-13 | 1.1231e-13 | 1.1712e-13 | 1.2263e-13 | 1.2911e-13 | 1.3519e-13 | 1.4157e-13 | 1.5245e-13 | 1.5614e-13 | 1.6311e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 1.6843e-13 | 9.992e-14% | 4391.6218 | 1.1535e-13 | 1.1189e-13 | 1.1719e-13 | 1.2162e-13 | 1.2554e-13 | 1.3173e-13 | 1.3733e-13 | 1.4511e-13 | 1.5321e-13 | 1.5984e-13 | 1.6608e-13 | 1.7536e-13 | 1.821e-13 | 1.8889e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13 | 1.9609e-13

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 162349945.5089 | 67.2% | 33.0819
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 70185987.1383 | 29.05% | 9.9906
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 3438927.3871 | 1.423% | 0.4767
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 5622421.9462 | 2.327% | 0.5178
|  | 241597281.9805 |  | 44.0669 | KW/h
|  |  |  | 44066.9381 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 1.3505; FY39: 6.8553; FY40: 6.8553; FY41: 6.8553; FY42: 6.8553; FY43: 6.8553; FY44: 6.8553; FY45: 6.8553; FY46: 6.8553; FY47: 6.8553; FY48: 6.8553; FY49: 6.8553; FY50: 6.8553; FY51: 6.8553; FY52: 6.8553; FY53: 6.8553; FY54: 6.8553 | [13 empty] | 1.1881 | 6.578 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014
98% | FY38: 0.24148; FY39: 2.9662; FY40: 2.9662; FY41: 2.9662; FY42: 2.9662; FY43: 2.9662; FY44: 2.9662; FY45: 2.9662; FY46: 2.9662; FY47: 2.9662; FY48: 2.9662; FY49: 2.9662; FY50: 2.9662; FY51: 2.9662; FY52: 2.9662; FY53: 2.9662; FY54: 2.9662 | [13 empty] | 0.16465 | 2.829 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154
97% | FY38: 0.0013947; FY39: 5.0096; FY40: 5.0096; FY41: 5.0096; FY42: 5.0096; FY43: 5.0096; FY44: 5.0096; FY45: 5.0096; FY46: 5.0096; FY47: 5.0096; FY48: 5.0096; FY49: 5.0096; FY50: 5.0096; FY51: 5.0096; FY52: 5.0096; FY53: 5.0096; FY54: 5.0096 | [14 empty] | 4.7378 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603
95% | FY39: 5.438; FY40: 5.438; FY41: 5.438; FY42: 5.438; FY43: 5.438; FY44: 5.438; FY45: 5.438; FY46: 5.438; FY47: 5.438; FY48: 5.438; FY49: 5.438; FY50: 5.438; FY51: 5.438; FY52: 5.438; FY53: 5.438; FY54: 5.438 | [14 empty] | 5.0366 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066
90% | FY39: 1.1871; FY40: 1.1871; FY41: 1.1871; FY42: 1.1871; FY43: 1.1871; FY44: 1.1871; FY45: 1.1871; FY46: 1.1871; FY47: 1.1871; FY48: 1.1871; FY49: 1.1871; FY50: 1.1871; FY51: 1.1871; FY52: 1.1871; FY53: 1.1871; FY54: 1.1871 | [14 empty] | 0.96877 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112
85% | [45 empty] | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5934 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3528 | 20.1502 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40584 | 6.0451 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0.11318 | 2.1947 | 5.1227 | 8.1758 | 10.6694 | 13.0209 | 16.5157 | 19.054 | 21.6119 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322
98% | [9 empty] | 0.87508 | 3.2558 | 7.3129 | 8.6873 | 11.2833 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | [7 empty] | 3.3498 | 9.147 | 15.192 | 20.1289 | 24.7847 | 31.7041 | 36.7296 | 41.794 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597
97% | [9 empty] | 0.36345 | 2.72 | 6.7359 | 8.0964 | 10.666 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | [7 empty] | 3.4655 | 12.073 | 21.0484 | 28.3786 | 35.2914 | 45.5652 | 53.0269 | 60.5463 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131
95% | [9 empty] | 0.005661 | 1.9163 | 5.8704 | 7.21 | 9.7401 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | [7 empty] | 2.3133 | 19.2034 | 36.8779 | 51.313 | 64.9257 | 85.1572 | 99.851 | 114.6586 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469
90% | [10 empty] | 3.2011 | 34.6587 | 46.2751 | 68.2157 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | [8 empty] | 11.5206 | 37.0512 | 57.9143 | 77.589 | 106.8298 | 128.0669 | 149.4685 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431
85% | [11 empty] | 9.0483 | 19.6826 | 40.4372 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | [9 empty] | 20.8552 | 57.9751 | 93.1296 | 145.3766 | 183.3229 | 221.5629 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775
80% | [12 empty] | 0.85207 | 14.0956 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | [10 empty] | 8.3371 | 32.6959 | 73.2642 | 102.7283 | 132.4206 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879
75% | FY39: 5.4612; FY40: 5.4612; FY41: 5.4612; FY42: 5.4612; FY43: 5.4612; FY44: 5.4612; FY45: 5.4612; FY46: 5.4612; FY47: 5.4612; FY48: 5.4612; FY49: 5.4612; FY50: 5.4612; FY51: 5.4612; FY52: 5.4612; FY53: 5.4612; FY54: 5.4612 | [11 empty] | 1.4859 | 30.6359 | 62.2684 | 94.1458 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194
70% | [42 empty] | 0.23614 | 16.3798 | 55.4308 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227
65% | [44 empty] | 1.1451 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2442 | 11.0932 | 63.6262 | 90.8034 | 154.4379 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.11318 | 11.3233 | 57.0666 | 139.2005 | 234.7164 | 342.9231 | 535.2848 | 701.4279 | 892.7844 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87094 | 7.7652 | 44.5384 | 63.5624 | 108.1065 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.033953 | 3.397 | 17.12 | 41.7601 | 70.4149 | 102.8769 | 160.5854 | 210.4284 | 267.8353 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [45 empty] | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257 | 3.0257
98% | [45 empty] | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707 | 1.0707
97% | [45 empty] | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257 | 1.257
95% | [45 empty] | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815 | 0.2815
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349 | 5.6349
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905 | 1.6905
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2.7199 | 5.2134 | 7.5649 | 11.0598 | 13.598 | 16.1559 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866 | 18.866
98% | [11 empty] | 1.9118 | 3.2862 | 5.8822 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | 7.8667 | [9 empty] | 4.3897 | 9.3267 | 13.9824 | 20.9019 | 25.9274 | 30.9918 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574 | 36.3574
97% | [11 empty] | 1.3896 | 2.7501 | 5.3197 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | 7.2841 | [9 empty] | 5.0095 | 12.3397 | 19.2525 | 29.5263 | 36.988 | 44.5074 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742 | 52.4742
95% | [11 empty] | 0.60639 | 1.9459 | 4.476 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | 6.4101 | [9 empty] | 5.2937 | 19.7287 | 33.3414 | 53.5729 | 68.2667 | 83.0743 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626 | 98.7626
90% | [11 empty] | 0.012229 | 3.3367 | 22.5665 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | 39.339 | [9 empty] | 0.21877 | 12.2654 | 31.9399 | 61.1806 | 82.4178 | 103.8193 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939 | 126.4939
85% | FY38: 1.9404; FY39: 13.1214; FY40: 13.1214; FY41: 13.1214; FY42: 13.1214; FY43: 13.1214; FY44: 13.1214; FY45: 13.1214; FY46: 13.1214; FY47: 13.1214; FY48: 13.1214; FY49: 13.1214; FY50: 13.1214; FY51: 13.1214; FY52: 13.1214; FY53: 13.1214; FY54: 13.1214 | [11 empty] | 13.2491 | 63.8113 | 101.7576 | 139.9976 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122 | 180.5122
80% | FY39: 3.3926e-06; FY40: 3.3926e-06; FY41: 3.3926e-06; FY42: 3.3926e-06; FY43: 3.3926e-06; FY44: 3.3926e-06; FY45: 3.3926e-06; FY46: 3.3926e-06; FY47: 3.3926e-06; FY48: 3.3926e-06; FY49: 3.3926e-06; FY50: 3.3926e-06; FY51: 3.3926e-06; FY52: 3.3926e-06; FY53: 3.3926e-06; FY54: 3.3926e-06 | [12 empty] | 11.45 | 39.3953 | 69.0875 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459 | 100.5459
75% | [43 empty] | 3.8038 | 26.1525 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254 | 59.9254
70% | [45 empty] | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485 | 14.3485
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.92 | 11.3189 | 40.1849 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | 74.0212 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6315 | 58.8739 | 119.3303 | 251.5028 | 372.1545 | 513.7863 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862 | 688.2862
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.744 | 7.9232 | 28.1294 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | 51.8149 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2894 | 17.6622 | 35.7991 | 75.4508 | 111.6464 | 154.1359 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858 | 206.4858
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 1.3505; FY39: 6.8553; FY40: 6.8553; FY41: 6.8553; FY42: 6.8553; FY43: 6.8553; FY44: 6.8553; FY45: 6.8553; FY46: 6.8553; FY47: 6.8553; FY48: 6.8553; FY49: 6.8553; FY50: 6.8553; FY51: 6.8553; FY52: 6.8553; FY53: 6.8553; FY54: 6.8553 | [13 empty] | 1.1881 | 6.578 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014
98% | FY38: 0.24148; FY39: 2.9662; FY40: 2.9662; FY41: 2.9662; FY42: 2.9662; FY43: 2.9662; FY44: 2.9662; FY45: 2.9662; FY46: 2.9662; FY47: 2.9662; FY48: 2.9662; FY49: 2.9662; FY50: 2.9662; FY51: 2.9662; FY52: 2.9662; FY53: 2.9662; FY54: 2.9662 | [13 empty] | 0.16465 | 2.829 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154
97% | FY38: 0.0013947; FY39: 5.0096; FY40: 5.0096; FY41: 5.0096; FY42: 5.0096; FY43: 5.0096; FY44: 5.0096; FY45: 5.0096; FY46: 5.0096; FY47: 5.0096; FY48: 5.0096; FY49: 5.0096; FY50: 5.0096; FY51: 5.0096; FY52: 5.0096; FY53: 5.0096; FY54: 5.0096 | [14 empty] | 4.7378 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603
95% | FY39: 5.438; FY40: 5.438; FY41: 5.438; FY42: 5.438; FY43: 5.438; FY44: 5.438; FY45: 5.438; FY46: 5.438; FY47: 5.438; FY48: 5.438; FY49: 5.438; FY50: 5.438; FY51: 5.438; FY52: 5.438; FY53: 5.438; FY54: 5.438 | [14 empty] | 5.0366 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066
90% | FY39: 1.1871; FY40: 1.1871; FY41: 1.1871; FY42: 1.1871; FY43: 1.1871; FY44: 1.1871; FY45: 1.1871; FY46: 1.1871; FY47: 1.1871; FY48: 1.1871; FY49: 1.1871; FY50: 1.1871; FY51: 1.1871; FY52: 1.1871; FY53: 1.1871; FY54: 1.1871 | [14 empty] | 0.96877 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112
85% | [45 empty] | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5934 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3528 | 20.1502 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40584 | 6.0451 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0.11318 | 2.1947 | 5.1227 | 8.1758 | 10.6694 | 13.0209 | 16.5157 | 19.054 | 21.6119 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322
98% | [9 empty] | 0.87508 | 3.2558 | 7.3129 | 8.6873 | 11.2833 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | [7 empty] | 3.3498 | 9.147 | 15.192 | 20.1289 | 24.7847 | 31.7041 | 36.7296 | 41.794 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597
97% | [9 empty] | 0.36345 | 2.72 | 6.7359 | 8.0964 | 10.666 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | [7 empty] | 3.4655 | 12.073 | 21.0484 | 28.3786 | 35.2914 | 45.5652 | 53.0269 | 60.5463 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131
95% | [9 empty] | 0.005661 | 1.9163 | 5.8704 | 7.21 | 9.7401 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | [7 empty] | 2.3133 | 19.2034 | 36.8779 | 51.313 | 64.9257 | 85.1572 | 99.851 | 114.6586 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469
90% | [10 empty] | 3.2011 | 34.6587 | 46.2751 | 68.2157 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | [8 empty] | 11.5206 | 37.0512 | 57.9143 | 77.589 | 106.8298 | 128.0669 | 149.4685 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431
85% | [11 empty] | 9.0483 | 19.6826 | 40.4372 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | [9 empty] | 20.8552 | 57.9751 | 93.1296 | 145.3766 | 183.3229 | 221.5629 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775
80% | [12 empty] | 0.85207 | 14.0956 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | [10 empty] | 8.3371 | 32.6959 | 73.2642 | 102.7283 | 132.4206 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879
75% | FY39: 5.4612; FY40: 5.4612; FY41: 5.4612; FY42: 5.4612; FY43: 5.4612; FY44: 5.4612; FY45: 5.4612; FY46: 5.4612; FY47: 5.4612; FY48: 5.4612; FY49: 5.4612; FY50: 5.4612; FY51: 5.4612; FY52: 5.4612; FY53: 5.4612; FY54: 5.4612 | [11 empty] | 1.4859 | 30.6359 | 62.2684 | 94.1458 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194
70% | [42 empty] | 0.23614 | 16.3798 | 55.4308 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227
65% | [44 empty] | 1.1451 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2442 | 11.0932 | 63.6262 | 90.8034 | 154.4379 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.11318 | 11.3233 | 57.0666 | 139.2005 | 234.7164 | 342.9231 | 535.2848 | 701.4279 | 892.7844 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87094 | 7.7652 | 44.5384 | 63.5624 | 108.1065 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.033953 | 3.397 | 17.12 | 41.7601 | 70.4149 | 102.8769 | 160.5854 | 210.4284 | 267.8353 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [45 empty] | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686 | 0.20686
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058 | 0.062058
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0.90123 | 3.3948 | 5.7463 | 9.2411 | 11.7794 | 14.3373 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473 | 17.0473
98% | [11 empty] | 0.131 | 1.4858 | 4.0818 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | 6.0663 | [9 empty] | 0.78895 | 5.7259 | 10.3817 | 17.3011 | 22.3266 | 27.391 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566 | 32.7566
97% | [12 empty] | 0.96799 | 3.5376 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | 5.502 | [9 empty] | 0.058929 | 6.9935 | 13.9062 | 24.18 | 31.6417 | 39.1611 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279 | 47.1279
95% | [12 empty] | 0.24274 | 2.7213 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | 4.6555 | [10 empty] | 9.2006 | 22.8134 | 43.0448 | 57.7386 | 72.5462 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345 | 88.2345
90% | FY38: 7.8392; FY39: 24.1226; FY40: 24.1226; FY41: 24.1226; FY42: 24.1226; FY43: 24.1226; FY44: 24.1226; FY45: 24.1226; FY46: 24.1226; FY47: 24.1226; FY48: 24.1226; FY49: 24.1226; FY50: 24.1226; FY51: 24.1226; FY52: 24.1226; FY53: 24.1226; FY54: 24.1226 | [10 empty] | 1.6978 | 16.7235 | 45.9642 | 67.2014 | 88.6029 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775 | 111.2775
85% | FY39: 2.57; FY40: 2.57; FY41: 2.57; FY42: 2.57; FY43: 2.57; FY44: 2.57; FY45: 2.57; FY46: 2.57; FY47: 2.57; FY48: 2.57; FY49: 2.57; FY50: 2.57; FY51: 2.57; FY52: 2.57; FY53: 2.57; FY54: 2.57 | [11 empty] | 0.67479 | 36.6229 | 74.5691 | 112.8091 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238 | 153.3238
80% | [42 empty] | 1.0893 | 18.4089 | 47.9765 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349 | 79.4349
75% | [44 empty] | 8.2799 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608 | 37.2608
70% | [45 empty] | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449 | 1.5449
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 2.6966 | 18.1799 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | 42.9163 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7491 | 27.0125 | 70.2458 | 177.4434 | 283.6657 | 411.1041 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082 | 568.0082
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0917 | 1.8876 | 12.7259 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | 30.0414 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52473 | 8.1038 | 21.0737 | 53.233 | 85.0997 | 123.3312 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025 | 170.4025
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 1.3505; FY39: 6.8553; FY40: 6.8553; FY41: 6.8553; FY42: 6.8553; FY43: 6.8553; FY44: 6.8553; FY45: 6.8553; FY46: 6.8553; FY47: 6.8553; FY48: 6.8553; FY49: 6.8553; FY50: 6.8553; FY51: 6.8553; FY52: 6.8553; FY53: 6.8553; FY54: 6.8553 | [13 empty] | 1.1881 | 6.578 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014
98% | FY38: 0.24148; FY39: 2.9662; FY40: 2.9662; FY41: 2.9662; FY42: 2.9662; FY43: 2.9662; FY44: 2.9662; FY45: 2.9662; FY46: 2.9662; FY47: 2.9662; FY48: 2.9662; FY49: 2.9662; FY50: 2.9662; FY51: 2.9662; FY52: 2.9662; FY53: 2.9662; FY54: 2.9662 | [13 empty] | 0.16465 | 2.829 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154
97% | FY38: 0.0013947; FY39: 5.0096; FY40: 5.0096; FY41: 5.0096; FY42: 5.0096; FY43: 5.0096; FY44: 5.0096; FY45: 5.0096; FY46: 5.0096; FY47: 5.0096; FY48: 5.0096; FY49: 5.0096; FY50: 5.0096; FY51: 5.0096; FY52: 5.0096; FY53: 5.0096; FY54: 5.0096 | [14 empty] | 4.7378 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603
95% | FY39: 5.438; FY40: 5.438; FY41: 5.438; FY42: 5.438; FY43: 5.438; FY44: 5.438; FY45: 5.438; FY46: 5.438; FY47: 5.438; FY48: 5.438; FY49: 5.438; FY50: 5.438; FY51: 5.438; FY52: 5.438; FY53: 5.438; FY54: 5.438 | [14 empty] | 5.0366 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066
90% | FY39: 1.1871; FY40: 1.1871; FY41: 1.1871; FY42: 1.1871; FY43: 1.1871; FY44: 1.1871; FY45: 1.1871; FY46: 1.1871; FY47: 1.1871; FY48: 1.1871; FY49: 1.1871; FY50: 1.1871; FY51: 1.1871; FY52: 1.1871; FY53: 1.1871; FY54: 1.1871 | [14 empty] | 0.96877 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112
85% | [45 empty] | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5934 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3528 | 20.1502 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40584 | 6.0451 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0.11318 | 2.1947 | 5.1227 | 8.1758 | 10.6694 | 13.0209 | 16.5157 | 19.054 | 21.6119 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322
98% | [9 empty] | 0.87508 | 3.2558 | 7.3129 | 8.6873 | 11.2833 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | [7 empty] | 3.3498 | 9.147 | 15.192 | 20.1289 | 24.7847 | 31.7041 | 36.7296 | 41.794 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597
97% | [9 empty] | 0.36345 | 2.72 | 6.7359 | 8.0964 | 10.666 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | [7 empty] | 3.4655 | 12.073 | 21.0484 | 28.3786 | 35.2914 | 45.5652 | 53.0269 | 60.5463 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131
95% | [9 empty] | 0.005661 | 1.9163 | 5.8704 | 7.21 | 9.7401 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | [7 empty] | 2.3133 | 19.2034 | 36.8779 | 51.313 | 64.9257 | 85.1572 | 99.851 | 114.6586 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469
90% | [10 empty] | 3.2011 | 34.6587 | 46.2751 | 68.2157 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | [8 empty] | 11.5206 | 37.0512 | 57.9143 | 77.589 | 106.8298 | 128.0669 | 149.4685 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431
85% | [11 empty] | 9.0483 | 19.6826 | 40.4372 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | [9 empty] | 20.8552 | 57.9751 | 93.1296 | 145.3766 | 183.3229 | 221.5629 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775
80% | [12 empty] | 0.85207 | 14.0956 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | [10 empty] | 8.3371 | 32.6959 | 73.2642 | 102.7283 | 132.4206 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879
75% | FY39: 5.4612; FY40: 5.4612; FY41: 5.4612; FY42: 5.4612; FY43: 5.4612; FY44: 5.4612; FY45: 5.4612; FY46: 5.4612; FY47: 5.4612; FY48: 5.4612; FY49: 5.4612; FY50: 5.4612; FY51: 5.4612; FY52: 5.4612; FY53: 5.4612; FY54: 5.4612 | [11 empty] | 1.4859 | 30.6359 | 62.2684 | 94.1458 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194
70% | [42 empty] | 0.23614 | 16.3798 | 55.4308 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227
65% | [44 empty] | 1.1451 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2442 | 11.0932 | 63.6262 | 90.8034 | 154.4379 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.11318 | 11.3233 | 57.0666 | 139.2005 | 234.7164 | 342.9231 | 535.2848 | 701.4279 | 892.7844 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87094 | 7.7652 | 44.5384 | 63.5624 | 108.1065 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.033953 | 3.397 | 17.12 | 41.7601 | 70.4149 | 102.8769 | 160.5854 | 210.4284 | 267.8353 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [45 empty] | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989 | 4.0989
98% | [45 empty] | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019 | 1.6019
97% | [45 empty] | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086 | 2.3086
95% | [45 empty] | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488 | 1.4488
90% | [45 empty] | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749 | 0.00083749
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459 | 9.459
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377 | 2.8377
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1.4575 | 4.3342 | 6.6844 | 8.9011 | 12.1926 | 14.5849 | 16.9954 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488 | 19.5488
98% | [11 empty] | 3.0332 | 4.2631 | 6.7132 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | 8.5426 | [8 empty] | 1.8903 | 7.5858 | 12.2391 | 16.6278 | 23.1448 | 27.8812 | 32.6538 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092 | 37.7092
97% | [11 empty] | 2.4997 | 3.7171 | 6.1423 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | 7.9531 | [8 empty] | 1.2984 | 9.755 | 16.664 | 23.1803 | 32.8565 | 39.889 | 46.9752 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813 | 54.4813
95% | [11 empty] | 1.6994 | 2.8981 | 5.286 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | 7.0689 | [8 empty] | 0.09135 | 14.6387 | 28.244 | 41.0761 | 60.1309 | 73.9795 | 87.9339 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152 | 102.7152
90% | [11 empty] | 2.2927 | 9.1184 | 29.5902 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | 45.0516 | [9 empty] | 5.9935 | 24.5725 | 43.1189 | 70.659 | 90.6746 | 110.843 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066 | 132.2066
85% | FY38: 5.4571; FY39: 18.5253; FY40: 18.5253; FY41: 18.5253; FY42: 18.5253; FY43: 18.5253; FY44: 18.5253; FY45: 18.5253; FY46: 18.5253; FY47: 18.5253; FY48: 18.5253; FY49: 18.5253; FY50: 18.5253; FY51: 18.5253; FY52: 18.5253; FY53: 18.5253; FY54: 18.5253 | [10 empty] | 5.2286 | 31.5388 | 80.7471 | 116.5108 | 152.5473 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195 | 190.7195
80% | FY39: 0.57993; FY40: 0.57993; FY41: 0.57993; FY42: 0.57993; FY43: 0.57993; FY44: 0.57993; FY45: 0.57993; FY46: 0.57993; FY47: 0.57993; FY48: 0.57993; FY49: 0.57993; FY50: 0.57993; FY51: 0.57993; FY52: 0.57993; FY53: 0.57993; FY54: 0.57993 | [11 empty] | 0.35774 | 23.0812 | 50.8507 | 78.832 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716 | 108.4716
75% | [42 empty] | 0.024813 | 10.1484 | 36.6135 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344 | 68.4344
70% | [44 empty] | 1.3671 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362 | 22.3362
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5251 | 19.9967 | 53.1887 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | 87.7214 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7376 | 42.3072 | 93.6326 | 164.8007 | 302.8368 | 424.5191 | 564.7613 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228 | 736.6228
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6675 | 13.9977 | 37.2321 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | 61.405 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4213 | 12.6922 | 28.0898 | 49.4402 | 90.851 | 127.3557 | 169.4284 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869 | 220.9869
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 1.3505; FY39: 6.8553; FY40: 6.8553; FY41: 6.8553; FY42: 6.8553; FY43: 6.8553; FY44: 6.8553; FY45: 6.8553; FY46: 6.8553; FY47: 6.8553; FY48: 6.8553; FY49: 6.8553; FY50: 6.8553; FY51: 6.8553; FY52: 6.8553; FY53: 6.8553; FY54: 6.8553 | [13 empty] | 1.1881 | 6.578 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014
98% | FY38: 0.24148; FY39: 2.9662; FY40: 2.9662; FY41: 2.9662; FY42: 2.9662; FY43: 2.9662; FY44: 2.9662; FY45: 2.9662; FY46: 2.9662; FY47: 2.9662; FY48: 2.9662; FY49: 2.9662; FY50: 2.9662; FY51: 2.9662; FY52: 2.9662; FY53: 2.9662; FY54: 2.9662 | [13 empty] | 0.16465 | 2.829 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154
97% | FY38: 0.0013947; FY39: 5.0096; FY40: 5.0096; FY41: 5.0096; FY42: 5.0096; FY43: 5.0096; FY44: 5.0096; FY45: 5.0096; FY46: 5.0096; FY47: 5.0096; FY48: 5.0096; FY49: 5.0096; FY50: 5.0096; FY51: 5.0096; FY52: 5.0096; FY53: 5.0096; FY54: 5.0096 | [14 empty] | 4.7378 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603
95% | FY39: 5.438; FY40: 5.438; FY41: 5.438; FY42: 5.438; FY43: 5.438; FY44: 5.438; FY45: 5.438; FY46: 5.438; FY47: 5.438; FY48: 5.438; FY49: 5.438; FY50: 5.438; FY51: 5.438; FY52: 5.438; FY53: 5.438; FY54: 5.438 | [14 empty] | 5.0366 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066
90% | FY39: 1.1871; FY40: 1.1871; FY41: 1.1871; FY42: 1.1871; FY43: 1.1871; FY44: 1.1871; FY45: 1.1871; FY46: 1.1871; FY47: 1.1871; FY48: 1.1871; FY49: 1.1871; FY50: 1.1871; FY51: 1.1871; FY52: 1.1871; FY53: 1.1871; FY54: 1.1871 | [14 empty] | 0.96877 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112
85% | [45 empty] | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5934 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3528 | 20.1502 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40584 | 6.0451 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0.11318 | 2.1947 | 5.1227 | 8.1758 | 10.6694 | 13.0209 | 16.5157 | 19.054 | 21.6119 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322
98% | [9 empty] | 0.87508 | 3.2558 | 7.3129 | 8.6873 | 11.2833 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | [7 empty] | 3.3498 | 9.147 | 15.192 | 20.1289 | 24.7847 | 31.7041 | 36.7296 | 41.794 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597
97% | [9 empty] | 0.36345 | 2.72 | 6.7359 | 8.0964 | 10.666 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | [7 empty] | 3.4655 | 12.073 | 21.0484 | 28.3786 | 35.2914 | 45.5652 | 53.0269 | 60.5463 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131
95% | [9 empty] | 0.005661 | 1.9163 | 5.8704 | 7.21 | 9.7401 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | [7 empty] | 2.3133 | 19.2034 | 36.8779 | 51.313 | 64.9257 | 85.1572 | 99.851 | 114.6586 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469
90% | [10 empty] | 3.2011 | 34.6587 | 46.2751 | 68.2157 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | [8 empty] | 11.5206 | 37.0512 | 57.9143 | 77.589 | 106.8298 | 128.0669 | 149.4685 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431
85% | [11 empty] | 9.0483 | 19.6826 | 40.4372 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | [9 empty] | 20.8552 | 57.9751 | 93.1296 | 145.3766 | 183.3229 | 221.5629 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775
80% | [12 empty] | 0.85207 | 14.0956 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | [10 empty] | 8.3371 | 32.6959 | 73.2642 | 102.7283 | 132.4206 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879
75% | FY39: 5.4612; FY40: 5.4612; FY41: 5.4612; FY42: 5.4612; FY43: 5.4612; FY44: 5.4612; FY45: 5.4612; FY46: 5.4612; FY47: 5.4612; FY48: 5.4612; FY49: 5.4612; FY50: 5.4612; FY51: 5.4612; FY52: 5.4612; FY53: 5.4612; FY54: 5.4612 | [11 empty] | 1.4859 | 30.6359 | 62.2684 | 94.1458 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194
70% | [42 empty] | 0.23614 | 16.3798 | 55.4308 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227
65% | [44 empty] | 1.1451 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2442 | 11.0932 | 63.6262 | 90.8034 | 154.4379 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.11318 | 11.3233 | 57.0666 | 139.2005 | 234.7164 | 342.9231 | 535.2848 | 701.4279 | 892.7844 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87094 | 7.7652 | 44.5384 | 63.5624 | 108.1065 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.033953 | 3.397 | 17.12 | 41.7601 | 70.4149 | 102.8769 | 160.5854 | 210.4284 | 267.8353 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 1.3505; FY39: 6.8553; FY40: 6.8553; FY41: 6.8553; FY42: 6.8553; FY43: 6.8553; FY44: 6.8553; FY45: 6.8553; FY46: 6.8553; FY47: 6.8553; FY48: 6.8553; FY49: 6.8553; FY50: 6.8553; FY51: 6.8553; FY52: 6.8553; FY53: 6.8553; FY54: 6.8553 | [13 empty] | 1.1881 | 6.578 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014 | 11.6014
98% | FY38: 0.24148; FY39: 2.9662; FY40: 2.9662; FY41: 2.9662; FY42: 2.9662; FY43: 2.9662; FY44: 2.9662; FY45: 2.9662; FY46: 2.9662; FY47: 2.9662; FY48: 2.9662; FY49: 2.9662; FY50: 2.9662; FY51: 2.9662; FY52: 2.9662; FY53: 2.9662; FY54: 2.9662 | [13 empty] | 0.16465 | 2.829 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154 | 5.3154
97% | FY38: 0.0013947; FY39: 5.0096; FY40: 5.0096; FY41: 5.0096; FY42: 5.0096; FY43: 5.0096; FY44: 5.0096; FY45: 5.0096; FY46: 5.0096; FY47: 5.0096; FY48: 5.0096; FY49: 5.0096; FY50: 5.0096; FY51: 5.0096; FY52: 5.0096; FY53: 5.0096; FY54: 5.0096 | [14 empty] | 4.7378 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603 | 9.6603
95% | FY39: 5.438; FY40: 5.438; FY41: 5.438; FY42: 5.438; FY43: 5.438; FY44: 5.438; FY45: 5.438; FY46: 5.438; FY47: 5.438; FY48: 5.438; FY49: 5.438; FY50: 5.438; FY51: 5.438; FY52: 5.438; FY53: 5.438; FY54: 5.438 | [14 empty] | 5.0366 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066 | 12.3066
90% | FY39: 1.1871; FY40: 1.1871; FY41: 1.1871; FY42: 1.1871; FY43: 1.1871; FY44: 1.1871; FY45: 1.1871; FY46: 1.1871; FY47: 1.1871; FY48: 1.1871; FY49: 1.1871; FY50: 1.1871; FY51: 1.1871; FY52: 1.1871; FY53: 1.1871; FY54: 1.1871 | [14 empty] | 0.96877 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112 | 7.2112
85% | [45 empty] | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148 | 10.5148
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5934 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | 21.4561 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3528 | 20.1502 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097 | 56.6097
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1154 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | 15.0193 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.40584 | 6.0451 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829 | 16.9829
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0.11318 | 2.1947 | 5.1227 | 8.1758 | 10.6694 | 13.0209 | 16.5157 | 19.054 | 21.6119 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322 | 24.322
98% | [9 empty] | 0.87508 | 3.2558 | 7.3129 | 8.6873 | 11.2833 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | 13.2678 | [7 empty] | 3.3498 | 9.147 | 15.192 | 20.1289 | 24.7847 | 31.7041 | 36.7296 | 41.794 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597 | 47.1597
97% | [9 empty] | 0.36345 | 2.72 | 6.7359 | 8.0964 | 10.666 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | 12.6304 | [7 empty] | 3.4655 | 12.073 | 21.0484 | 28.3786 | 35.2914 | 45.5652 | 53.0269 | 60.5463 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131 | 68.5131
95% | [9 empty] | 0.005661 | 1.9163 | 5.8704 | 7.21 | 9.7401 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | 11.6742 | [7 empty] | 2.3133 | 19.2034 | 36.8779 | 51.313 | 64.9257 | 85.1572 | 99.851 | 114.6586 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469 | 130.3469
90% | [10 empty] | 3.2011 | 34.6587 | 46.2751 | 68.2157 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | 84.9881 | [8 empty] | 11.5206 | 37.0512 | 57.9143 | 77.589 | 106.8298 | 128.0669 | 149.4685 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431 | 172.1431
85% | [11 empty] | 9.0483 | 19.6826 | 40.4372 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | 56.3031 | [9 empty] | 20.8552 | 57.9751 | 93.1296 | 145.3766 | 183.3229 | 221.5629 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775 | 262.0775
80% | [12 empty] | 0.85207 | 14.0956 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | 30.6867 | [10 empty] | 8.3371 | 32.6959 | 73.2642 | 102.7283 | 132.4206 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879 | 163.879
75% | FY39: 5.4612; FY40: 5.4612; FY41: 5.4612; FY42: 5.4612; FY43: 5.4612; FY44: 5.4612; FY45: 5.4612; FY46: 5.4612; FY47: 5.4612; FY48: 5.4612; FY49: 5.4612; FY50: 5.4612; FY51: 5.4612; FY52: 5.4612; FY53: 5.4612; FY54: 5.4612 | [11 empty] | 1.4859 | 30.6359 | 62.2684 | 94.1458 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194 | 127.9194
70% | [42 empty] | 0.23614 | 16.3798 | 55.4308 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227 | 102.8227
65% | [44 empty] | 1.1451 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849 | 23.849
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2442 | 11.0932 | 63.6262 | 90.8034 | 154.4379 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | 215.0114 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.11318 | 11.3233 | 57.0666 | 139.2005 | 234.7164 | 342.9231 | 535.2848 | 701.4279 | 892.7844 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322 | 1123.0322
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87094 | 7.7652 | 44.5384 | 63.5624 | 108.1065 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | 150.508 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.033953 | 3.397 | 17.12 | 41.7601 | 70.4149 | 102.8769 | 160.5854 | 210.4284 | 267.8353 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097 | 336.9097

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [6 empty] | 0.70577 | 4.889 | 9.1736 | 13.4198 | 17.192 | 21.3053 | 22.8666 | 28.1875 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | [6 empty] | 0.64937 | 4.0637 | 8.9403 | 13.1902 | 17.1984 | 21.3648 | 26.3618 | 28.0252 | 33.415 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384
98% | [6 empty] | 0.071104 | 2.1278 | 4.2486 | 6.3504 | 8.2175 | 10.2535 | 11.0263 | 13.66 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | [6 empty] | 0.053027 | 1.7193 | 4.1331 | 6.2367 | 8.2207 | 10.2829 | 12.7563 | 13.5796 | 16.2475 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339
97% | [7 empty] | 3.6223 | 7.8207 | 11.9816 | 15.678 | 19.7086 | 21.2385 | 26.4525 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | [7 empty] | 2.8135 | 7.5921 | 11.7566 | 15.6842 | 19.7668 | 24.6634 | 26.2934 | 31.5749 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973
95% | [7 empty] | 4.0083 | 10.209 | 16.3544 | 21.8137 | 27.7665 | 30.0261 | 37.7267 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | [7 empty] | 2.8139 | 9.8715 | 16.0221 | 21.8229 | 27.8526 | 35.0845 | 37.4918 | 45.2922 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622
90% | [7 empty] | 0.98442 | 6.6577 | 12.5791 | 17.8393 | 23.5751 | 25.7523 | 33.1722 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | [7 empty] | 0.37545 | 6.3325 | 12.2589 | 17.8482 | 23.658 | 30.6263 | 32.9458 | 40.4618 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668
85% | [8 empty] | 20.0858 | 86.2285 | 145.9389 | 211.0486 | 235.7631 | 319.9882 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | [8 empty] | 17.1787 | 82.5939 | 146.0401 | 211.9896 | 291.0889 | 317.4182 | 402.735 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509
80% | [9 empty] | 57.2904 | 198.839 | 355.7224 | 415.2725 | 618.215 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | [9 empty] | 50.1874 | 199.0829 | 357.9899 | 548.5814 | 612.0224 | 817.5955 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908
75% | [10 empty] | 111.5439 | 535.0016 | 708.9052 | 1301.556 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | [10 empty] | 112.007 | 541.6233 | 1098.2057 | 1283.4719 | 1883.8048 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188
70% | [11 empty] | 126.8698 | 348.7928 | 1584.0712 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | [11 empty] | 133.3684 | 1141.751 | 1544.7353 | 2850.5576 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921
65% | FY38: 294.6441; FY39: 1579.0533; FY40: 1579.0533; FY41: 1579.0533; FY42: 1579.0533; FY43: 1579.0533; FY44: 1579.0533; FY45: 1579.0533; FY46: 1579.0533; FY47: 1579.0533; FY48: 1579.0533; FY49: 1579.0533; FY50: 1579.0533; FY51: 1579.0533; FY52: 1579.0533; FY53: 1579.0533; FY54: 1579.0533 | [12 empty] | 76.7951 | 269.7865 | 1507.6591 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278
60% | FY39: 156.5762; FY40: 156.5762; FY41: 156.5762; FY42: 156.5762; FY43: 156.5762; FY44: 156.5762; FY45: 156.5762; FY46: 156.5762; FY47: 156.5762; FY48: 156.5762; FY49: 156.5762; FY50: 156.5762; FY51: 156.5762; FY52: 156.5762; FY53: 156.5762; FY54: 156.5762 | [14 empty] | 127.8543 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349
55% | [45 empty] | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.77687 | 15.6318 | 58.1954 | 204.2042 | 537.0622 | 1331.2514 | 1819.6435 | 4257.6733 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.7024 | 11.7859 | 54.0481 | 192.2458 | 537.9044 | 1347.8964 | 3285.9144 | 4165.77 | 7757.1976 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54381 | 10.9422 | 40.7368 | 142.943 | 375.9435 | 931.876 | 1273.7505 | 2980.3713 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0.21072 | 3.5358 | 16.2144 | 57.6737 | 161.3713 | 404.3689 | 985.7743 | 1249.731 | 2327.1593 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.7051 | 8.402 | 10.397 | 12.0653 | 13.5423 | 15.875 | 17.983 | 20.911 | 23.9642 | 26.4578 | 28.8093 | 32.3041 | 34.8424 | 37.4003 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103
98% | 3.0359 | 1.692 | 3.4354 | 4.8134 | 6.4493 | 8.1364 | 9.929 | 11.9813 | 14.3984 | 16.6634 | 19.0441 | 23.1013 | 24.4757 | 27.0717 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 |  | 18.5371 | 15.957 | 19.9071 | 23.21 | 26.1343 | 30.7529 | 34.9266 | 40.7237 | 46.7687 | 51.7057 | 56.3614 | 63.2809 | 68.3063 | 73.3707 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364
97% | 2.6626 | 1.3324 | 3.0581 | 4.4221 | 6.0414 | 7.7113 | 9.4857 | 11.5172 | 13.9098 | 16.1518 | 18.5083 | 22.5243 | 23.8848 | 26.4544 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 |  | 26.4959 | 22.6651 | 28.5301 | 33.4341 | 37.7761 | 44.6336 | 50.8306 | 59.4381 | 68.4134 | 75.7437 | 82.6565 | 92.9302 | 100.3919 | 107.9114 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781
95% | 2.1027 | 0.79293 | 2.4921 | 3.8351 | 5.4295 | 7.0737 | 8.8209 | 10.821 | 13.1768 | 15.3844 | 17.7046 | 21.6588 | 22.9983 | 25.5284 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 |  | 49.0629 | 41.5191 | 53.0686 | 62.7258 | 71.2761 | 84.7802 | 96.9834 | 113.9335 | 131.6081 | 146.0431 | 159.6559 | 179.8873 | 194.5811 | 209.3887 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771
90% | 7.211 | 0.46983 | 10.5424 | 22.189 | 36.0153 | 50.2742 | 65.4249 | 82.7703 | 103.1994 | 122.3429 | 142.4641 | 176.7539 | 188.3703 | 210.3109 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 |  | 59.8428 | 48.9397 | 65.6323 | 79.59 | 91.9479 | 111.4655 | 129.1029 | 153.6012 | 179.1464 | 200.0095 | 219.6842 | 248.925 | 270.1622 | 291.5637 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383
85% |  |  | 0.12403 | 5.0863 | 17.6582 | 31.1464 | 45.4782 | 61.886 | 81.2108 | 99.3195 | 118.353 | 150.7894 | 161.7778 | 182.5325 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 |  | 75.9291 | 56.4476 | 86.2737 | 111.2131 | 133.294 | 168.1679 | 199.6822 | 243.4553 | 289.0992 | 326.3772 | 361.5317 | 413.7787 | 451.725 | 489.965 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796
80% |  |  |  |  | 2.1761 | 13.3539 | 28.3682 | 45.5574 | 65.8024 | 84.7734 | 104.7133 | 138.6943 | 150.206 | 171.9489 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 |  | 31.9709 | 16.8441 | 40.0032 | 59.3679 | 76.5131 | 103.5916 | 128.0615 | 162.0501 | 197.4913 | 226.4365 | 253.7329 | 294.3012 | 323.7654 | 353.4576 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916
75% | [5 empty] | 0.28 | 10.7866 | 35.764 | 66.1929 | 94.7069 | 124.6772 | 175.7516 | 193.054 | 225.7343 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 |  | 5.2097 | 0.078894 | 11.0304 | 31.0269 | 49.4339 | 78.5051 | 104.7759 | 141.2658 | 179.3152 | 210.3906 | 239.6959 | 283.2497 | 314.8822 | 346.7596 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331
70% | [7 empty] | 11.4544 | 77.9184 | 154.6071 | 235.2127 | 372.5782 | 419.1133 | 507.0075 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 |  |  |  |  | 3.2418 | 18.2702 | 57.9299 | 94.7937 | 145.9972 | 199.3891 | 242.9949 | 284.1168 | 345.2326 | 389.6202 | 434.3514 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433
65% | [8 empty] | 2.9215 | 54.2203 | 155.7961 | 333.7328 | 394.0122 | 507.8662 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | [6 empty] | 8.1995 | 40.5294 | 100.1197 | 162.2568 | 213.0049 | 260.8623 | 331.9885 | 383.6465 | 435.7043 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587
60% | [10 empty] | 57.7158 | 601.0433 | 826.0446 | 1251.0202 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | [7 empty] | 0.041494 | 56.9141 | 203.2484 | 330.1188 | 449.7623 | 627.5777 | 756.7226 | 886.8672 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531
55% | [11 empty] | 74.6128 | 275.2322 | 964.0448 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | [9 empty] | 15.1021 | 84.7165 | 187.9668 | 345.4981 | 459.9109 | 575.2094 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661
50% | FY38: 8.3889; FY39: 297.914; FY40: 297.914; FY41: 297.914; FY42: 297.914; FY43: 297.914; FY44: 297.914; FY45: 297.914; FY46: 297.914; FY47: 297.914; FY48: 297.914; FY49: 297.914; FY50: 297.914; FY51: 297.914; FY52: 297.914; FY53: 297.914; FY54: 297.914 | [11 empty] | 21.3613 | 220.8583 | 468.0136 | 725.7963 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125
45% | [43 empty] | 38.4581 | 283.8992 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0122 | 4.2872 | 19.652 | 40.3458 | 73.7697 | 117.9759 | 178.2936 | 271.7517 | 438.7305 | 658.1697 | 994.1892 | 2091.2406 | 2679.1692 | 4107.9087 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | E @ R (MWh) | 276.7535 | 210.8534 | 314.8423 | 415.8748 | 518.1878 | 703.9012 | 897.7107 | 1238.4098 | 1695.8029 | 2133.9992 | 2606.1972 | 3479.8123 | 4255.0284 | 5251.6447 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616
Option 1 Summer POE50 W E @ R (MWh) N 1 | 10.5085 | 3.001 | 13.7564 | 28.242 | 51.6388 | 82.5831 | 124.8055 | 190.2262 | 307.1113 | 460.7188 | 695.9325 | 1463.8684 | 1875.4184 | 2875.5361 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 83.026 | 63.256 | 94.4527 | 124.7624 | 155.4564 | 211.1703 | 269.3132 | 371.5229 | 508.7409 | 640.1998 | 781.8592 | 1043.9437 | 1276.5085 | 1575.4934 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 0.5979 | 4.8442 | 8.6164 | 12.7296 | 14.291 | 19.6119 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | 25.1167 | [8 empty] | 0.36463 | 4.6146 | 8.6228 | 12.7891 | 17.7862 | 19.4495 | 24.8394 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627 | 29.8627
98% | [8 empty] | 0.038828 | 2.1056 | 3.9728 | 6.0087 | 6.7815 | 9.4153 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | 12.14 | [8 empty] | 0.0021244 | 1.992 | 3.9759 | 6.0382 | 8.5116 | 9.3349 | 12.0027 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892 | 14.4892
97% | [9 empty] | 3.5783 | 7.2747 | 11.3053 | 12.8352 | 18.0492 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | 23.4433 | [9 empty] | 3.3533 | 7.281 | 11.3635 | 16.2602 | 17.8901 | 23.1716 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094 | 28.094
95% | [9 empty] | 3.9434 | 9.4026 | 15.3555 | 17.6151 | 25.3157 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | 33.2825 | [9 empty] | 3.6111 | 9.4119 | 15.4416 | 22.6735 | 25.0807 | 32.8811 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512 | 40.1512
90% | [9 empty] | 0.9442 | 5.8807 | 11.6166 | 13.7938 | 21.2137 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | [9 empty] | 0.75091 | 5.8897 | 11.6995 | 18.6678 | 20.9872 | 28.5033 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082 | 35.5082
85% | [10 empty] | 13.5042 | 75.3032 | 100.0176 | 184.2428 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | 271.3792 | [10 empty] | 13.5726 | 76.2442 | 155.3434 | 181.6727 | 266.9896 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055 | 346.5055
80% | [11 empty] | 37.2993 | 88.1907 | 291.1331 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | 501.0905 | [11 empty] | 38.8599 | 221.4995 | 284.9406 | 490.5136 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109 | 682.109
75% | [12 empty] | 0.18682 | 346.3821 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | 959.5186 | [12 empty] | 158.459 | 328.2981 | 928.631 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145 | 1488.145
70% | FY38: 9.356; FY39: 840.0841; FY40: 840.0841; FY41: 840.0841; FY42: 840.0841; FY43: 840.0841; FY44: 840.0841; FY45: 840.0841; FY46: 840.0841; FY47: 840.0841; FY48: 840.0841; FY49: 840.0841; FY50: 840.0841; FY51: 840.0841; FY52: 840.0841; FY53: 840.0841; FY54: 840.0841 | [13 empty] | 5.1201 | 772.8984 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328 | 1989.9328
65% | FY39: 8.5787; FY40: 8.5787; FY41: 8.5787; FY42: 8.5787; FY43: 8.5787; FY44: 8.5787; FY45: 8.5787; FY46: 8.5787; FY47: 8.5787; FY48: 8.5787; FY49: 8.5787; FY50: 8.5787; FY51: 8.5787; FY52: 8.5787; FY53: 8.5787; FY54: 8.5787 | [14 empty] | 2.617 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448 | 611.1448
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63673 | 15.4157 | 48.6513 | 169.6182 | 253.7118 | 924.7196 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | 2703.5237 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36676 | 14.3219 | 48.7538 | 172.436 | 619.2011 | 892.7739 | 2583.0476 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424 | 5265.9424
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44571 | 10.791 | 34.0559 | 118.7328 | 177.5983 | 647.3038 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | 1892.4666 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11003 | 4.2966 | 14.6261 | 51.7308 | 185.7603 | 267.8322 | 774.9143 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827 | 1579.7827
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.7051 | 8.402 | 10.397 | 6.6093 | 8.0863 | 10.419 | 12.5271 | 15.4551 | 18.5082 | 21.0018 | 23.3533 | 26.8481 | 29.3864 | 31.9443 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544 | 34.6544
98% | 3.0359 | 1.692 | 3.4354 |  | 1.0482 | 2.7353 | 4.5279 | 6.5802 | 8.9973 | 11.2623 | 13.643 | 17.7001 | 19.0746 | 21.6705 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 | 23.655 |  | 18.5371 | 15.957 | 19.9071 | 12.4077 | 15.332 | 19.9506 | 24.1243 | 29.9215 | 35.9664 | 40.9034 | 45.5592 | 52.4786 | 57.5041 | 62.5685 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341 | 67.9341
97% | 2.6626 | 1.3324 | 3.0581 |  | 0.69507 | 2.365 | 4.1394 | 6.1709 | 8.5635 | 10.8055 | 13.162 | 17.178 | 18.5385 | 21.1081 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 | 23.0724 |  | 26.4959 | 22.6651 | 28.5301 | 17.3952 | 21.7372 | 28.5948 | 34.7917 | 43.3992 | 52.3745 | 59.7048 | 66.6176 | 76.8913 | 84.353 | 91.8725 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393 | 99.8393
95% | 2.1027 | 0.79293 | 2.4921 |  | 0.19036 | 1.8097 | 3.5568 | 5.557 | 7.9128 | 10.1203 | 12.4406 | 16.3947 | 17.7343 | 20.2644 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 | 22.1985 |  | 49.0629 | 41.5191 | 53.0686 | 31.1415 | 39.6918 | 53.1959 | 65.3991 | 82.3492 | 100.0238 | 114.4588 | 128.0716 | 148.303 | 162.9969 | 177.8044 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928 | 193.4928
90% | 7.211 | 0.46983 | 10.5424 |  |  | 5.037 | 19.7758 | 37.1212 | 57.5503 | 76.6937 | 96.8149 | 131.1048 | 142.7211 | 164.6617 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 | 181.4342 |  | 59.8428 | 48.9397 | 65.6323 | 33.9408 | 46.2987 | 65.8163 | 83.4538 | 107.952 | 133.4973 | 154.3604 | 174.0351 | 203.2759 | 224.513 | 245.9146 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891 | 268.5891
85% |  |  | 0.12403 |  |  |  | 3.484 | 18.7043 | 38.0292 | 56.1378 | 75.1714 | 107.6078 | 118.5962 | 139.3508 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 | 155.2167 |  | 75.9291 | 56.4476 | 86.2737 | 29.6478 | 51.7287 | 86.6025 | 118.1169 | 161.89 | 207.5339 | 244.8119 | 279.9664 | 332.2134 | 370.1597 | 408.3997 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143 | 448.9143
80% | [7 empty] | 2.7201 | 20.5645 | 39.5355 | 59.4754 | 93.4564 | 104.9681 | 126.711 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 | 143.3323 |  | 31.9709 | 16.8441 | 40.0032 | 1.842 | 13.2198 | 40.2585 | 64.7285 | 98.717 | 134.1582 | 163.1034 | 190.3999 | 230.9681 | 260.4323 | 290.1245 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583 | 321.583
75% | [8 empty] | 3.4843 | 26.713 | 56.6832 | 107.7577 | 125.0601 | 157.7404 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 | 182.7228 |  | 5.2097 | 0.078894 | 11.0304 |  |  | 11.2491 | 36.782 | 73.2719 | 111.3212 | 142.3966 | 171.7019 | 215.2557 | 246.8882 | 278.7656 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392 | 312.5392
70% | [9 empty] | 2.8028 | 52.3817 | 189.7074 | 236.2425 | 324.1367 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | 391.3273 | [7 empty] | 6.6686 | 50.5864 | 103.9782 | 147.5841 | 188.706 | 249.8218 | 294.2094 | 338.9405 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324 | 386.3324
65% | [11 empty] | 96.8507 | 157.1301 | 270.9841 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | 358.0195 | [8 empty] | 4.6135 | 51.2183 | 101.9664 | 149.8238 | 220.95 | 272.608 | 324.6658 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202 | 379.8202
60% | [11 empty] | 2.1357 | 59.8171 | 366.8248 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | 691.6967 | [9 empty] | 2.4035 | 60.3008 | 172.1661 | 349.9815 | 479.1264 | 609.271 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569 | 747.1569
55% | FY38: 0.023787; FY39: 140.767; FY40: 140.767; FY41: 140.767; FY42: 140.767; FY43: 140.767; FY44: 140.767; FY45: 140.767; FY46: 140.767; FY47: 140.767; FY48: 140.767; FY49: 140.767; FY50: 140.767; FY51: 140.767; FY52: 140.767; FY53: 140.767; FY54: 140.767 | [11 empty] | 6.4952 | 100.3412 | 213.9812 | 329.2797 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364 | 451.4364
50% | [43 empty] | 40.3372 | 191.3265 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664 | 449.0664
45% | [45 empty] | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963 | 29.1963
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0122 | 4.2872 | 19.652 | 0 | 1.9336 | 11.947 | 35.484 | 76.8537 | 145.1018 | 234.0709 | 379.7723 | 779.8933 | 999.8825 | 1613.4764 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | 2313.4424 | E @ R (MWh) | 276.7535 | 210.8534 | 314.8423 | 132.9844 | 196.0946 | 316.0869 | 446.5919 | 668.1557 | 950.9836 | 1250.5925 | 1596.896 | 2207.3287 | 2736.4958 | 3380.8776 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546 | 4190.5546
Option 2 Summer POE50 W E @ R (MWh) N 1 | 10.5085 | 3.001 | 13.7564 | 0 | 1.3535 | 8.3629 | 24.8388 | 53.7976 | 101.5712 | 163.8497 | 265.8406 | 545.9253 | 699.9178 | 1129.4335 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | 1619.4097 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 83.026 | 63.256 | 94.4527 | 39.8953 | 58.8284 | 94.8261 | 133.9776 | 200.4467 | 285.2951 | 375.1777 | 479.0688 | 662.1986 | 820.9487 | 1014.2633 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664 | 1257.1664
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [6 empty] | 0.70577 | 4.889 | 9.1736 | 13.4198 | 17.192 | 21.3053 | 22.8666 | 28.1875 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | [6 empty] | 0.64937 | 4.0637 | 8.9403 | 13.1902 | 17.1984 | 21.3648 | 26.3618 | 28.0252 | 33.415 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384
98% | [6 empty] | 0.071104 | 2.1278 | 4.2486 | 6.3504 | 8.2175 | 10.2535 | 11.0263 | 13.66 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | [6 empty] | 0.053027 | 1.7193 | 4.1331 | 6.2367 | 8.2207 | 10.2829 | 12.7563 | 13.5796 | 16.2475 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339
97% | [7 empty] | 3.6223 | 7.8207 | 11.9816 | 15.678 | 19.7086 | 21.2385 | 26.4525 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | [7 empty] | 2.8135 | 7.5921 | 11.7566 | 15.6842 | 19.7668 | 24.6634 | 26.2934 | 31.5749 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973
95% | [7 empty] | 4.0083 | 10.209 | 16.3544 | 21.8137 | 27.7665 | 30.0261 | 37.7267 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | [7 empty] | 2.8139 | 9.8715 | 16.0221 | 21.8229 | 27.8526 | 35.0845 | 37.4918 | 45.2922 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622
90% | [7 empty] | 0.98442 | 6.6577 | 12.5791 | 17.8393 | 23.5751 | 25.7523 | 33.1722 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | [7 empty] | 0.37545 | 6.3325 | 12.2589 | 17.8482 | 23.658 | 30.6263 | 32.9458 | 40.4618 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668
85% | [8 empty] | 20.0858 | 86.2285 | 145.9389 | 211.0486 | 235.7631 | 319.9882 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | [8 empty] | 17.1787 | 82.5939 | 146.0401 | 211.9896 | 291.0889 | 317.4182 | 402.735 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509
80% | [9 empty] | 57.2904 | 198.839 | 355.7224 | 415.2725 | 618.215 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | [9 empty] | 50.1874 | 199.0829 | 357.9899 | 548.5814 | 612.0224 | 817.5955 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908
75% | [10 empty] | 111.5439 | 535.0016 | 708.9052 | 1301.556 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | [10 empty] | 112.007 | 541.6233 | 1098.2057 | 1283.4719 | 1883.8048 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188
70% | [11 empty] | 126.8698 | 348.7928 | 1584.0712 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | [11 empty] | 133.3684 | 1141.751 | 1544.7353 | 2850.5576 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921
65% | FY38: 294.6441; FY39: 1579.0533; FY40: 1579.0533; FY41: 1579.0533; FY42: 1579.0533; FY43: 1579.0533; FY44: 1579.0533; FY45: 1579.0533; FY46: 1579.0533; FY47: 1579.0533; FY48: 1579.0533; FY49: 1579.0533; FY50: 1579.0533; FY51: 1579.0533; FY52: 1579.0533; FY53: 1579.0533; FY54: 1579.0533 | [12 empty] | 76.7951 | 269.7865 | 1507.6591 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278
60% | FY39: 156.5762; FY40: 156.5762; FY41: 156.5762; FY42: 156.5762; FY43: 156.5762; FY44: 156.5762; FY45: 156.5762; FY46: 156.5762; FY47: 156.5762; FY48: 156.5762; FY49: 156.5762; FY50: 156.5762; FY51: 156.5762; FY52: 156.5762; FY53: 156.5762; FY54: 156.5762 | [14 empty] | 127.8543 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349
55% | [45 empty] | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.77687 | 15.6318 | 58.1954 | 204.2042 | 537.0622 | 1331.2514 | 1819.6435 | 4257.6733 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.7024 | 11.7859 | 54.0481 | 192.2458 | 537.9044 | 1347.8964 | 3285.9144 | 4165.77 | 7757.1976 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54381 | 10.9422 | 40.7368 | 142.943 | 375.9435 | 931.876 | 1273.7505 | 2980.3713 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0.21072 | 3.5358 | 16.2144 | 57.6737 | 161.3713 | 404.3689 | 985.7743 | 1249.731 | 2327.1593 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.7051 | 8.402 | 10.397 | 12.0653 | 13.5423 | 15.875 | 17.983 | 20.911 | 23.9642 | 26.4578 | 28.8093 | 32.3041 | 34.8424 | 37.4003 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103
98% | 3.0359 | 1.692 | 3.4354 | 4.8134 | 6.4493 | 8.1364 | 9.929 | 11.9813 | 14.3984 | 16.6634 | 19.0441 | 23.1013 | 24.4757 | 27.0717 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 |  | 18.5371 | 15.957 | 19.9071 | 23.21 | 26.1343 | 30.7529 | 34.9266 | 40.7237 | 46.7687 | 51.7057 | 56.3614 | 63.2809 | 68.3063 | 73.3707 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364
97% | 2.6626 | 1.3324 | 3.0581 | 4.4221 | 6.0414 | 7.7113 | 9.4857 | 11.5172 | 13.9098 | 16.1518 | 18.5083 | 22.5243 | 23.8848 | 26.4544 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 |  | 26.4959 | 22.6651 | 28.5301 | 33.4341 | 37.7761 | 44.6336 | 50.8306 | 59.4381 | 68.4134 | 75.7437 | 82.6565 | 92.9302 | 100.3919 | 107.9114 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781
95% | 2.1027 | 0.79293 | 2.4921 | 3.8351 | 5.4295 | 7.0737 | 8.8209 | 10.821 | 13.1768 | 15.3844 | 17.7046 | 21.6588 | 22.9983 | 25.5284 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 |  | 49.0629 | 41.5191 | 53.0686 | 62.7258 | 71.2761 | 84.7802 | 96.9834 | 113.9335 | 131.6081 | 146.0431 | 159.6559 | 179.8873 | 194.5811 | 209.3887 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771
90% | 7.211 | 0.46983 | 10.5424 | 22.189 | 36.0153 | 50.2742 | 65.4249 | 82.7703 | 103.1994 | 122.3429 | 142.4641 | 176.7539 | 188.3703 | 210.3109 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 |  | 59.8428 | 48.9397 | 65.6323 | 79.59 | 91.9479 | 111.4655 | 129.1029 | 153.6012 | 179.1464 | 200.0095 | 219.6842 | 248.925 | 270.1622 | 291.5637 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383
85% |  |  | 0.12403 | 5.0863 | 17.6582 | 31.1464 | 45.4782 | 61.886 | 81.2108 | 99.3195 | 118.353 | 150.7894 | 161.7778 | 182.5325 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 |  | 75.9291 | 56.4476 | 86.2737 | 111.2131 | 133.294 | 168.1679 | 199.6822 | 243.4553 | 289.0992 | 326.3772 | 361.5317 | 413.7787 | 451.725 | 489.965 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796
80% |  |  |  |  | 2.1761 | 13.3539 | 28.3682 | 45.5574 | 65.8024 | 84.7734 | 104.7133 | 138.6943 | 150.206 | 171.9489 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 |  | 31.9709 | 16.8441 | 40.0032 | 59.3679 | 76.5131 | 103.5916 | 128.0615 | 162.0501 | 197.4913 | 226.4365 | 253.7329 | 294.3012 | 323.7654 | 353.4576 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916
75% | [5 empty] | 0.28 | 10.7866 | 35.764 | 66.1929 | 94.7069 | 124.6772 | 175.7516 | 193.054 | 225.7343 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 |  | 5.2097 | 0.078894 | 11.0304 | 31.0269 | 49.4339 | 78.5051 | 104.7759 | 141.2658 | 179.3152 | 210.3906 | 239.6959 | 283.2497 | 314.8822 | 346.7596 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331
70% | [7 empty] | 11.4544 | 77.9184 | 154.6071 | 235.2127 | 372.5782 | 419.1133 | 507.0075 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 |  |  |  |  | 3.2418 | 18.2702 | 57.9299 | 94.7937 | 145.9972 | 199.3891 | 242.9949 | 284.1168 | 345.2326 | 389.6202 | 434.3514 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433
65% | [8 empty] | 2.9215 | 54.2203 | 155.7961 | 333.7328 | 394.0122 | 507.8662 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | [6 empty] | 8.1995 | 40.5294 | 100.1197 | 162.2568 | 213.0049 | 260.8623 | 331.9885 | 383.6465 | 435.7043 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587
60% | [10 empty] | 57.7158 | 601.0433 | 826.0446 | 1251.0202 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | [7 empty] | 0.041494 | 56.9141 | 203.2484 | 330.1188 | 449.7623 | 627.5777 | 756.7226 | 886.8672 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531
55% | [11 empty] | 74.6128 | 275.2322 | 964.0448 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | [9 empty] | 15.1021 | 84.7165 | 187.9668 | 345.4981 | 459.9109 | 575.2094 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661
50% | FY38: 8.3889; FY39: 297.914; FY40: 297.914; FY41: 297.914; FY42: 297.914; FY43: 297.914; FY44: 297.914; FY45: 297.914; FY46: 297.914; FY47: 297.914; FY48: 297.914; FY49: 297.914; FY50: 297.914; FY51: 297.914; FY52: 297.914; FY53: 297.914; FY54: 297.914 | [11 empty] | 21.3613 | 220.8583 | 468.0136 | 725.7963 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125
45% | [43 empty] | 38.4581 | 283.8992 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0122 | 4.2872 | 19.652 | 40.3458 | 73.7697 | 117.9759 | 178.2936 | 271.7517 | 438.7305 | 658.1697 | 994.1892 | 2091.2406 | 2679.1692 | 4107.9087 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | E @ R (MWh) | 276.7535 | 210.8534 | 314.8423 | 415.8748 | 518.1878 | 703.9012 | 897.7107 | 1238.4098 | 1695.8029 | 2133.9992 | 2606.1972 | 3479.8123 | 4255.0284 | 5251.6447 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616
Option 3 Summer POE50 W E @ R (MWh) N 1 | 10.5085 | 3.001 | 13.7564 | 28.242 | 51.6388 | 82.5831 | 124.8055 | 190.2262 | 307.1113 | 460.7188 | 695.9325 | 1463.8684 | 1875.4184 | 2875.5361 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 83.026 | 63.256 | 94.4527 | 124.7624 | 155.4564 | 211.1703 | 269.3132 | 371.5229 | 508.7409 | 640.1998 | 781.8592 | 1043.9437 | 1276.5085 | 1575.4934 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [9 empty] | 1.9856 | 5.7578 | 9.8711 | 11.4324 | 16.7533 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | 22.2581 | [9 empty] | 1.756 | 5.7642 | 9.9305 | 14.9276 | 16.5909 | 21.9808 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042 | 27.0042
98% | [9 empty] | 0.69071 | 2.5578 | 4.5938 | 5.3666 | 8.0003 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | 10.7251 | [9 empty] | 0.57706 | 2.561 | 4.6232 | 7.0967 | 7.92 | 10.5878 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743 | 13.0743
97% | [9 empty] | 0.77723 | 4.4736 | 8.5042 | 10.0341 | 15.2481 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | 20.6422 | [9 empty] | 0.55223 | 4.4799 | 8.5624 | 13.4591 | 15.089 | 20.3705 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929 | 25.2929
95% | [9 empty] | 0.14011 | 5.2656 | 11.2185 | 13.4781 | 21.1787 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | 29.1455 | [9 empty] | 0.039341 | 5.2749 | 11.3046 | 18.5365 | 20.9437 | 28.7441 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142 | 36.0142
90% | [10 empty] | 1.9219 | 7.6304 | 9.8076 | 17.2275 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | 24.9038 | [10 empty] | 1.9299 | 7.7133 | 14.6816 | 17.0011 | 24.5171 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221 | 31.5221
85% | [11 empty] | 30.0587 | 54.7692 | 138.9943 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | 226.1308 | [11 empty] | 30.9957 | 110.095 | 136.4242 | 221.7411 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257 | 301.257
80% | [12 empty] | 11.032 | 182.1058 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | 392.0633 | [11 empty] | 0.00094757 | 112.4722 | 175.9133 | 381.4863 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817 | 573.0817
75% | FY38: 81.9885; FY39: 641.1274; FY40: 641.1274; FY41: 641.1274; FY42: 641.1274; FY43: 641.1274; FY44: 641.1274; FY45: 641.1274; FY46: 641.1274; FY47: 641.1274; FY48: 641.1274; FY49: 641.1274; FY50: 641.1274; FY51: 641.1274; FY52: 641.1274; FY53: 641.1274; FY54: 641.1274 | [12 empty] | 7.232 | 72.164 | 610.2397 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537 | 1169.7537
70% | FY39: 249.7678; FY40: 249.7678; FY41: 249.7678; FY42: 249.7678; FY43: 249.7678; FY44: 249.7678; FY45: 249.7678; FY46: 249.7678; FY47: 249.7678; FY48: 249.7678; FY49: 249.7678; FY50: 249.7678; FY51: 249.7678; FY52: 249.7678; FY53: 249.7678; FY54: 249.7678 | [14 empty] | 209.905 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798 | 1297.3798
65% | [45 empty] | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235 | 137.8235
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5937 | 19.9768 | 71.8767 | 115.9201 | 481.4966 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | 1616.7639 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9246 | 20.0099 | 73.1308 | 298.5006 | 462.0463 | 1529.5726 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032 | 3612.2032
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5156 | 13.9838 | 50.3137 | 81.1441 | 337.0476 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | 1131.7348 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.87739 | 6.003 | 21.9392 | 89.5502 | 138.6139 | 458.8718 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661 | 1083.661
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.7051 | 8.402 | 10.397 | 4.7906 | 6.2677 | 8.6004 | 10.7084 | 13.6364 | 16.6896 | 19.1831 | 21.5346 | 25.0295 | 27.5677 | 30.1256 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357 | 32.8357
98% | 3.0359 | 1.692 | 3.4354 |  |  | 0.93488 | 2.7275 | 4.7798 | 7.1969 | 9.4619 | 11.8426 | 15.8998 | 17.2742 | 19.8702 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 | 21.8546 |  | 18.5371 | 15.957 | 19.9071 | 8.807 | 11.7313 | 16.3499 | 20.5235 | 26.3207 | 32.3657 | 37.3026 | 41.9584 | 48.8778 | 53.9033 | 58.9677 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334 | 64.3334
97% | 2.6626 | 1.3324 | 3.0581 |  |  | 0.58293 | 2.3573 | 4.3888 | 6.7814 | 9.0234 | 11.3799 | 15.3959 | 16.7564 | 19.326 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 | 21.2903 |  | 26.4959 | 22.6651 | 28.5301 | 12.0489 | 16.3909 | 23.2485 | 29.4454 | 38.0529 | 47.0282 | 54.3585 | 61.2713 | 71.545 | 79.0067 | 86.5262 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493 | 94.493
95% | 2.1027 | 0.79293 | 2.4921 |  |  | 0.11764 | 1.8021 | 3.8023 | 6.1581 | 8.3656 | 10.6859 | 14.6401 | 15.9796 | 18.5097 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 | 20.4438 |  | 49.0629 | 41.5191 | 53.0686 | 20.6134 | 29.1637 | 42.6678 | 54.871 | 71.8212 | 89.4957 | 103.9307 | 117.5435 | 137.775 | 152.4688 | 167.2763 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647 | 182.9647
90% | 7.211 | 0.46983 | 10.5424 |  |  |  | 4.9858 | 21.9048 | 42.3339 | 61.4773 | 81.5985 | 115.8884 | 127.5047 | 149.4454 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 | 166.2178 |  | 59.8428 | 48.9397 | 65.6323 | 18.7244 | 31.0823 | 50.5999 | 68.2374 | 92.7356 | 118.2809 | 139.144 | 158.8187 | 188.0595 | 209.2966 | 230.6982 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728 | 253.3728
85% |  |  | 0.12403 |  |  |  |  | 4.8825 | 23.6353 | 41.744 | 60.7775 | 93.2139 | 104.2023 | 124.9569 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 | 140.8228 |  | 75.9291 | 56.4476 | 86.2737 | 5.4352 | 24.5403 | 59.4141 | 90.9284 | 134.7016 | 180.3455 | 217.6235 | 252.778 | 305.025 | 342.9712 | 381.2112 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259 | 421.7259
80% | [8 empty] | 6.0637 | 24.4562 | 44.3961 | 78.3771 | 89.8888 | 111.6317 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 | 128.253 |  | 31.9709 | 16.8441 | 40.0032 |  | 0.6697 | 19.1475 | 43.6175 | 77.606 | 113.0472 | 141.9924 | 169.2888 | 209.8571 | 239.3213 | 269.0135 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719 | 300.4719
75% | [9 empty] | 6.6429 | 34.0186 | 85.093 | 102.3955 | 135.0758 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 | 160.0582 |  | 5.2097 | 0.078894 | 11.0304 |  |  | 0.34765 | 14.3139 | 50.6072 | 88.6566 | 119.732 | 149.0373 | 192.5911 | 224.2236 | 256.101 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745 | 289.8745
70% | [10 empty] | 9.3435 | 128.7505 | 175.2856 | 263.1798 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | 330.3704 | [8 empty] | 19.6201 | 72.1746 | 115.7804 | 156.9024 | 218.0182 | 262.4058 | 307.1369 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288 | 354.5288
65% | [11 empty] | 30.0926 | 78.2356 | 192.0234 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | 279.0588 | [9 empty] | 17.9317 | 64.9536 | 112.811 | 183.9372 | 235.5951 | 287.653 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073 | 342.8073
60% | FY38: 127.4985; FY39: 396.9649; FY40: 396.9649; FY41: 396.9649; FY42: 396.9649; FY43: 396.9649; FY44: 396.9649; FY45: 396.9649; FY46: 396.9649; FY47: 396.9649; FY48: 396.9649; FY49: 396.9649; FY50: 396.9649; FY51: 396.9649; FY52: 396.9649; FY53: 396.9649; FY54: 396.9649 | [10 empty] | 10.6343 | 82.0316 | 257.4494 | 386.5943 | 516.7389 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248 | 654.6248
55% | FY39: 1.5828; FY40: 1.5828; FY41: 1.5828; FY42: 1.5828; FY43: 1.5828; FY44: 1.5828; FY45: 1.5828; FY46: 1.5828; FY47: 1.5828; FY48: 1.5828; FY49: 1.5828; FY50: 1.5828; FY51: 1.5828; FY52: 1.5828; FY53: 1.5828; FY54: 1.5828 | [12 empty] | 38.2581 | 132.0047 | 247.3031 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598 | 369.4598
50% | [43 empty] | 0.71785 | 72.9913 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389 | 268.0389
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0122 | 4.2872 | 19.652 | 0 | 0 | 1.6355 | 11.8728 | 39.7582 | 92.1693 | 161.1714 | 264.0427 | 577.3512 | 727.5227 | 1161.5173 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | 1666.9175 | E @ R (MWh) | 276.7535 | 210.8534 | 314.8423 | 70.4196 | 119.8459 | 220.3757 | 332.6456 | 525.1017 | 776.0157 | 1024.6353 | 1323.9755 | 1876.4228 | 2346.077 | 2911.743 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315 | 3629.5315
Option 4 Summer POE50 W E @ R (MWh) N 1 | 10.5085 | 3.001 | 13.7564 | 0 | 0 | 1.1448 | 8.311 | 27.8308 | 64.5185 | 112.82 | 184.8299 | 404.1458 | 509.2659 | 813.0621 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | 1166.8423 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 83.026 | 63.256 | 94.4527 | 21.1259 | 35.9538 | 66.1127 | 99.7937 | 157.5305 | 232.8047 | 307.3906 | 397.1927 | 562.9268 | 703.8231 | 873.5229 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595 | 1088.8595
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [6 empty] | 0.70577 | 4.889 | 9.1736 | 13.4198 | 17.192 | 21.3053 | 22.8666 | 28.1875 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | [6 empty] | 0.64937 | 4.0637 | 8.9403 | 13.1902 | 17.1984 | 21.3648 | 26.3618 | 28.0252 | 33.415 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384
98% | [6 empty] | 0.071104 | 2.1278 | 4.2486 | 6.3504 | 8.2175 | 10.2535 | 11.0263 | 13.66 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | [6 empty] | 0.053027 | 1.7193 | 4.1331 | 6.2367 | 8.2207 | 10.2829 | 12.7563 | 13.5796 | 16.2475 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339
97% | [7 empty] | 3.6223 | 7.8207 | 11.9816 | 15.678 | 19.7086 | 21.2385 | 26.4525 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | [7 empty] | 2.8135 | 7.5921 | 11.7566 | 15.6842 | 19.7668 | 24.6634 | 26.2934 | 31.5749 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973
95% | [7 empty] | 4.0083 | 10.209 | 16.3544 | 21.8137 | 27.7665 | 30.0261 | 37.7267 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | [7 empty] | 2.8139 | 9.8715 | 16.0221 | 21.8229 | 27.8526 | 35.0845 | 37.4918 | 45.2922 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622
90% | [7 empty] | 0.98442 | 6.6577 | 12.5791 | 17.8393 | 23.5751 | 25.7523 | 33.1722 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | [7 empty] | 0.37545 | 6.3325 | 12.2589 | 17.8482 | 23.658 | 30.6263 | 32.9458 | 40.4618 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668
85% | [8 empty] | 20.0858 | 86.2285 | 145.9389 | 211.0486 | 235.7631 | 319.9882 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | [8 empty] | 17.1787 | 82.5939 | 146.0401 | 211.9896 | 291.0889 | 317.4182 | 402.735 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509
80% | [9 empty] | 57.2904 | 198.839 | 355.7224 | 415.2725 | 618.215 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | [9 empty] | 50.1874 | 199.0829 | 357.9899 | 548.5814 | 612.0224 | 817.5955 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908
75% | [10 empty] | 111.5439 | 535.0016 | 708.9052 | 1301.556 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | [10 empty] | 112.007 | 541.6233 | 1098.2057 | 1283.4719 | 1883.8048 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188
70% | [11 empty] | 126.8698 | 348.7928 | 1584.0712 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | [11 empty] | 133.3684 | 1141.751 | 1544.7353 | 2850.5576 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921
65% | FY38: 294.6441; FY39: 1579.0533; FY40: 1579.0533; FY41: 1579.0533; FY42: 1579.0533; FY43: 1579.0533; FY44: 1579.0533; FY45: 1579.0533; FY46: 1579.0533; FY47: 1579.0533; FY48: 1579.0533; FY49: 1579.0533; FY50: 1579.0533; FY51: 1579.0533; FY52: 1579.0533; FY53: 1579.0533; FY54: 1579.0533 | [12 empty] | 76.7951 | 269.7865 | 1507.6591 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278
60% | FY39: 156.5762; FY40: 156.5762; FY41: 156.5762; FY42: 156.5762; FY43: 156.5762; FY44: 156.5762; FY45: 156.5762; FY46: 156.5762; FY47: 156.5762; FY48: 156.5762; FY49: 156.5762; FY50: 156.5762; FY51: 156.5762; FY52: 156.5762; FY53: 156.5762; FY54: 156.5762 | [14 empty] | 127.8543 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349
55% | [45 empty] | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.77687 | 15.6318 | 58.1954 | 204.2042 | 537.0622 | 1331.2514 | 1819.6435 | 4257.6733 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.7024 | 11.7859 | 54.0481 | 192.2458 | 537.9044 | 1347.8964 | 3285.9144 | 4165.77 | 7757.1976 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54381 | 10.9422 | 40.7368 | 142.943 | 375.9435 | 931.876 | 1273.7505 | 2980.3713 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0.21072 | 3.5358 | 16.2144 | 57.6737 | 161.3713 | 404.3689 | 985.7743 | 1249.731 | 2327.1593 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.7051 | 8.402 | 10.397 | 12.0653 | 13.5423 | 15.875 | 17.983 | 20.911 | 23.9642 | 26.4578 | 28.8093 | 32.3041 | 34.8424 | 37.4003 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103
98% | 3.0359 | 1.692 | 3.4354 | 4.8134 | 6.4493 | 8.1364 | 9.929 | 11.9813 | 14.3984 | 16.6634 | 19.0441 | 23.1013 | 24.4757 | 27.0717 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 |  | 18.5371 | 15.957 | 19.9071 | 23.21 | 26.1343 | 30.7529 | 34.9266 | 40.7237 | 46.7687 | 51.7057 | 56.3614 | 63.2809 | 68.3063 | 73.3707 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364
97% | 2.6626 | 1.3324 | 3.0581 | 4.4221 | 6.0414 | 7.7113 | 9.4857 | 11.5172 | 13.9098 | 16.1518 | 18.5083 | 22.5243 | 23.8848 | 26.4544 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 |  | 26.4959 | 22.6651 | 28.5301 | 33.4341 | 37.7761 | 44.6336 | 50.8306 | 59.4381 | 68.4134 | 75.7437 | 82.6565 | 92.9302 | 100.3919 | 107.9114 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781
95% | 2.1027 | 0.79293 | 2.4921 | 3.8351 | 5.4295 | 7.0737 | 8.8209 | 10.821 | 13.1768 | 15.3844 | 17.7046 | 21.6588 | 22.9983 | 25.5284 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 |  | 49.0629 | 41.5191 | 53.0686 | 62.7258 | 71.2761 | 84.7802 | 96.9834 | 113.9335 | 131.6081 | 146.0431 | 159.6559 | 179.8873 | 194.5811 | 209.3887 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771
90% | 7.211 | 0.46983 | 10.5424 | 22.189 | 36.0153 | 50.2742 | 65.4249 | 82.7703 | 103.1994 | 122.3429 | 142.4641 | 176.7539 | 188.3703 | 210.3109 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 |  | 59.8428 | 48.9397 | 65.6323 | 79.59 | 91.9479 | 111.4655 | 129.1029 | 153.6012 | 179.1464 | 200.0095 | 219.6842 | 248.925 | 270.1622 | 291.5637 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383
85% |  |  | 0.12403 | 5.0863 | 17.6582 | 31.1464 | 45.4782 | 61.886 | 81.2108 | 99.3195 | 118.353 | 150.7894 | 161.7778 | 182.5325 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 |  | 75.9291 | 56.4476 | 86.2737 | 111.2131 | 133.294 | 168.1679 | 199.6822 | 243.4553 | 289.0992 | 326.3772 | 361.5317 | 413.7787 | 451.725 | 489.965 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796
80% |  |  |  |  | 2.1761 | 13.3539 | 28.3682 | 45.5574 | 65.8024 | 84.7734 | 104.7133 | 138.6943 | 150.206 | 171.9489 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 |  | 31.9709 | 16.8441 | 40.0032 | 59.3679 | 76.5131 | 103.5916 | 128.0615 | 162.0501 | 197.4913 | 226.4365 | 253.7329 | 294.3012 | 323.7654 | 353.4576 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916
75% | [5 empty] | 0.28 | 10.7866 | 35.764 | 66.1929 | 94.7069 | 124.6772 | 175.7516 | 193.054 | 225.7343 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 |  | 5.2097 | 0.078894 | 11.0304 | 31.0269 | 49.4339 | 78.5051 | 104.7759 | 141.2658 | 179.3152 | 210.3906 | 239.6959 | 283.2497 | 314.8822 | 346.7596 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331
70% | [7 empty] | 11.4544 | 77.9184 | 154.6071 | 235.2127 | 372.5782 | 419.1133 | 507.0075 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 |  |  |  |  | 3.2418 | 18.2702 | 57.9299 | 94.7937 | 145.9972 | 199.3891 | 242.9949 | 284.1168 | 345.2326 | 389.6202 | 434.3514 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433
65% | [8 empty] | 2.9215 | 54.2203 | 155.7961 | 333.7328 | 394.0122 | 507.8662 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | [6 empty] | 8.1995 | 40.5294 | 100.1197 | 162.2568 | 213.0049 | 260.8623 | 331.9885 | 383.6465 | 435.7043 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587
60% | [10 empty] | 57.7158 | 601.0433 | 826.0446 | 1251.0202 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | [7 empty] | 0.041494 | 56.9141 | 203.2484 | 330.1188 | 449.7623 | 627.5777 | 756.7226 | 886.8672 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531
55% | [11 empty] | 74.6128 | 275.2322 | 964.0448 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | [9 empty] | 15.1021 | 84.7165 | 187.9668 | 345.4981 | 459.9109 | 575.2094 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661
50% | FY38: 8.3889; FY39: 297.914; FY40: 297.914; FY41: 297.914; FY42: 297.914; FY43: 297.914; FY44: 297.914; FY45: 297.914; FY46: 297.914; FY47: 297.914; FY48: 297.914; FY49: 297.914; FY50: 297.914; FY51: 297.914; FY52: 297.914; FY53: 297.914; FY54: 297.914 | [11 empty] | 21.3613 | 220.8583 | 468.0136 | 725.7963 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125
45% | [43 empty] | 38.4581 | 283.8992 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0122 | 4.2872 | 19.652 | 40.3458 | 73.7697 | 117.9759 | 178.2936 | 271.7517 | 438.7305 | 658.1697 | 994.1892 | 2091.2406 | 2679.1692 | 4107.9087 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | E @ R (MWh) | 276.7535 | 210.8534 | 314.8423 | 415.8748 | 518.1878 | 703.9012 | 897.7107 | 1238.4098 | 1695.8029 | 2133.9992 | 2606.1972 | 3479.8123 | 4255.0284 | 5251.6447 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616
Option 5 Summer POE50 W E @ R (MWh) N 1 | 10.5085 | 3.001 | 13.7564 | 28.242 | 51.6388 | 82.5831 | 124.8055 | 190.2262 | 307.1113 | 460.7188 | 695.9325 | 1463.8684 | 1875.4184 | 2875.5361 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 83.026 | 63.256 | 94.4527 | 124.7624 | 155.4564 | 211.1703 | 269.3132 | 371.5229 | 508.7409 | 640.1998 | 781.8592 | 1043.9437 | 1276.5085 | 1575.4934 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 3.1352 | 7.1562 | 10.7165 | 14.5102 | 15.8421 | 20.9313 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | 26.1899 | [8 empty] | 3.1794 | 7.1519 | 10.9348 | 14.8892 | 19.5668 | 21.0006 | 26.1588 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359 | 30.9359
98% | [8 empty] | 1.2597 | 3.25 | 5.0123 | 6.8901 | 7.5493 | 10.0684 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | 12.6712 | [8 empty] | 1.2816 | 3.2479 | 5.1203 | 7.0777 | 9.3929 | 10.1027 | 12.6558 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204 | 15.0204
97% | [8 empty] | 1.9037 | 5.8439 | 9.3326 | 13.0501 | 14.3552 | 19.3421 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | 24.4949 | [8 empty] | 1.947 | 5.8397 | 9.5465 | 13.4214 | 18.005 | 19.41 | 24.4645 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456 | 29.1456
95% | [8 empty] | 1.4702 | 7.2895 | 12.442 | 17.9325 | 19.86 | 27.2253 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | 34.8356 | [8 empty] | 1.534 | 7.2832 | 12.758 | 18.4809 | 25.2504 | 27.3256 | 34.7907 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043 | 41.7043
90% | [8 empty] | 0.032341 | 3.8446 | 8.8093 | 14.0996 | 15.9568 | 23.0536 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | 30.3865 | [8 empty] | 0.040222 | 3.8386 | 9.1138 | 14.628 | 21.1508 | 23.1503 | 30.3432 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048 | 37.0048
85% | [9 empty] | 2.3355 | 43.4362 | 103.4886 | 124.5707 | 205.1288 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | 288.3668 | [9 empty] | 2.3158 | 46.8927 | 109.487 | 183.5289 | 206.2258 | 287.8756 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931 | 363.4931
80% | [10 empty] | 3.1035 | 96.554 | 147.3519 | 341.4584 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | 542.0225 | [10 empty] | 5.0136 | 111.0072 | 289.4129 | 344.1018 | 540.8389 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041 | 723.041
75% | [11 empty] | 1.4686 | 34.7777 | 493.3467 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | 1079.0519 | [11 empty] | 6.521 | 341.3587 | 501.066 | 1075.5955 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782 | 1607.6782
70% | FY38: 89.6193; FY39: 1100.0884; FY40: 1100.0884; FY41: 1100.0884; FY42: 1100.0884; FY43: 1100.0884; FY44: 1100.0884; FY45: 1100.0884; FY46: 1100.0884; FY47: 1100.0884; FY48: 1100.0884; FY49: 1100.0884; FY50: 1100.0884; FY51: 1100.0884; FY52: 1100.0884; FY53: 1100.0884; FY54: 1100.0884 | [12 empty] | 8.0531 | 96.0474 | 1092.5702 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372 | 2249.9372
65% | FY39: 63.4034; FY40: 63.4034; FY41: 63.4034; FY42: 63.4034; FY43: 63.4034; FY44: 63.4034; FY45: 63.4034; FY46: 63.4034; FY47: 63.4034; FY48: 63.4034; FY49: 63.4034; FY50: 63.4034; FY51: 63.4034; FY52: 63.4034; FY53: 63.4034; FY54: 63.4034 | [14 empty] | 61.1207 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161 | 869.4161
60% | [45 empty] | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227 | 0.13227
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8012 | 29.7198 | 92.8523 | 267.9936 | 380.2637 | 1230.1738 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | 3201.5112 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9822 | 29.6771 | 99.3797 | 295.5123 | 915.7195 | 1248.4301 | 3186.4141 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088 | 5967.5088
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4609 | 20.8039 | 64.9966 | 187.5955 | 266.1846 | 861.1217 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | 2241.0578 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3947 | 8.9031 | 29.8139 | 88.6537 | 274.7159 | 374.529 | 955.9242 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526 | 1790.2526
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.1145 | 5.4478 | 7.33 | 8.9047 | 10.2995 | 12.4989 | 14.4869 | 17.2459 | 20.1225 | 22.4728 | 24.6894 | 27.981 | 30.3733 | 32.7838 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371 | 35.3371
98% | 0.47136 |  | 0.39913 | 1.6846 | 3.2391 | 4.7943 | 6.468 | 8.3529 | 10.5954 | 12.7185 | 14.9657 | 18.8216 | 20.0515 | 22.5016 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 | 24.3309 |  | 13.408 | 10.108 | 13.8345 | 16.9524 | 19.7139 | 24.0686 | 28.0045 | 33.467 | 39.1626 | 43.8158 | 48.2045 | 54.7215 | 59.4579 | 64.2305 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859 | 69.2859
97% | 0.12764 |  | 0.073618 | 1.3251 | 2.8638 | 4.4031 | 6.0598 | 7.9257 | 10.1453 | 12.2469 | 14.4713 | 18.2881 | 19.5055 | 21.9307 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 | 23.7415 |  | 18.8805 | 13.9807 | 19.5137 | 24.1431 | 28.2433 | 34.709 | 40.5529 | 48.6635 | 57.1201 | 64.029 | 70.5453 | 80.2216 | 87.2541 | 94.3403 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464 | 101.8464
95% |  |  |  | 0.78573 | 2.3008 | 3.8164 | 5.4477 | 7.2848 | 9.4703 | 11.5395 | 13.7297 | 17.4877 | 18.6864 | 21.0743 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 | 22.8573 |  | 34.0663 | 24.4176 | 35.3133 | 44.4297 | 52.5038 | 65.2363 | 76.7442 | 92.7159 | 109.3689 | 122.9742 | 135.8063 | 154.861 | 168.7097 | 182.664 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453 | 197.4453
90% |  |  |  | 0.4546 | 8.8834 | 22.0272 | 36.173 | 52.1043 | 71.0568 | 89.0011 | 107.9939 | 140.5831 | 150.978 | 171.6854 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 | 187.1469 |  | 38.168 | 24.2226 | 39.9704 | 53.1463 | 64.8161 | 83.2185 | 99.851 | 122.9351 | 147.0038 | 166.6677 | 185.2141 | 212.7542 | 232.7698 | 252.9382 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018 | 274.3018
85% |  |  |  |  | 0.0056845 | 4.9698 | 17.8074 | 32.8775 | 50.8056 | 67.7799 | 85.7461 | 116.5737 | 126.4067 | 145.9948 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 | 160.6205 |  | 37.2009 | 12.5795 | 40.4213 | 63.964 | 84.8153 | 117.6965 | 147.4152 | 188.6616 | 231.6672 | 266.8025 | 299.9409 | 349.1492 | 384.9129 | 420.9494 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216 | 459.1216
80% | [6 empty] | 2.2501 | 15.1676 | 33.9494 | 51.732 | 70.5537 | 102.8493 | 113.1505 | 133.6714 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 | 148.9936 |  | 4.6047 |  | 6.1462 | 22.6803 | 38.8708 | 64.402 | 87.4778 | 119.5044 | 152.897 | 180.1785 | 205.9095 | 244.1182 | 271.8877 | 299.8691 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086 | 329.5086
75% | [7 empty] | 0.75363 | 18.3169 | 45.0446 | 73.3343 | 121.8756 | 137.3586 | 168.2021 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 | 191.2318 |  |  |  |  | 1.1243 | 10.0854 | 36.4315 | 61.2055 | 95.589 | 131.4391 | 160.7283 | 188.353 | 229.3736 | 259.1867 | 289.2273 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481 | 321.0481
70% | [8 empty] | 0.0039821 | 26.1184 | 97.1252 | 227.6776 | 269.3195 | 352.2735 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | 414.2123 | [6 empty] | 6.4261 | 33.6545 | 81.9024 | 132.2081 | 173.3075 | 212.0712 | 269.6324 | 311.4669 | 353.6206 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724 | 398.2724
65% | [10 empty] | 9.9208 | 146.0356 | 199.9764 | 307.4311 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | 387.6636 | [7 empty] | 0.22521 | 26.6091 | 84.0721 | 131.9032 | 177.0161 | 244.0054 | 292.6922 | 341.7503 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158 | 393.7158
60% | [11 empty] | 43.4534 | 146.2897 | 502.8685 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | 802.3475 | [9 empty] | 31.4326 | 127.3646 | 240.1467 | 407.62 | 529.3369 | 651.9823 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961 | 781.8961
55% | FY38: 26.0924; FY39: 248.4217; FY40: 248.4217; FY41: 248.4217; FY42: 248.4217; FY43: 248.4217; FY44: 248.4217; FY45: 248.4217; FY46: 248.4217; FY47: 248.4217; FY48: 248.4217; FY49: 248.4217; FY50: 248.4217; FY51: 248.4217; FY52: 248.4217; FY53: 248.4217; FY54: 248.4217 | [10 empty] | 0.35445 | 29.7663 | 150.6319 | 258.464 | 367.1188 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127 | 482.2127
50% | [42 empty] | 4.4607 | 85.9735 | 263.2452 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757 | 517.8757
45% | [45 empty] | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475 | 68.7475
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.599 | 0 | 0.47275 | 4.25 | 17.2928 | 40.0107 | 74.206 | 124.4664 | 204.3437 | 316.181 | 487.8408 | 953.6458 | 1201.7227 | 1873.7257 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | 2611.5675 | E @ R (MWh) | 153.4429 | 90.7563 | 162.5295 | 235.345 | 309.348 | 444.6875 | 589.6175 | 827.2939 | 1136.494 | 1460.5986 | 1817.6633 | 2429.5306 | 2972.4855 | 3614.7199 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153 | 4430.6153
Option 6 Summer POE50 W E @ R (MWh) N 1 | 0.4193 | 0 | 0.33092 | 2.975 | 12.1049 | 28.0075 | 51.9442 | 87.1265 | 143.0406 | 221.3267 | 341.4885 | 667.552 | 841.2059 | 1311.608 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | 1828.0972 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 46.0329 | 27.2269 | 48.7588 | 70.6035 | 92.8044 | 133.4063 | 176.8852 | 248.1882 | 340.9482 | 438.1796 | 545.299 | 728.8592 | 891.7457 | 1084.416 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846 | 1329.1846
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [6 empty] | 0.70577 | 4.889 | 9.1736 | 13.4198 | 17.192 | 21.3053 | 22.8666 | 28.1875 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | [6 empty] | 0.64937 | 4.0637 | 8.9403 | 13.1902 | 17.1984 | 21.3648 | 26.3618 | 28.0252 | 33.415 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384
98% | [6 empty] | 0.071104 | 2.1278 | 4.2486 | 6.3504 | 8.2175 | 10.2535 | 11.0263 | 13.66 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | [6 empty] | 0.053027 | 1.7193 | 4.1331 | 6.2367 | 8.2207 | 10.2829 | 12.7563 | 13.5796 | 16.2475 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339
97% | [7 empty] | 3.6223 | 7.8207 | 11.9816 | 15.678 | 19.7086 | 21.2385 | 26.4525 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | [7 empty] | 2.8135 | 7.5921 | 11.7566 | 15.6842 | 19.7668 | 24.6634 | 26.2934 | 31.5749 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973
95% | [7 empty] | 4.0083 | 10.209 | 16.3544 | 21.8137 | 27.7665 | 30.0261 | 37.7267 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | [7 empty] | 2.8139 | 9.8715 | 16.0221 | 21.8229 | 27.8526 | 35.0845 | 37.4918 | 45.2922 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622
90% | [7 empty] | 0.98442 | 6.6577 | 12.5791 | 17.8393 | 23.5751 | 25.7523 | 33.1722 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | [7 empty] | 0.37545 | 6.3325 | 12.2589 | 17.8482 | 23.658 | 30.6263 | 32.9458 | 40.4618 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668
85% | [8 empty] | 20.0858 | 86.2285 | 145.9389 | 211.0486 | 235.7631 | 319.9882 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | [8 empty] | 17.1787 | 82.5939 | 146.0401 | 211.9896 | 291.0889 | 317.4182 | 402.735 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509
80% | [9 empty] | 57.2904 | 198.839 | 355.7224 | 415.2725 | 618.215 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | [9 empty] | 50.1874 | 199.0829 | 357.9899 | 548.5814 | 612.0224 | 817.5955 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908
75% | [10 empty] | 111.5439 | 535.0016 | 708.9052 | 1301.556 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | [10 empty] | 112.007 | 541.6233 | 1098.2057 | 1283.4719 | 1883.8048 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188
70% | [11 empty] | 126.8698 | 348.7928 | 1584.0712 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | [11 empty] | 133.3684 | 1141.751 | 1544.7353 | 2850.5576 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921
65% | FY38: 294.6441; FY39: 1579.0533; FY40: 1579.0533; FY41: 1579.0533; FY42: 1579.0533; FY43: 1579.0533; FY44: 1579.0533; FY45: 1579.0533; FY46: 1579.0533; FY47: 1579.0533; FY48: 1579.0533; FY49: 1579.0533; FY50: 1579.0533; FY51: 1579.0533; FY52: 1579.0533; FY53: 1579.0533; FY54: 1579.0533 | [12 empty] | 76.7951 | 269.7865 | 1507.6591 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278
60% | FY39: 156.5762; FY40: 156.5762; FY41: 156.5762; FY42: 156.5762; FY43: 156.5762; FY44: 156.5762; FY45: 156.5762; FY46: 156.5762; FY47: 156.5762; FY48: 156.5762; FY49: 156.5762; FY50: 156.5762; FY51: 156.5762; FY52: 156.5762; FY53: 156.5762; FY54: 156.5762 | [14 empty] | 127.8543 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349
55% | [45 empty] | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.77687 | 15.6318 | 58.1954 | 204.2042 | 537.0622 | 1331.2514 | 1819.6435 | 4257.6733 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.7024 | 11.7859 | 54.0481 | 192.2458 | 537.9044 | 1347.8964 | 3285.9144 | 4165.77 | 7757.1976 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54381 | 10.9422 | 40.7368 | 142.943 | 375.9435 | 931.876 | 1273.7505 | 2980.3713 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0.21072 | 3.5358 | 16.2144 | 57.6737 | 161.3713 | 404.3689 | 985.7743 | 1249.731 | 2327.1593 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.7051 | 8.402 | 10.397 | 12.0653 | 13.5423 | 15.875 | 17.983 | 20.911 | 23.9642 | 26.4578 | 28.8093 | 32.3041 | 34.8424 | 37.4003 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103
98% | 3.0359 | 1.692 | 3.4354 | 4.8134 | 6.4493 | 8.1364 | 9.929 | 11.9813 | 14.3984 | 16.6634 | 19.0441 | 23.1013 | 24.4757 | 27.0717 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 |  | 18.5371 | 15.957 | 19.9071 | 23.21 | 26.1343 | 30.7529 | 34.9266 | 40.7237 | 46.7687 | 51.7057 | 56.3614 | 63.2809 | 68.3063 | 73.3707 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364
97% | 2.6626 | 1.3324 | 3.0581 | 4.4221 | 6.0414 | 7.7113 | 9.4857 | 11.5172 | 13.9098 | 16.1518 | 18.5083 | 22.5243 | 23.8848 | 26.4544 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 |  | 26.4959 | 22.6651 | 28.5301 | 33.4341 | 37.7761 | 44.6336 | 50.8306 | 59.4381 | 68.4134 | 75.7437 | 82.6565 | 92.9302 | 100.3919 | 107.9114 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781
95% | 2.1027 | 0.79293 | 2.4921 | 3.8351 | 5.4295 | 7.0737 | 8.8209 | 10.821 | 13.1768 | 15.3844 | 17.7046 | 21.6588 | 22.9983 | 25.5284 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 |  | 49.0629 | 41.5191 | 53.0686 | 62.7258 | 71.2761 | 84.7802 | 96.9834 | 113.9335 | 131.6081 | 146.0431 | 159.6559 | 179.8873 | 194.5811 | 209.3887 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771
90% | 7.211 | 0.46983 | 10.5424 | 22.189 | 36.0153 | 50.2742 | 65.4249 | 82.7703 | 103.1994 | 122.3429 | 142.4641 | 176.7539 | 188.3703 | 210.3109 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 |  | 59.8428 | 48.9397 | 65.6323 | 79.59 | 91.9479 | 111.4655 | 129.1029 | 153.6012 | 179.1464 | 200.0095 | 219.6842 | 248.925 | 270.1622 | 291.5637 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383
85% |  |  | 0.12403 | 5.0863 | 17.6582 | 31.1464 | 45.4782 | 61.886 | 81.2108 | 99.3195 | 118.353 | 150.7894 | 161.7778 | 182.5325 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 |  | 75.9291 | 56.4476 | 86.2737 | 111.2131 | 133.294 | 168.1679 | 199.6822 | 243.4553 | 289.0992 | 326.3772 | 361.5317 | 413.7787 | 451.725 | 489.965 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796
80% |  |  |  |  | 2.1761 | 13.3539 | 28.3682 | 45.5574 | 65.8024 | 84.7734 | 104.7133 | 138.6943 | 150.206 | 171.9489 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 |  | 31.9709 | 16.8441 | 40.0032 | 59.3679 | 76.5131 | 103.5916 | 128.0615 | 162.0501 | 197.4913 | 226.4365 | 253.7329 | 294.3012 | 323.7654 | 353.4576 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916
75% | [5 empty] | 0.28 | 10.7866 | 35.764 | 66.1929 | 94.7069 | 124.6772 | 175.7516 | 193.054 | 225.7343 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 |  | 5.2097 | 0.078894 | 11.0304 | 31.0269 | 49.4339 | 78.5051 | 104.7759 | 141.2658 | 179.3152 | 210.3906 | 239.6959 | 283.2497 | 314.8822 | 346.7596 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331
70% | [7 empty] | 11.4544 | 77.9184 | 154.6071 | 235.2127 | 372.5782 | 419.1133 | 507.0075 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 |  |  |  |  | 3.2418 | 18.2702 | 57.9299 | 94.7937 | 145.9972 | 199.3891 | 242.9949 | 284.1168 | 345.2326 | 389.6202 | 434.3514 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433
65% | [8 empty] | 2.9215 | 54.2203 | 155.7961 | 333.7328 | 394.0122 | 507.8662 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | [6 empty] | 8.1995 | 40.5294 | 100.1197 | 162.2568 | 213.0049 | 260.8623 | 331.9885 | 383.6465 | 435.7043 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587
60% | [10 empty] | 57.7158 | 601.0433 | 826.0446 | 1251.0202 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | [7 empty] | 0.041494 | 56.9141 | 203.2484 | 330.1188 | 449.7623 | 627.5777 | 756.7226 | 886.8672 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531
55% | [11 empty] | 74.6128 | 275.2322 | 964.0448 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | [9 empty] | 15.1021 | 84.7165 | 187.9668 | 345.4981 | 459.9109 | 575.2094 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661
50% | FY38: 8.3889; FY39: 297.914; FY40: 297.914; FY41: 297.914; FY42: 297.914; FY43: 297.914; FY44: 297.914; FY45: 297.914; FY46: 297.914; FY47: 297.914; FY48: 297.914; FY49: 297.914; FY50: 297.914; FY51: 297.914; FY52: 297.914; FY53: 297.914; FY54: 297.914 | [11 empty] | 21.3613 | 220.8583 | 468.0136 | 725.7963 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125
45% | [43 empty] | 38.4581 | 283.8992 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0122 | 4.2872 | 19.652 | 40.3458 | 73.7697 | 117.9759 | 178.2936 | 271.7517 | 438.7305 | 658.1697 | 994.1892 | 2091.2406 | 2679.1692 | 4107.9087 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | E @ R (MWh) | 276.7535 | 210.8534 | 314.8423 | 415.8748 | 518.1878 | 703.9012 | 897.7107 | 1238.4098 | 1695.8029 | 2133.9992 | 2606.1972 | 3479.8123 | 4255.0284 | 5251.6447 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616
Option 7 Summer POE50 W E @ R (MWh) N 1 | 10.5085 | 3.001 | 13.7564 | 28.242 | 51.6388 | 82.5831 | 124.8055 | 190.2262 | 307.1113 | 460.7188 | 695.9325 | 1463.8684 | 1875.4184 | 2875.5361 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 83.026 | 63.256 | 94.4527 | 124.7624 | 155.4564 | 211.1703 | 269.3132 | 371.5229 | 508.7409 | 640.1998 | 781.8592 | 1043.9437 | 1276.5085 | 1575.4934 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [6 empty] | 0.70577 | 4.889 | 9.1736 | 13.4198 | 17.192 | 21.3053 | 22.8666 | 28.1875 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | 33.6923 | [6 empty] | 0.64937 | 4.0637 | 8.9403 | 13.1902 | 17.1984 | 21.3648 | 26.3618 | 28.0252 | 33.415 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384 | 38.4384
98% | [6 empty] | 0.071104 | 2.1278 | 4.2486 | 6.3504 | 8.2175 | 10.2535 | 11.0263 | 13.66 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | 16.3847 | [6 empty] | 0.053027 | 1.7193 | 4.1331 | 6.2367 | 8.2207 | 10.2829 | 12.7563 | 13.5796 | 16.2475 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339 | 18.7339
97% | [7 empty] | 3.6223 | 7.8207 | 11.9816 | 15.678 | 19.7086 | 21.2385 | 26.4525 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | 31.8466 | [7 empty] | 2.8135 | 7.5921 | 11.7566 | 15.6842 | 19.7668 | 24.6634 | 26.2934 | 31.5749 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973 | 36.4973
95% | [7 empty] | 4.0083 | 10.209 | 16.3544 | 21.8137 | 27.7665 | 30.0261 | 37.7267 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | 45.6935 | [7 empty] | 2.8139 | 9.8715 | 16.0221 | 21.8229 | 27.8526 | 35.0845 | 37.4918 | 45.2922 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622 | 52.5622
90% | [7 empty] | 0.98442 | 6.6577 | 12.5791 | 17.8393 | 23.5751 | 25.7523 | 33.1722 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | 40.8485 | [7 empty] | 0.37545 | 6.3325 | 12.2589 | 17.8482 | 23.658 | 30.6263 | 32.9458 | 40.4618 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668 | 47.4668
85% | [8 empty] | 20.0858 | 86.2285 | 145.9389 | 211.0486 | 235.7631 | 319.9882 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | 407.1247 | [8 empty] | 17.1787 | 82.5939 | 146.0401 | 211.9896 | 291.0889 | 317.4182 | 402.735 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509 | 482.2509
80% | [9 empty] | 57.2904 | 198.839 | 355.7224 | 415.2725 | 618.215 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | 828.1724 | [9 empty] | 50.1874 | 199.0829 | 357.9899 | 548.5814 | 612.0224 | 817.5955 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908 | 1009.1908
75% | [10 empty] | 111.5439 | 535.0016 | 708.9052 | 1301.556 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | 1914.6925 | [10 empty] | 112.007 | 541.6233 | 1098.2057 | 1283.4719 | 1883.8048 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188 | 2443.3188
70% | [11 empty] | 126.8698 | 348.7928 | 1584.0712 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | 2917.7433 | [11 empty] | 133.3684 | 1141.751 | 1544.7353 | 2850.5576 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921 | 4067.5921
65% | FY38: 294.6441; FY39: 1579.0533; FY40: 1579.0533; FY41: 1579.0533; FY42: 1579.0533; FY43: 1579.0533; FY44: 1579.0533; FY45: 1579.0533; FY46: 1579.0533; FY47: 1579.0533; FY48: 1579.0533; FY49: 1579.0533; FY50: 1579.0533; FY51: 1579.0533; FY52: 1579.0533; FY53: 1579.0533; FY54: 1579.0533 | [12 empty] | 76.7951 | 269.7865 | 1507.6591 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278 | 2800.9278
60% | FY39: 156.5762; FY40: 156.5762; FY41: 156.5762; FY42: 156.5762; FY43: 156.5762; FY44: 156.5762; FY45: 156.5762; FY46: 156.5762; FY47: 156.5762; FY48: 156.5762; FY49: 156.5762; FY50: 156.5762; FY51: 156.5762; FY52: 156.5762; FY53: 156.5762; FY54: 156.5762 | [14 empty] | 127.8543 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349 | 1062.9349
55% | [45 empty] | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646 | 0.5646
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.77687 | 15.6318 | 58.1954 | 204.2042 | 537.0622 | 1331.2514 | 1819.6435 | 4257.6733 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | 7971.828 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.7024 | 11.7859 | 54.0481 | 192.2458 | 537.9044 | 1347.8964 | 3285.9144 | 4165.77 | 7757.1976 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785 | 12060.4785
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54381 | 10.9422 | 40.7368 | 142.943 | 375.9435 | 931.876 | 1273.7505 | 2980.3713 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | 5580.2796 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0.21072 | 3.5358 | 16.2144 | 57.6737 | 161.3713 | 404.3689 | 985.7743 | 1249.731 | 2327.1593 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436 | 3618.1436
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.7051 | 8.402 | 10.397 | 12.0653 | 13.5423 | 15.875 | 17.983 | 20.911 | 23.9642 | 26.4578 | 28.8093 | 32.3041 | 34.8424 | 37.4003 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103 | 40.1103
98% | 3.0359 | 1.692 | 3.4354 | 4.8134 | 6.4493 | 8.1364 | 9.929 | 11.9813 | 14.3984 | 16.6634 | 19.0441 | 23.1013 | 24.4757 | 27.0717 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 | 29.0562 |  | 18.5371 | 15.957 | 19.9071 | 23.21 | 26.1343 | 30.7529 | 34.9266 | 40.7237 | 46.7687 | 51.7057 | 56.3614 | 63.2809 | 68.3063 | 73.3707 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364 | 78.7364
97% | 2.6626 | 1.3324 | 3.0581 | 4.4221 | 6.0414 | 7.7113 | 9.4857 | 11.5172 | 13.9098 | 16.1518 | 18.5083 | 22.5243 | 23.8848 | 26.4544 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 | 28.4187 |  | 26.4959 | 22.6651 | 28.5301 | 33.4341 | 37.7761 | 44.6336 | 50.8306 | 59.4381 | 68.4134 | 75.7437 | 82.6565 | 92.9302 | 100.3919 | 107.9114 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781 | 115.8781
95% | 2.1027 | 0.79293 | 2.4921 | 3.8351 | 5.4295 | 7.0737 | 8.8209 | 10.821 | 13.1768 | 15.3844 | 17.7046 | 21.6588 | 22.9983 | 25.5284 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 | 27.4625 |  | 49.0629 | 41.5191 | 53.0686 | 62.7258 | 71.2761 | 84.7802 | 96.9834 | 113.9335 | 131.6081 | 146.0431 | 159.6559 | 179.8873 | 194.5811 | 209.3887 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771 | 225.0771
90% | 7.211 | 0.46983 | 10.5424 | 22.189 | 36.0153 | 50.2742 | 65.4249 | 82.7703 | 103.1994 | 122.3429 | 142.4641 | 176.7539 | 188.3703 | 210.3109 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 | 227.0833 |  | 59.8428 | 48.9397 | 65.6323 | 79.59 | 91.9479 | 111.4655 | 129.1029 | 153.6012 | 179.1464 | 200.0095 | 219.6842 | 248.925 | 270.1622 | 291.5637 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383 | 314.2383
85% |  |  | 0.12403 | 5.0863 | 17.6582 | 31.1464 | 45.4782 | 61.886 | 81.2108 | 99.3195 | 118.353 | 150.7894 | 161.7778 | 182.5325 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 | 198.3983 |  | 75.9291 | 56.4476 | 86.2737 | 111.2131 | 133.294 | 168.1679 | 199.6822 | 243.4553 | 289.0992 | 326.3772 | 361.5317 | 413.7787 | 451.725 | 489.965 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796 | 530.4796
80% |  |  |  |  | 2.1761 | 13.3539 | 28.3682 | 45.5574 | 65.8024 | 84.7734 | 104.7133 | 138.6943 | 150.206 | 171.9489 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 | 188.5703 |  | 31.9709 | 16.8441 | 40.0032 | 59.3679 | 76.5131 | 103.5916 | 128.0615 | 162.0501 | 197.4913 | 226.4365 | 253.7329 | 294.3012 | 323.7654 | 353.4576 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916 | 384.916
75% | [5 empty] | 0.28 | 10.7866 | 35.764 | 66.1929 | 94.7069 | 124.6772 | 175.7516 | 193.054 | 225.7343 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 | 250.7167 |  | 5.2097 | 0.078894 | 11.0304 | 31.0269 | 49.4339 | 78.5051 | 104.7759 | 141.2658 | 179.3152 | 210.3906 | 239.6959 | 283.2497 | 314.8822 | 346.7596 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331 | 380.5331
70% | [7 empty] | 11.4544 | 77.9184 | 154.6071 | 235.2127 | 372.5782 | 419.1133 | 507.0075 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 | 574.1981 |  |  |  |  | 3.2418 | 18.2702 | 57.9299 | 94.7937 | 145.9972 | 199.3891 | 242.9949 | 284.1168 | 345.2326 | 389.6202 | 434.3514 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433 | 481.7433
65% | [8 empty] | 2.9215 | 54.2203 | 155.7961 | 333.7328 | 394.0122 | 507.8662 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | 594.9016 | [6 empty] | 8.1995 | 40.5294 | 100.1197 | 162.2568 | 213.0049 | 260.8623 | 331.9885 | 383.6465 | 435.7043 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587 | 490.8587
60% | [10 empty] | 57.7158 | 601.0433 | 826.0446 | 1251.0202 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | 1575.8921 | [7 empty] | 0.041494 | 56.9141 | 203.2484 | 330.1188 | 449.7623 | 627.5777 | 756.7226 | 886.8672 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531 | 1024.7531
55% | [11 empty] | 74.6128 | 275.2322 | 964.0448 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | 1597.7213 | [9 empty] | 15.1021 | 84.7165 | 187.9668 | 345.4981 | 459.9109 | 575.2094 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661 | 697.3661
50% | FY38: 8.3889; FY39: 297.914; FY40: 297.914; FY41: 297.914; FY42: 297.914; FY43: 297.914; FY44: 297.914; FY45: 297.914; FY46: 297.914; FY47: 297.914; FY48: 297.914; FY49: 297.914; FY50: 297.914; FY51: 297.914; FY52: 297.914; FY53: 297.914; FY54: 297.914 | [11 empty] | 21.3613 | 220.8583 | 468.0136 | 725.7963 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125 | 998.9125
45% | [43 empty] | 38.4581 | 283.8992 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759 | 768.759
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0122 | 4.2872 | 19.652 | 40.3458 | 73.7697 | 117.9759 | 178.2936 | 271.7517 | 438.7305 | 658.1697 | 994.1892 | 2091.2406 | 2679.1692 | 4107.9087 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | 5590.3332 | E @ R (MWh) | 276.7535 | 210.8534 | 314.8423 | 415.8748 | 518.1878 | 703.9012 | 897.7107 | 1238.4098 | 1695.8029 | 2133.9992 | 2606.1972 | 3479.8123 | 4255.0284 | 5251.6447 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616 | 6532.3616
Option 8 Summer POE50 W E @ R (MWh) N 1 | 10.5085 | 3.001 | 13.7564 | 28.242 | 51.6388 | 82.5831 | 124.8055 | 190.2262 | 307.1113 | 460.7188 | 695.9325 | 1463.8684 | 1875.4184 | 2875.5361 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | 3913.2332 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 83.026 | 63.256 | 94.4527 | 124.7624 | 155.4564 | 211.1703 | 269.3132 | 371.5229 | 508.7409 | 640.1998 | 781.8592 | 1043.9437 | 1276.5085 | 1575.4934 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085 | 1959.7085

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 15.9 | 14.2872 | 16.81 | 20.0388 | 23.1651 | 25.9461 | 29.7718 | 33.955 | 38.2396 | 42.4859 | 46.258 | 50.3713 | 51.9326 | 57.2535 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 |  | 19.0877 | 17.4876 | 20.1545 | 23.4232 | 26.4701 | 29.7154 | 33.1297 | 38.0063 | 42.2562 | 46.2644 | 50.4308 | 55.4278 | 57.0912 | 62.481 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044
98% | 7.7241 | 6.9258 | 8.1744 | 9.7727 | 11.3201 | 12.6966 | 14.5902 | 16.6608 | 18.7816 | 20.8834 | 22.7505 | 24.7865 | 25.5593 | 28.193 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 |  | 9.3019 | 8.5099 | 9.8299 | 11.4479 | 12.956 | 14.5623 | 16.2523 | 18.6661 | 20.7697 | 22.7537 | 24.8159 | 27.2893 | 28.1126 | 30.7805 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669
97% | 14.9962 | 13.4158 | 15.8878 | 19.0518 | 22.1153 | 24.8403 | 28.5891 | 32.6883 | 36.8867 | 41.0476 | 44.744 | 48.7746 | 50.3045 | 55.5185 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 |  | 18.1198 | 16.5518 | 19.1651 | 22.3682 | 25.3538 | 28.5339 | 31.8796 | 36.6581 | 40.8226 | 44.7503 | 48.8328 | 53.7295 | 55.3594 | 60.6409 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633
95% | 21.4775 | 19.1434 | 22.7943 | 27.4673 | 31.9918 | 36.0164 | 41.5532 | 47.6073 | 53.8081 | 59.9534 | 65.4127 | 71.3656 | 73.6252 | 81.3258 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 |  | 26.0908 | 23.775 | 27.6347 | 32.3653 | 36.7748 | 41.4715 | 46.4129 | 53.4705 | 59.6211 | 65.4219 | 71.4516 | 78.6835 | 81.0908 | 88.8912 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612
90% | 19.1049 | 16.8559 | 20.3737 | 24.8763 | 29.2359 | 33.1138 | 38.4487 | 44.2821 | 50.2568 | 56.1781 | 61.4383 | 67.1741 | 69.3514 | 76.7712 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 |  | 23.55 | 21.3187 | 25.0376 | 29.5958 | 33.8445 | 38.37 | 43.1312 | 49.9315 | 55.8579 | 61.4472 | 67.257 | 74.2253 | 76.5448 | 84.0608 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658
85% | 188.5861 | 163.0564 | 202.9891 | 254.0993 | 303.5863 | 347.6059 | 408.1639 | 474.3809 | 542.2018 | 609.4168 | 669.1272 | 734.2369 | 758.9514 | 843.1765 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 |  | 239.0441 | 213.7155 | 255.9301 | 307.6717 | 355.9007 | 407.2711 | 461.3172 | 538.5094 | 605.7822 | 669.2284 | 735.178 | 814.2772 | 840.6065 | 925.9234 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392
80% | 378.0005 | 316.4863 | 412.7049 | 535.8562 | 655.0962 | 761.1625 | 907.0785 | 1066.6301 | 1230.0461 | 1392.0022 | 1535.8758 | 1692.7592 | 1752.3093 | 1955.2518 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 |  | 499.5803 | 438.5505 | 540.2675 | 664.9401 | 781.1492 | 904.9273 | 1035.1526 | 1221.1492 | 1383.2444 | 1536.1197 | 1695.0267 | 1885.6182 | 1949.0592 | 2154.6323 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276
75% | 851.9655 | 672.3262 | 953.3124 | 1312.9498 | 1661.1654 | 1970.9098 | 2397.0265 | 2862.9635 | 3340.1856 | 3813.1444 | 4233.297 | 4691.442 | 4865.3456 | 5457.9964 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 |  | 1207.0139 | 1028.7891 | 1325.8323 | 1689.9124 | 2029.2767 | 2390.7446 | 2771.0402 | 3314.204 | 3787.5692 | 4234.0092 | 4698.0637 | 5254.6461 | 5439.9123 | 6040.2452 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592
70% | 1229.6514 | 838.9064 | 1450.0975 | 2232.3676 | 2989.7935 | 3663.5381 | 4590.4118 | 5603.901 | 6641.937 | 7670.6997 | 8584.6003 | 9581.1407 | 9959.4095 | 11248.5219 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 |  | 2001.9397 | 1614.2716 | 2260.3891 | 3052.3229 | 3790.4957 | 4576.7476 | 5403.9526 | 6585.4229 | 7615.0695 | 8586.1496 | 9595.544 | 10806.2017 | 11209.186 | 12515.0083 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428
65% | 545.9482 | 179.044 | 780.2029 | 1611.4739 | 2416.3444 | 3132.292 | 4117.2244 | 5194.1979 | 6297.2558 | 7390.4596 | 8361.6063 | 9420.5693 | 9822.5326 | 11192.3942 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 |  | 1366.6121 | 954.6607 | 1641.2505 | 2482.7906 | 3267.202 | 4102.7043 | 4981.7249 | 6237.2017 | 7331.3448 | 8363.2527 | 9435.8749 | 10722.3674 | 11150.5944 | 12538.2125 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813
60% | 8.8727 |  | 74.4011 | 747.9553 | 1573.7203 | 2308.2539 | 3318.7553 | 4423.6871 | 5555.3805 | 6676.9639 | 7673.3217 | 8759.7755 | 9172.1738 | 10577.5971 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 |  | 496.8079 | 162.7993 | 778.5049 | 1641.8914 | 2446.6663 | 3303.8582 | 4205.6983 | 5493.7674 | 6616.3145 | 7675.0108 | 8775.4784 | 10095.3683 | 10534.7121 | 11958.353 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951
55% |  |  |  | 32.0716 | 599.6383 | 1452.362 | 2630.7435 | 3919.2438 | 5238.9517 | 6546.87 | 7708.7583 | 8975.7107 | 9456.623 | 11095.5371 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 |  |  |  | 40.7106 | 675.5647 | 1613.7696 | 2613.3716 | 3665.0394 | 5167.1025 | 6476.1446 | 7710.728 | 8994.0224 | 10533.193 | 11045.5274 | 12705.6856 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633
50% | [5 empty] | 207.7028 | 1260.6583 | 2666.6676 | 4106.7306 | 5533.9289 | 6801.7793 | 8184.2757 | 8709.0464 | 10497.4266 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | [5 empty] | 304.0909 | 1241.702 | 2389.2801 | 4028.3289 | 5456.7534 | 6803.9287 | 8204.2574 | 9883.7977 | 10442.8561 | 12254.418 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048
45% | [6 empty] | 36.3146 | 916.1414 | 2624.9978 | 4361.2249 | 5903.601 | 7585.447 | 8223.8454 | 10399.4608 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | [6 empty] | 32.351 | 656.0457 | 2529.6198 | 4267.3388 | 5906.2158 | 7609.7553 | 9652.9638 | 10333.0742 | 12536.8906 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611
40% | [8 empty] | 409.8056 | 2216.6902 | 4565.0284 | 7145.9569 | 8125.6309 | 11464.2883 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | [8 empty] | 350.4931 | 2085.8253 | 4569.041 | 7183.26 | 10318.7284 | 11362.4128 | 14744.347 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306
35% | [10 empty] | 189.5467 | 1001.8484 | 1459.5503 | 3369.4171 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | [10 empty] | 190.3335 | 1017.8501 | 2700.6042 | 3309.939 | 5284.4155 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398
30% | FY38: 68.1292; FY39: 397.7914; FY40: 397.7914; FY41: 397.7914; FY42: 397.7914; FY43: 397.7914; FY44: 397.7914; FY45: 397.7914; FY46: 397.7914; FY47: 397.7914; FY48: 397.7914; FY49: 397.7914; FY50: 397.7914; FY51: 397.7914; FY52: 397.7914; FY53: 397.7914; FY54: 397.7914 | [12 empty] | 17.757 | 62.3815 | 375.2896 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588
25% | [45 empty] | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 3282.2271 | 2240.4473 | 3957.7482 | 6827.9805 | 10317.1725 | 13976.4402 | 19819.3296 | 27303.0069 | 36185.4651 | 46431.9489 | 56467.1453 | 68035.6344 | 72576.1912 | 88468.2588 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | E @ R (MWh) | 5907.1482 | 4500.4298 | 6944.7067 | 10634.2942 | 14723.9503 | 19726.3308 | 25740.0567 | 35662.5315 | 45844.7143 | 56484.655 | 68207.0991 | 82974.8783 | 87978.4603 | 104360.2754 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854
Option 1 Winter POE50 W E @ R (MWh) N 2 | 2297.559 | 1568.3131 | 2770.4237 | 4779.5863 | 7222.0207 | 9783.5081 | 13873.5307 | 19112.1048 | 25329.8256 | 32502.3642 | 39527.0017 | 47624.9441 | 50803.3338 | 61927.7812 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 1772.1445 | 1350.1289 | 2083.412 | 3190.2883 | 4417.1851 | 5917.8992 | 7722.017 | 10698.7595 | 13753.4143 | 16945.3965 | 20462.1297 | 24892.4635 | 26393.5381 | 31308.0826 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.5712 | 25.2681 | 27.2632 | 28.9314 | 30.4084 | 32.7411 | 34.8492 | 37.7772 | 40.8303 | 43.3239 | 45.6754 | 49.1702 | 51.7085 | 54.2664 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764
98% | 19.902 | 18.5582 | 20.3015 | 21.6795 | 23.3154 | 25.0025 | 26.7951 | 28.8474 | 31.2645 | 33.5296 | 35.9103 | 39.9674 | 41.3418 | 43.9378 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 |  | 52.2693 | 49.6893 | 53.6393 | 56.9422 | 59.8666 | 64.4851 | 68.6588 | 74.456 | 80.5009 | 85.4379 | 90.0937 | 97.0131 | 102.0386 | 107.103 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686
97% | 19.5287 | 18.1985 | 19.9242 | 21.2882 | 22.9075 | 24.5775 | 26.3519 | 28.3833 | 30.7759 | 33.0179 | 35.3745 | 39.3904 | 40.7509 | 43.3205 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 |  | 77.0943 | 73.2635 | 79.1285 | 84.0325 | 88.3745 | 95.232 | 101.429 | 110.0365 | 119.0118 | 126.3421 | 133.2548 | 143.5286 | 150.9903 | 158.5098 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765
95% | 18.9688 | 17.6591 | 19.3582 | 20.7012 | 22.2956 | 23.9399 | 25.687 | 27.6872 | 30.043 | 32.2505 | 34.5708 | 38.5249 | 39.8645 | 42.3945 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 |  | 150.2596 | 142.7159 | 154.2653 | 163.9225 | 172.4729 | 185.977 | 198.1802 | 215.1303 | 232.8048 | 247.2399 | 260.8526 | 281.0841 | 295.7779 | 310.5855 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738
90% | 158.9609 | 147.603 | 162.3376 | 173.9841 | 187.8104 | 202.0693 | 217.2201 | 234.5655 | 254.9946 | 274.138 | 294.2592 | 328.5491 | 340.1654 | 362.106 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 |  | 211.6379 | 200.7348 | 217.4274 | 231.3851 | 243.743 | 263.2606 | 280.8981 | 305.3963 | 330.9416 | 351.8047 | 371.4794 | 400.7202 | 421.9573 | 443.3589 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334
85% | 142.1633 | 131.4193 | 145.3574 | 156.3744 | 169.4533 | 182.9415 | 197.2733 | 213.6811 | 233.0059 | 251.1146 | 270.1482 | 302.5845 | 313.573 | 334.3276 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 |  | 362.6533 | 343.1717 | 372.9978 | 397.9373 | 420.0182 | 454.892 | 486.4063 | 530.1795 | 575.8234 | 613.1014 | 648.2559 | 700.5029 | 738.4491 | 776.6892 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038
80% | 139.2952 | 128.0395 | 142.6414 | 154.183 | 167.8848 | 182.0152 | 197.0295 | 214.2186 | 234.4637 | 253.4347 | 273.3746 | 307.3555 | 318.8672 | 340.6102 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 |  | 268.0967 | 252.9699 | 276.1289 | 295.4937 | 312.6389 | 339.7174 | 364.1873 | 398.1759 | 433.617 | 462.5623 | 489.8587 | 530.427 | 559.8911 | 589.5834 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418
75% | 193.0098 | 176.0923 | 198.0394 | 215.3867 | 235.9809 | 257.2193 | 279.7863 | 305.6221 | 336.051 | 364.5649 | 394.5352 | 445.6097 | 462.9121 | 495.5924 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 |  | 271.4717 | 255.2317 | 280.0951 | 300.8849 | 319.2919 | 348.3632 | 374.634 | 411.1238 | 449.1732 | 480.2486 | 509.5539 | 553.1077 | 584.7402 | 616.6176 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911
70% | 469.0487 | 423.5487 | 482.5757 | 529.2318 | 584.62 | 641.7413 | 702.4354 | 771.9211 | 853.7602 | 930.449 | 1011.0545 | 1148.42 | 1194.9552 | 1282.8494 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 |  | 354.8208 | 332.0323 | 366.9214 | 396.0942 | 421.9233 | 462.7169 | 499.5807 | 550.7843 | 604.1761 | 647.782 | 688.9039 | 750.0197 | 794.4073 | 839.1384 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303
65% | 533.1398 | 474.2012 | 550.662 | 611.0981 | 682.8453 | 756.8374 | 835.4577 | 925.4663 | 1031.4767 | 1130.8157 | 1235.2282 | 1413.165 | 1473.4444 | 1587.2983 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 |  | 378.0426 | 351.5215 | 392.1251 | 426.0763 | 456.136 | 503.6113 | 546.5132 | 606.1035 | 668.2406 | 718.9887 | 766.8461 | 837.9723 | 889.6303 | 941.6881 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425
60% | 1667.6879 | 1447.6916 | 1733.0919 | 1958.678 | 2226.4845 | 2502.6704 | 2796.1316 | 3132.1009 | 3527.7995 | 3898.5961 | 4288.3305 | 4952.5041 | 5177.5054 | 5602.481 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 |  | 843.9098 | 777.607 | 879.116 | 963.9939 | 1039.1433 | 1157.8315 | 1265.0862 | 1414.062 | 1569.4047 | 1696.2751 | 1815.9186 | 1993.734 | 2122.8789 | 2253.0235 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094
55% | 2514.8345 | 2085.7224 | 2642.408 | 3082.4232 | 3604.7912 | 4143.5036 | 4715.9123 | 5371.2346 | 6143.0617 | 6866.3161 | 7626.5097 | 8922.0086 | 9360.8832 | 10189.8163 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 |  | 642.3969 | 583.6576 | 673.587 | 748.7826 | 815.3594 | 920.5083 | 1015.528 | 1147.5095 | 1285.1317 | 1397.5294 | 1503.5247 | 1661.056 | 1775.4688 | 1890.7673 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924
50% | 2944.1269 | 2171.9912 | 3173.6801 | 3965.4346 | 4905.3732 | 5874.7215 | 6904.7022 | 8083.8762 | 9472.6864 | 10774.0959 | 12141.9731 | 14473.068 | 15262.7701 | 16754.3358 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 |  | 1156.1376 | 1024.8091 | 1225.8721 | 1393.9931 | 1542.8446 | 1777.9352 | 1990.3789 | 2285.4613 | 2593.155 | 2844.4523 | 3081.435 | 3433.6413 | 3689.4439 | 3947.2265 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428
45% | 1108.4231 | 443.0694 | 1353.4228 | 2204.0046 | 3213.7805 | 4255.1512 | 5361.6593 | 6628.4458 | 8120.4444 | 9518.5484 | 10988.0587 | 13492.3535 | 14340.7305 | 15943.1192 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 |  | 1939.0178 | 1627.346 | 2104.5134 | 2503.5023 | 2856.7601 | 3414.6827 | 3918.8591 | 4619.1556 | 5349.3816 | 5945.7663 | 6508.1793 | 7344.0436 | 7951.1202 | 8562.8961 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621
40% |  |  | 7.3214 | 300.2304 | 1157.9309 | 2547.9279 | 4191.5383 | 6073.2266 | 8289.4458 | 10366.1936 | 12549.0086 | 16268.8956 | 17529.0771 | 19909.2702 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 |  | 1665.5761 | 1116.1967 | 1957.2926 | 2660.5844 | 3283.2668 | 4266.7086 | 5155.4129 | 6389.8151 | 7676.9738 | 8728.2121 | 9719.5692 | 11192.9347 | 12263.0198 | 13341.388 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006
35% | [5 empty] | 11.585 | 446.2949 | 1644.5809 | 3860.0801 | 6143.4967 | 8543.5357 | 12633.6093 | 14019.1986 | 16636.2579 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 |  | 91.8208 | 1.3905 | 194.4116 | 584.94 | 1085.9465 | 2064.329 | 2960.5014 | 4205.2768 | 5503.2519 | 6563.3242 | 7563.0119 | 9048.7587 | 10127.8361 | 11215.2662 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798
30% | [8 empty] | 9.221 | 171.1327 | 536.9198 | 1523.9285 | 1890.3492 | 2582.4336 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | [6 empty] | 150.8022 | 745.6853 | 2229.0514 | 4368.6458 | 6166.1952 | 7861.3513 | 10380.7107 | 12210.4866 | 14054.4262 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485
25% | [11 empty] | 28.8835 | 106.5455 | 374.8407 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | [9 empty] | 149.9073 | 840.9199 | 1952.4029 | 4324.797 | 6462.3758 | 8651.8252 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509
20% | [43 empty] | 15.4293 | 113.8997 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9929.0896 | 7683.7944 | 10651.1216 | 13414.698 | 17205.4734 | 21631.9035 | 26924.275 | 33683.8576 | 42458.5743 | 51041.6943 | 60258.7914 | 76358.8177 | 81912.9341 | 92524.9915 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | E @ R (MWh) | 8491.7765 | 7157.6056 | 9254.7848 | 11237.4964 | 13148.1944 | 16503.7942 | 20006.7886 | 25529.4948 | 32030.9718 | 37959.506 | 44010.1673 | 53723.2218 | 61207.65 | 68868.2589 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388
Option 1 Summer POE50 W E @ R (MWh) N 2 | 6950.3627 | 5378.6561 | 7455.7851 | 9390.2886 | 12043.8314 | 15142.3325 | 18846.9925 | 23578.7003 | 29721.002 | 35729.186 | 42181.154 | 53451.1724 | 57339.0539 | 64767.494 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 2547.5329 | 2147.2817 | 2776.4354 | 3371.2489 | 3944.4583 | 4951.1383 | 6002.0366 | 7658.8484 | 9609.2915 | 11387.8518 | 13203.0502 | 16116.9665 | 18362.295 | 20660.4777 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 15.9 | 14.2872 | 16.81 | 11.4632 | 14.5895 | 17.3704 | 21.1961 | 25.3794 | 29.6639 | 33.9102 | 37.6824 | 41.7957 | 43.357 | 48.6779 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 | 54.1827 |  | 19.0877 | 17.4876 | 20.1545 | 14.8476 | 17.8944 | 21.1397 | 24.5541 | 29.4307 | 33.6806 | 37.6888 | 41.8551 | 46.8522 | 48.5155 | 53.9054 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288 | 58.9288
98% | 7.7241 | 6.9258 | 8.1744 | 5.5279 | 7.0754 | 8.4518 | 10.3455 | 12.4161 | 14.5368 | 16.6386 | 18.5058 | 20.5417 | 21.3146 | 23.9483 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 | 26.673 |  | 9.3019 | 8.5099 | 9.8299 | 7.2031 | 8.7112 | 10.3176 | 12.0076 | 14.4214 | 16.525 | 18.5089 | 20.5712 | 23.0446 | 23.8679 | 26.5357 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222 | 29.0222
97% | 14.9962 | 13.4158 | 15.8878 | 10.6485 | 13.712 | 16.437 | 20.1858 | 24.285 | 28.4834 | 32.6443 | 36.3407 | 40.3713 | 41.9012 | 47.1152 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 | 52.5093 |  | 18.1198 | 16.5518 | 19.1651 | 13.9649 | 16.9505 | 20.1306 | 23.4763 | 28.2548 | 32.4193 | 36.347 | 40.4296 | 45.3262 | 46.9561 | 52.2376 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16 | 57.16
95% | 21.4775 | 19.1434 | 22.7943 | 15.0563 | 19.5808 | 23.6054 | 29.1422 | 35.1963 | 41.3971 | 47.5424 | 53.0017 | 58.9546 | 61.2142 | 68.9147 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 | 76.8815 |  | 26.0908 | 23.775 | 27.6347 | 19.9543 | 24.3638 | 29.0605 | 34.0019 | 41.0595 | 47.2101 | 53.0109 | 59.0406 | 66.2725 | 68.6798 | 76.4802 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502 | 83.7502
90% | 19.1049 | 16.8559 | 20.3737 | 12.9178 | 17.2774 | 21.1553 | 26.4901 | 32.3235 | 38.2982 | 44.2196 | 49.4798 | 55.2156 | 57.3928 | 64.8127 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 | 72.489 |  | 23.55 | 21.3187 | 25.0376 | 17.6373 | 21.886 | 26.4115 | 31.1727 | 37.973 | 43.8994 | 49.4887 | 55.2985 | 62.2668 | 64.5863 | 72.1023 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073 | 79.1073
85% | 188.5861 | 163.0564 | 202.9891 | 118.3538 | 167.8408 | 211.8604 | 272.4184 | 338.6355 | 406.4564 | 473.6714 | 533.3817 | 598.4915 | 623.2059 | 707.4311 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 | 794.5675 |  | 239.0441 | 213.7155 | 255.9301 | 171.9262 | 220.1553 | 271.5257 | 325.5717 | 402.764 | 470.0367 | 533.483 | 599.4325 | 678.5318 | 704.861 | 790.1779 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938 | 869.6938
80% | 378.0005 | 316.4863 | 412.7049 | 208.7743 | 328.0144 | 434.0807 | 579.9966 | 739.5482 | 902.9642 | 1064.9203 | 1208.7939 | 1365.6773 | 1425.2275 | 1628.1699 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 | 1838.1273 |  | 499.5803 | 438.5505 | 540.2675 | 337.8583 | 454.0674 | 577.8455 | 708.0708 | 894.0673 | 1056.1626 | 1209.0378 | 1367.9448 | 1558.5363 | 1621.9773 | 1827.5504 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458 | 2019.1458
75% | 851.9655 | 672.3262 | 953.3124 | 357.776 | 705.9916 | 1015.736 | 1441.8527 | 1907.7897 | 2385.0118 | 2857.9706 | 3278.1231 | 3736.2682 | 3910.1718 | 4502.8226 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 | 5115.9591 |  | 1207.0139 | 1028.7891 | 1325.8323 | 734.7386 | 1074.1028 | 1435.5708 | 1815.8664 | 2359.0302 | 2832.3954 | 3278.8354 | 3742.8899 | 4299.4723 | 4484.7385 | 5085.0714 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854 | 5644.5854
70% | 1229.6514 | 838.9064 | 1450.0975 | 179.6743 | 912.1342 | 1585.8789 | 2512.7525 | 3526.2417 | 4564.2777 | 5593.0404 | 6506.941 | 7503.4814 | 7881.7502 | 9170.8626 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 | 10504.5348 |  | 2001.9397 | 1614.2716 | 2260.3891 | 974.6636 | 1712.8364 | 2499.0883 | 3326.2934 | 4507.7636 | 5537.4103 | 6508.4904 | 7517.8848 | 8728.5424 | 9131.5267 | 10437.349 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835 | 11654.3835
65% | 545.9482 | 179.044 | 780.2029 |  | 234.4558 | 924.4895 | 1909.4219 | 2986.3954 | 4089.4533 | 5182.6571 | 6153.8038 | 7212.7668 | 7614.7301 | 8984.5917 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 | 10401.8042 |  | 1366.6121 | 954.6607 | 1641.2505 | 287.3232 | 1059.3996 | 1894.9018 | 2773.9224 | 4029.3992 | 5123.5423 | 6155.4502 | 7228.0724 | 8514.5649 | 8942.7919 | 10330.4101 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788 | 11623.6788
60% | 8.8727 |  | 74.4011 |  |  | 145.1705 | 1053.638 | 2158.5699 | 3290.2632 | 4411.8467 | 5408.2044 | 6494.6583 | 6907.0566 | 8312.4799 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 | 9766.4833 |  | 496.8079 | 162.7993 | 778.5049 |  | 231.4204 | 1038.741 | 1940.5811 | 3228.6502 | 4351.1973 | 5409.8936 | 6510.3612 | 7830.2511 | 8269.5949 | 9693.2358 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779 | 11020.0779
55% | [6 empty] | 162.9745 | 1277.8101 | 2597.518 | 3905.4363 | 5067.3245 | 6334.2769 | 6815.1893 | 8454.1033 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 | 10149.6685 |  |  |  | 40.7106 |  |  | 154.35 | 1023.6056 | 2525.6688 | 3834.7109 | 5069.2943 | 6352.5887 | 7891.7592 | 8404.0936 | 10064.2519 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296 | 11611.5296
50% | [7 empty] | 123.363 | 1224.4026 | 2651.6009 | 3919.4513 | 5301.9477 | 5826.7184 | 7615.0986 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | 9465.2964 | [7 empty] | 38.8402 | 1146.0009 | 2574.4254 | 3921.6007 | 5321.9294 | 7001.4697 | 7560.5281 | 9372.09 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768 | 11060.4768
45% | [8 empty] | 28.9307 | 900.9934 | 2397.1672 | 4079.0132 | 4717.4116 | 6893.027 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | 9143.8451 | [8 empty] | 15.7974 | 825.2237 | 2399.782 | 4103.3215 | 6146.53 | 6826.6404 | 9030.4568 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273 | 11084.4273
40% | [10 empty] | 275.5222 | 1834.1797 | 2744.725 | 6083.3825 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | 9537.4447 | [10 empty] | 276.9183 | 1865.8396 | 4937.8225 | 5981.5069 | 9363.4412 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247 | 12515.4247
35% | [12 empty] | 0.31747 | 595.445 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | 2244.4669 | [12 empty] | 269.2695 | 561.619 | 2142.8783 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026 | 3983.1026
30% | FY39: 1.9836; FY40: 1.9836; FY41: 1.9836; FY42: 1.9836; FY43: 1.9836; FY44: 1.9836; FY45: 1.9836; FY46: 1.9836; FY47: 1.9836; FY48: 1.9836; FY49: 1.9836; FY50: 1.9836; FY51: 1.9836; FY52: 1.9836; FY53: 1.9836; FY54: 1.9836 | [14 empty] | 0.60511 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121 | 141.3121
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 3282.2271 | 2240.4473 | 3957.7482 | 920.1921 | 2420.6717 | 4404.2359 | 8040.4144 | 13187.9538 | 19641.6574 | 27217.0922 | 34943.7235 | 44677.6399 | 48691.6836 | 63200.8829 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | 79246.9171 | E @ R (MWh) | 5907.1482 | 4500.4298 | 6944.7067 | 2580.117 | 4841.7879 | 7979.0829 | 12077.9641 | 19260.2809 | 26778.8389 | 34957.8299 | 44827.4597 | 58100.5119 | 62742.4841 | 78418.779 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068 | 93535.8068
Option 2 Winter POE50 W E @ R (MWh) N 2 | 2297.559 | 1568.3131 | 2770.4237 | 644.1345 | 1694.4702 | 3082.9651 | 5628.2901 | 9231.5677 | 13749.1602 | 19051.9645 | 24460.6065 | 31274.3479 | 34084.1786 | 44240.618 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | 55472.8419 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 1772.1445 | 1350.1289 | 2083.412 | 774.0351 | 1452.5364 | 2393.7249 | 3623.3892 | 5778.0843 | 8033.6517 | 10487.349 | 13448.2379 | 17430.1536 | 18822.7452 | 23525.6337 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742 | 28060.742
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.5712 | 25.2681 | 27.2632 | 23.4754 | 24.9524 | 27.2852 | 29.3932 | 32.3212 | 35.3744 | 37.8679 | 40.2194 | 43.7143 | 46.2525 | 48.8104 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205 | 51.5205
98% | 19.902 | 18.5582 | 20.3015 | 16.2784 | 17.9143 | 19.6014 | 21.394 | 23.4463 | 25.8634 | 28.1284 | 30.5091 | 34.5663 | 35.9407 | 38.5367 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 | 40.5212 |  | 52.2693 | 49.6893 | 53.6393 | 46.14 | 49.0643 | 53.6829 | 57.8565 | 63.6537 | 69.6987 | 74.6357 | 79.2914 | 86.2108 | 91.2363 | 96.3007 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664 | 101.6664
97% | 19.5287 | 18.1985 | 19.9242 | 15.9419 | 17.5612 | 19.2312 | 21.0056 | 23.037 | 25.4296 | 27.6716 | 30.0282 | 34.0441 | 35.4046 | 37.9742 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 | 39.9385 |  | 77.0943 | 73.2635 | 79.1285 | 67.9936 | 72.3356 | 79.1931 | 85.3901 | 93.9976 | 102.9729 | 110.3032 | 117.2159 | 127.4897 | 134.9514 | 142.4709 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376 | 150.4376
95% | 18.9688 | 17.6591 | 19.3582 | 15.4372 | 17.0315 | 18.6758 | 20.4229 | 22.4231 | 24.7789 | 26.9864 | 29.3067 | 33.2609 | 34.6004 | 37.1305 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 | 39.0646 |  | 150.2596 | 142.7159 | 154.2653 | 132.3383 | 140.8886 | 154.3927 | 166.5959 | 183.546 | 201.2206 | 215.6556 | 229.2684 | 249.4998 | 264.1936 | 279.0012 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895 | 294.6895
90% | 158.9609 | 147.603 | 162.3376 | 128.335 | 142.1612 | 156.4201 | 171.5709 | 188.9163 | 209.3454 | 228.4889 | 248.61 | 282.8999 | 294.5163 | 316.4569 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 | 333.2293 |  | 211.6379 | 200.7348 | 217.4274 | 185.736 | 198.0939 | 217.6115 | 235.2489 | 259.7471 | 285.2924 | 306.1555 | 325.8302 | 355.071 | 376.3082 | 397.7097 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843 | 420.3843
85% | 142.1633 | 131.4193 | 145.3574 | 113.1928 | 126.2717 | 139.7599 | 154.0917 | 170.4995 | 189.8243 | 207.933 | 226.9665 | 259.4029 | 270.3913 | 291.146 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 | 307.0118 |  | 362.6533 | 343.1717 | 372.9978 | 316.3719 | 338.4529 | 373.3267 | 404.841 | 448.6142 | 494.2581 | 531.536 | 566.6906 | 618.9376 | 656.8838 | 695.1238 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385 | 735.6385
80% | 139.2952 | 128.0395 | 142.6414 | 108.9451 | 122.6469 | 136.7773 | 151.7916 | 168.9807 | 189.2258 | 208.1968 | 228.1367 | 262.1176 | 273.6293 | 295.3723 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 | 311.9936 |  | 268.0967 | 252.9699 | 276.1289 | 232.1606 | 249.3058 | 276.3843 | 300.8543 | 334.8428 | 370.284 | 399.2292 | 426.5256 | 467.0939 | 496.5581 | 526.2503 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087 | 557.7087
75% | 193.0098 | 176.0923 | 198.0394 | 147.3928 | 167.9869 | 189.2254 | 211.7923 | 237.6281 | 268.057 | 296.571 | 326.5413 | 377.6157 | 394.9181 | 427.5984 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 | 452.5808 |  | 271.4717 | 255.2317 | 280.0951 | 232.891 | 251.298 | 280.3692 | 306.64 | 343.1299 | 381.1793 | 412.2547 | 441.5599 | 485.1138 | 516.7463 | 548.6237 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972 | 582.3972
70% | 469.0487 | 423.5487 | 482.5757 | 346.361 | 401.7492 | 458.8705 | 519.5646 | 589.0504 | 670.8894 | 747.5782 | 828.1837 | 965.5492 | 1012.0844 | 1099.9786 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 | 1167.1691 |  | 354.8208 | 332.0323 | 366.9214 | 300.6834 | 326.5125 | 367.3061 | 404.1699 | 455.3734 | 508.7653 | 552.3711 | 593.493 | 654.6088 | 698.9964 | 743.7276 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195 | 791.1195
65% | 533.1398 | 474.2012 | 550.662 | 374.216 | 445.9632 | 519.9553 | 598.5756 | 688.5841 | 794.5946 | 893.9335 | 998.3461 | 1176.2829 | 1236.5623 | 1350.4162 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 | 1437.4517 |  | 378.0426 | 351.5215 | 392.1251 | 315.0378 | 345.0975 | 392.5728 | 435.4747 | 495.065 | 557.2021 | 607.9503 | 655.8076 | 726.9338 | 778.5918 | 830.6496 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804 | 885.804
60% | 1667.6879 | 1447.6916 | 1733.0919 | 1074.4826 | 1342.2891 | 1618.475 | 1911.9363 | 2247.9055 | 2643.6042 | 3014.4007 | 3404.1351 | 4068.3087 | 4293.31 | 4718.2856 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 | 5043.1575 |  | 843.9098 | 777.607 | 879.116 | 686.3977 | 761.5471 | 880.2353 | 987.49 | 1136.4657 | 1291.8085 | 1418.6789 | 1538.3223 | 1716.1378 | 1845.2827 | 1975.4273 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132 | 2113.3132
55% | 2514.8345 | 2085.7224 | 2642.408 | 1357.7624 | 1880.1304 | 2418.8428 | 2991.2515 | 3646.5739 | 4418.4009 | 5141.6553 | 5901.849 | 7197.3479 | 7636.2225 | 8465.1556 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 | 9098.832 |  | 642.3969 | 583.6576 | 673.587 | 502.8529 | 569.4297 | 674.5786 | 769.5983 | 901.5798 | 1039.202 | 1151.5998 | 1257.595 | 1415.1263 | 1529.5391 | 1644.8376 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943 | 1766.9943
50% | 2944.1269 | 2171.9912 | 3173.6801 | 862.6661 | 1802.0531 | 2771.4014 | 3801.3821 | 4980.5561 | 6369.3663 | 7670.7758 | 9038.653 | 11369.7479 | 12159.45 | 13651.0157 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 | 14791.2404 |  | 1156.1376 | 1024.8091 | 1225.8721 | 844.147 | 992.9985 | 1228.0891 | 1440.5328 | 1735.6152 | 2043.3089 | 2294.6062 | 2531.5889 | 2883.7952 | 3139.5977 | 3397.3804 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967 | 3670.4967
45% | 1108.4231 | 443.0694 | 1353.4228 |  | 225.6149 | 935.9038 | 2027.763 | 3294.5494 | 4786.548 | 6184.6521 | 7654.1624 | 10158.4572 | 11006.8341 | 12609.2229 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 | 13834.1662 |  | 1939.0178 | 1627.346 | 2104.5134 | 1198.5944 | 1551.8523 | 2109.7748 | 2613.9512 | 3314.2477 | 4044.4738 | 4640.8584 | 5203.2714 | 6039.1357 | 6646.2124 | 7257.9882 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542 | 7906.1542
40% |  |  | 7.3214 |  |  |  | 205.6556 | 1248.5822 | 3337.2663 | 5414.0141 | 7596.8291 | 11316.7161 | 12576.8977 | 14957.0907 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 | 16776.6251 |  | 1665.5761 | 1116.1967 | 1957.2926 | 462.7946 | 983.8263 | 1966.5669 | 2855.2712 | 4089.6734 | 5376.8321 | 6428.0704 | 7419.4275 | 8892.793 | 9962.8781 | 11041.2463 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589 | 12183.7589
35% | [8 empty] | 144.1613 | 1145.5848 | 3099.1108 | 7188.6109 | 8574.2002 | 11191.2595 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 | 13191.8659 |  | 91.8208 | 1.3905 | 194.4116 |  |  | 198.2657 | 726.6385 | 1885.8061 | 3183.7812 | 4243.8535 | 5243.5413 | 6729.2881 | 7808.3654 | 8895.7956 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091 | 10047.9091
30% | [11 empty] | 307.3572 | 542.7755 | 1142.4974 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | 1671.5601 | [8 empty] | 84.8492 | 958.3616 | 2286.0855 | 3928.2584 | 6447.6178 | 8277.3937 | 10121.3333 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556 | 12074.9556
25% | FY38: 0.0092082; FY39: 54.4925; FY40: 54.4925; FY41: 54.4925; FY42: 54.4925; FY43: 54.4925; FY44: 54.4925; FY45: 54.4925; FY46: 54.4925; FY47: 54.4925; FY48: 54.4925; FY49: 54.4925; FY50: 54.4925; FY51: 54.4925; FY52: 54.4925; FY53: 54.4925; FY54: 54.4925 | [11 empty] | 64.4735 | 996.0149 | 2287.5514 | 4044.0963 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496 | 6301.4496
20% | [45 empty] | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135 | 11.7135
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9929.0896 | 7683.7944 | 10651.1216 | 4561.0113 | 6709.3737 | 9403.1399 | 12808.1978 | 17530.7326 | 24097.3555 | 31236.5706 | 39641.3677 | 55032.2854 | 60377.7374 | 70629.1464 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | 78590.9004 | E @ R (MWh) | 8491.7765 | 7157.6056 | 9254.7848 | 5547.6145 | 6855.6552 | 9279.6348 | 11819.9465 | 15858.5282 | 20944.0158 | 25711.7118 | 30662.3805 | 38934.5823 | 45557.539 | 52686.773 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112 | 60648.1112
Option 2 Summer POE50 W E @ R (MWh) N 2 | 6950.3627 | 5378.6561 | 7455.7851 | 3192.7079 | 4696.5616 | 6582.1979 | 8965.7384 | 12271.5129 | 16868.1488 | 21865.5994 | 27748.9574 | 38522.5998 | 42264.4161 | 49440.4025 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | 55013.6303 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 2547.5329 | 2147.2817 | 2776.4354 | 1664.2843 | 2056.6966 | 2783.8905 | 3545.984 | 4757.5584 | 6283.2047 | 7713.5136 | 9198.7141 | 11680.3747 | 13667.2617 | 15806.0319 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333 | 18194.4333
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 15.9 | 14.2872 | 16.81 | 20.0388 | 23.1651 | 25.9461 | 29.7718 | 33.955 | 38.2396 | 42.4859 | 46.258 | 50.3713 | 51.9326 | 57.2535 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 |  | 19.0877 | 17.4876 | 20.1545 | 23.4232 | 26.4701 | 29.7154 | 33.1297 | 38.0063 | 42.2562 | 46.2644 | 50.4308 | 55.4278 | 57.0912 | 62.481 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044
98% | 7.7241 | 6.9258 | 8.1744 | 9.7727 | 11.3201 | 12.6966 | 14.5902 | 16.6608 | 18.7816 | 20.8834 | 22.7505 | 24.7865 | 25.5593 | 28.193 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 |  | 9.3019 | 8.5099 | 9.8299 | 11.4479 | 12.956 | 14.5623 | 16.2523 | 18.6661 | 20.7697 | 22.7537 | 24.8159 | 27.2893 | 28.1126 | 30.7805 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669
97% | 14.9962 | 13.4158 | 15.8878 | 19.0518 | 22.1153 | 24.8403 | 28.5891 | 32.6883 | 36.8867 | 41.0476 | 44.744 | 48.7746 | 50.3045 | 55.5185 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 |  | 18.1198 | 16.5518 | 19.1651 | 22.3682 | 25.3538 | 28.5339 | 31.8796 | 36.6581 | 40.8226 | 44.7503 | 48.8328 | 53.7295 | 55.3594 | 60.6409 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633
95% | 21.4775 | 19.1434 | 22.7943 | 27.4673 | 31.9918 | 36.0164 | 41.5532 | 47.6073 | 53.8081 | 59.9534 | 65.4127 | 71.3656 | 73.6252 | 81.3258 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 |  | 26.0908 | 23.775 | 27.6347 | 32.3653 | 36.7748 | 41.4715 | 46.4129 | 53.4705 | 59.6211 | 65.4219 | 71.4516 | 78.6835 | 81.0908 | 88.8912 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612
90% | 19.1049 | 16.8559 | 20.3737 | 24.8763 | 29.2359 | 33.1138 | 38.4487 | 44.2821 | 50.2568 | 56.1781 | 61.4383 | 67.1741 | 69.3514 | 76.7712 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 |  | 23.55 | 21.3187 | 25.0376 | 29.5958 | 33.8445 | 38.37 | 43.1312 | 49.9315 | 55.8579 | 61.4472 | 67.257 | 74.2253 | 76.5448 | 84.0608 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658
85% | 188.5861 | 163.0564 | 202.9891 | 254.0993 | 303.5863 | 347.6059 | 408.1639 | 474.3809 | 542.2018 | 609.4168 | 669.1272 | 734.2369 | 758.9514 | 843.1765 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 |  | 239.0441 | 213.7155 | 255.9301 | 307.6717 | 355.9007 | 407.2711 | 461.3172 | 538.5094 | 605.7822 | 669.2284 | 735.178 | 814.2772 | 840.6065 | 925.9234 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392
80% | 378.0005 | 316.4863 | 412.7049 | 535.8562 | 655.0962 | 761.1625 | 907.0785 | 1066.6301 | 1230.0461 | 1392.0022 | 1535.8758 | 1692.7592 | 1752.3093 | 1955.2518 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 |  | 499.5803 | 438.5505 | 540.2675 | 664.9401 | 781.1492 | 904.9273 | 1035.1526 | 1221.1492 | 1383.2444 | 1536.1197 | 1695.0267 | 1885.6182 | 1949.0592 | 2154.6323 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276
75% | 851.9655 | 672.3262 | 953.3124 | 1312.9498 | 1661.1654 | 1970.9098 | 2397.0265 | 2862.9635 | 3340.1856 | 3813.1444 | 4233.297 | 4691.442 | 4865.3456 | 5457.9964 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 |  | 1207.0139 | 1028.7891 | 1325.8323 | 1689.9124 | 2029.2767 | 2390.7446 | 2771.0402 | 3314.204 | 3787.5692 | 4234.0092 | 4698.0637 | 5254.6461 | 5439.9123 | 6040.2452 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592
70% | 1229.6514 | 838.9064 | 1450.0975 | 2232.3676 | 2989.7935 | 3663.5381 | 4590.4118 | 5603.901 | 6641.937 | 7670.6997 | 8584.6003 | 9581.1407 | 9959.4095 | 11248.5219 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 |  | 2001.9397 | 1614.2716 | 2260.3891 | 3052.3229 | 3790.4957 | 4576.7476 | 5403.9526 | 6585.4229 | 7615.0695 | 8586.1496 | 9595.544 | 10806.2017 | 11209.186 | 12515.0083 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428
65% | 545.9482 | 179.044 | 780.2029 | 1611.4739 | 2416.3444 | 3132.292 | 4117.2244 | 5194.1979 | 6297.2558 | 7390.4596 | 8361.6063 | 9420.5693 | 9822.5326 | 11192.3942 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 |  | 1366.6121 | 954.6607 | 1641.2505 | 2482.7906 | 3267.202 | 4102.7043 | 4981.7249 | 6237.2017 | 7331.3448 | 8363.2527 | 9435.8749 | 10722.3674 | 11150.5944 | 12538.2125 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813
60% | 8.8727 |  | 74.4011 | 747.9553 | 1573.7203 | 2308.2539 | 3318.7553 | 4423.6871 | 5555.3805 | 6676.9639 | 7673.3217 | 8759.7755 | 9172.1738 | 10577.5971 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 |  | 496.8079 | 162.7993 | 778.5049 | 1641.8914 | 2446.6663 | 3303.8582 | 4205.6983 | 5493.7674 | 6616.3145 | 7675.0108 | 8775.4784 | 10095.3683 | 10534.7121 | 11958.353 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951
55% |  |  |  | 32.0716 | 599.6383 | 1452.362 | 2630.7435 | 3919.2438 | 5238.9517 | 6546.87 | 7708.7583 | 8975.7107 | 9456.623 | 11095.5371 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 |  |  |  | 40.7106 | 675.5647 | 1613.7696 | 2613.3716 | 3665.0394 | 5167.1025 | 6476.1446 | 7710.728 | 8994.0224 | 10533.193 | 11045.5274 | 12705.6856 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633
50% | [5 empty] | 207.7028 | 1260.6583 | 2666.6676 | 4106.7306 | 5533.9289 | 6801.7793 | 8184.2757 | 8709.0464 | 10497.4266 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | [5 empty] | 304.0909 | 1241.702 | 2389.2801 | 4028.3289 | 5456.7534 | 6803.9287 | 8204.2574 | 9883.7977 | 10442.8561 | 12254.418 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048
45% | [6 empty] | 36.3146 | 916.1414 | 2624.9978 | 4361.2249 | 5903.601 | 7585.447 | 8223.8454 | 10399.4608 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | [6 empty] | 32.351 | 656.0457 | 2529.6198 | 4267.3388 | 5906.2158 | 7609.7553 | 9652.9638 | 10333.0742 | 12536.8906 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611
40% | [8 empty] | 409.8056 | 2216.6902 | 4565.0284 | 7145.9569 | 8125.6309 | 11464.2883 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | [8 empty] | 350.4931 | 2085.8253 | 4569.041 | 7183.26 | 10318.7284 | 11362.4128 | 14744.347 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306
35% | [10 empty] | 189.5467 | 1001.8484 | 1459.5503 | 3369.4171 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | [10 empty] | 190.3335 | 1017.8501 | 2700.6042 | 3309.939 | 5284.4155 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398
30% | FY38: 68.1292; FY39: 397.7914; FY40: 397.7914; FY41: 397.7914; FY42: 397.7914; FY43: 397.7914; FY44: 397.7914; FY45: 397.7914; FY46: 397.7914; FY47: 397.7914; FY48: 397.7914; FY49: 397.7914; FY50: 397.7914; FY51: 397.7914; FY52: 397.7914; FY53: 397.7914; FY54: 397.7914 | [12 empty] | 17.757 | 62.3815 | 375.2896 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588
25% | [45 empty] | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 3282.2271 | 2240.4473 | 3957.7482 | 6827.9805 | 10317.1725 | 13976.4402 | 19819.3296 | 27303.0069 | 36185.4651 | 46431.9489 | 56467.1453 | 68035.6344 | 72576.1912 | 88468.2588 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | E @ R (MWh) | 5907.1482 | 4500.4298 | 6944.7067 | 10634.2942 | 14723.9503 | 19726.3308 | 25740.0567 | 35662.5315 | 45844.7143 | 56484.655 | 68207.0991 | 82974.8783 | 87978.4603 | 104360.2754 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854
Option 3 Winter POE50 W E @ R (MWh) N 2 | 2297.559 | 1568.3131 | 2770.4237 | 4779.5863 | 7222.0207 | 9783.5081 | 13873.5307 | 19112.1048 | 25329.8256 | 32502.3642 | 39527.0017 | 47624.9441 | 50803.3338 | 61927.7812 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 1772.1445 | 1350.1289 | 2083.412 | 3190.2883 | 4417.1851 | 5917.8992 | 7722.017 | 10698.7595 | 13753.4143 | 16945.3965 | 20462.1297 | 24892.4635 | 26393.5381 | 31308.0826 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.5712 | 25.2681 | 27.2632 | 28.9314 | 30.4084 | 32.7411 | 34.8492 | 37.7772 | 40.8303 | 43.3239 | 45.6754 | 49.1702 | 51.7085 | 54.2664 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764
98% | 19.902 | 18.5582 | 20.3015 | 21.6795 | 23.3154 | 25.0025 | 26.7951 | 28.8474 | 31.2645 | 33.5296 | 35.9103 | 39.9674 | 41.3418 | 43.9378 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 |  | 52.2693 | 49.6893 | 53.6393 | 56.9422 | 59.8666 | 64.4851 | 68.6588 | 74.456 | 80.5009 | 85.4379 | 90.0937 | 97.0131 | 102.0386 | 107.103 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686
97% | 19.5287 | 18.1985 | 19.9242 | 21.2882 | 22.9075 | 24.5775 | 26.3519 | 28.3833 | 30.7759 | 33.0179 | 35.3745 | 39.3904 | 40.7509 | 43.3205 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 |  | 77.0943 | 73.2635 | 79.1285 | 84.0325 | 88.3745 | 95.232 | 101.429 | 110.0365 | 119.0118 | 126.3421 | 133.2548 | 143.5286 | 150.9903 | 158.5098 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765
95% | 18.9688 | 17.6591 | 19.3582 | 20.7012 | 22.2956 | 23.9399 | 25.687 | 27.6872 | 30.043 | 32.2505 | 34.5708 | 38.5249 | 39.8645 | 42.3945 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 |  | 150.2596 | 142.7159 | 154.2653 | 163.9225 | 172.4729 | 185.977 | 198.1802 | 215.1303 | 232.8048 | 247.2399 | 260.8526 | 281.0841 | 295.7779 | 310.5855 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738
90% | 158.9609 | 147.603 | 162.3376 | 173.9841 | 187.8104 | 202.0693 | 217.2201 | 234.5655 | 254.9946 | 274.138 | 294.2592 | 328.5491 | 340.1654 | 362.106 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 |  | 211.6379 | 200.7348 | 217.4274 | 231.3851 | 243.743 | 263.2606 | 280.8981 | 305.3963 | 330.9416 | 351.8047 | 371.4794 | 400.7202 | 421.9573 | 443.3589 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334
85% | 142.1633 | 131.4193 | 145.3574 | 156.3744 | 169.4533 | 182.9415 | 197.2733 | 213.6811 | 233.0059 | 251.1146 | 270.1482 | 302.5845 | 313.573 | 334.3276 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 |  | 362.6533 | 343.1717 | 372.9978 | 397.9373 | 420.0182 | 454.892 | 486.4063 | 530.1795 | 575.8234 | 613.1014 | 648.2559 | 700.5029 | 738.4491 | 776.6892 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038
80% | 139.2952 | 128.0395 | 142.6414 | 154.183 | 167.8848 | 182.0152 | 197.0295 | 214.2186 | 234.4637 | 253.4347 | 273.3746 | 307.3555 | 318.8672 | 340.6102 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 |  | 268.0967 | 252.9699 | 276.1289 | 295.4937 | 312.6389 | 339.7174 | 364.1873 | 398.1759 | 433.617 | 462.5623 | 489.8587 | 530.427 | 559.8911 | 589.5834 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418
75% | 193.0098 | 176.0923 | 198.0394 | 215.3867 | 235.9809 | 257.2193 | 279.7863 | 305.6221 | 336.051 | 364.5649 | 394.5352 | 445.6097 | 462.9121 | 495.5924 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 |  | 271.4717 | 255.2317 | 280.0951 | 300.8849 | 319.2919 | 348.3632 | 374.634 | 411.1238 | 449.1732 | 480.2486 | 509.5539 | 553.1077 | 584.7402 | 616.6176 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911
70% | 469.0487 | 423.5487 | 482.5757 | 529.2318 | 584.62 | 641.7413 | 702.4354 | 771.9211 | 853.7602 | 930.449 | 1011.0545 | 1148.42 | 1194.9552 | 1282.8494 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 |  | 354.8208 | 332.0323 | 366.9214 | 396.0942 | 421.9233 | 462.7169 | 499.5807 | 550.7843 | 604.1761 | 647.782 | 688.9039 | 750.0197 | 794.4073 | 839.1384 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303
65% | 533.1398 | 474.2012 | 550.662 | 611.0981 | 682.8453 | 756.8374 | 835.4577 | 925.4663 | 1031.4767 | 1130.8157 | 1235.2282 | 1413.165 | 1473.4444 | 1587.2983 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 |  | 378.0426 | 351.5215 | 392.1251 | 426.0763 | 456.136 | 503.6113 | 546.5132 | 606.1035 | 668.2406 | 718.9887 | 766.8461 | 837.9723 | 889.6303 | 941.6881 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425
60% | 1667.6879 | 1447.6916 | 1733.0919 | 1958.678 | 2226.4845 | 2502.6704 | 2796.1316 | 3132.1009 | 3527.7995 | 3898.5961 | 4288.3305 | 4952.5041 | 5177.5054 | 5602.481 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 |  | 843.9098 | 777.607 | 879.116 | 963.9939 | 1039.1433 | 1157.8315 | 1265.0862 | 1414.062 | 1569.4047 | 1696.2751 | 1815.9186 | 1993.734 | 2122.8789 | 2253.0235 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094
55% | 2514.8345 | 2085.7224 | 2642.408 | 3082.4232 | 3604.7912 | 4143.5036 | 4715.9123 | 5371.2346 | 6143.0617 | 6866.3161 | 7626.5097 | 8922.0086 | 9360.8832 | 10189.8163 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 |  | 642.3969 | 583.6576 | 673.587 | 748.7826 | 815.3594 | 920.5083 | 1015.528 | 1147.5095 | 1285.1317 | 1397.5294 | 1503.5247 | 1661.056 | 1775.4688 | 1890.7673 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924
50% | 2944.1269 | 2171.9912 | 3173.6801 | 3965.4346 | 4905.3732 | 5874.7215 | 6904.7022 | 8083.8762 | 9472.6864 | 10774.0959 | 12141.9731 | 14473.068 | 15262.7701 | 16754.3358 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 |  | 1156.1376 | 1024.8091 | 1225.8721 | 1393.9931 | 1542.8446 | 1777.9352 | 1990.3789 | 2285.4613 | 2593.155 | 2844.4523 | 3081.435 | 3433.6413 | 3689.4439 | 3947.2265 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428
45% | 1108.4231 | 443.0694 | 1353.4228 | 2204.0046 | 3213.7805 | 4255.1512 | 5361.6593 | 6628.4458 | 8120.4444 | 9518.5484 | 10988.0587 | 13492.3535 | 14340.7305 | 15943.1192 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 |  | 1939.0178 | 1627.346 | 2104.5134 | 2503.5023 | 2856.7601 | 3414.6827 | 3918.8591 | 4619.1556 | 5349.3816 | 5945.7663 | 6508.1793 | 7344.0436 | 7951.1202 | 8562.8961 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621
40% |  |  | 7.3214 | 300.2304 | 1157.9309 | 2547.9279 | 4191.5383 | 6073.2266 | 8289.4458 | 10366.1936 | 12549.0086 | 16268.8956 | 17529.0771 | 19909.2702 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 |  | 1665.5761 | 1116.1967 | 1957.2926 | 2660.5844 | 3283.2668 | 4266.7086 | 5155.4129 | 6389.8151 | 7676.9738 | 8728.2121 | 9719.5692 | 11192.9347 | 12263.0198 | 13341.388 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006
35% | [5 empty] | 11.585 | 446.2949 | 1644.5809 | 3860.0801 | 6143.4967 | 8543.5357 | 12633.6093 | 14019.1986 | 16636.2579 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 |  | 91.8208 | 1.3905 | 194.4116 | 584.94 | 1085.9465 | 2064.329 | 2960.5014 | 4205.2768 | 5503.2519 | 6563.3242 | 7563.0119 | 9048.7587 | 10127.8361 | 11215.2662 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798
30% | [8 empty] | 9.221 | 171.1327 | 536.9198 | 1523.9285 | 1890.3492 | 2582.4336 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | [6 empty] | 150.8022 | 745.6853 | 2229.0514 | 4368.6458 | 6166.1952 | 7861.3513 | 10380.7107 | 12210.4866 | 14054.4262 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485
25% | [11 empty] | 28.8835 | 106.5455 | 374.8407 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | [9 empty] | 149.9073 | 840.9199 | 1952.4029 | 4324.797 | 6462.3758 | 8651.8252 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509
20% | [43 empty] | 15.4293 | 113.8997 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9929.0896 | 7683.7944 | 10651.1216 | 13414.698 | 17205.4734 | 21631.9035 | 26924.275 | 33683.8576 | 42458.5743 | 51041.6943 | 60258.7914 | 76358.8177 | 81912.9341 | 92524.9915 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | E @ R (MWh) | 8491.7765 | 7157.6056 | 9254.7848 | 11237.4964 | 13148.1944 | 16503.7942 | 20006.7886 | 25529.4948 | 32030.9718 | 37959.506 | 44010.1673 | 53723.2218 | 61207.65 | 68868.2589 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388
Option 3 Summer POE50 W E @ R (MWh) N 2 | 6950.3627 | 5378.6561 | 7455.7851 | 9390.2886 | 12043.8314 | 15142.3325 | 18846.9925 | 23578.7003 | 29721.002 | 35729.186 | 42181.154 | 53451.1724 | 57339.0539 | 64767.494 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 2547.5329 | 2147.2817 | 2776.4354 | 3371.2489 | 3944.4583 | 4951.1383 | 6002.0366 | 7658.8484 | 9609.2915 | 11387.8518 | 13203.0502 | 16116.9665 | 18362.295 | 20660.4777 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 15.9 | 14.2872 | 16.81 | 8.6046 | 11.7309 | 14.5118 | 18.3376 | 22.5208 | 26.8054 | 31.0516 | 34.8238 | 38.9371 | 40.4984 | 45.8193 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 | 51.3241 |  | 19.0877 | 17.4876 | 20.1545 | 11.989 | 15.0359 | 18.2812 | 21.6955 | 26.5721 | 30.822 | 34.8302 | 38.9966 | 43.9936 | 45.657 | 51.0468 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702 | 56.0702
98% | 7.7241 | 6.9258 | 8.1744 | 4.113 | 5.6605 | 7.0369 | 8.9306 | 11.0012 | 13.1219 | 15.2237 | 17.0909 | 19.1268 | 19.8996 | 22.5334 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 | 25.2581 |  | 9.3019 | 8.5099 | 9.8299 | 5.7882 | 7.2963 | 8.9027 | 10.5927 | 13.0065 | 15.1101 | 17.094 | 19.1563 | 21.6297 | 22.453 | 25.1208 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073 | 27.6073
97% | 14.9962 | 13.4158 | 15.8878 | 7.8474 | 10.9109 | 13.6359 | 17.3847 | 21.4839 | 25.6823 | 29.8432 | 33.5396 | 37.5702 | 39.1001 | 44.3141 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 | 49.7082 |  | 18.1198 | 16.5518 | 19.1651 | 11.1638 | 14.1494 | 17.3295 | 20.6752 | 25.4537 | 29.6182 | 33.5459 | 37.6285 | 42.5251 | 44.155 | 49.4365 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589 | 54.3589
95% | 21.4775 | 19.1434 | 22.7943 | 10.9193 | 15.4438 | 19.4684 | 25.0052 | 31.0593 | 37.2601 | 43.4054 | 48.8647 | 54.8176 | 57.0772 | 64.7777 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 | 72.7445 |  | 26.0908 | 23.775 | 27.6347 | 15.8173 | 20.2268 | 24.9235 | 29.8649 | 36.9225 | 43.0731 | 48.8739 | 54.9036 | 62.1355 | 64.5428 | 72.3432 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132 | 79.6132
90% | 19.1049 | 16.8559 | 20.3737 | 8.9316 | 13.2912 | 17.1691 | 22.504 | 28.3374 | 34.3121 | 40.2334 | 45.4936 | 51.2294 | 53.4067 | 60.8265 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 | 68.5028 |  | 23.55 | 21.3187 | 25.0376 | 13.6511 | 17.8998 | 22.4253 | 27.1865 | 33.9868 | 39.9132 | 45.5025 | 51.3123 | 58.2806 | 60.6001 | 68.1161 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211 | 75.1211
85% | 188.5861 | 163.0564 | 202.9891 | 73.1054 | 122.5924 | 166.612 | 227.17 | 293.387 | 361.2079 | 428.4229 | 488.1333 | 553.243 | 577.9575 | 662.1826 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 | 749.3191 |  | 239.0441 | 213.7155 | 255.9301 | 126.6778 | 174.9068 | 226.2772 | 280.3233 | 357.5155 | 424.7883 | 488.2345 | 554.184 | 633.2833 | 659.6126 | 744.9294 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453 | 824.4453
80% | 378.0005 | 316.4863 | 412.7049 | 99.747 | 218.9871 | 325.0534 | 470.9693 | 630.5209 | 793.9369 | 955.893 | 1099.7666 | 1256.6501 | 1316.2002 | 1519.1426 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 | 1729.1 |  | 499.5803 | 438.5505 | 540.2675 | 228.831 | 345.0401 | 468.8182 | 599.0435 | 785.04 | 947.1353 | 1100.0105 | 1258.9175 | 1449.509 | 1512.9501 | 1718.5231 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185 | 1910.1185
75% | 851.9655 | 672.3262 | 953.3124 | 56.3948 | 387.6003 | 697.3447 | 1123.4614 | 1589.3984 | 2066.6205 | 2539.5793 | 2959.7319 | 3417.8769 | 3591.7805 | 4184.4313 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 | 4797.5678 |  | 1207.0139 | 1028.7891 | 1325.8323 | 416.3473 | 755.7116 | 1117.1795 | 1497.4751 | 2040.639 | 2514.0041 | 2960.4442 | 3424.4987 | 3981.081 | 4166.3472 | 4766.6802 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942 | 5326.1942
70% | 1229.6514 | 838.9064 | 1450.0975 |  | 230.3644 | 893.3258 | 1820.1994 | 2833.6886 | 3871.7246 | 4900.4873 | 5814.3879 | 6810.9283 | 7189.1971 | 8478.3095 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 | 9811.9817 |  | 2001.9397 | 1614.2716 | 2260.3891 | 284.8116 | 1020.2833 | 1806.5352 | 2633.7403 | 3815.2105 | 4844.8572 | 5815.9373 | 6825.3317 | 8035.9893 | 8438.9736 | 9744.796 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304 | 10961.8304
65% | 545.9482 | 179.044 | 780.2029 |  |  | 219.5489 | 1173.4877 | 2250.4612 | 3353.5191 | 4446.7229 | 5417.8696 | 6476.8327 | 6878.796 | 8248.6575 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 | 9665.8701 |  | 1366.6121 | 954.6607 | 1641.2505 |  | 329.0653 | 1158.9676 | 2037.9883 | 3293.4651 | 4387.6081 | 5419.516 | 6492.1382 | 7778.6307 | 8206.8577 | 9594.4759 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446 | 10887.7446
60% | 8.8727 |  | 74.4011 |  |  |  | 319.0145 | 1403.5308 | 2535.2242 | 3656.8076 | 4653.1654 | 5739.6192 | 6152.0175 | 7557.4408 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 | 9011.4443 |  | 496.8079 | 162.7993 | 778.5049 |  |  | 307.1348 | 1185.542 | 2473.6111 | 3596.1582 | 4654.8545 | 5755.3221 | 7075.212 | 7514.5558 | 8938.1967 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388 | 10265.0388
55% | [7 empty] | 428.5083 | 1717.0401 | 3024.9584 | 4186.8466 | 5453.799 | 5934.7113 | 7573.6254 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 | 9269.1906 |  |  |  | 40.7106 |  |  |  | 249.0466 | 1645.1909 | 2954.2329 | 4188.8164 | 5472.1107 | 7011.2813 | 7523.6157 | 9183.774 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517 | 10731.0517
50% | [8 empty] | 374.799 | 1690.8248 | 2958.6753 | 4341.1717 | 4865.9424 | 6654.3226 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | 8504.5204 | [8 empty] | 324.8666 | 1613.6494 | 2960.8247 | 4361.1534 | 6040.6937 | 6599.7521 | 8411.314 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008 | 10099.7008
45% | [9 empty] | 185.4794 | 1232.2616 | 2910.2019 | 3548.6004 | 5724.2157 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | 7975.0338 | [9 empty] | 150.5218 | 1234.7451 | 2934.5103 | 4977.7187 | 5657.8292 | 7861.6455 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616 | 9915.616
40% | [11 empty] | 613.2804 | 1205.5188 | 4289.7472 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | 7743.8094 | [11 empty] | 632.4067 | 3144.1872 | 4187.8717 | 7569.8059 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895 | 10721.7895
35% | FY38: 139.3232; FY39: 1272.0053; FY40: 1272.0053; FY41: 1272.0053; FY42: 1272.0053; FY43: 1272.0053; FY44: 1272.0053; FY45: 1272.0053; FY46: 1272.0053; FY47: 1272.0053; FY48: 1272.0053; FY49: 1272.0053; FY50: 1272.0053; FY51: 1272.0053; FY52: 1272.0053; FY53: 1272.0053; FY54: 1272.0053 | [12 empty] | 12.2893 | 122.6284 | 1190.3851 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236 | 2935.9236
30% | [45 empty] | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683 | 31.8683
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 3282.2271 | 2240.4473 | 3957.7482 | 269.663 | 1016.5813 | 2373.707 | 5226.4643 | 9543.8979 | 15211.2541 | 21988.9331 | 28990.6507 | 37775.2843 | 41470.7037 | 55269.6695 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | 70797.3803 | E @ R (MWh) | 5907.1482 | 4500.4298 | 6944.7067 | 1115.077 | 2699.6153 | 5176.7747 | 8593.1738 | 14871.4802 | 21591.4919 | 29003.2297 | 37912.5705 | 50368.4402 | 54828.4019 | 69990.5891 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923 | 84904.0923
Option 4 Winter POE50 W E @ R (MWh) N 2 | 2297.559 | 1568.3131 | 2770.4237 | 188.7641 | 711.6069 | 1661.5949 | 3658.525 | 6680.7285 | 10647.8779 | 15392.2532 | 20293.4555 | 26442.699 | 29029.4926 | 38688.7686 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | 49558.1662 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 1772.1445 | 1350.1289 | 2083.412 | 334.5231 | 809.8846 | 1553.0324 | 2577.9521 | 4461.4441 | 6477.4476 | 8700.9689 | 11373.7711 | 15110.5321 | 16448.5206 | 20997.1767 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277 | 25471.2277
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.5712 | 25.2681 | 27.2632 | 21.6568 | 23.1338 | 25.4665 | 27.5745 | 30.5026 | 33.5557 | 36.0493 | 38.4008 | 41.8956 | 44.4339 | 46.9918 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018 | 49.7018
98% | 19.902 | 18.5582 | 20.3015 | 14.478 | 16.1139 | 17.801 | 19.5936 | 21.6459 | 24.063 | 26.3281 | 28.7088 | 32.7659 | 34.1403 | 36.7363 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 | 38.7208 |  | 52.2693 | 49.6893 | 53.6393 | 42.5392 | 45.4635 | 50.0821 | 54.2558 | 60.053 | 66.0979 | 71.0349 | 75.6907 | 82.6101 | 87.6356 | 92.7 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656 | 98.0656
97% | 19.5287 | 18.1985 | 19.9242 | 14.1598 | 15.7791 | 17.4491 | 19.2235 | 21.2549 | 23.6475 | 25.8895 | 28.2461 | 32.262 | 33.6225 | 36.1921 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 | 38.1564 |  | 77.0943 | 73.2635 | 79.1285 | 62.6473 | 66.9893 | 73.8468 | 80.0438 | 88.6513 | 97.6266 | 104.9569 | 111.8696 | 122.1434 | 129.6051 | 137.1246 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913 | 145.0913
95% | 18.9688 | 17.6591 | 19.3582 | 13.6825 | 15.2769 | 16.9211 | 18.6683 | 20.6684 | 23.0242 | 25.2318 | 27.552 | 31.5062 | 32.8457 | 35.3758 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 | 37.3099 |  | 150.2596 | 142.7159 | 154.2653 | 121.8102 | 130.3605 | 143.8646 | 156.0678 | 173.0179 | 190.6925 | 205.1275 | 218.7403 | 238.9717 | 253.6655 | 268.4731 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614 | 284.1614
90% | 158.9609 | 147.603 | 162.3376 | 113.1186 | 126.9449 | 141.2038 | 156.3546 | 173.6999 | 194.129 | 213.2725 | 233.3937 | 267.6835 | 279.2999 | 301.2405 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 | 318.013 |  | 211.6379 | 200.7348 | 217.4274 | 170.5196 | 182.8775 | 202.3951 | 220.0325 | 244.5308 | 270.076 | 290.9391 | 310.6138 | 339.8546 | 361.0918 | 382.4933 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679 | 405.1679
85% | 142.1633 | 131.4193 | 145.3574 | 98.7989 | 111.8778 | 125.366 | 139.6978 | 156.1056 | 175.4304 | 193.5391 | 212.5726 | 245.009 | 255.9975 | 276.7521 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 | 292.6179 |  | 362.6533 | 343.1717 | 372.9978 | 289.1835 | 311.2644 | 346.1383 | 377.6526 | 421.4257 | 467.0697 | 504.3476 | 539.5021 | 591.7491 | 629.6954 | 667.9354 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45 | 708.45
80% | 139.2952 | 128.0395 | 142.6414 | 93.8658 | 107.5676 | 121.698 | 136.7123 | 153.9014 | 174.1465 | 193.1175 | 213.0574 | 247.0383 | 258.55 | 280.293 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 | 296.9143 |  | 268.0967 | 252.9699 | 276.1289 | 211.0496 | 228.1948 | 255.2733 | 279.7432 | 313.7318 | 349.1729 | 378.1182 | 405.4146 | 445.9829 | 475.4471 | 505.1393 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977 | 536.5977
75% | 193.0098 | 176.0923 | 198.0394 | 124.7282 | 145.3223 | 166.5608 | 189.1277 | 214.9635 | 245.3924 | 273.9064 | 303.8766 | 354.9511 | 372.2535 | 404.9338 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 | 429.9162 |  | 271.4717 | 255.2317 | 280.0951 | 210.2263 | 228.6333 | 257.7046 | 283.9754 | 320.4652 | 358.5146 | 389.59 | 418.8953 | 462.4491 | 494.0816 | 525.959 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326 | 559.7326
70% | 469.0487 | 423.5487 | 482.5757 | 285.4041 | 340.7923 | 397.9135 | 458.6077 | 528.0934 | 609.9325 | 686.6213 | 767.2268 | 904.5923 | 951.1275 | 1039.0216 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 | 1106.2122 |  | 354.8208 | 332.0323 | 366.9214 | 268.8797 | 294.7089 | 335.5024 | 372.3663 | 423.5698 | 476.9617 | 520.5675 | 561.6894 | 622.8052 | 667.1928 | 711.924 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159 | 759.3159
65% | 533.1398 | 474.2012 | 550.662 | 295.2553 | 367.0025 | 440.9946 | 519.6149 | 609.6234 | 715.6339 | 814.9728 | 919.3854 | 1097.3222 | 1157.6016 | 1271.4555 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 | 1358.491 |  | 378.0426 | 351.5215 | 392.1251 | 278.0249 | 308.0847 | 355.56 | 398.4619 | 458.0522 | 520.1893 | 570.9374 | 618.7948 | 689.921 | 741.5789 | 793.6368 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911 | 848.7911
60% | 1667.6879 | 1447.6916 | 1733.0919 | 779.7508 | 1047.5573 | 1323.7432 | 1617.2045 | 1953.1737 | 2348.8724 | 2719.6689 | 3109.4033 | 3773.5769 | 3998.5782 | 4423.5538 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 | 4748.4257 |  | 843.9098 | 777.607 | 879.116 | 593.8656 | 669.015 | 787.7032 | 894.9579 | 1043.9337 | 1199.2764 | 1326.1468 | 1445.7903 | 1623.6057 | 1752.7506 | 1882.8952 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811 | 2020.7811
55% | 2514.8345 | 2085.7224 | 2642.408 | 782.8755 | 1305.2435 | 1843.9559 | 2416.3646 | 3071.6869 | 3843.514 | 4566.7684 | 5326.962 | 6622.461 | 7061.3355 | 7890.2687 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 | 8523.9451 |  | 642.3969 | 583.6576 | 673.587 | 420.8763 | 487.4531 | 592.6021 | 687.6218 | 819.6033 | 957.2255 | 1069.6232 | 1175.6185 | 1333.1498 | 1447.5626 | 1562.861 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177 | 1685.0177
50% | 2944.1269 | 2171.9912 | 3173.6801 | 136.8912 | 772.6425 | 1736.9614 | 2766.9421 | 3946.116 | 5334.9262 | 6636.3357 | 8004.213 | 10335.3078 | 11125.01 | 12616.5757 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 | 13756.8004 |  | 1156.1376 | 1024.8091 | 1225.8721 | 660.865 | 809.7164 | 1044.807 | 1257.2507 | 1552.3331 | 1860.0269 | 2111.3241 | 2348.3069 | 2700.5131 | 2956.3157 | 3214.0983 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146 | 3487.2146
45% | 1108.4231 | 443.0694 | 1353.4228 |  |  | 194.5556 | 931.6253 | 2183.2506 | 3675.2493 | 5073.3533 | 6542.8636 | 9047.1584 | 9895.5353 | 11497.9241 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 | 12722.8674 |  | 1939.0178 | 1627.346 | 2104.5134 | 763.6251 | 1116.883 | 1674.8055 | 2178.9819 | 2879.2784 | 3609.5045 | 4205.8891 | 4768.3021 | 5604.1664 | 6211.2431 | 6823.019 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849 | 7471.1849
40% |  |  | 7.3214 |  |  |  |  | 288.2055 | 1717.2732 | 3763.2877 | 5946.1026 | 9665.9896 | 10926.1712 | 13306.3642 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 | 15125.8986 |  | 1665.5761 | 1116.1967 | 1957.2926 | 78.8903 | 367.9984 | 1199.853 | 2088.5573 | 3322.9595 | 4610.1181 | 5661.3565 | 6652.7135 | 8126.0791 | 9196.1641 | 10274.5324 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045 | 11417.045
35% | [9 empty] | 274.8517 | 1541.9848 | 5373.6114 | 6759.2007 | 9376.26 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 | 11376.8664 |  | 91.8208 | 1.3905 | 194.4116 |  |  | 6.1273 | 252.2831 | 1122.4882 | 2410.6244 | 3470.6967 | 4470.3844 | 5956.1312 | 7035.2086 | 8122.6387 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522 | 9274.7522
30% | [11 empty] | 94.9798 | 246.9312 | 705.8982 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | 1191.5814 | [9 empty] | 329.7941 | 1267.0434 | 2633.5594 | 5136.5868 | 6966.3627 | 8810.3024 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246 | 10763.9246
25% | FY39: 0.61273; FY40: 0.61273; FY41: 0.61273; FY42: 0.61273; FY43: 0.61273; FY44: 0.61273; FY45: 0.61273; FY46: 0.61273; FY47: 0.61273; FY48: 0.61273; FY49: 0.61273; FY50: 0.61273; FY51: 0.61273; FY52: 0.61273; FY53: 0.61273; FY54: 0.61273 | [12 empty] | 379.7602 | 1313.2254 | 2750.6828 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024 | 4753.9024
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9929.0896 | 7683.7944 | 10651.1216 | 2753.0087 | 4372.1206 | 6545.124 | 9389.7368 | 13342.3895 | 19105.2346 | 25487.1445 | 33205.5487 | 48126.2154 | 53388.2005 | 63498.8454 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | 71363.3494 | E @ R (MWh) | 8491.7765 | 7157.6056 | 9254.7848 | 4194.6594 | 5270.7766 | 7351.7319 | 9609.8265 | 13274.5964 | 17806.5268 | 22183.7483 | 26794.2865 | 34498.3752 | 40763.2605 | 47573.407 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981 | 55268.8981
Option 4 Summer POE50 W E @ R (MWh) N 2 | 6950.3627 | 5378.6561 | 7455.7851 | 1927.1061 | 3060.4844 | 4581.5868 | 6572.8158 | 9339.6726 | 13373.6642 | 17841.0012 | 23243.8841 | 33688.3508 | 37371.7404 | 44449.1918 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | 49954.3446 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 2547.5329 | 2147.2817 | 2776.4354 | 1258.3978 | 1581.233 | 2205.5196 | 2882.948 | 3982.3789 | 5341.958 | 6655.1245 | 8038.286 | 10349.5126 | 12228.9782 | 14272.0221 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694 | 16580.6694
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 15.9 | 14.2872 | 16.81 | 20.0388 | 23.1651 | 25.9461 | 29.7718 | 33.955 | 38.2396 | 42.4859 | 46.258 | 50.3713 | 51.9326 | 57.2535 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 |  | 19.0877 | 17.4876 | 20.1545 | 23.4232 | 26.4701 | 29.7154 | 33.1297 | 38.0063 | 42.2562 | 46.2644 | 50.4308 | 55.4278 | 57.0912 | 62.481 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044
98% | 7.7241 | 6.9258 | 8.1744 | 9.7727 | 11.3201 | 12.6966 | 14.5902 | 16.6608 | 18.7816 | 20.8834 | 22.7505 | 24.7865 | 25.5593 | 28.193 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 |  | 9.3019 | 8.5099 | 9.8299 | 11.4479 | 12.956 | 14.5623 | 16.2523 | 18.6661 | 20.7697 | 22.7537 | 24.8159 | 27.2893 | 28.1126 | 30.7805 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669
97% | 14.9962 | 13.4158 | 15.8878 | 19.0518 | 22.1153 | 24.8403 | 28.5891 | 32.6883 | 36.8867 | 41.0476 | 44.744 | 48.7746 | 50.3045 | 55.5185 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 |  | 18.1198 | 16.5518 | 19.1651 | 22.3682 | 25.3538 | 28.5339 | 31.8796 | 36.6581 | 40.8226 | 44.7503 | 48.8328 | 53.7295 | 55.3594 | 60.6409 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633
95% | 21.4775 | 19.1434 | 22.7943 | 27.4673 | 31.9918 | 36.0164 | 41.5532 | 47.6073 | 53.8081 | 59.9534 | 65.4127 | 71.3656 | 73.6252 | 81.3258 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 |  | 26.0908 | 23.775 | 27.6347 | 32.3653 | 36.7748 | 41.4715 | 46.4129 | 53.4705 | 59.6211 | 65.4219 | 71.4516 | 78.6835 | 81.0908 | 88.8912 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612
90% | 19.1049 | 16.8559 | 20.3737 | 24.8763 | 29.2359 | 33.1138 | 38.4487 | 44.2821 | 50.2568 | 56.1781 | 61.4383 | 67.1741 | 69.3514 | 76.7712 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 |  | 23.55 | 21.3187 | 25.0376 | 29.5958 | 33.8445 | 38.37 | 43.1312 | 49.9315 | 55.8579 | 61.4472 | 67.257 | 74.2253 | 76.5448 | 84.0608 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658
85% | 188.5861 | 163.0564 | 202.9891 | 254.0993 | 303.5863 | 347.6059 | 408.1639 | 474.3809 | 542.2018 | 609.4168 | 669.1272 | 734.2369 | 758.9514 | 843.1765 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 |  | 239.0441 | 213.7155 | 255.9301 | 307.6717 | 355.9007 | 407.2711 | 461.3172 | 538.5094 | 605.7822 | 669.2284 | 735.178 | 814.2772 | 840.6065 | 925.9234 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392
80% | 378.0005 | 316.4863 | 412.7049 | 535.8562 | 655.0962 | 761.1625 | 907.0785 | 1066.6301 | 1230.0461 | 1392.0022 | 1535.8758 | 1692.7592 | 1752.3093 | 1955.2518 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 |  | 499.5803 | 438.5505 | 540.2675 | 664.9401 | 781.1492 | 904.9273 | 1035.1526 | 1221.1492 | 1383.2444 | 1536.1197 | 1695.0267 | 1885.6182 | 1949.0592 | 2154.6323 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276
75% | 851.9655 | 672.3262 | 953.3124 | 1312.9498 | 1661.1654 | 1970.9098 | 2397.0265 | 2862.9635 | 3340.1856 | 3813.1444 | 4233.297 | 4691.442 | 4865.3456 | 5457.9964 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 |  | 1207.0139 | 1028.7891 | 1325.8323 | 1689.9124 | 2029.2767 | 2390.7446 | 2771.0402 | 3314.204 | 3787.5692 | 4234.0092 | 4698.0637 | 5254.6461 | 5439.9123 | 6040.2452 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592
70% | 1229.6514 | 838.9064 | 1450.0975 | 2232.3676 | 2989.7935 | 3663.5381 | 4590.4118 | 5603.901 | 6641.937 | 7670.6997 | 8584.6003 | 9581.1407 | 9959.4095 | 11248.5219 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 |  | 2001.9397 | 1614.2716 | 2260.3891 | 3052.3229 | 3790.4957 | 4576.7476 | 5403.9526 | 6585.4229 | 7615.0695 | 8586.1496 | 9595.544 | 10806.2017 | 11209.186 | 12515.0083 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428
65% | 545.9482 | 179.044 | 780.2029 | 1611.4739 | 2416.3444 | 3132.292 | 4117.2244 | 5194.1979 | 6297.2558 | 7390.4596 | 8361.6063 | 9420.5693 | 9822.5326 | 11192.3942 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 |  | 1366.6121 | 954.6607 | 1641.2505 | 2482.7906 | 3267.202 | 4102.7043 | 4981.7249 | 6237.2017 | 7331.3448 | 8363.2527 | 9435.8749 | 10722.3674 | 11150.5944 | 12538.2125 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813
60% | 8.8727 |  | 74.4011 | 747.9553 | 1573.7203 | 2308.2539 | 3318.7553 | 4423.6871 | 5555.3805 | 6676.9639 | 7673.3217 | 8759.7755 | 9172.1738 | 10577.5971 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 |  | 496.8079 | 162.7993 | 778.5049 | 1641.8914 | 2446.6663 | 3303.8582 | 4205.6983 | 5493.7674 | 6616.3145 | 7675.0108 | 8775.4784 | 10095.3683 | 10534.7121 | 11958.353 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951
55% |  |  |  | 32.0716 | 599.6383 | 1452.362 | 2630.7435 | 3919.2438 | 5238.9517 | 6546.87 | 7708.7583 | 8975.7107 | 9456.623 | 11095.5371 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 |  |  |  | 40.7106 | 675.5647 | 1613.7696 | 2613.3716 | 3665.0394 | 5167.1025 | 6476.1446 | 7710.728 | 8994.0224 | 10533.193 | 11045.5274 | 12705.6856 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633
50% | [5 empty] | 207.7028 | 1260.6583 | 2666.6676 | 4106.7306 | 5533.9289 | 6801.7793 | 8184.2757 | 8709.0464 | 10497.4266 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | [5 empty] | 304.0909 | 1241.702 | 2389.2801 | 4028.3289 | 5456.7534 | 6803.9287 | 8204.2574 | 9883.7977 | 10442.8561 | 12254.418 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048
45% | [6 empty] | 36.3146 | 916.1414 | 2624.9978 | 4361.2249 | 5903.601 | 7585.447 | 8223.8454 | 10399.4608 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | [6 empty] | 32.351 | 656.0457 | 2529.6198 | 4267.3388 | 5906.2158 | 7609.7553 | 9652.9638 | 10333.0742 | 12536.8906 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611
40% | [8 empty] | 409.8056 | 2216.6902 | 4565.0284 | 7145.9569 | 8125.6309 | 11464.2883 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | [8 empty] | 350.4931 | 2085.8253 | 4569.041 | 7183.26 | 10318.7284 | 11362.4128 | 14744.347 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306
35% | [10 empty] | 189.5467 | 1001.8484 | 1459.5503 | 3369.4171 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | [10 empty] | 190.3335 | 1017.8501 | 2700.6042 | 3309.939 | 5284.4155 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398
30% | FY38: 68.1292; FY39: 397.7914; FY40: 397.7914; FY41: 397.7914; FY42: 397.7914; FY43: 397.7914; FY44: 397.7914; FY45: 397.7914; FY46: 397.7914; FY47: 397.7914; FY48: 397.7914; FY49: 397.7914; FY50: 397.7914; FY51: 397.7914; FY52: 397.7914; FY53: 397.7914; FY54: 397.7914 | [12 empty] | 17.757 | 62.3815 | 375.2896 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588
25% | [45 empty] | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 3282.2271 | 2240.4473 | 3957.7482 | 6827.9805 | 10317.1725 | 13976.4402 | 19819.3296 | 27303.0069 | 36185.4651 | 46431.9489 | 56467.1453 | 68035.6344 | 72576.1912 | 88468.2588 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | E @ R (MWh) | 5907.1482 | 4500.4298 | 6944.7067 | 10634.2942 | 14723.9503 | 19726.3308 | 25740.0567 | 35662.5315 | 45844.7143 | 56484.655 | 68207.0991 | 82974.8783 | 87978.4603 | 104360.2754 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854
Option 5 Winter POE50 W E @ R (MWh) N 2 | 2297.559 | 1568.3131 | 2770.4237 | 4779.5863 | 7222.0207 | 9783.5081 | 13873.5307 | 19112.1048 | 25329.8256 | 32502.3642 | 39527.0017 | 47624.9441 | 50803.3338 | 61927.7812 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 1772.1445 | 1350.1289 | 2083.412 | 3190.2883 | 4417.1851 | 5917.8992 | 7722.017 | 10698.7595 | 13753.4143 | 16945.3965 | 20462.1297 | 24892.4635 | 26393.5381 | 31308.0826 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.5712 | 25.2681 | 27.2632 | 28.9314 | 30.4084 | 32.7411 | 34.8492 | 37.7772 | 40.8303 | 43.3239 | 45.6754 | 49.1702 | 51.7085 | 54.2664 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764
98% | 19.902 | 18.5582 | 20.3015 | 21.6795 | 23.3154 | 25.0025 | 26.7951 | 28.8474 | 31.2645 | 33.5296 | 35.9103 | 39.9674 | 41.3418 | 43.9378 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 |  | 52.2693 | 49.6893 | 53.6393 | 56.9422 | 59.8666 | 64.4851 | 68.6588 | 74.456 | 80.5009 | 85.4379 | 90.0937 | 97.0131 | 102.0386 | 107.103 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686
97% | 19.5287 | 18.1985 | 19.9242 | 21.2882 | 22.9075 | 24.5775 | 26.3519 | 28.3833 | 30.7759 | 33.0179 | 35.3745 | 39.3904 | 40.7509 | 43.3205 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 |  | 77.0943 | 73.2635 | 79.1285 | 84.0325 | 88.3745 | 95.232 | 101.429 | 110.0365 | 119.0118 | 126.3421 | 133.2548 | 143.5286 | 150.9903 | 158.5098 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765
95% | 18.9688 | 17.6591 | 19.3582 | 20.7012 | 22.2956 | 23.9399 | 25.687 | 27.6872 | 30.043 | 32.2505 | 34.5708 | 38.5249 | 39.8645 | 42.3945 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 |  | 150.2596 | 142.7159 | 154.2653 | 163.9225 | 172.4729 | 185.977 | 198.1802 | 215.1303 | 232.8048 | 247.2399 | 260.8526 | 281.0841 | 295.7779 | 310.5855 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738
90% | 158.9609 | 147.603 | 162.3376 | 173.9841 | 187.8104 | 202.0693 | 217.2201 | 234.5655 | 254.9946 | 274.138 | 294.2592 | 328.5491 | 340.1654 | 362.106 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 |  | 211.6379 | 200.7348 | 217.4274 | 231.3851 | 243.743 | 263.2606 | 280.8981 | 305.3963 | 330.9416 | 351.8047 | 371.4794 | 400.7202 | 421.9573 | 443.3589 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334
85% | 142.1633 | 131.4193 | 145.3574 | 156.3744 | 169.4533 | 182.9415 | 197.2733 | 213.6811 | 233.0059 | 251.1146 | 270.1482 | 302.5845 | 313.573 | 334.3276 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 |  | 362.6533 | 343.1717 | 372.9978 | 397.9373 | 420.0182 | 454.892 | 486.4063 | 530.1795 | 575.8234 | 613.1014 | 648.2559 | 700.5029 | 738.4491 | 776.6892 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038
80% | 139.2952 | 128.0395 | 142.6414 | 154.183 | 167.8848 | 182.0152 | 197.0295 | 214.2186 | 234.4637 | 253.4347 | 273.3746 | 307.3555 | 318.8672 | 340.6102 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 |  | 268.0967 | 252.9699 | 276.1289 | 295.4937 | 312.6389 | 339.7174 | 364.1873 | 398.1759 | 433.617 | 462.5623 | 489.8587 | 530.427 | 559.8911 | 589.5834 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418
75% | 193.0098 | 176.0923 | 198.0394 | 215.3867 | 235.9809 | 257.2193 | 279.7863 | 305.6221 | 336.051 | 364.5649 | 394.5352 | 445.6097 | 462.9121 | 495.5924 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 |  | 271.4717 | 255.2317 | 280.0951 | 300.8849 | 319.2919 | 348.3632 | 374.634 | 411.1238 | 449.1732 | 480.2486 | 509.5539 | 553.1077 | 584.7402 | 616.6176 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911
70% | 469.0487 | 423.5487 | 482.5757 | 529.2318 | 584.62 | 641.7413 | 702.4354 | 771.9211 | 853.7602 | 930.449 | 1011.0545 | 1148.42 | 1194.9552 | 1282.8494 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 |  | 354.8208 | 332.0323 | 366.9214 | 396.0942 | 421.9233 | 462.7169 | 499.5807 | 550.7843 | 604.1761 | 647.782 | 688.9039 | 750.0197 | 794.4073 | 839.1384 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303
65% | 533.1398 | 474.2012 | 550.662 | 611.0981 | 682.8453 | 756.8374 | 835.4577 | 925.4663 | 1031.4767 | 1130.8157 | 1235.2282 | 1413.165 | 1473.4444 | 1587.2983 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 |  | 378.0426 | 351.5215 | 392.1251 | 426.0763 | 456.136 | 503.6113 | 546.5132 | 606.1035 | 668.2406 | 718.9887 | 766.8461 | 837.9723 | 889.6303 | 941.6881 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425
60% | 1667.6879 | 1447.6916 | 1733.0919 | 1958.678 | 2226.4845 | 2502.6704 | 2796.1316 | 3132.1009 | 3527.7995 | 3898.5961 | 4288.3305 | 4952.5041 | 5177.5054 | 5602.481 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 |  | 843.9098 | 777.607 | 879.116 | 963.9939 | 1039.1433 | 1157.8315 | 1265.0862 | 1414.062 | 1569.4047 | 1696.2751 | 1815.9186 | 1993.734 | 2122.8789 | 2253.0235 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094
55% | 2514.8345 | 2085.7224 | 2642.408 | 3082.4232 | 3604.7912 | 4143.5036 | 4715.9123 | 5371.2346 | 6143.0617 | 6866.3161 | 7626.5097 | 8922.0086 | 9360.8832 | 10189.8163 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 |  | 642.3969 | 583.6576 | 673.587 | 748.7826 | 815.3594 | 920.5083 | 1015.528 | 1147.5095 | 1285.1317 | 1397.5294 | 1503.5247 | 1661.056 | 1775.4688 | 1890.7673 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924
50% | 2944.1269 | 2171.9912 | 3173.6801 | 3965.4346 | 4905.3732 | 5874.7215 | 6904.7022 | 8083.8762 | 9472.6864 | 10774.0959 | 12141.9731 | 14473.068 | 15262.7701 | 16754.3358 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 |  | 1156.1376 | 1024.8091 | 1225.8721 | 1393.9931 | 1542.8446 | 1777.9352 | 1990.3789 | 2285.4613 | 2593.155 | 2844.4523 | 3081.435 | 3433.6413 | 3689.4439 | 3947.2265 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428
45% | 1108.4231 | 443.0694 | 1353.4228 | 2204.0046 | 3213.7805 | 4255.1512 | 5361.6593 | 6628.4458 | 8120.4444 | 9518.5484 | 10988.0587 | 13492.3535 | 14340.7305 | 15943.1192 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 |  | 1939.0178 | 1627.346 | 2104.5134 | 2503.5023 | 2856.7601 | 3414.6827 | 3918.8591 | 4619.1556 | 5349.3816 | 5945.7663 | 6508.1793 | 7344.0436 | 7951.1202 | 8562.8961 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621
40% |  |  | 7.3214 | 300.2304 | 1157.9309 | 2547.9279 | 4191.5383 | 6073.2266 | 8289.4458 | 10366.1936 | 12549.0086 | 16268.8956 | 17529.0771 | 19909.2702 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 |  | 1665.5761 | 1116.1967 | 1957.2926 | 2660.5844 | 3283.2668 | 4266.7086 | 5155.4129 | 6389.8151 | 7676.9738 | 8728.2121 | 9719.5692 | 11192.9347 | 12263.0198 | 13341.388 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006
35% | [5 empty] | 11.585 | 446.2949 | 1644.5809 | 3860.0801 | 6143.4967 | 8543.5357 | 12633.6093 | 14019.1986 | 16636.2579 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 |  | 91.8208 | 1.3905 | 194.4116 | 584.94 | 1085.9465 | 2064.329 | 2960.5014 | 4205.2768 | 5503.2519 | 6563.3242 | 7563.0119 | 9048.7587 | 10127.8361 | 11215.2662 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798
30% | [8 empty] | 9.221 | 171.1327 | 536.9198 | 1523.9285 | 1890.3492 | 2582.4336 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | [6 empty] | 150.8022 | 745.6853 | 2229.0514 | 4368.6458 | 6166.1952 | 7861.3513 | 10380.7107 | 12210.4866 | 14054.4262 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485
25% | [11 empty] | 28.8835 | 106.5455 | 374.8407 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | [9 empty] | 149.9073 | 840.9199 | 1952.4029 | 4324.797 | 6462.3758 | 8651.8252 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509
20% | [43 empty] | 15.4293 | 113.8997 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9929.0896 | 7683.7944 | 10651.1216 | 13414.698 | 17205.4734 | 21631.9035 | 26924.275 | 33683.8576 | 42458.5743 | 51041.6943 | 60258.7914 | 76358.8177 | 81912.9341 | 92524.9915 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | E @ R (MWh) | 8491.7765 | 7157.6056 | 9254.7848 | 11237.4964 | 13148.1944 | 16503.7942 | 20006.7886 | 25529.4948 | 32030.9718 | 37959.506 | 44010.1673 | 53723.2218 | 61207.65 | 68868.2589 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388
Option 5 Summer POE50 W E @ R (MWh) N 2 | 6950.3627 | 5378.6561 | 7455.7851 | 9390.2886 | 12043.8314 | 15142.3325 | 18846.9925 | 23578.7003 | 29721.002 | 35729.186 | 42181.154 | 53451.1724 | 57339.0539 | 64767.494 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 2547.5329 | 2147.2817 | 2776.4354 | 3371.2489 | 3944.4583 | 4951.1383 | 6002.0366 | 7658.8484 | 9609.2915 | 11387.8518 | 13203.0502 | 16116.9665 | 18362.295 | 20660.4777 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 11.8282 | 9.6439 | 11.9891 | 15.0711 | 18.0681 | 20.6396 | 24.2765 | 28.1941 | 32.2013 | 36.2223 | 39.7825 | 43.5763 | 44.9081 | 49.9973 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 | 55.2559 |  | 15.0159 | 12.8442 | 15.3336 | 18.4555 | 21.3731 | 24.4089 | 27.6344 | 32.2454 | 36.2179 | 40.0008 | 43.9552 | 48.6328 | 50.0666 | 55.2248 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019 | 60.0019
98% | 5.7086 | 4.6274 | 5.7882 | 7.3138 | 8.7972 | 10.07 | 11.8702 | 13.8093 | 15.7928 | 17.783 | 19.5453 | 21.4231 | 22.0823 | 24.6014 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 | 27.2042 |  | 7.2864 | 6.2115 | 7.4437 | 8.989 | 10.4331 | 11.9357 | 13.5323 | 15.8146 | 17.7809 | 19.6533 | 21.6107 | 23.9259 | 24.6357 | 27.1888 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534 | 29.5534
97% | 11.0062 | 8.8658 | 11.1639 | 14.1839 | 17.1207 | 19.6405 | 23.2043 | 27.0431 | 30.9698 | 34.9099 | 38.3986 | 42.1161 | 43.4212 | 48.4081 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 | 53.561 |  | 14.1298 | 12.0018 | 14.4412 | 17.5003 | 20.3592 | 23.334 | 26.4947 | 31.013 | 34.9057 | 38.6126 | 42.4874 | 47.071 | 48.476 | 53.5305 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116 | 58.2116
95% | 15.5846 | 12.4233 | 15.8174 | 20.2778 | 24.6152 | 28.3367 | 33.6002 | 39.2699 | 45.0692 | 50.8885 | 56.041 | 61.5315 | 63.459 | 70.8243 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 | 78.4347 |  | 20.1979 | 17.055 | 20.6577 | 25.1759 | 29.3983 | 33.7918 | 38.4599 | 45.133 | 50.8823 | 56.357 | 62.0799 | 68.8495 | 70.9246 | 78.3897 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033 | 85.3033
90% | 13.4269 | 10.3808 | 13.6512 | 17.949 | 22.1283 | 25.714 | 30.7857 | 36.2486 | 41.8365 | 47.4437 | 52.4083 | 57.6986 | 59.5559 | 66.6526 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 | 73.9855 |  | 17.872 | 14.8437 | 18.3151 | 22.6685 | 26.7369 | 30.9703 | 35.4682 | 41.898 | 47.4376 | 52.7128 | 58.2271 | 64.7498 | 66.7493 | 73.9422 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038 | 80.6038
85% | 124.1325 | 89.5561 | 126.6791 | 175.4647 | 222.9053 | 263.6087 | 321.1783 | 383.1903 | 446.6204 | 510.2693 | 566.6245 | 626.6769 | 647.759 | 728.3171 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 | 811.5551 |  | 174.5905 | 140.2152 | 179.6201 | 229.0371 | 275.2197 | 323.2739 | 374.3316 | 447.3188 | 510.2007 | 570.081 | 632.6753 | 706.7172 | 729.4141 | 811.0639 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814 | 886.6814
80% | 222.6981 | 139.3855 | 228.8343 | 346.3844 | 460.6934 | 558.7692 | 697.4846 | 846.904 | 999.7403 | 1153.104 | 1288.8931 | 1433.5908 | 1484.3887 | 1678.4952 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 | 1879.0593 |  | 344.278 | 261.4497 | 356.3969 | 475.4683 | 586.7464 | 702.534 | 825.5588 | 1001.4231 | 1152.9387 | 1297.2215 | 1448.044 | 1626.4497 | 1681.1386 | 1877.8757 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777 | 2060.0777
75% | 398.4376 | 155.1406 | 416.3569 | 759.6372 | 1093.4528 | 1379.8626 | 1784.9518 | 2221.2997 | 2667.626 | 3115.4925 | 3512.036 | 3934.5951 | 4082.9397 | 4649.7871 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 | 5235.4923 |  | 753.486 | 511.6035 | 788.8767 | 1136.5998 | 1461.5641 | 1799.6975 | 2158.9655 | 2672.5402 | 3115.0096 | 3536.3574 | 3976.8027 | 4497.7992 | 4657.5064 | 5232.0359 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187 | 5764.1187
70% | 250.2519 | 1.0776 | 284.8307 | 1028.8223 | 1754.9258 | 2377.914 | 3259.0492 | 4208.1771 | 5179.0098 | 6153.1929 | 7015.7396 | 7934.8748 | 8257.5487 | 9490.5345 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 | 10764.5391 |  | 1015.4422 | 489.3084 | 1092.423 | 1848.7775 | 2555.628 | 3291.1234 | 4072.59 | 5189.699 | 6152.1424 | 7068.6428 | 8026.6834 | 9159.9358 | 9507.3252 | 10757.0209 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878 | 11914.3878
65% |  |  |  | 337.1725 | 1104.1254 | 1766.1372 | 2702.4661 | 3711.0468 | 4742.6918 | 5777.8971 | 6694.4732 | 7671.1824 | 8014.0684 | 9324.2876 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 | 10678.0951 |  | 324.51 | 15.7862 | 400.4426 | 1203.8559 | 1954.9831 | 2736.5494 | 3566.9666 | 4754.0506 | 5776.7808 | 6750.6902 | 7768.7418 | 8972.9805 | 9342.1301 | 10670.106 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696 | 11899.9696
60% |  |  |  |  | 264.183 | 906.6336 | 1867.2697 | 2902.0332 | 3960.4599 | 5022.5392 | 5962.9097 | 6964.9744 | 7316.7616 | 8660.9943 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 | 10049.9467 |  |  |  |  | 344.542 | 1100.382 | 1902.2379 | 2754.2128 | 3972.1135 | 5021.3939 | 6020.5861 | 7065.0664 | 8300.5672 | 8679.3 | 10041.7502 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412 | 11303.5412
55% | [5 empty] | 87.8116 | 938.1147 | 2144.7892 | 3379.0581 | 4617.5865 | 5714.186 | 6882.7293 | 7292.9609 | 8860.5184 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | 10480.2252 | [5 empty] | 191.4901 | 978.8923 | 1972.4105 | 3392.6479 | 4616.251 | 5781.4445 | 6999.4502 | 8440.2116 | 8881.8653 | 10470.6669 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863 | 11942.0863
50% | [6 empty] | 20.9399 | 739.8297 | 2077.2179 | 3428.698 | 4625.3055 | 5900.4179 | 6348.062 | 8058.5781 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | 9825.9994 | [6 empty] | 28.8052 | 579.0292 | 2092.047 | 3427.2406 | 4698.6979 | 6027.7836 | 7599.9399 | 8081.8718 | 9815.5694 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797 | 11421.1797
45% | [8 empty] | 412.2551 | 1800.1518 | 3255.8588 | 4807.0692 | 5351.641 | 7432.5323 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | 9582.6504 | [8 empty] | 422.6376 | 1798.3789 | 3345.1427 | 4962.0132 | 6874.586 | 7460.8697 | 9569.9621 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326 | 11523.2326
40% | [9 empty] | 47.6497 | 910.9965 | 2882.3118 | 3718.0012 | 6911.2969 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | 10210.8269 | [9 empty] | 47.2486 | 996.7673 | 3120.0858 | 6055.0833 | 6954.7831 | 10191.3556 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807 | 13188.807
35% | [11 empty] | 2.4955 | 59.0978 | 903.8405 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | 2637.608 | [11 empty] | 11.0811 | 585.9566 | 921.6558 | 2626.2401 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437 | 4376.2437
30% | FY39: 14.6605; FY40: 14.6605; FY41: 14.6605; FY42: 14.6605; FY43: 14.6605; FY44: 14.6605; FY45: 14.6605; FY46: 14.6605; FY47: 14.6605; FY48: 14.6605; FY49: 14.6605; FY50: 14.6605; FY51: 14.6605; FY52: 14.6605; FY53: 14.6605; FY54: 14.6605 | [14 empty] | 14.1327 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586 | 201.0586
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1053.0746 | 431.101 | 1115.1109 | 2722.2767 | 4991.0154 | 7445.1377 | 11715.1912 | 17301.8349 | 24030.5487 | 31813.8286 | 39753.1986 | 49267.2636 | 52806.6554 | 66959.6658 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | 82459.0992 | E @ R (MWh) | 2686.8087 | 1481.3192 | 2893.9507 | 5331.0698 | 8234.3141 | 11887.5544 | 16445.6547 | 24110.5816 | 31804.8096 | 40272.968 | 50266.7878 | 63073.4558 | 67158.7122 | 82366.0557 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585 | 96795.0585
Option 6 Winter POE50 W E @ R (MWh) N 2 | 737.1523 | 301.7707 | 780.5776 | 1905.5937 | 3493.7108 | 5211.5964 | 8200.6338 | 12111.2844 | 16821.3841 | 22269.68 | 27827.2391 | 34487.0845 | 36964.6588 | 46871.766 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | 57721.3695 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 806.0426 | 444.3958 | 868.1852 | 1599.3209 | 2470.2942 | 3566.2663 | 4933.6964 | 7233.1745 | 9541.4429 | 12081.8904 | 15080.0363 | 18922.0367 | 20147.6137 | 24709.8167 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176 | 29038.5176
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23.9807 | 22.3139 | 24.1961 | 25.7709 | 27.1656 | 29.3651 | 31.353 | 34.112 | 36.9887 | 39.3389 | 41.5555 | 44.8471 | 47.2394 | 49.6499 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033 | 52.2033
98% | 17.3375 | 15.6337 | 17.2653 | 18.5508 | 20.1052 | 21.6604 | 23.3341 | 25.2191 | 27.4615 | 29.5846 | 31.8318 | 35.6877 | 36.9176 | 39.3677 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 | 41.1971 |  | 47.1403 | 43.8403 | 47.5668 | 50.6847 | 53.4462 | 57.8009 | 61.7367 | 67.1993 | 72.8948 | 77.548 | 81.9368 | 88.4538 | 93.1902 | 97.9628 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182 | 103.0182
97% | 16.9902 | 15.3037 | 16.9187 | 18.1912 | 19.7299 | 21.2692 | 22.926 | 24.7918 | 27.0115 | 29.113 | 31.3374 | 35.1542 | 36.3716 | 38.7968 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 | 40.6076 |  | 69.4789 | 64.5791 | 70.1121 | 74.7415 | 78.8417 | 85.3074 | 91.1513 | 99.2619 | 107.7185 | 114.6274 | 121.1437 | 130.8199 | 137.8525 | 144.9387 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448 | 152.4448
95% | 16.4694 | 14.8088 | 16.399 | 17.6519 | 19.1669 | 20.6826 | 22.3138 | 24.1509 | 26.3364 | 28.4057 | 30.5958 | 34.3539 | 35.5526 | 37.9404 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 | 39.7234 |  | 135.263 | 125.6143 | 136.5101 | 145.6264 | 153.7006 | 166.4331 | 177.941 | 193.9127 | 210.5656 | 224.171 | 237.003 | 256.0578 | 269.9065 | 283.8608 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421 | 298.6421
90% | 137.2861 | 122.8859 | 136.6757 | 147.5405 | 160.6786 | 173.8223 | 187.9681 | 203.8994 | 222.852 | 240.7962 | 259.7891 | 292.3783 | 302.7731 | 323.4805 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 | 338.942 |  | 189.9632 | 176.0178 | 191.7655 | 204.9415 | 216.6112 | 235.0136 | 251.6461 | 274.7302 | 298.7989 | 318.4629 | 337.0093 | 364.5493 | 384.565 | 404.7334 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969 | 426.0969
85% | 121.6601 | 108.0383 | 121.0827 | 131.3602 | 143.7881 | 156.2214 | 169.6026 | 184.6727 | 202.6008 | 219.5751 | 237.5413 | 268.3689 | 278.2019 | 297.79 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 | 312.4157 |  | 323.9251 | 299.0076 | 327.1455 | 350.6881 | 371.5394 | 404.4206 | 434.1394 | 475.3858 | 518.3914 | 553.5267 | 586.6651 | 635.8733 | 671.637 | 707.6736 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458 | 745.8458
80% | 117.8157 | 103.5452 | 117.2107 | 127.9777 | 140.9974 | 154.0227 | 168.0411 | 183.8288 | 202.6106 | 220.3932 | 239.215 | 271.5106 | 281.8118 | 302.3326 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 | 317.6548 |  | 238.0254 | 218.6777 | 240.526 | 258.8061 | 274.9965 | 300.5278 | 323.6035 | 355.6302 | 389.0228 | 416.3043 | 442.0353 | 480.244 | 508.0135 | 535.9948 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344 | 565.6344
75% | 160.7255 | 139.2765 | 159.8162 | 175.9993 | 195.5683 | 215.1457 | 236.2158 | 259.9453 | 288.1749 | 314.9027 | 343.1923 | 391.7336 | 407.2166 | 438.0601 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 | 461.0898 |  | 239.1874 | 218.4159 | 241.872 | 261.4974 | 278.8793 | 306.2896 | 331.0635 | 365.4471 | 401.2971 | 430.5864 | 458.211 | 499.2316 | 529.0447 | 559.0853 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062 | 590.9062
70% | 382.2195 | 324.5321 | 379.774 | 423.2985 | 475.9298 | 528.5836 | 585.2519 | 649.0727 | 724.9967 | 796.8815 | 872.967 | 1003.5195 | 1045.1613 | 1128.1154 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 | 1190.0541 |  | 309.5186 | 280.3715 | 313.2857 | 340.8247 | 365.2154 | 403.6781 | 438.4415 | 486.6894 | 536.9952 | 578.0946 | 616.8582 | 674.4194 | 716.2539 | 758.4077 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595 | 803.0595
65% | 420.6653 | 345.9398 | 417.4976 | 473.8771 | 542.0532 | 610.2584 | 683.6639 | 766.3343 | 864.6826 | 957.7987 | 1056.3563 | 1225.4677 | 1279.4085 | 1386.8633 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 | 1467.0958 |  | 325.3202 | 291.3989 | 329.7043 | 361.7539 | 390.1397 | 434.9024 | 475.3598 | 531.5104 | 590.0559 | 637.8871 | 682.9999 | 749.9892 | 798.676 | 847.7342 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997 | 899.6997
60% | 1247.8613 | 968.9378 | 1236.0373 | 1446.4818 | 1700.9584 | 1955.5437 | 2229.5399 | 2538.1187 | 2905.2175 | 3252.7864 | 3620.666 | 4251.898 | 4453.2396 | 4854.3293 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 | 5153.8083 |  | 712.1037 | 627.3006 | 723.064 | 803.1881 | 874.1525 | 986.0592 | 1087.2027 | 1227.5792 | 1373.9429 | 1493.5209 | 1606.303 | 1773.7763 | 1895.4931 | 2018.1386 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524 | 2148.0524
55% | 1695.945 | 1151.8927 | 1672.8817 | 2083.3626 | 2579.7301 | 3076.3096 | 3610.7509 | 4212.6471 | 4928.6888 | 5606.6367 | 6324.2017 | 7555.4466 | 7948.172 | 8730.5145 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 | 9314.6611 |  | 525.6265 | 450.4972 | 535.3365 | 606.3205 | 669.1898 | 768.3307 | 857.9365 | 982.2996 | 1111.967 | 1217.9042 | 1317.8208 | 1466.1898 | 1574.0219 | 1682.6767 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707 | 1797.7707
50% | 1470.6334 | 536.1069 | 1429.1338 | 2167.745 | 3060.8987 | 3954.4339 | 4916.0969 | 5999.1368 | 7287.5681 | 8507.454 | 9798.626 | 12014.1036 | 12720.7658 | 14128.4973 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 | 15179.599 |  | 895.0641 | 727.091 | 916.7734 | 1075.4786 | 1216.0407 | 1437.6987 | 1638.0379 | 1916.0873 | 2205.9959 | 2442.8488 | 2666.2409 | 2997.9621 | 3239.0517 | 3481.9806 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306 | 3739.306
45% | 90.7264 |  | 77.9769 | 440.1868 | 1232.2618 | 2192.1865 | 3225.3009 | 4388.8106 | 5772.9721 | 7083.4954 | 8470.6013 | 10850.6885 | 11609.8556 | 13122.1813 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 | 14251.3797 |  | 1319.432 | 920.7944 | 1370.9532 | 1747.5959 | 2081.1813 | 2607.2254 | 3082.6751 | 3742.5484 | 4430.5663 | 4992.6713 | 5522.8307 | 6310.0794 | 6882.2387 | 7458.7634 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542 | 8069.4542
40% |  |  |  |  | 0.33554 | 293.3542 | 1170.6694 | 2746.4659 | 4802.5035 | 6749.1587 | 8809.5699 | 12344.9585 | 13472.6275 | 15719.0407 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 | 17396.3552 |  | 621.1175 | 182.5879 | 695.0307 | 1328.1596 | 1916.1656 | 2843.4157 | 3681.4837 | 4844.6326 | 6057.3916 | 7048.2058 | 7982.7099 | 9370.3814 | 10378.9182 | 11395.1497 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053 | 12471.6053
35% | [7 empty] | 31.1813 | 757.9176 | 2239.6003 | 4431.9646 | 8319.1795 | 9559.0691 | 12029.0353 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 | 13873.2688 |  |  |  |  | 19.8164 | 177.7546 | 717.6121 | 1474.1863 | 2647.1096 | 3870.0598 | 4869.2001 | 5811.5572 | 7210.8898 | 8227.9017 | 9252.6729 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744 | 10338.1744
30% | [10 empty] | 31.3125 | 494.9465 | 745.7124 | 1364.0482 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | 1851.7579 | [7 empty] | 4.142 | 489.3856 | 1760.3356 | 3293.4935 | 4891.4347 | 7264.2629 | 8988.7953 | 10726.4851 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543 | 12567.1543
25% | FY38: 10.1007; FY39: 96.1669; FY40: 96.1669; FY41: 96.1669; FY42: 96.1669; FY43: 96.1669; FY44: 96.1669; FY45: 96.1669; FY46: 96.1669; FY47: 96.1669; FY48: 96.1669; FY49: 96.1669; FY50: 96.1669; FY51: 96.1669; FY52: 96.1669; FY53: 96.1669; FY54: 96.1669 | [10 empty] | 3.5184 | 295.4688 | 1513.2964 | 2914.0942 | 4711.2325 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744 | 6885.8744
20% | [45 empty] | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813 | 27.5813
15%
10%
5%
9.992e-14%
E @ R (MWh) | 5896.3355 | 3846.9013 | 5798.6696 | 7672.2232 | 10292.2018 | 13373.494 | 17251.6752 | 22238.2755 | 29041.5945 | 36276.5822 | 44589.7679 | 59389.3956 | 64212.8569 | 73950.4942 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | 81325.7772 | E @ R (MWh) | 5975.1465 | 4648.5083 | 6163.8418 | 7655.8944 | 9145.0201 | 11784.0804 | 14442.0999 | 18733.5212 | 23972.988 | 28751.9101 | 33699.7838 | 41831.3236 | 48256.8936 | 55117.1405 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238 | 62682.5238
Option 6 Summer POE50 W E @ R (MWh) N 2 | 4127.4349 | 2692.8309 | 4059.0687 | 5370.5563 | 7204.5412 | 9361.4458 | 12076.1727 | 15566.7928 | 20329.1161 | 25393.6076 | 31212.8376 | 41572.5769 | 44948.9998 | 51765.3459 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | 56928.044 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 1792.544 | 1394.5525 | 1849.1525 | 2296.7683 | 2743.506 | 3535.2241 | 4332.63 | 5620.0564 | 7191.8964 | 8625.573 | 10109.9352 | 12549.3971 | 14477.0681 | 16535.1422 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571 | 18804.7571
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 15.9 | 14.2872 | 16.81 | 20.0388 | 23.1651 | 25.9461 | 29.7718 | 33.955 | 38.2396 | 42.4859 | 46.258 | 50.3713 | 51.9326 | 57.2535 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 |  | 19.0877 | 17.4876 | 20.1545 | 23.4232 | 26.4701 | 29.7154 | 33.1297 | 38.0063 | 42.2562 | 46.2644 | 50.4308 | 55.4278 | 57.0912 | 62.481 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044
98% | 7.7241 | 6.9258 | 8.1744 | 9.7727 | 11.3201 | 12.6966 | 14.5902 | 16.6608 | 18.7816 | 20.8834 | 22.7505 | 24.7865 | 25.5593 | 28.193 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 |  | 9.3019 | 8.5099 | 9.8299 | 11.4479 | 12.956 | 14.5623 | 16.2523 | 18.6661 | 20.7697 | 22.7537 | 24.8159 | 27.2893 | 28.1126 | 30.7805 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669
97% | 14.9962 | 13.4158 | 15.8878 | 19.0518 | 22.1153 | 24.8403 | 28.5891 | 32.6883 | 36.8867 | 41.0476 | 44.744 | 48.7746 | 50.3045 | 55.5185 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 |  | 18.1198 | 16.5518 | 19.1651 | 22.3682 | 25.3538 | 28.5339 | 31.8796 | 36.6581 | 40.8226 | 44.7503 | 48.8328 | 53.7295 | 55.3594 | 60.6409 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633
95% | 21.4775 | 19.1434 | 22.7943 | 27.4673 | 31.9918 | 36.0164 | 41.5532 | 47.6073 | 53.8081 | 59.9534 | 65.4127 | 71.3656 | 73.6252 | 81.3258 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 |  | 26.0908 | 23.775 | 27.6347 | 32.3653 | 36.7748 | 41.4715 | 46.4129 | 53.4705 | 59.6211 | 65.4219 | 71.4516 | 78.6835 | 81.0908 | 88.8912 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612
90% | 19.1049 | 16.8559 | 20.3737 | 24.8763 | 29.2359 | 33.1138 | 38.4487 | 44.2821 | 50.2568 | 56.1781 | 61.4383 | 67.1741 | 69.3514 | 76.7712 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 |  | 23.55 | 21.3187 | 25.0376 | 29.5958 | 33.8445 | 38.37 | 43.1312 | 49.9315 | 55.8579 | 61.4472 | 67.257 | 74.2253 | 76.5448 | 84.0608 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658
85% | 188.5861 | 163.0564 | 202.9891 | 254.0993 | 303.5863 | 347.6059 | 408.1639 | 474.3809 | 542.2018 | 609.4168 | 669.1272 | 734.2369 | 758.9514 | 843.1765 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 |  | 239.0441 | 213.7155 | 255.9301 | 307.6717 | 355.9007 | 407.2711 | 461.3172 | 538.5094 | 605.7822 | 669.2284 | 735.178 | 814.2772 | 840.6065 | 925.9234 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392
80% | 378.0005 | 316.4863 | 412.7049 | 535.8562 | 655.0962 | 761.1625 | 907.0785 | 1066.6301 | 1230.0461 | 1392.0022 | 1535.8758 | 1692.7592 | 1752.3093 | 1955.2518 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 |  | 499.5803 | 438.5505 | 540.2675 | 664.9401 | 781.1492 | 904.9273 | 1035.1526 | 1221.1492 | 1383.2444 | 1536.1197 | 1695.0267 | 1885.6182 | 1949.0592 | 2154.6323 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276
75% | 851.9655 | 672.3262 | 953.3124 | 1312.9498 | 1661.1654 | 1970.9098 | 2397.0265 | 2862.9635 | 3340.1856 | 3813.1444 | 4233.297 | 4691.442 | 4865.3456 | 5457.9964 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 |  | 1207.0139 | 1028.7891 | 1325.8323 | 1689.9124 | 2029.2767 | 2390.7446 | 2771.0402 | 3314.204 | 3787.5692 | 4234.0092 | 4698.0637 | 5254.6461 | 5439.9123 | 6040.2452 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592
70% | 1229.6514 | 838.9064 | 1450.0975 | 2232.3676 | 2989.7935 | 3663.5381 | 4590.4118 | 5603.901 | 6641.937 | 7670.6997 | 8584.6003 | 9581.1407 | 9959.4095 | 11248.5219 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 |  | 2001.9397 | 1614.2716 | 2260.3891 | 3052.3229 | 3790.4957 | 4576.7476 | 5403.9526 | 6585.4229 | 7615.0695 | 8586.1496 | 9595.544 | 10806.2017 | 11209.186 | 12515.0083 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428
65% | 545.9482 | 179.044 | 780.2029 | 1611.4739 | 2416.3444 | 3132.292 | 4117.2244 | 5194.1979 | 6297.2558 | 7390.4596 | 8361.6063 | 9420.5693 | 9822.5326 | 11192.3942 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 |  | 1366.6121 | 954.6607 | 1641.2505 | 2482.7906 | 3267.202 | 4102.7043 | 4981.7249 | 6237.2017 | 7331.3448 | 8363.2527 | 9435.8749 | 10722.3674 | 11150.5944 | 12538.2125 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813
60% | 8.8727 |  | 74.4011 | 747.9553 | 1573.7203 | 2308.2539 | 3318.7553 | 4423.6871 | 5555.3805 | 6676.9639 | 7673.3217 | 8759.7755 | 9172.1738 | 10577.5971 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 |  | 496.8079 | 162.7993 | 778.5049 | 1641.8914 | 2446.6663 | 3303.8582 | 4205.6983 | 5493.7674 | 6616.3145 | 7675.0108 | 8775.4784 | 10095.3683 | 10534.7121 | 11958.353 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951
55% |  |  |  | 32.0716 | 599.6383 | 1452.362 | 2630.7435 | 3919.2438 | 5238.9517 | 6546.87 | 7708.7583 | 8975.7107 | 9456.623 | 11095.5371 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 |  |  |  | 40.7106 | 675.5647 | 1613.7696 | 2613.3716 | 3665.0394 | 5167.1025 | 6476.1446 | 7710.728 | 8994.0224 | 10533.193 | 11045.5274 | 12705.6856 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633
50% | [5 empty] | 207.7028 | 1260.6583 | 2666.6676 | 4106.7306 | 5533.9289 | 6801.7793 | 8184.2757 | 8709.0464 | 10497.4266 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | [5 empty] | 304.0909 | 1241.702 | 2389.2801 | 4028.3289 | 5456.7534 | 6803.9287 | 8204.2574 | 9883.7977 | 10442.8561 | 12254.418 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048
45% | [6 empty] | 36.3146 | 916.1414 | 2624.9978 | 4361.2249 | 5903.601 | 7585.447 | 8223.8454 | 10399.4608 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | [6 empty] | 32.351 | 656.0457 | 2529.6198 | 4267.3388 | 5906.2158 | 7609.7553 | 9652.9638 | 10333.0742 | 12536.8906 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611
40% | [8 empty] | 409.8056 | 2216.6902 | 4565.0284 | 7145.9569 | 8125.6309 | 11464.2883 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | [8 empty] | 350.4931 | 2085.8253 | 4569.041 | 7183.26 | 10318.7284 | 11362.4128 | 14744.347 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306
35% | [10 empty] | 189.5467 | 1001.8484 | 1459.5503 | 3369.4171 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | [10 empty] | 190.3335 | 1017.8501 | 2700.6042 | 3309.939 | 5284.4155 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398
30% | FY38: 68.1292; FY39: 397.7914; FY40: 397.7914; FY41: 397.7914; FY42: 397.7914; FY43: 397.7914; FY44: 397.7914; FY45: 397.7914; FY46: 397.7914; FY47: 397.7914; FY48: 397.7914; FY49: 397.7914; FY50: 397.7914; FY51: 397.7914; FY52: 397.7914; FY53: 397.7914; FY54: 397.7914 | [12 empty] | 17.757 | 62.3815 | 375.2896 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588
25% | [45 empty] | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 3282.2271 | 2240.4473 | 3957.7482 | 6827.9805 | 10317.1725 | 13976.4402 | 19819.3296 | 27303.0069 | 36185.4651 | 46431.9489 | 56467.1453 | 68035.6344 | 72576.1912 | 88468.2588 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | E @ R (MWh) | 5907.1482 | 4500.4298 | 6944.7067 | 10634.2942 | 14723.9503 | 19726.3308 | 25740.0567 | 35662.5315 | 45844.7143 | 56484.655 | 68207.0991 | 82974.8783 | 87978.4603 | 104360.2754 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854
Option 7 Winter POE50 W E @ R (MWh) N 2 | 2297.559 | 1568.3131 | 2770.4237 | 4779.5863 | 7222.0207 | 9783.5081 | 13873.5307 | 19112.1048 | 25329.8256 | 32502.3642 | 39527.0017 | 47624.9441 | 50803.3338 | 61927.7812 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 1772.1445 | 1350.1289 | 2083.412 | 3190.2883 | 4417.1851 | 5917.8992 | 7722.017 | 10698.7595 | 13753.4143 | 16945.3965 | 20462.1297 | 24892.4635 | 26393.5381 | 31308.0826 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.5712 | 25.2681 | 27.2632 | 28.9314 | 30.4084 | 32.7411 | 34.8492 | 37.7772 | 40.8303 | 43.3239 | 45.6754 | 49.1702 | 51.7085 | 54.2664 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764
98% | 19.902 | 18.5582 | 20.3015 | 21.6795 | 23.3154 | 25.0025 | 26.7951 | 28.8474 | 31.2645 | 33.5296 | 35.9103 | 39.9674 | 41.3418 | 43.9378 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 |  | 52.2693 | 49.6893 | 53.6393 | 56.9422 | 59.8666 | 64.4851 | 68.6588 | 74.456 | 80.5009 | 85.4379 | 90.0937 | 97.0131 | 102.0386 | 107.103 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686
97% | 19.5287 | 18.1985 | 19.9242 | 21.2882 | 22.9075 | 24.5775 | 26.3519 | 28.3833 | 30.7759 | 33.0179 | 35.3745 | 39.3904 | 40.7509 | 43.3205 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 |  | 77.0943 | 73.2635 | 79.1285 | 84.0325 | 88.3745 | 95.232 | 101.429 | 110.0365 | 119.0118 | 126.3421 | 133.2548 | 143.5286 | 150.9903 | 158.5098 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765
95% | 18.9688 | 17.6591 | 19.3582 | 20.7012 | 22.2956 | 23.9399 | 25.687 | 27.6872 | 30.043 | 32.2505 | 34.5708 | 38.5249 | 39.8645 | 42.3945 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 |  | 150.2596 | 142.7159 | 154.2653 | 163.9225 | 172.4729 | 185.977 | 198.1802 | 215.1303 | 232.8048 | 247.2399 | 260.8526 | 281.0841 | 295.7779 | 310.5855 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738
90% | 158.9609 | 147.603 | 162.3376 | 173.9841 | 187.8104 | 202.0693 | 217.2201 | 234.5655 | 254.9946 | 274.138 | 294.2592 | 328.5491 | 340.1654 | 362.106 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 |  | 211.6379 | 200.7348 | 217.4274 | 231.3851 | 243.743 | 263.2606 | 280.8981 | 305.3963 | 330.9416 | 351.8047 | 371.4794 | 400.7202 | 421.9573 | 443.3589 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334
85% | 142.1633 | 131.4193 | 145.3574 | 156.3744 | 169.4533 | 182.9415 | 197.2733 | 213.6811 | 233.0059 | 251.1146 | 270.1482 | 302.5845 | 313.573 | 334.3276 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 |  | 362.6533 | 343.1717 | 372.9978 | 397.9373 | 420.0182 | 454.892 | 486.4063 | 530.1795 | 575.8234 | 613.1014 | 648.2559 | 700.5029 | 738.4491 | 776.6892 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038
80% | 139.2952 | 128.0395 | 142.6414 | 154.183 | 167.8848 | 182.0152 | 197.0295 | 214.2186 | 234.4637 | 253.4347 | 273.3746 | 307.3555 | 318.8672 | 340.6102 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 |  | 268.0967 | 252.9699 | 276.1289 | 295.4937 | 312.6389 | 339.7174 | 364.1873 | 398.1759 | 433.617 | 462.5623 | 489.8587 | 530.427 | 559.8911 | 589.5834 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418
75% | 193.0098 | 176.0923 | 198.0394 | 215.3867 | 235.9809 | 257.2193 | 279.7863 | 305.6221 | 336.051 | 364.5649 | 394.5352 | 445.6097 | 462.9121 | 495.5924 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 |  | 271.4717 | 255.2317 | 280.0951 | 300.8849 | 319.2919 | 348.3632 | 374.634 | 411.1238 | 449.1732 | 480.2486 | 509.5539 | 553.1077 | 584.7402 | 616.6176 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911
70% | 469.0487 | 423.5487 | 482.5757 | 529.2318 | 584.62 | 641.7413 | 702.4354 | 771.9211 | 853.7602 | 930.449 | 1011.0545 | 1148.42 | 1194.9552 | 1282.8494 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 |  | 354.8208 | 332.0323 | 366.9214 | 396.0942 | 421.9233 | 462.7169 | 499.5807 | 550.7843 | 604.1761 | 647.782 | 688.9039 | 750.0197 | 794.4073 | 839.1384 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303
65% | 533.1398 | 474.2012 | 550.662 | 611.0981 | 682.8453 | 756.8374 | 835.4577 | 925.4663 | 1031.4767 | 1130.8157 | 1235.2282 | 1413.165 | 1473.4444 | 1587.2983 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 |  | 378.0426 | 351.5215 | 392.1251 | 426.0763 | 456.136 | 503.6113 | 546.5132 | 606.1035 | 668.2406 | 718.9887 | 766.8461 | 837.9723 | 889.6303 | 941.6881 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425
60% | 1667.6879 | 1447.6916 | 1733.0919 | 1958.678 | 2226.4845 | 2502.6704 | 2796.1316 | 3132.1009 | 3527.7995 | 3898.5961 | 4288.3305 | 4952.5041 | 5177.5054 | 5602.481 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 |  | 843.9098 | 777.607 | 879.116 | 963.9939 | 1039.1433 | 1157.8315 | 1265.0862 | 1414.062 | 1569.4047 | 1696.2751 | 1815.9186 | 1993.734 | 2122.8789 | 2253.0235 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094
55% | 2514.8345 | 2085.7224 | 2642.408 | 3082.4232 | 3604.7912 | 4143.5036 | 4715.9123 | 5371.2346 | 6143.0617 | 6866.3161 | 7626.5097 | 8922.0086 | 9360.8832 | 10189.8163 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 |  | 642.3969 | 583.6576 | 673.587 | 748.7826 | 815.3594 | 920.5083 | 1015.528 | 1147.5095 | 1285.1317 | 1397.5294 | 1503.5247 | 1661.056 | 1775.4688 | 1890.7673 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924
50% | 2944.1269 | 2171.9912 | 3173.6801 | 3965.4346 | 4905.3732 | 5874.7215 | 6904.7022 | 8083.8762 | 9472.6864 | 10774.0959 | 12141.9731 | 14473.068 | 15262.7701 | 16754.3358 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 |  | 1156.1376 | 1024.8091 | 1225.8721 | 1393.9931 | 1542.8446 | 1777.9352 | 1990.3789 | 2285.4613 | 2593.155 | 2844.4523 | 3081.435 | 3433.6413 | 3689.4439 | 3947.2265 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428
45% | 1108.4231 | 443.0694 | 1353.4228 | 2204.0046 | 3213.7805 | 4255.1512 | 5361.6593 | 6628.4458 | 8120.4444 | 9518.5484 | 10988.0587 | 13492.3535 | 14340.7305 | 15943.1192 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 |  | 1939.0178 | 1627.346 | 2104.5134 | 2503.5023 | 2856.7601 | 3414.6827 | 3918.8591 | 4619.1556 | 5349.3816 | 5945.7663 | 6508.1793 | 7344.0436 | 7951.1202 | 8562.8961 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621
40% |  |  | 7.3214 | 300.2304 | 1157.9309 | 2547.9279 | 4191.5383 | 6073.2266 | 8289.4458 | 10366.1936 | 12549.0086 | 16268.8956 | 17529.0771 | 19909.2702 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 |  | 1665.5761 | 1116.1967 | 1957.2926 | 2660.5844 | 3283.2668 | 4266.7086 | 5155.4129 | 6389.8151 | 7676.9738 | 8728.2121 | 9719.5692 | 11192.9347 | 12263.0198 | 13341.388 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006
35% | [5 empty] | 11.585 | 446.2949 | 1644.5809 | 3860.0801 | 6143.4967 | 8543.5357 | 12633.6093 | 14019.1986 | 16636.2579 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 |  | 91.8208 | 1.3905 | 194.4116 | 584.94 | 1085.9465 | 2064.329 | 2960.5014 | 4205.2768 | 5503.2519 | 6563.3242 | 7563.0119 | 9048.7587 | 10127.8361 | 11215.2662 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798
30% | [8 empty] | 9.221 | 171.1327 | 536.9198 | 1523.9285 | 1890.3492 | 2582.4336 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | [6 empty] | 150.8022 | 745.6853 | 2229.0514 | 4368.6458 | 6166.1952 | 7861.3513 | 10380.7107 | 12210.4866 | 14054.4262 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485
25% | [11 empty] | 28.8835 | 106.5455 | 374.8407 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | [9 empty] | 149.9073 | 840.9199 | 1952.4029 | 4324.797 | 6462.3758 | 8651.8252 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509
20% | [43 empty] | 15.4293 | 113.8997 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9929.0896 | 7683.7944 | 10651.1216 | 13414.698 | 17205.4734 | 21631.9035 | 26924.275 | 33683.8576 | 42458.5743 | 51041.6943 | 60258.7914 | 76358.8177 | 81912.9341 | 92524.9915 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | E @ R (MWh) | 8491.7765 | 7157.6056 | 9254.7848 | 11237.4964 | 13148.1944 | 16503.7942 | 20006.7886 | 25529.4948 | 32030.9718 | 37959.506 | 44010.1673 | 53723.2218 | 61207.65 | 68868.2589 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388
Option 7 Summer POE50 W E @ R (MWh) N 2 | 6950.3627 | 5378.6561 | 7455.7851 | 9390.2886 | 12043.8314 | 15142.3325 | 18846.9925 | 23578.7003 | 29721.002 | 35729.186 | 42181.154 | 53451.1724 | 57339.0539 | 64767.494 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 2547.5329 | 2147.2817 | 2776.4354 | 3371.2489 | 3944.4583 | 4951.1383 | 6002.0366 | 7658.8484 | 9609.2915 | 11387.8518 | 13203.0502 | 16116.9665 | 18362.295 | 20660.4777 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 15.9 | 14.2872 | 16.81 | 20.0388 | 23.1651 | 25.9461 | 29.7718 | 33.955 | 38.2396 | 42.4859 | 46.258 | 50.3713 | 51.9326 | 57.2535 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 | 62.7583 |  | 19.0877 | 17.4876 | 20.1545 | 23.4232 | 26.4701 | 29.7154 | 33.1297 | 38.0063 | 42.2562 | 46.2644 | 50.4308 | 55.4278 | 57.0912 | 62.481 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044 | 67.5044
98% | 7.7241 | 6.9258 | 8.1744 | 9.7727 | 11.3201 | 12.6966 | 14.5902 | 16.6608 | 18.7816 | 20.8834 | 22.7505 | 24.7865 | 25.5593 | 28.193 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 | 30.9177 |  | 9.3019 | 8.5099 | 9.8299 | 11.4479 | 12.956 | 14.5623 | 16.2523 | 18.6661 | 20.7697 | 22.7537 | 24.8159 | 27.2893 | 28.1126 | 30.7805 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669 | 33.2669
97% | 14.9962 | 13.4158 | 15.8878 | 19.0518 | 22.1153 | 24.8403 | 28.5891 | 32.6883 | 36.8867 | 41.0476 | 44.744 | 48.7746 | 50.3045 | 55.5185 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 | 60.9126 |  | 18.1198 | 16.5518 | 19.1651 | 22.3682 | 25.3538 | 28.5339 | 31.8796 | 36.6581 | 40.8226 | 44.7503 | 48.8328 | 53.7295 | 55.3594 | 60.6409 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633 | 65.5633
95% | 21.4775 | 19.1434 | 22.7943 | 27.4673 | 31.9918 | 36.0164 | 41.5532 | 47.6073 | 53.8081 | 59.9534 | 65.4127 | 71.3656 | 73.6252 | 81.3258 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 | 89.2925 |  | 26.0908 | 23.775 | 27.6347 | 32.3653 | 36.7748 | 41.4715 | 46.4129 | 53.4705 | 59.6211 | 65.4219 | 71.4516 | 78.6835 | 81.0908 | 88.8912 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612 | 96.1612
90% | 19.1049 | 16.8559 | 20.3737 | 24.8763 | 29.2359 | 33.1138 | 38.4487 | 44.2821 | 50.2568 | 56.1781 | 61.4383 | 67.1741 | 69.3514 | 76.7712 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 | 84.4475 |  | 23.55 | 21.3187 | 25.0376 | 29.5958 | 33.8445 | 38.37 | 43.1312 | 49.9315 | 55.8579 | 61.4472 | 67.257 | 74.2253 | 76.5448 | 84.0608 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658 | 91.0658
85% | 188.5861 | 163.0564 | 202.9891 | 254.0993 | 303.5863 | 347.6059 | 408.1639 | 474.3809 | 542.2018 | 609.4168 | 669.1272 | 734.2369 | 758.9514 | 843.1765 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 | 930.313 |  | 239.0441 | 213.7155 | 255.9301 | 307.6717 | 355.9007 | 407.2711 | 461.3172 | 538.5094 | 605.7822 | 669.2284 | 735.178 | 814.2772 | 840.6065 | 925.9234 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392 | 1005.4392
80% | 378.0005 | 316.4863 | 412.7049 | 535.8562 | 655.0962 | 761.1625 | 907.0785 | 1066.6301 | 1230.0461 | 1392.0022 | 1535.8758 | 1692.7592 | 1752.3093 | 1955.2518 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 | 2165.2092 |  | 499.5803 | 438.5505 | 540.2675 | 664.9401 | 781.1492 | 904.9273 | 1035.1526 | 1221.1492 | 1383.2444 | 1536.1197 | 1695.0267 | 1885.6182 | 1949.0592 | 2154.6323 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276 | 2346.2276
75% | 851.9655 | 672.3262 | 953.3124 | 1312.9498 | 1661.1654 | 1970.9098 | 2397.0265 | 2862.9635 | 3340.1856 | 3813.1444 | 4233.297 | 4691.442 | 4865.3456 | 5457.9964 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 | 6071.1329 |  | 1207.0139 | 1028.7891 | 1325.8323 | 1689.9124 | 2029.2767 | 2390.7446 | 2771.0402 | 3314.204 | 3787.5692 | 4234.0092 | 4698.0637 | 5254.6461 | 5439.9123 | 6040.2452 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592 | 6599.7592
70% | 1229.6514 | 838.9064 | 1450.0975 | 2232.3676 | 2989.7935 | 3663.5381 | 4590.4118 | 5603.901 | 6641.937 | 7670.6997 | 8584.6003 | 9581.1407 | 9959.4095 | 11248.5219 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 | 12582.194 |  | 2001.9397 | 1614.2716 | 2260.3891 | 3052.3229 | 3790.4957 | 4576.7476 | 5403.9526 | 6585.4229 | 7615.0695 | 8586.1496 | 9595.544 | 10806.2017 | 11209.186 | 12515.0083 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428 | 13732.0428
65% | 545.9482 | 179.044 | 780.2029 | 1611.4739 | 2416.3444 | 3132.292 | 4117.2244 | 5194.1979 | 6297.2558 | 7390.4596 | 8361.6063 | 9420.5693 | 9822.5326 | 11192.3942 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 | 12609.6067 |  | 1366.6121 | 954.6607 | 1641.2505 | 2482.7906 | 3267.202 | 4102.7043 | 4981.7249 | 6237.2017 | 7331.3448 | 8363.2527 | 9435.8749 | 10722.3674 | 11150.5944 | 12538.2125 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813 | 13831.4813
60% | 8.8727 |  | 74.4011 | 747.9553 | 1573.7203 | 2308.2539 | 3318.7553 | 4423.6871 | 5555.3805 | 6676.9639 | 7673.3217 | 8759.7755 | 9172.1738 | 10577.5971 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 | 12031.6006 |  | 496.8079 | 162.7993 | 778.5049 | 1641.8914 | 2446.6663 | 3303.8582 | 4205.6983 | 5493.7674 | 6616.3145 | 7675.0108 | 8775.4784 | 10095.3683 | 10534.7121 | 11958.353 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951 | 13285.1951
55% |  |  |  | 32.0716 | 599.6383 | 1452.362 | 2630.7435 | 3919.2438 | 5238.9517 | 6546.87 | 7708.7583 | 8975.7107 | 9456.623 | 11095.5371 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 | 12791.1022 |  |  |  | 40.7106 | 675.5647 | 1613.7696 | 2613.3716 | 3665.0394 | 5167.1025 | 6476.1446 | 7710.728 | 8994.0224 | 10533.193 | 11045.5274 | 12705.6856 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633 | 14252.9633
50% | [5 empty] | 207.7028 | 1260.6583 | 2666.6676 | 4106.7306 | 5533.9289 | 6801.7793 | 8184.2757 | 8709.0464 | 10497.4266 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | 12347.6245 | [5 empty] | 304.0909 | 1241.702 | 2389.2801 | 4028.3289 | 5456.7534 | 6803.9287 | 8204.2574 | 9883.7977 | 10442.8561 | 12254.418 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048 | 13942.8048
45% | [6 empty] | 36.3146 | 916.1414 | 2624.9978 | 4361.2249 | 5903.601 | 7585.447 | 8223.8454 | 10399.4608 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | 12650.2789 | [6 empty] | 32.351 | 656.0457 | 2529.6198 | 4267.3388 | 5906.2158 | 7609.7553 | 9652.9638 | 10333.0742 | 12536.8906 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611 | 14590.8611
40% | [8 empty] | 409.8056 | 2216.6902 | 4565.0284 | 7145.9569 | 8125.6309 | 11464.2883 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | 14918.3505 | [8 empty] | 350.4931 | 2085.8253 | 4569.041 | 7183.26 | 10318.7284 | 11362.4128 | 14744.347 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306 | 17896.3306
35% | [10 empty] | 189.5467 | 1001.8484 | 1459.5503 | 3369.4171 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | 5386.0041 | [10 empty] | 190.3335 | 1017.8501 | 2700.6042 | 3309.939 | 5284.4155 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398 | 7124.6398
30% | FY38: 68.1292; FY39: 397.7914; FY40: 397.7914; FY41: 397.7914; FY42: 397.7914; FY43: 397.7914; FY44: 397.7914; FY45: 397.7914; FY46: 397.7914; FY47: 397.7914; FY48: 397.7914; FY49: 397.7914; FY50: 397.7914; FY51: 397.7914; FY52: 397.7914; FY53: 397.7914; FY54: 397.7914 | [12 empty] | 17.757 | 62.3815 | 375.2896 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588 | 869.4588
25% | [45 empty] | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715 | 0.088715
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 3282.2271 | 2240.4473 | 3957.7482 | 6827.9805 | 10317.1725 | 13976.4402 | 19819.3296 | 27303.0069 | 36185.4651 | 46431.9489 | 56467.1453 | 68035.6344 | 72576.1912 | 88468.2588 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | 105209.5367 | E @ R (MWh) | 5907.1482 | 4500.4298 | 6944.7067 | 10634.2942 | 14723.9503 | 19726.3308 | 25740.0567 | 35662.5315 | 45844.7143 | 56484.655 | 68207.0991 | 82974.8783 | 87978.4603 | 104360.2754 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854 | 119830.854
Option 8 Winter POE50 W E @ R (MWh) N 2 | 2297.559 | 1568.3131 | 2770.4237 | 4779.5863 | 7222.0207 | 9783.5081 | 13873.5307 | 19112.1048 | 25329.8256 | 32502.3642 | 39527.0017 | 47624.9441 | 50803.3338 | 61927.7812 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | 73646.6757 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 1772.1445 | 1350.1289 | 2083.412 | 3190.2883 | 4417.1851 | 5917.8992 | 7722.017 | 10698.7595 | 13753.4143 | 16945.3965 | 20462.1297 | 24892.4635 | 26393.5381 | 31308.0826 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562 | 35949.2562
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.5712 | 25.2681 | 27.2632 | 28.9314 | 30.4084 | 32.7411 | 34.8492 | 37.7772 | 40.8303 | 43.3239 | 45.6754 | 49.1702 | 51.7085 | 54.2664 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764 | 56.9764
98% | 19.902 | 18.5582 | 20.3015 | 21.6795 | 23.3154 | 25.0025 | 26.7951 | 28.8474 | 31.2645 | 33.5296 | 35.9103 | 39.9674 | 41.3418 | 43.9378 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 | 45.9223 |  | 52.2693 | 49.6893 | 53.6393 | 56.9422 | 59.8666 | 64.4851 | 68.6588 | 74.456 | 80.5009 | 85.4379 | 90.0937 | 97.0131 | 102.0386 | 107.103 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686 | 112.4686
97% | 19.5287 | 18.1985 | 19.9242 | 21.2882 | 22.9075 | 24.5775 | 26.3519 | 28.3833 | 30.7759 | 33.0179 | 35.3745 | 39.3904 | 40.7509 | 43.3205 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 | 45.2848 |  | 77.0943 | 73.2635 | 79.1285 | 84.0325 | 88.3745 | 95.232 | 101.429 | 110.0365 | 119.0118 | 126.3421 | 133.2548 | 143.5286 | 150.9903 | 158.5098 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765 | 166.4765
95% | 18.9688 | 17.6591 | 19.3582 | 20.7012 | 22.2956 | 23.9399 | 25.687 | 27.6872 | 30.043 | 32.2505 | 34.5708 | 38.5249 | 39.8645 | 42.3945 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 | 44.3287 |  | 150.2596 | 142.7159 | 154.2653 | 163.9225 | 172.4729 | 185.977 | 198.1802 | 215.1303 | 232.8048 | 247.2399 | 260.8526 | 281.0841 | 295.7779 | 310.5855 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738 | 326.2738
90% | 158.9609 | 147.603 | 162.3376 | 173.9841 | 187.8104 | 202.0693 | 217.2201 | 234.5655 | 254.9946 | 274.138 | 294.2592 | 328.5491 | 340.1654 | 362.106 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 | 378.8785 |  | 211.6379 | 200.7348 | 217.4274 | 231.3851 | 243.743 | 263.2606 | 280.8981 | 305.3963 | 330.9416 | 351.8047 | 371.4794 | 400.7202 | 421.9573 | 443.3589 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334 | 466.0334
85% | 142.1633 | 131.4193 | 145.3574 | 156.3744 | 169.4533 | 182.9415 | 197.2733 | 213.6811 | 233.0059 | 251.1146 | 270.1482 | 302.5845 | 313.573 | 334.3276 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 | 350.1934 |  | 362.6533 | 343.1717 | 372.9978 | 397.9373 | 420.0182 | 454.892 | 486.4063 | 530.1795 | 575.8234 | 613.1014 | 648.2559 | 700.5029 | 738.4491 | 776.6892 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038 | 817.2038
80% | 139.2952 | 128.0395 | 142.6414 | 154.183 | 167.8848 | 182.0152 | 197.0295 | 214.2186 | 234.4637 | 253.4347 | 273.3746 | 307.3555 | 318.8672 | 340.6102 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 | 357.2315 |  | 268.0967 | 252.9699 | 276.1289 | 295.4937 | 312.6389 | 339.7174 | 364.1873 | 398.1759 | 433.617 | 462.5623 | 489.8587 | 530.427 | 559.8911 | 589.5834 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418 | 621.0418
75% | 193.0098 | 176.0923 | 198.0394 | 215.3867 | 235.9809 | 257.2193 | 279.7863 | 305.6221 | 336.051 | 364.5649 | 394.5352 | 445.6097 | 462.9121 | 495.5924 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 | 520.5748 |  | 271.4717 | 255.2317 | 280.0951 | 300.8849 | 319.2919 | 348.3632 | 374.634 | 411.1238 | 449.1732 | 480.2486 | 509.5539 | 553.1077 | 584.7402 | 616.6176 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911 | 650.3911
70% | 469.0487 | 423.5487 | 482.5757 | 529.2318 | 584.62 | 641.7413 | 702.4354 | 771.9211 | 853.7602 | 930.449 | 1011.0545 | 1148.42 | 1194.9552 | 1282.8494 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 | 1350.0399 |  | 354.8208 | 332.0323 | 366.9214 | 396.0942 | 421.9233 | 462.7169 | 499.5807 | 550.7843 | 604.1761 | 647.782 | 688.9039 | 750.0197 | 794.4073 | 839.1384 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303 | 886.5303
65% | 533.1398 | 474.2012 | 550.662 | 611.0981 | 682.8453 | 756.8374 | 835.4577 | 925.4663 | 1031.4767 | 1130.8157 | 1235.2282 | 1413.165 | 1473.4444 | 1587.2983 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 | 1674.3338 |  | 378.0426 | 351.5215 | 392.1251 | 426.0763 | 456.136 | 503.6113 | 546.5132 | 606.1035 | 668.2406 | 718.9887 | 766.8461 | 837.9723 | 889.6303 | 941.6881 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425 | 996.8425
60% | 1667.6879 | 1447.6916 | 1733.0919 | 1958.678 | 2226.4845 | 2502.6704 | 2796.1316 | 3132.1009 | 3527.7995 | 3898.5961 | 4288.3305 | 4952.5041 | 5177.5054 | 5602.481 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 | 5927.3529 |  | 843.9098 | 777.607 | 879.116 | 963.9939 | 1039.1433 | 1157.8315 | 1265.0862 | 1414.062 | 1569.4047 | 1696.2751 | 1815.9186 | 1993.734 | 2122.8789 | 2253.0235 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094 | 2390.9094
55% | 2514.8345 | 2085.7224 | 2642.408 | 3082.4232 | 3604.7912 | 4143.5036 | 4715.9123 | 5371.2346 | 6143.0617 | 6866.3161 | 7626.5097 | 8922.0086 | 9360.8832 | 10189.8163 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 | 10823.4928 |  | 642.3969 | 583.6576 | 673.587 | 748.7826 | 815.3594 | 920.5083 | 1015.528 | 1147.5095 | 1285.1317 | 1397.5294 | 1503.5247 | 1661.056 | 1775.4688 | 1890.7673 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924 | 2012.924
50% | 2944.1269 | 2171.9912 | 3173.6801 | 3965.4346 | 4905.3732 | 5874.7215 | 6904.7022 | 8083.8762 | 9472.6864 | 10774.0959 | 12141.9731 | 14473.068 | 15262.7701 | 16754.3358 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 | 17894.5606 |  | 1156.1376 | 1024.8091 | 1225.8721 | 1393.9931 | 1542.8446 | 1777.9352 | 1990.3789 | 2285.4613 | 2593.155 | 2844.4523 | 3081.435 | 3433.6413 | 3689.4439 | 3947.2265 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428 | 4220.3428
45% | 1108.4231 | 443.0694 | 1353.4228 | 2204.0046 | 3213.7805 | 4255.1512 | 5361.6593 | 6628.4458 | 8120.4444 | 9518.5484 | 10988.0587 | 13492.3535 | 14340.7305 | 15943.1192 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 | 17168.0625 |  | 1939.0178 | 1627.346 | 2104.5134 | 2503.5023 | 2856.7601 | 3414.6827 | 3918.8591 | 4619.1556 | 5349.3816 | 5945.7663 | 6508.1793 | 7344.0436 | 7951.1202 | 8562.8961 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621 | 9211.0621
40% |  |  | 7.3214 | 300.2304 | 1157.9309 | 2547.9279 | 4191.5383 | 6073.2266 | 8289.4458 | 10366.1936 | 12549.0086 | 16268.8956 | 17529.0771 | 19909.2702 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 | 21728.8046 |  | 1665.5761 | 1116.1967 | 1957.2926 | 2660.5844 | 3283.2668 | 4266.7086 | 5155.4129 | 6389.8151 | 7676.9738 | 8728.2121 | 9719.5692 | 11192.9347 | 12263.0198 | 13341.388 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006 | 14483.9006
35% | [5 empty] | 11.585 | 446.2949 | 1644.5809 | 3860.0801 | 6143.4967 | 8543.5357 | 12633.6093 | 14019.1986 | 16636.2579 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 | 18636.8643 |  | 91.8208 | 1.3905 | 194.4116 | 584.94 | 1085.9465 | 2064.329 | 2960.5014 | 4205.2768 | 5503.2519 | 6563.3242 | 7563.0119 | 9048.7587 | 10127.8361 | 11215.2662 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798 | 12367.3798
30% | [8 empty] | 9.221 | 171.1327 | 536.9198 | 1523.9285 | 1890.3492 | 2582.4336 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | 3111.4963 | [6 empty] | 150.8022 | 745.6853 | 2229.0514 | 4368.6458 | 6166.1952 | 7861.3513 | 10380.7107 | 12210.4866 | 14054.4262 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485 | 16008.0485
25% | [11 empty] | 28.8835 | 106.5455 | 374.8407 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | 677.0151 | [9 empty] | 149.9073 | 840.9199 | 1952.4029 | 4324.797 | 6462.3758 | 8651.8252 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509 | 10971.509
20% | [43 empty] | 15.4293 | 113.8997 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243 | 308.4243
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9929.0896 | 7683.7944 | 10651.1216 | 13414.698 | 17205.4734 | 21631.9035 | 26924.275 | 33683.8576 | 42458.5743 | 51041.6943 | 60258.7914 | 76358.8177 | 81912.9341 | 92524.9915 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | 100734.4367 | E @ R (MWh) | 8491.7765 | 7157.6056 | 9254.7848 | 11237.4964 | 13148.1944 | 16503.7942 | 20006.7886 | 25529.4948 | 32030.9718 | 37959.506 | 44010.1673 | 53723.2218 | 61207.65 | 68868.2589 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388 | 77074.7388
Option 8 Summer POE50 W E @ R (MWh) N 2 | 6950.3627 | 5378.6561 | 7455.7851 | 9390.2886 | 12043.8314 | 15142.3325 | 18846.9925 | 23578.7003 | 29721.002 | 35729.186 | 42181.154 | 53451.1724 | 57339.0539 | 64767.494 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | 70514.1057 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 2547.5329 | 2147.2817 | 2776.4354 | 3371.2489 | 3944.4583 | 4951.1383 | 6002.0366 | 7658.8484 | 9609.2915 | 11387.8518 | 13203.0502 | 16116.9665 | 18362.295 | 20660.4777 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216 | 23122.4216

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-CLN-TRNFMR-9000006730 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 2 Pof | DS-CLN-TRNFMR-9000001306 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 3 Pof | DS-CLN-TRNFMR-XXXXXXXXXXXX | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543%
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.3954% | 0.3997% | 0.4449% | 0.4933% | 0.545% | 0.6% | 0.6585% | 0.7205% | 0.7861% | 0.8553% | 0.9283% | 1.005% | 1.086% | 1.17% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259%
N-1 Risk |  | 0.1525% | 0.1542% | 0.1716% | 0.1903% | 0.2103% | 0.2315% | 0.254% | 0.278% | 0.3033% | 0.33% | 0.3581% | 0.3878% | 0.4189% | 0.4515% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856%
N-2 Risk |  | 9.757e-05% | 0.0001015% | 0.0001271% | 0.0001578% | 0.0001945% | 0.000238% | 0.0002892% | 0.0003491% | 0.0004187% | 0.0004994% | 0.0005922% | 0.0006986% | 0.0008201% | 0.0009581% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114%
N Risk |  | 99.85% | 99.85% | 99.83% | 99.81% | 99.79% | 99.77% | 99.75% | 99.72% | 99.7% | 99.67% | 99.64% | 99.61% | 99.58% | 99.55% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0.045053 | 4.5065 | 22.7062 | 55.3723 | 94.4969 | 146.6262 | 271.7549 | 363.3351 | 505.7951 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.18975 | 0.13589 | 0.24703 | 0.38728 | 0.57911 | 0.90495 | 1.3434 | 2.1621 | 3.628 | 5.9664 | 10.1969 | 21.3354 | 29.5025 | 53.8039 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.016811 | 0.013501 | 0.024259 | 0.041 | 0.066949 | 0.10583 | 0.16614 | 0.26261 | 0.40397 | 0.59195 | 0.83766 | 1.2189 | 1.541 | 2.0979 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677
Total EUE (MWh) - Option 1 | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744
Cost of EUE ($) - Option 1 | 9102.603 | 6583.2133 | 11954.7133 | 18873.1026 | 28469.9314 | 46527.7581 | 265107.9226 | 1107442.1562 | 2617764.1441 | 4453195.1399 | 6947626.053 | 12969302.8638 | 17379055.3216 | 24752263.006 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715
Hours at Risk pA. (Hrs) (N) | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.97256 | 5.1324 | 8.5358 | 14.9646 | 20.2589 | 26.3096 | 35.3855 | 36.2771 | 60.1044 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466 | 87.4466
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0136 | 23.4131 | 47.442 | 103.5952 | 158.3602 | 241.3161 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687 | 343.7687
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.18975 | 0.13589 | 0.24703 | 0.10098 | 0.16829 | 0.3177 | 0.53662 | 0.94028 | 1.5767 | 2.4605 | 3.8953 | 7.5646 | 10.5807 | 20.1277 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339 | 37.6339
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.016811 | 0.013501 | 0.024259 | 0.012724 | 0.02439 | 0.044378 | 0.078355 | 0.13826 | 0.232 | 0.36313 | 0.54469 | 0.85095 | 1.1003 | 1.565 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368 | 2.1368
Total EUE (MWh) - Option 2 | 0.20656 | 0.14939 | 0.27129 | 0.11371 | 0.19268 | 0.36207 | 0.61497 | 1.0785 | 8.8223 | 26.2367 | 51.882 | 112.0107 | 170.0411 | 263.0088 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394 | 383.5394
Cost of EUE ($) - Option 2 | 9102.603 | 6583.2133 | 11954.7133 | 5010.6965 | 8490.7982 | 15955.5079 | 27100.0383 | 47528.2171 | 388770.412 | 1156169.0417 | 2286280.8737 | 4935967.1577 | 7493191.5396 | 11589994.4072 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189 | 16901407.189
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0.045053 | 4.5065 | 22.7062 | 55.3723 | 94.4969 | 146.6262 | 271.7549 | 363.3351 | 505.7951 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.18975 | 0.13589 | 0.24703 | 0.38728 | 0.57911 | 0.90495 | 1.3434 | 2.1621 | 3.628 | 5.9664 | 10.1969 | 21.3354 | 29.5025 | 53.8039 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.016811 | 0.013501 | 0.024259 | 0.041 | 0.066949 | 0.10583 | 0.16614 | 0.26261 | 0.40397 | 0.59195 | 0.83766 | 1.2189 | 1.541 | 2.0979 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677
Total EUE (MWh) - Option 3 | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744
Cost of EUE ($) - Option 3 | 9102.603 | 6583.2133 | 11954.7133 | 18873.1026 | 28469.9314 | 46527.7581 | 265107.9226 | 1107442.1562 | 2617764.1441 | 4453195.1399 | 6947626.053 | 12969302.8638 | 17379055.3216 | 24752263.006 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69577 | 10.7424 | 27.9275 | 70.6464 | 115.2076 | 180.1373 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625 | 265.3625
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.18975 | 0.13589 | 0.24703 | 0.053473 | 0.10054 | 0.20707 | 0.36527 | 0.68528 | 1.2023 | 1.876 | 2.9177 | 5.6001 | 7.798 | 14.1878 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266 | 26.7266
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.016811 | 0.013501 | 0.024259 | 0.0076197 | 0.015353 | 0.03013 | 0.056748 | 0.1058 | 0.18526 | 0.29864 | 0.4583 | 0.73721 | 0.9624 | 1.3944 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308 | 1.9308
Total EUE (MWh) - Option 4 | 0.20656 | 0.14939 | 0.27129 | 0.061093 | 0.11589 | 0.2372 | 0.42202 | 0.79108 | 2.0833 | 12.917 | 31.3035 | 76.9837 | 123.968 | 195.7195 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02 | 294.02
Cost of EUE ($) - Option 4 | 9102.603 | 6583.2133 | 11954.7133 | 2692.1886 | 5107.0493 | 10452.7549 | 18597.1018 | 34860.2886 | 91804.3844 | 569212.8742 | 1379448.7296 | 3392435.5148 | 5462888.1917 | 8624760.7525 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035 | 12956559.0035
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0.045053 | 4.5065 | 22.7062 | 55.3723 | 94.4969 | 146.6262 | 271.7549 | 363.3351 | 505.7951 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.18975 | 0.13589 | 0.24703 | 0.38728 | 0.57911 | 0.90495 | 1.3434 | 2.1621 | 3.628 | 5.9664 | 10.1969 | 21.3354 | 29.5025 | 53.8039 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.016811 | 0.013501 | 0.024259 | 0.041 | 0.066949 | 0.10583 | 0.16614 | 0.26261 | 0.40397 | 0.59195 | 0.83766 | 1.2189 | 1.541 | 2.0979 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677
Total EUE (MWh) - Option 5 | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744
Cost of EUE ($) - Option 5 | 9102.603 | 6583.2133 | 11954.7133 | 18873.1026 | 28469.9314 | 46527.7581 | 265107.9226 | 1107442.1562 | 2617764.1441 | 4453195.1399 | 6947626.053 | 12969302.8638 | 17379055.3216 | 24752263.006 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.885 | 16.8293 | 37.2359 | 65.5196 | 129.1959 | 187.2111 | 273.6149 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944 | 376.944
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.094237 | 0.055841 | 0.11206 | 0.18624 | 0.29336 | 0.49696 | 0.77318 | 1.2472 | 2.0014 | 3.0832 | 4.8458 | 9.2271 | 12.6864 | 23.6571 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149 | 42.5149
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0093832 | 0.0063705 | 0.012351 | 0.022345 | 0.038847 | 0.064432 | 0.10603 | 0.17467 | 0.27801 | 0.41977 | 0.6126 | 0.9245 | 1.1774 | 1.6453 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148 | 2.2148
Total EUE (MWh) - Option 6 | 0.10362 | 0.062212 | 0.12442 | 0.20859 | 0.33221 | 0.56139 | 0.87922 | 3.3069 | 19.1087 | 40.7389 | 70.978 | 139.3475 | 201.0749 | 298.9173 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737 | 421.6737
Cost of EUE ($) - Option 6 | 4566.2078 | 2741.4859 | 5482.6296 | 9191.7154 | 14639.5216 | 24738.7596 | 38744.3552 | 145723.8657 | 842062.4383 | 1795237.9861 | 3127781.6087 | 6140616.4979 | 8860753.4734 | 13172368.3037 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248 | 18581870.2248
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0.045053 | 4.5065 | 22.7062 | 55.3723 | 94.4969 | 146.6262 | 271.7549 | 363.3351 | 505.7951 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.18975 | 0.13589 | 0.24703 | 0.38728 | 0.57911 | 0.90495 | 1.3434 | 2.1621 | 3.628 | 5.9664 | 10.1969 | 21.3354 | 29.5025 | 53.8039 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.016811 | 0.013501 | 0.024259 | 0.041 | 0.066949 | 0.10583 | 0.16614 | 0.26261 | 0.40397 | 0.59195 | 0.83766 | 1.2189 | 1.541 | 2.0979 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677
Total EUE (MWh) - Option 7 | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744
Cost of EUE ($) - Option 7 | 9102.603 | 6583.2133 | 11954.7133 | 18873.1026 | 28469.9314 | 46527.7581 | 265107.9226 | 1107442.1562 | 2617764.1441 | 4453195.1399 | 6947626.053 | 12969302.8638 | 17379055.3216 | 24752263.006 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0.045053 | 4.5065 | 22.7062 | 55.3723 | 94.4969 | 146.6262 | 271.7549 | 363.3351 | 505.7951 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965 | 681.0965
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.18975 | 0.13589 | 0.24703 | 0.38728 | 0.57911 | 0.90495 | 1.3434 | 2.1621 | 3.628 | 5.9664 | 10.1969 | 21.3354 | 29.5025 | 53.8039 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102 | 88.4102
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.016811 | 0.013501 | 0.024259 | 0.041 | 0.066949 | 0.10583 | 0.16614 | 0.26261 | 0.40397 | 0.59195 | 0.83766 | 1.2189 | 1.541 | 2.0979 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677 | 2.7677
Total EUE (MWh) - Option 8 | 0.20656 | 0.14939 | 0.27129 | 0.42828 | 0.64606 | 1.0558 | 6.016 | 25.1309 | 59.4043 | 101.0552 | 157.6607 | 294.3091 | 394.3786 | 561.6969 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744 | 772.2744
Cost of EUE ($) - Option 8 | 9102.603 | 6583.2133 | 11954.7133 | 18873.1026 | 28469.9314 | 46527.7581 | 265107.9226 | 1107442.1562 | 2617764.1441 | 4453195.1399 | 6947626.053 | 12969302.8638 | 17379055.3216 | 24752263.006 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715 | 34031769.7715