## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 162349945.5089 | 67.2% | 33.0819
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 70185987.1383 | 29.05% | 9.9906
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 3438927.3871 | 1.423% | 0.4767
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 5622421.9462 | 2.327% | 0.5178
[5 empty] | 241597281.9805 |  | 44.0669
Customer No. and Vol per Feeder | [6 empty] | 44066.9381 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 70185987.1383 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 1.0764 | E@R MWh | 1.0764
RESIDENTL | 162349945.5089 | [14 empty] | cost of EUE ($) | 47432.9909 | cost of EUE ($M) | 0.047433
FARM | 5622421.9462
INDUSTRIAL | 3438927.3871
Forecast (FCT)
Forecast | 2031
Summer POE50 | 123.2461
Summer POE10 | 141.634
Winter POE50 | 107.1286
Winter POE10 | 112.2902
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 16.69 |  | Summer POE50 | 104.8894 |  |  | 100% | 0 | 104.8894 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 123.2773 |  |  | 99% | 0 | 103.8405 | 99% |  | 99% | 0 | 99% | 0
Embedded Generation |  |  | Winter POE50 | 88.7719 |  |  | 98% | 0.37816 | 102.7916 | 98% |  | 98% | 5.3382 | 98% | 22.2043
|  |  | Winter POE10 | 93.9335 |  |  | 97% | 0.75633 | 101.7427 | 97% |  | 97% | 4.9415 | 97% | 21.8077
Year | 2031 | [5 empty] | 95% | 1.1345 | 99.6449 | 95% |  | 95% | 4.3466 | 95% | 21.2127
Capacity | 0 | [5 empty] | 90% | 4.538 | 94.4005 | 90% |  | 90% | 26.6244 | 90% | 178.4195
[7 empty] | 85% | 7.9414 | 89.156 | 85% |  | 85% | 8.7756 | 85% | 160.5701
Demand Mangement | [6 empty] | 80% | 11.7231 | 83.9115 | 80% |  | 80% |  | 80% | 158.5785
[7 empty] | 75% | 17.7737 | 78.6671 | 75% |  | 75% |  | 75% | 221.9933
Year | 2031 | [5 empty] | 70% | 35.1693 | 73.4226 | 70% |  | 70% |  | 70% | 547.0002
Capacity | 1.6667 | [5 empty] | 65% | 59.3718 | 68.1781 | 65% |  | 65% |  | 65% | 634.1144
[7 empty] | 60% | 156.9382 | 62.9336 | 60% |  | 60% |  | 60% | 2044.5895
LDC | [6 empty] | 55% | 363.794 | 57.6892 | 55% |  | 55% |  | 55% | 3249.9973
[7 empty] | 50% | 771.4551 | 52.4447 | 50% |  | 50% |  | 50% | 4266.9641
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 1255.5054 | 47.2002 | 45% |  | 45% |  | 45% | 2527.9377
100% | 0% | 0 |  |  |  |  | 40% | 2059.1045 | 41.9558 | 40% |  | 40% |  | 40% | 518.0035
99% | 0% | 0 |  |  |  |  | 35% | 3060.4836 | 36.7113 | 35% |  | 35% |  | 35%
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3366.0403 | 31.4668 | 30% |  | 30% |  | 30%
97% | 0.01722% | 0.75633 |  |  |  |  | 25% | 3686.3454 | 26.2224 | 25% |  | 25% |  | 25%
95% | 0.02583% | 1.1345 |  |  |  |  | 20% | 4028.5841 | 20.9779 | 20% |  | 20% |  | 20%
90% | 0.1033% | 4.538 |  |  |  |  | 15% | 4345.1076 | 15.7334 | 15% |  | 15% |  | 15%
85% | 0.1808% | 7.9414 |  |  |  |  | 10% | 4381.0332 | 10.4889 | 10% |  | 10% |  | 10%
80% | 0.2669% | 11.7231 |  |  |  |  | 5% | 4391.6218 | 5.2445 | 5% |  | 5% |  | 5%
75% | 0.4047% | 17.7737 |  |  |  |  | 9.992e-14% | 4391.6218 | 1.0481e-13 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
70% | 0.8008% | 35.1693 | [7 empty] | Total E@R | 0 | Total E@R | 50.0263 | Total E@R | 14573.3927
65% | 1.352% | 59.3718 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.17748 | Total WE@R | 0.088282
60% | 3.573% | 156.9382 |  |  |  |  | MD Weighted LDC
55% | 8.283% | 363.794
50% | 17.57% | 771.4551 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 28.59% | 1255.5054 |  |  |  |  | 100% | 0 | 123.2773 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 46.88% | 2059.1045 |  |  |  |  | 99% | 0.37816 | 122.0445
35% | 69.68% | 3060.4836 |  |  |  |  | 98% | 1.1345 | 120.8117 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 76.64% | 3366.0403 |  |  |  |  | 97% | 2.269 | 119.579 | 100% |  | 100% |  | 100%
25% | 83.93% | 3686.3454 |  |  |  |  | 95% | 4.538 | 117.1134 | 99% |  | 99% | 12.6537 | 99% | 29.5198
20% | 91.73% | 4028.5841 |  |  |  |  | 90% | 7.9414 | 110.9496 | 98% |  | 98% | 24.3751 | 98% | 58.1073
15% | 98.93% | 4345.1076 |  |  |  |  | 85% | 14.3702 | 104.7857 | 97% |  | 97% | 35.164 | 97% | 85.7624
10% | 99.75% | 4381.0332 |  |  |  |  | 80% | 19.6645 | 98.6218 | 95% |  | 95% | 66.1323 | 95% | 167.3291
5% | 99.99% | 4391.6218 |  |  |  |  | 75% | 25.7152 | 92.458 | 90% |  | 90% | 84.5135 | 90% | 236.3086
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 34.7911 | 86.2941 | 85% |  | 85% | 120.0103 | 85% | 406.7345
[7 empty] | 65% | 46.136 | 80.1302 | 80% |  | 80% | 66.1987 | 80% | 302.3245
[7 empty] | 60% | 76.7673 | 73.9664 | 75% |  | 75% | 38.3604 | 75% | 308.2184
[7 empty] | 55% | 106.2642 | 67.8025 | 70% |  | 70% | 7.8145 | 70% | 406.3848
LDC | [6 empty] | 50% | 178.4935 | 61.6386 | 65% |  | 65% |  | 65% | 438.0523
[7 empty] | 45% | 367.9538 | 55.4748 | 60% |  | 60% |  | 60% | 993.9341
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 741.202 | 49.3109 | 55% |  | 55% |  | 55% | 775.3074
100% | 0% | 0 |  |  |  |  | 35% | 1167.7713 | 43.1471 | 50% |  | 50% |  | 50% | 1453.2969
99% | 0.00861% | 0.37816 |  |  |  |  | 30% | 2002.3799 | 36.9832 | 45% |  | 45% |  | 45% | 2644.2434
98% | 0.02583% | 1.1345 |  |  |  |  | 25% | 3173.5547 | 30.8193 | 40% |  | 40% |  | 40% | 2908.6668
97% | 0.05166% | 2.269 |  |  |  |  | 20% | 3477.5988 | 24.6555 | 35% |  | 35% |  | 35% | 767.9228
95% | 0.1033% | 4.538 |  |  |  |  | 15% | 3788.4498 | 18.4916 | 30% |  | 30% |  | 30%
90% | 0.1808% | 7.9414 |  |  |  |  | 10% | 4317.5016 | 12.3277 | 25% |  | 25% |  | 25%
85% | 0.3272% | 14.3702 |  |  |  |  | 5% | 4391.6218 | 6.1639 | 20% |  | 20% |  | 20%
80% | 0.4477% | 19.6645 |  |  |  |  | 9.992e-14% | 4391.6218 | 1.2318e-13 | 15% |  | 15% |  | 15%
75% | 0.5855% | 25.7152 | [7 empty] | 10% |  | 10% |  | 10%
70% | 0.7921% | 34.7911 | [7 empty] | 5% |  | 5% |  | 5%
65% | 1.05% | 46.136 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
60% | 1.748% | 76.7673 | [7 empty] | Total E@R | 0 | Total E@R | 455.2225 | Total E@R | 11982.1132
55% | 2.419% | 106.2642 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.69216 | Total WE@R | 0.031108
50% | 4.064% | 178.4935
45% | 8.378% | 367.9538 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 16.88% | 741.202 |  |  |  |  | 100% | 0 | 88.7719
35% | 26.59% | 1167.7713 |  |  |  |  | 99% | 0.5944 | 87.8842 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 45.59% | 2002.3799 |  |  |  |  | 98% | 0.8916 | 86.9965
25% | 72.26% | 3173.5547 |  |  |  |  | 97% | 1.486 | 86.1088 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 79.18% | 3477.5988 |  |  |  |  | 95% | 2.3776 | 84.3333 | 100% |  | 100% |  | 100%
15% | 86.26% | 3788.4498 |  |  |  |  | 90% | 3.2692 | 79.8947 | 99% |  | 99% |  | 99% | 23.4359
10% | 98.3% | 4317.5016 |  |  |  |  | 85% | 13.9683 | 75.4561 | 98% |  | 98% |  | 98% | 11.4541
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 41.3106 | 71.0175 | 97% |  | 97% |  | 97% | 22.3806
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 126.3094 | 66.579 | 95% |  | 95% |  | 95% | 32.3837
[7 empty] | 70% | 323.9464 | 62.1404 | 90% |  | 90% |  | 90% | 29.6135
[7 empty] | 65% | 549.5201 | 57.7018 | 85% |  | 85% |  | 85% | 307.8727
[7 empty] | 60% | 799.4641 | 53.2632 | 80% |  | 80% |  | 80% | 665.4245
LDC | [6 empty] | 55% | 1116.2777 | 48.8246 | 75% |  | 75% |  | 75% | 1691.327
[7 empty] | 50% | 1494.9086 | 44.386 | 70% |  | 70% |  | 70% | 3055.3998
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 2004.0097 | 39.9474 | 65% |  | 65% |  | 65% | 2486.0603
100% | 0% | 0 |  |  |  |  | 40% | 2877.179 | 35.5088 | 60% |  | 60% |  | 60% | 1645.246
99% | 0.01353% | 0.5944 |  |  |  |  | 35% | 3454.933 | 31.0702 | 55% |  | 55% |  | 55% | 679.408
98% | 0.0203% | 0.8916 |  |  |  |  | 30% | 3663.5664 | 26.6316 | 50% |  | 50% |  | 50%
97% | 0.03383% | 1.486 |  |  |  |  | 25% | 3862.6894 | 22.193 | 45% |  | 45% |  | 45%
95% | 0.05413% | 2.3776 |  |  |  |  | 20% | 4122.7381 | 17.7544 | 40% |  | 40% |  | 40%
90% | 0.07443% | 3.2692 |  |  |  |  | 15% | 4372.3849 | 13.3158 | 35% |  | 35% |  | 35%
85% | 0.318% | 13.9683 |  |  |  |  | 10% | 4374.4653 | 8.8772 | 30% |  | 30% |  | 30%
80% | 0.9406% | 41.3106 |  |  |  |  | 5% | 4374.7625 | 4.4386 | 25% |  | 25% |  | 25%
75% | 2.876% | 126.3094 |  |  |  |  | 9.992e-14% | 4375.9513 | 8.8701e-14 | 20% |  | 20% |  | 20%
70% | 7.376% | 323.9464 | [7 empty] | 15% |  | 15% |  | 15%
65% | 12.51% | 549.5201 | [7 empty] | 10% |  | 10% |  | 10%
60% | 18.2% | 799.4641 | [7 empty] | 5% |  | 5% |  | 5%
55% | 25.42% | 1116.2777 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 34.04% | 1494.9086 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 0 | Total E@R | 10650.0061
45% | 45.63% | 2004.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 0 | Total WE@R | 0.054814
40% | 65.51% | 2877.179 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 78.66% | 3454.933 |  |  |  |  | 100% | 0 | 93.9335 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 83.41% | 3663.5664 |  |  |  |  | 99% | 0.5944 | 92.9942
25% | 87.95% | 3862.6894 |  |  |  |  | 98% | 0.8916 | 92.0548 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 93.87% | 4122.7381 |  |  |  |  | 97% | 1.486 | 91.1155 | 100% |  | 100% |  | 100%
15% | 99.55% | 4372.3849 |  |  |  |  | 95% | 2.3776 | 89.2368 | 99% |  | 99% |  | 99% | 26.4886
10% | 99.6% | 4374.4653 |  |  |  |  | 90% | 3.2692 | 84.5401 | 98% |  | 98% |  | 98% | 12.9651
5% | 99.61% | 4374.7625 |  |  |  |  | 85% | 13.9683 | 79.8435 | 97% |  | 97% |  | 97% | 25.3719
9.992e-14% | 99.63% | 4375.9513 |  |  |  |  | 80% | 41.3106 | 75.1468 | 95% |  | 95% |  | 95% | 36.8016
[7 empty] | 75% | 126.3094 | 70.4501 | 90% |  | 90% |  | 90% | 33.8704
[7 empty] | 70% | 323.9464 | 65.7534 | 85% |  | 85% |  | 85% | 356.1939
[7 empty] | 65% | 549.5201 | 61.0568 | 80% |  | 80% |  | 80% | 781.8556
LDC | [6 empty] | 60% | 799.4641 | 56.3601 | 75% |  | 75% |  | 75% | 2031.3394
[7 empty] | 55% | 1116.2777 | 51.6634 | 70% |  | 70% |  | 70% | 3794.9824
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 1494.9086 | 46.9667 | 65% |  | 65% |  | 65% | 3271.9699
100% | 0% | 0 |  |  |  |  | 45% | 2004.0097 | 42.2701 | 60% |  | 60% |  | 60% | 2451.5579
99% | 0.01353% | 0.5944 |  |  |  |  | 40% | 2877.179 | 37.5734 | 55% |  | 55% |  | 55% | 1619.4738
98% | 0.0203% | 0.8916 |  |  |  |  | 35% | 3454.933 | 32.8767 | 50% |  | 50% |  | 50% | 307.8144
97% | 0.03383% | 1.486 |  |  |  |  | 30% | 3663.5664 | 28.18 | 45% |  | 45% |  | 45%
95% | 0.05413% | 2.3776 |  |  |  |  | 25% | 3862.6894 | 23.4834 | 40% |  | 40% |  | 40%
90% | 0.07443% | 3.2692 |  |  |  |  | 20% | 4122.7381 | 18.7867 | 35% |  | 35% |  | 35%
85% | 0.318% | 13.9683 |  |  |  |  | 15% | 4372.3849 | 14.09 | 30% |  | 30% |  | 30%
80% | 0.9406% | 41.3106 |  |  |  |  | 10% | 4374.4653 | 9.3933 | 25% |  | 25% |  | 25%
75% | 2.876% | 126.3094 |  |  |  |  | 5% | 4374.7625 | 4.6967 | 20% |  | 20% |  | 20%
70% | 7.376% | 323.9464 |  |  |  |  | 9.992e-14% | 4375.9513 | 9.3858e-14 | 15% |  | 15% |  | 15%
65% | 12.51% | 549.5201 | [7 empty] | 10% |  | 10% |  | 10%
60% | 18.2% | 799.4641 | [7 empty] | 5% |  | 5% |  | 5%
55% | 25.42% | 1116.2777 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 34.04% | 1494.9086 | [7 empty] | Total E@R | 0 | Total E@R | 0 | Total E@R | 14750.6849
45% | 45.63% | 2004.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 0 | Total WE@R | 0.032537
40% | 65.51% | 2877.179
35% | 78.66% | 3454.933
30% | 83.41% | 3663.5664
25% | 87.95% | 3862.6894
20% | 93.87% | 4122.7381
15% | 99.55% | 4372.3849
10% | 99.6% | 4374.4653
5% | 99.61% | 4374.7625
9.992e-14% | 99.63% | 4375.9513
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 130.95 |  |  | Year | 2031
SCR (N-1) | 89.2 |  |  | SCR (N) | 130.95
SCR (N-2) | 44.6 |  |  | SCR (N-1) | 89.2
WCR (N) | 142.95 |  |  | SCR (N-2) | 44.6
WCR (N-1) | 97.8 |  |  | WCR (N) | 142.95
WCR (N-2) | 48.9 |  |  | WCR (N-1) | 97.8
|  |  |  | WCR (N-2) | 48.9
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.0048647 | 0.002422 | 0.0055077 | 0.0099165 | 0.016365 | 0.029127 | 0.047433 | 0.079452 | 0.3519 | 1.0193 | 1.969 | 4.2416 | 6.4187 | 10.0002 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936
Total EUE (MWh) | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379
Residual Values
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0048647 | 0.002422 | 0.0055077 | 0.00094022 | 0.0025321 | 0.0067301 | 0.013656 | 0.02812 | 0.053257 | 0.087351 | 0.19911 | 1.0237 | 2.0189 | 3.5517 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963 | 5.7963
Total EUE (MWh) | 0.11039 | 0.054962 | 0.12498 | 0.021336 | 0.057459 | 0.15272 | 0.30988 | 0.63812 | 1.2085 | 1.9822 | 4.5184 | 23.2306 | 45.8142 | 80.5986 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0048647 | 0.002422 | 0.0055077 | 0.0099165 | 0.016365 | 0.029127 | 0.047433 | 0.079452 | 0.3519 | 1.0193 | 1.969 | 4.2416 | 6.4187 | 10.0002 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936
Total EUE (MWh) | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0048647 | 0.002422 | 0.0055077 | 0.00022584 | 0.00075532 | 0.0032147 | 0.0078328 | 0.018528 | 0.037139 | 0.063804 | 0.10265 | 0.47902 | 1.2026 | 2.3492 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029 | 4.1029
Total EUE (MWh) | 0.11039 | 0.054962 | 0.12498 | 0.005125 | 0.01714 | 0.07295 | 0.17775 | 0.42046 | 0.84278 | 1.4479 | 2.3295 | 10.8702 | 27.2912 | 53.3106 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0048647 | 0.002422 | 0.0055077 | 0.0099165 | 0.016365 | 0.029127 | 0.047433 | 0.079452 | 0.3519 | 1.0193 | 1.969 | 4.2416 | 6.4187 | 10.0002 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936
Total EUE (MWh) | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0016885 | 0.00032204 | 0.0014755 | 0.0033556 | 0.0063223 | 0.012741 | 0.022354 | 0.041073 | 0.071155 | 0.12533 | 0.45119 | 1.4573 | 2.5845 | 4.2248 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534 | 6.5534
Total EUE (MWh) | 0.038317 | 0.007308 | 0.033484 | 0.076149 | 0.14347 | 0.28912 | 0.50728 | 0.93206 | 1.6147 | 2.8441 | 10.2387 | 33.0711 | 58.6485 | 95.8732 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0048647 | 0.002422 | 0.0055077 | 0.0099165 | 0.016365 | 0.029127 | 0.047433 | 0.079452 | 0.3519 | 1.0193 | 1.969 | 4.2416 | 6.4187 | 10.0002 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936
Total EUE (MWh) | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0048647 | 0.002422 | 0.0055077 | 0.0099165 | 0.016365 | 0.029127 | 0.047433 | 0.079452 | 0.3519 | 1.0193 | 1.969 | 4.2416 | 6.4187 | 10.0002 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936 | 14.6936
Total EUE (MWh) | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379

## Key Model Assumption & Inputs
Select ZSS & Region | CLN | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Base | 100% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | High | 150%
Option 2 - 1A New PHS ZSS + Four new feeders | 1A New PHS ZSS + Four new feeders
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Option 6 - Non Network | Non Network
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 |  | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | 6.8848 | 7.8511 | 8.1512 | 8.3996 | 8.6182 | 8.9724 | 9.2916 | 9.7408 | 10.2098 | 10.5907 | 10.9491 | 11.4893 | 11.8773 | 12.269 | 12.6854
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Transfers (MVA) Option 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Transfers (MVA) Option 4 |  |  |  | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Transfers (MVA) Option 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
CLN | N/A | DS-CLN-TRNFMR-XXXXXXXXXXXX | New CLN 3rd TX | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | CLN
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 89.7351 | 104.3341 | 108.3435 | 111.4611 | 115.2173 | 119.0984 | 123.2461 | 128.0275 | 133.6994 | 139.0092 | 144.6013 | 154.2938 | 157.43 | 163.5566 | 168.1999
Summer POE10 | 10 |  |  | 104.9463 | 119.6766 | 124.2514 | 128.0364 | 131.3686 | 136.7682 | 141.634 | 148.4809 | 155.6302 | 161.4365 | 166.8996 | 175.1342 | 181.0486 | 187.0195 | 193.3671
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 69.1182 | 84.5179 | 88.1502 | 92.8679 | 97.437 | 101.4753 | 107.1286 | 113.3315 | 119.6901 | 125.9989 | 131.579 | 137.6925 | 139.8743 | 147.8441 | 156.1056
Winter POE10 | 10 |  |  | 74.018 | 89.4372 | 93.2911 | 98.0701 | 102.5171 | 107.2692 | 112.2902 | 119.5588 | 125.8642 | 131.807 | 137.993 | 145.465 | 147.8036 | 155.8793 | 163.4009
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | CLN | 0 | 18 | 17.73 | 17.46 | 17.2 | 16.94 | 16.69 | 16.44 | 16.19 | 15.95 | 15.71 | 15.48 | 15.24 | 15.01 | 14.79
|  | PowerFactor | 1

## Load Duration Curves
Station
CLN
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.01353% | 0.5944 | 0.00861% | 0.37816 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.02583% | 1.1345 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.03383% | 1.486 | 0.05166% | 2.269 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.05413% | 2.3776 | 0.1033% | 4.538 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.07443% | 3.2692 | 0.1808% | 7.9414 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 0.318% | 13.9683 | 0.3272% | 14.3702 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 0.9406% | 41.3106 | 0.4477% | 19.6645 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 2.876% | 126.3094 | 0.5855% | 25.7152 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 7.376% | 323.9464 | 0.7921% | 34.7911 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 12.51% | 549.5201 | 1.05% | 46.136 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 18.2% | 799.4641 | 1.748% | 76.7673 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 25.42% | 1116.2777 | 2.419% | 106.2642 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 34.04% | 1494.9086 | 4.064% | 178.4935 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 45.63% | 2004.0097 | 8.378% | 367.9538 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 65.51% | 2877.179 | 16.88% | 741.202 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 78.66% | 3454.933 | 26.59% | 1167.7713 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 83.41% | 3663.5664 | 45.59% | 2002.3799 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 87.95% | 3862.6894 | 72.26% | 3173.5547 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 93.87% | 4122.7381 | 79.18% | 3477.5988 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.55% | 4372.3849 | 86.26% | 3788.4498 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.6% | 4374.4653 | 98.3% | 4317.5016 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.61% | 4374.7625 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.63% | 4375.9513 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.01353% | 0.5944 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.03383% | 1.486 | 0.01722% | 0.75633 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.05413% | 2.3776 | 0.02583% | 1.1345 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.07443% | 3.2692 | 0.1033% | 4.538 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 0.318% | 13.9683 | 0.1808% | 7.9414 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 0.9406% | 41.3106 | 0.2669% | 11.7231 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 2.876% | 126.3094 | 0.4047% | 17.7737 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 7.376% | 323.9464 | 0.8008% | 35.1693 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 12.51% | 549.5201 | 1.352% | 59.3718 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 18.2% | 799.4641 | 3.573% | 156.9382 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 25.42% | 1116.2777 | 8.283% | 363.794 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 34.04% | 1494.9086 | 17.57% | 771.4551 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 45.63% | 2004.0097 | 28.59% | 1255.5054 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 65.51% | 2877.179 | 46.88% | 2059.1045 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 78.66% | 3454.933 | 69.68% | 3060.4836 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 83.41% | 3663.5664 | 76.64% | 3366.0403 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 87.95% | 3862.6894 | 83.93% | 3686.3454 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 93.87% | 4122.7381 | 91.73% | 4028.5841 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.55% | 4372.3849 | 98.93% | 4345.1076 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.6% | 4374.4653 | 99.75% | 4381.0332 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.61% | 4374.7625 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.63% | 4375.9513 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 1 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 2 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 3 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 4 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 5 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 6 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 7 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 8 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 1 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 3 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 4 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 5 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 6 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 7 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 8 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 1 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 2 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 3 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 4 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 7 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 8 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 69.1182 | 84.5179 | 88.1502 | 92.8679 | 97.437 | 101.4753 | 107.1286 | 113.3315 | 119.6901 | 125.9989 | 131.579 | 137.6925 | 139.8743 | 147.8441 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056 | 156.1056
Maximum Demand (MVA) - P10 | 74.018 | 89.4372 | 93.2911 | 98.0701 | 102.5171 | 107.2692 | 112.2902 | 119.5588 | 125.8642 | 131.807 | 137.993 | 145.465 | 147.8036 | 155.8793 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009 | 163.4009
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 18 | 17.73 | 17.46 | 17.2 | 16.94 | 16.69 | 16.44 | 16.19 | 15.95 | 15.71 | 15.48 | 15.24 | 15.01 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79
Demand management (MVA) | 0 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 89.7351 | 104.3341 | 108.3435 | 111.4611 | 115.2173 | 119.0984 | 123.2461 | 128.0275 | 133.6994 | 139.0092 | 144.6013 | 154.2938 | 157.43 | 163.5566 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999 | 168.1999
Maximum Demand (MVA) - P10 | 104.9463 | 119.6766 | 124.2514 | 128.0364 | 131.3686 | 136.7682 | 141.634 | 148.4809 | 155.6302 | 161.4365 | 166.8996 | 175.1342 | 181.0486 | 187.0195 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671 | 193.3671
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 18 | 17.73 | 17.46 | 17.2 | 16.94 | 16.69 | 16.44 | 16.19 | 15.95 | 15.71 | 15.48 | 15.24 | 15.01 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79
Demand management (MVA) | 0 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104
Option 2 - 1A New PHS ZSS + Four new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 69.1182 | 64.8512 | 68.7535 | 59.2412 | 64.0704 | 68.3686 | 74.2719 | 80.7248 | 87.3334 | 93.8823 | 99.7024 | 106.0459 | 108.4676 | 116.6674 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 74.018 | 69.7706 | 73.8944 | 64.4434 | 69.1505 | 74.1625 | 79.4335 | 86.9521 | 93.5075 | 99.6904 | 106.1164 | 113.8183 | 116.3969 | 124.7027 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 89.7351 | 84.6674 | 88.9468 | 77.8344 | 81.8506 | 85.9917 | 90.3894 | 95.4209 | 101.3428 | 106.8925 | 112.7246 | 122.6472 | 126.0234 | 132.3799 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 104.9463 | 100.01 | 104.8547 | 94.4098 | 98.0019 | 103.6615 | 108.7773 | 115.8742 | 123.2735 | 129.3198 | 135.023 | 143.4876 | 149.6419 | 155.8428 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333 | 19.3333
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 69.1182 | 64.8512 | 68.7535 | 54.4079 | 59.237 | 63.5353 | 69.4386 | 75.8915 | 82.5001 | 89.0489 | 94.869 | 101.2125 | 103.6343 | 111.8341 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 74.018 | 69.7706 | 73.8944 | 59.6101 | 64.3171 | 69.3292 | 74.6002 | 82.1188 | 88.6742 | 94.857 | 101.283 | 108.985 | 111.5636 | 119.8693 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 89.7351 | 84.6674 | 88.9468 | 73.0011 | 77.0173 | 81.1584 | 85.5561 | 90.5875 | 96.5094 | 102.0592 | 107.8913 | 117.8138 | 121.19 | 127.5466 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 104.9463 | 100.01 | 104.8547 | 89.5764 | 93.1686 | 98.8282 | 103.944 | 111.0409 | 118.4402 | 124.4865 | 130.1896 | 138.6542 | 144.8086 | 151.0095 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104
Option 6 - Non Network
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 6.8848 | 7.8511 | 8.1512 | 8.3996 | 8.6182 | 8.9724 | 9.2916 | 9.7408 | 10.2098 | 10.5907 | 10.9491 | 11.4893 | 11.8773 | 12.269 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854 | 12.6854
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 62.2334 | 57.0001 | 60.6023 | 65.3416 | 69.9522 | 73.8962 | 79.4803 | 85.484 | 91.6236 | 97.7916 | 103.2533 | 109.0566 | 111.0903 | 118.8984 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 67.1333 | 61.9194 | 65.7432 | 70.5439 | 75.0323 | 79.6901 | 84.6419 | 91.7113 | 97.7977 | 103.5997 | 109.6673 | 116.829 | 119.0196 | 126.9337 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 82.8503 | 76.8163 | 80.7955 | 83.9349 | 87.7324 | 91.5193 | 95.5978 | 100.1801 | 105.633 | 110.8018 | 116.2755 | 125.6579 | 128.6461 | 134.6109 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 98.0615 | 92.1588 | 96.7035 | 100.5102 | 103.8837 | 109.1891 | 113.9857 | 120.6335 | 127.5637 | 133.2291 | 138.5739 | 146.4983 | 152.2646 | 158.0738 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 100% | 0 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
99% | 0.5944 | 68.427 | 64.2027 | 68.066 | 73.0038 | 77.7847 | 82.0399 | 87.8842 | 94.2725 | 100.8151 | 107.2984 | 113.0603 | 119.3404 | 121.738 | 129.8557 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 99% | 0.5944 | 73.2778 | 69.0729 | 73.1555 | 78.154 | 82.814 | 87.7759 | 92.9942 | 100.4376 | 106.9274 | 113.0485 | 119.4102 | 127.0352 | 129.5879 | 137.8107 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748
98% | 0.8916 | 67.7358 | 63.5542 | 67.3784 | 72.2664 | 76.999 | 81.2112 | 86.9965 | 93.3203 | 99.7967 | 106.2146 | 111.9183 | 118.135 | 120.5083 | 128.544 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 98% | 0.8916 | 72.5377 | 68.3752 | 72.4165 | 77.3646 | 81.9775 | 86.8893 | 92.0548 | 99.4231 | 105.8473 | 111.9066 | 118.204 | 125.752 | 128.279 | 136.4186 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053
97% | 1.486 | 67.0447 | 62.9057 | 66.6909 | 71.529 | 76.2133 | 80.3826 | 86.1088 | 92.3681 | 98.7784 | 105.1308 | 110.7763 | 116.9295 | 119.2786 | 127.2324 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 97% | 1.486 | 71.7975 | 67.6774 | 71.6776 | 76.5751 | 81.1409 | 86.0026 | 91.1155 | 98.4086 | 104.7673 | 110.7647 | 116.9979 | 124.4688 | 126.97 | 135.0266 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359
95% | 2.3776 | 65.6623 | 61.6087 | 65.3158 | 70.0541 | 74.6418 | 78.7252 | 84.3333 | 90.4636 | 96.7417 | 102.9631 | 108.4922 | 114.5186 | 116.8193 | 124.609 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 95% | 2.3776 | 70.3171 | 66.282 | 70.1997 | 74.9963 | 79.4679 | 84.2294 | 89.2368 | 96.3795 | 102.6071 | 108.4809 | 114.5855 | 121.9024 | 124.3521 | 132.2425 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597
90% | 3.2692 | 62.2064 | 58.3661 | 61.8782 | 66.3671 | 70.7133 | 74.5817 | 79.8947 | 85.7023 | 91.6501 | 97.544 | 102.7821 | 108.4913 | 110.6709 | 118.0507 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 90% | 3.2692 | 66.6162 | 62.7935 | 66.505 | 71.0491 | 75.2854 | 79.7963 | 84.5401 | 91.3069 | 97.2067 | 102.7713 | 108.5547 | 115.4865 | 117.8072 | 125.2824 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498
85% | 13.9683 | 58.7505 | 55.1235 | 58.4405 | 62.68 | 66.7848 | 70.4383 | 75.4561 | 80.9411 | 86.5584 | 92.1249 | 97.072 | 102.464 | 104.5225 | 111.4923 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 85% | 13.9683 | 62.9153 | 59.305 | 62.8103 | 67.1019 | 71.1029 | 75.3631 | 79.8435 | 86.2343 | 91.8064 | 97.0618 | 102.5239 | 109.0706 | 111.2624 | 118.3223 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026
80% | 41.3106 | 55.2946 | 51.881 | 55.0028 | 58.993 | 62.8563 | 66.2949 | 71.0175 | 76.1798 | 81.4667 | 86.7058 | 91.3619 | 96.4367 | 98.3741 | 104.9339 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 80% | 41.3106 | 59.2144 | 55.8165 | 59.1156 | 63.1548 | 66.9204 | 70.93 | 75.1468 | 81.1617 | 86.406 | 91.3523 | 96.4931 | 102.6547 | 104.7175 | 111.3621 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554
75% | 126.3094 | 51.8387 | 48.6384 | 51.5651 | 55.3059 | 58.9278 | 62.1515 | 66.579 | 71.4186 | 76.375 | 81.2867 | 85.6518 | 90.4094 | 92.2257 | 98.3755 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 75% | 126.3094 | 55.5135 | 52.3279 | 55.4208 | 59.2076 | 62.7378 | 66.4969 | 70.4501 | 76.0891 | 81.0056 | 85.6428 | 90.4623 | 96.2388 | 98.1727 | 104.402 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082
70% | 323.9464 | 48.3827 | 45.3959 | 48.1275 | 51.6188 | 54.9993 | 58.008 | 62.1404 | 66.6574 | 71.2834 | 75.8676 | 79.9417 | 84.3821 | 86.0773 | 91.8172 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 70% | 323.9464 | 51.8126 | 48.8394 | 51.7261 | 55.2604 | 58.5553 | 62.0638 | 65.7534 | 71.0165 | 75.6052 | 79.9333 | 84.4314 | 89.8228 | 91.6278 | 97.4419 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861
65% | 549.5201 | 44.9268 | 42.1533 | 44.6898 | 47.9318 | 51.0707 | 53.8646 | 57.7018 | 61.8961 | 66.1917 | 70.4485 | 74.2315 | 78.3548 | 79.929 | 85.2588 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 65% | 549.5201 | 48.1117 | 45.3509 | 48.0314 | 51.3132 | 54.3728 | 57.6306 | 61.0568 | 65.9439 | 70.2049 | 74.2237 | 78.4006 | 83.4069 | 85.083 | 90.4817 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137
60% | 799.4641 | 41.4709 | 38.9107 | 41.2521 | 44.2447 | 47.1422 | 49.7212 | 53.2632 | 57.1349 | 61.1 | 65.0294 | 68.5214 | 72.3275 | 73.7806 | 78.7004 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 60% | 799.4641 | 44.4108 | 41.8623 | 44.3367 | 47.3661 | 50.1903 | 53.1975 | 56.3601 | 60.8713 | 64.8045 | 68.5142 | 72.3698 | 76.991 | 78.5381 | 83.5216 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665
55% | 1116.2777 | 38.015 | 35.6682 | 37.8144 | 40.5577 | 43.2137 | 45.5777 | 48.8246 | 52.3736 | 56.0084 | 59.6102 | 62.8113 | 66.3002 | 67.6322 | 72.1421 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 55% | 1116.2777 | 40.7099 | 38.3738 | 40.6419 | 43.4189 | 46.0078 | 48.7644 | 51.6634 | 55.7987 | 59.4041 | 62.8047 | 66.339 | 70.5751 | 71.9933 | 76.5615 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193
50% | 1494.9086 | 34.5591 | 32.4256 | 34.3768 | 36.8706 | 39.2852 | 41.4343 | 44.386 | 47.6124 | 50.9167 | 54.1911 | 57.1012 | 60.2729 | 61.4838 | 65.5837 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 50% | 1494.9086 | 37.009 | 34.8853 | 36.9472 | 39.4717 | 41.8252 | 44.3313 | 46.9667 | 50.7261 | 54.0037 | 57.0952 | 60.3082 | 64.1592 | 65.4485 | 69.6013 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721
45% | 2004.0097 | 31.1032 | 29.183 | 30.9391 | 33.1835 | 35.3567 | 37.2909 | 39.9474 | 42.8512 | 45.825 | 48.772 | 51.3911 | 54.2456 | 55.3354 | 59.0253 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 45% | 2004.0097 | 33.3081 | 31.3968 | 33.2525 | 35.5246 | 37.6427 | 39.8981 | 42.2701 | 45.6535 | 48.6034 | 51.3857 | 54.2774 | 57.7433 | 58.9036 | 62.6412 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249
40% | 2877.179 | 27.6473 | 25.9405 | 27.5014 | 29.4965 | 31.4281 | 33.1474 | 35.5088 | 38.0899 | 40.7334 | 43.3529 | 45.6809 | 48.2184 | 49.1871 | 52.467 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 40% | 2877.179 | 29.6072 | 27.9082 | 29.5578 | 31.5774 | 33.4602 | 35.465 | 37.5734 | 40.5808 | 43.203 | 45.6762 | 48.2465 | 51.3273 | 52.3588 | 55.6811 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777
35% | 3454.933 | 24.1914 | 22.6979 | 24.0637 | 25.8094 | 27.4996 | 29.004 | 31.0702 | 33.3287 | 35.6417 | 37.9338 | 39.9708 | 42.1911 | 43.0387 | 45.9086 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 35% | 3454.933 | 25.9063 | 24.4197 | 25.8631 | 27.6302 | 29.2777 | 31.0319 | 32.8767 | 35.5082 | 37.8026 | 39.9666 | 42.2157 | 44.9114 | 45.8139 | 48.7209 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305
30% | 3663.5664 | 20.7355 | 19.4554 | 20.6261 | 22.1224 | 23.5711 | 24.8606 | 26.6316 | 28.5674 | 30.55 | 32.5147 | 34.2607 | 36.1638 | 36.8903 | 39.3502 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 30% | 3663.5664 | 22.2054 | 20.9312 | 22.1683 | 23.683 | 25.0951 | 26.5988 | 28.18 | 30.4356 | 32.4022 | 34.2571 | 36.1849 | 38.4955 | 39.2691 | 41.7608 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833
25% | 3862.6894 | 17.2796 | 16.2128 | 17.1884 | 18.4353 | 19.6426 | 20.7172 | 22.193 | 23.8062 | 25.4583 | 27.0956 | 28.5506 | 30.1365 | 30.7419 | 32.7918 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 25% | 3862.6894 | 18.5045 | 17.4426 | 18.4736 | 19.7359 | 20.9126 | 22.1656 | 23.4834 | 25.363 | 27.0019 | 28.5476 | 30.1541 | 32.0796 | 32.7242 | 34.8007 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361
20% | 4122.7381 | 13.8236 | 12.9702 | 13.7507 | 14.7482 | 15.7141 | 16.5737 | 17.7544 | 19.045 | 20.3667 | 21.6765 | 22.8405 | 24.1092 | 24.5935 | 26.2335 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 20% | 4122.7381 | 14.8036 | 13.9541 | 14.7789 | 15.7887 | 16.7301 | 17.7325 | 18.7867 | 20.2904 | 21.6015 | 22.8381 | 24.1233 | 25.6637 | 26.1794 | 27.8405 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888
15% | 4372.3849 | 10.3677 | 9.7277 | 10.313 | 11.0612 | 11.7856 | 12.4303 | 13.3158 | 14.2837 | 15.275 | 16.2573 | 17.1304 | 18.0819 | 18.4451 | 19.6751 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 15% | 4372.3849 | 11.1027 | 10.4656 | 11.0842 | 11.8415 | 12.5476 | 13.2994 | 14.09 | 15.2178 | 16.2011 | 17.1286 | 18.0925 | 19.2478 | 19.6345 | 20.8804 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416
10% | 4374.4653 | 6.9118 | 6.4851 | 6.8754 | 7.3741 | 7.857 | 8.2869 | 8.8772 | 9.5225 | 10.1833 | 10.8382 | 11.4202 | 12.0546 | 12.2968 | 13.1167 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 10% | 4374.4653 | 7.4018 | 6.9771 | 7.3894 | 7.8943 | 8.365 | 8.8663 | 9.3933 | 10.1452 | 10.8007 | 11.419 | 12.0616 | 12.8318 | 13.0897 | 13.9203 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944
5% | 4374.7625 | 3.4559 | 3.2426 | 3.4377 | 3.6871 | 3.9285 | 4.1434 | 4.4386 | 4.7612 | 5.0917 | 5.4191 | 5.7101 | 6.0273 | 6.1484 | 6.5584 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 5% | 4374.7625 | 3.7009 | 3.4885 | 3.6947 | 3.9472 | 4.1825 | 4.4331 | 4.6967 | 5.0726 | 5.4004 | 5.7095 | 6.0308 | 6.4159 | 6.5448 | 6.9601 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472
9.992e-14% | 4375.9513 | 6.9063e-14 | 6.4799e-14 | 6.8699e-14 | 7.3682e-14 | 7.8508e-14 | 8.2802e-14 | 8.8701e-14 | 9.5149e-14 | 1.0175e-13 | 1.083e-13 | 1.1411e-13 | 1.2045e-13 | 1.2287e-13 | 1.3106e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 9.992e-14% | 4375.9513 | 7.3959e-14 | 6.9715e-14 | 7.3835e-14 | 7.888e-14 | 8.3584e-14 | 8.8592e-14 | 9.3858e-14 | 1.0137e-13 | 1.0792e-13 | 1.141e-13 | 1.2052e-13 | 1.2822e-13 | 1.3079e-13 | 1.3909e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 100% | 0 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104
99% | 0 | 88.8377 | 83.8207 | 88.0573 | 91.4111 | 95.3871 | 99.4868 | 103.8405 | 108.8216 | 114.6843 | 120.1786 | 125.9523 | 135.7757 | 139.1181 | 145.4111 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 99% | 0.37816 | 103.8968 | 99.0099 | 103.8062 | 107.8207 | 111.3769 | 116.9799 | 122.0445 | 129.0705 | 136.3958 | 142.3816 | 148.0278 | 156.4077 | 162.5005 | 168.6394 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413
98% | 0.37816 | 87.9404 | 82.9741 | 87.1679 | 90.4877 | 94.4236 | 98.4819 | 102.7916 | 107.7224 | 113.5259 | 118.9647 | 124.6801 | 134.4042 | 137.7129 | 143.9423 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 98% | 1.1345 | 102.8473 | 98.0098 | 102.7576 | 106.7316 | 110.2519 | 115.7983 | 120.8117 | 127.7667 | 135.018 | 140.9434 | 146.5325 | 154.8278 | 160.8591 | 166.9359 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722
97% | 0.75633 | 87.043 | 82.1274 | 86.2784 | 89.5644 | 93.4601 | 97.4769 | 101.7427 | 106.6232 | 112.3675 | 117.7507 | 123.4079 | 133.0328 | 136.3077 | 142.4735 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 97% | 2.269 | 101.7979 | 97.0097 | 101.7091 | 105.6425 | 109.1268 | 114.6167 | 119.579 | 126.463 | 133.6403 | 139.5052 | 145.0373 | 153.2479 | 159.2176 | 165.2325 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031
95% | 1.1345 | 85.2483 | 80.434 | 84.4994 | 87.7177 | 91.5331 | 95.4671 | 99.6449 | 104.4248 | 110.0506 | 115.3229 | 120.8634 | 130.2898 | 133.4972 | 139.5359 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 95% | 4.538 | 99.699 | 95.0095 | 99.612 | 103.4643 | 106.8768 | 112.2534 | 117.1134 | 123.8555 | 130.8848 | 136.6288 | 142.0468 | 150.0882 | 155.9348 | 161.8257 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649
90% | 4.538 | 80.7616 | 76.2007 | 80.0521 | 83.101 | 86.7155 | 90.4425 | 94.4005 | 98.9288 | 104.2585 | 109.2533 | 114.5021 | 123.4325 | 126.471 | 132.1919 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 90% | 7.9414 | 94.4516 | 90.009 | 94.3693 | 98.0188 | 101.2517 | 106.3454 | 110.9496 | 117.3368 | 123.9961 | 129.4378 | 134.5707 | 142.1888 | 147.7277 | 153.3085 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194
85% | 7.9414 | 76.2748 | 71.9673 | 75.6048 | 78.4843 | 81.898 | 85.4179 | 89.156 | 93.4327 | 98.4663 | 103.1836 | 108.1409 | 116.5751 | 119.4449 | 124.8479 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 85% | 14.3702 | 89.2043 | 85.0085 | 89.1265 | 92.5733 | 95.6266 | 100.4373 | 104.7857 | 110.8181 | 117.1075 | 122.2468 | 127.0945 | 134.2894 | 139.5206 | 144.7914 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738
80% | 11.7231 | 71.788 | 67.7339 | 71.1574 | 73.8675 | 77.0805 | 80.3933 | 83.9115 | 87.9367 | 92.6742 | 97.114 | 101.7797 | 109.7177 | 112.4187 | 117.5039 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 80% | 19.6645 | 83.957 | 80.008 | 83.8838 | 87.1278 | 90.0015 | 94.5292 | 98.6218 | 104.2994 | 110.2188 | 115.0559 | 119.6184 | 126.39 | 131.3135 | 136.2742 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283
75% | 17.7737 | 67.3013 | 63.5006 | 66.7101 | 69.2508 | 72.2629 | 75.3688 | 78.6671 | 82.4406 | 86.8821 | 91.0444 | 95.4184 | 102.8604 | 105.3925 | 110.16 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 75% | 25.7152 | 78.7097 | 75.0075 | 78.641 | 81.6823 | 84.3764 | 88.6211 | 92.458 | 97.7807 | 103.3301 | 107.8649 | 112.1422 | 118.4907 | 123.1064 | 127.7571 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828
70% | 35.1693 | 62.8145 | 59.2672 | 62.2628 | 64.6341 | 67.4454 | 70.3442 | 73.4226 | 76.9446 | 81.0899 | 84.9748 | 89.0572 | 96.003 | 98.3664 | 102.816 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 70% | 34.7911 | 73.4624 | 70.007 | 73.3983 | 76.2368 | 78.7513 | 82.7131 | 86.2941 | 91.262 | 96.4414 | 100.6739 | 104.6661 | 110.5913 | 114.8993 | 119.24 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373
65% | 59.3718 | 58.3278 | 55.0338 | 57.8154 | 60.0174 | 62.6279 | 65.3196 | 68.1781 | 71.4486 | 75.2978 | 78.9051 | 82.696 | 89.1457 | 91.3402 | 95.472 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 65% | 46.136 | 68.2151 | 65.0065 | 68.1556 | 70.7913 | 73.1262 | 76.805 | 80.1302 | 84.7432 | 89.5528 | 93.4829 | 97.1899 | 102.6919 | 106.6922 | 110.7228 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918
60% | 156.9382 | 53.841 | 50.8005 | 53.3681 | 55.4007 | 57.8104 | 60.295 | 62.9336 | 65.9525 | 69.5057 | 72.8355 | 76.3348 | 82.2883 | 84.314 | 88.128 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 60% | 76.7673 | 62.9678 | 60.006 | 62.9128 | 65.3459 | 67.5011 | 70.8969 | 73.9664 | 78.2245 | 82.6641 | 86.2919 | 89.7138 | 94.7925 | 98.4851 | 102.2057 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462
55% | 363.794 | 49.3543 | 46.5671 | 48.9207 | 50.7839 | 52.9928 | 55.2704 | 57.6892 | 60.4565 | 63.7135 | 66.7659 | 69.9735 | 75.4309 | 77.2879 | 80.784 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 55% | 106.2642 | 57.7205 | 55.0055 | 57.6701 | 59.9004 | 61.876 | 64.9888 | 67.8025 | 71.7058 | 75.7754 | 79.1009 | 82.2376 | 86.8932 | 90.278 | 93.6885 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007
50% | 771.4551 | 44.8675 | 42.3337 | 44.4734 | 46.1672 | 48.1753 | 50.2458 | 52.4447 | 54.9604 | 57.9214 | 60.6963 | 63.6123 | 68.5736 | 70.2617 | 73.44 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 50% | 178.4935 | 52.4731 | 50.005 | 52.4274 | 54.4549 | 56.251 | 59.0808 | 61.6386 | 65.1871 | 68.8867 | 71.9099 | 74.7615 | 78.9938 | 82.0709 | 85.1714 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552
45% | 1255.5054 | 40.3808 | 38.1003 | 40.0261 | 41.5505 | 43.3578 | 45.2213 | 47.2002 | 49.4644 | 52.1292 | 54.6266 | 57.2511 | 61.7162 | 63.2355 | 66.096 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 45% | 367.9538 | 47.2258 | 45.0045 | 47.1846 | 49.0094 | 50.6259 | 53.1727 | 55.4748 | 58.6684 | 61.9981 | 64.7189 | 67.2853 | 71.0944 | 73.8639 | 76.6543 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097
40% | 2059.1045 | 35.894 | 33.867 | 35.5787 | 36.9338 | 38.5402 | 40.1967 | 41.9558 | 43.9683 | 46.3371 | 48.557 | 50.8898 | 54.8589 | 56.2094 | 58.752 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 40% | 741.202 | 41.9785 | 40.004 | 41.9419 | 43.5639 | 45.0008 | 47.2646 | 49.3109 | 52.1497 | 55.1094 | 57.5279 | 59.8092 | 63.195 | 65.6568 | 68.1371 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642
35% | 3060.4836 | 31.4073 | 29.6336 | 31.1314 | 32.317 | 33.7227 | 35.1721 | 36.7113 | 38.4723 | 40.545 | 42.4874 | 44.5286 | 48.0015 | 49.1832 | 51.408 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 35% | 1167.7713 | 36.7312 | 35.0035 | 36.6992 | 38.1184 | 39.3757 | 41.3565 | 43.1471 | 45.631 | 48.2207 | 50.3369 | 52.333 | 55.2956 | 57.4497 | 59.62 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186
30% | 3366.0403 | 26.9205 | 25.4002 | 26.684 | 27.7003 | 28.9052 | 30.1475 | 31.4668 | 32.9763 | 34.7528 | 36.4178 | 38.1674 | 41.1442 | 42.157 | 44.064 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 30% | 2002.3799 | 31.4839 | 30.003 | 31.4564 | 32.6729 | 33.7506 | 35.4485 | 36.9832 | 39.1123 | 41.332 | 43.1459 | 44.8569 | 47.3963 | 49.2426 | 51.1028 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731
25% | 3686.3454 | 22.4338 | 21.1669 | 22.2367 | 23.0836 | 24.0876 | 25.1229 | 26.2224 | 27.4802 | 28.9607 | 30.3481 | 31.8061 | 34.2868 | 35.1308 | 36.72 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 25% | 3173.5547 | 26.2366 | 25.0025 | 26.2137 | 27.2274 | 28.1255 | 29.5404 | 30.8193 | 32.5936 | 34.4434 | 35.955 | 37.3807 | 39.4969 | 41.0355 | 42.5857 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276
20% | 4028.5841 | 17.947 | 16.9335 | 17.7894 | 18.4669 | 19.2701 | 20.0983 | 20.9779 | 21.9842 | 23.1686 | 24.2785 | 25.4449 | 27.4294 | 28.1047 | 29.376 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 20% | 3477.5988 | 20.9893 | 20.002 | 20.9709 | 21.782 | 22.5004 | 23.6323 | 24.6555 | 26.0748 | 27.5547 | 28.764 | 29.9046 | 31.5975 | 32.8284 | 34.0686 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821
15% | 4345.1076 | 13.4603 | 12.7001 | 13.342 | 13.8502 | 14.4526 | 15.0738 | 15.7334 | 16.4881 | 17.3764 | 18.2089 | 19.0837 | 20.5721 | 21.0785 | 22.032 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 15% | 3788.4498 | 15.7419 | 15.0015 | 15.7282 | 16.3365 | 16.8753 | 17.7242 | 18.4916 | 19.5561 | 20.666 | 21.573 | 22.4284 | 23.6981 | 24.6213 | 25.5514 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366
10% | 4381.0332 | 8.9735 | 8.4667 | 8.8947 | 9.2334 | 9.6351 | 10.0492 | 10.4889 | 10.9921 | 11.5843 | 12.1393 | 12.7225 | 13.7147 | 14.0523 | 14.688 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 10% | 4317.5016 | 10.4946 | 10.001 | 10.4855 | 10.891 | 11.2502 | 11.8162 | 12.3277 | 13.0374 | 13.7773 | 14.382 | 14.9523 | 15.7988 | 16.4142 | 17.0343 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691
5% | 4391.6218 | 4.4868 | 4.2334 | 4.4473 | 4.6167 | 4.8175 | 5.0246 | 5.2445 | 5.496 | 5.7921 | 6.0696 | 6.3612 | 6.8574 | 7.0262 | 7.344 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 5% | 4391.6218 | 5.2473 | 5.0005 | 5.2427 | 5.4455 | 5.6251 | 5.9081 | 6.1639 | 6.5187 | 6.8887 | 7.191 | 7.4761 | 7.8994 | 8.2071 | 8.5171 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455
9.992e-14% | 4391.6218 | 8.9663e-14 | 8.46e-14 | 8.8876e-14 | 9.2261e-14 | 9.6274e-14 | 1.0041e-13 | 1.0481e-13 | 1.0983e-13 | 1.1575e-13 | 1.213e-13 | 1.2712e-13 | 1.3704e-13 | 1.4041e-13 | 1.4676e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 9.992e-14% | 4391.6218 | 1.0486e-13 | 9.993e-14 | 1.0477e-13 | 1.0882e-13 | 1.1241e-13 | 1.1807e-13 | 1.2318e-13 | 1.3027e-13 | 1.3766e-13 | 1.437e-13 | 1.494e-13 | 1.5786e-13 | 1.6401e-13 | 1.7021e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 69.1182 | 64.8512 | 68.7535 | 59.2412 | 64.0704 | 68.3686 | 74.2719 | 80.7248 | 87.3334 | 93.8823 | 99.7024 | 106.0459 | 108.4676 | 116.6674 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 125.1489 | 100% | 0 | 74.018 | 69.7706 | 73.8944 | 64.4434 | 69.1505 | 74.1625 | 79.4335 | 86.9521 | 93.5075 | 99.6904 | 106.1164 | 113.8183 | 116.3969 | 124.7027 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442 | 132.4442
99% | 0.5944 | 68.427 | 64.2027 | 68.066 | 58.6488 | 63.4297 | 67.6849 | 73.5292 | 79.9175 | 86.4601 | 92.9434 | 98.7053 | 104.9854 | 107.383 | 115.5007 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 123.8975 | 99% | 0.5944 | 73.2778 | 69.0729 | 73.1555 | 63.799 | 68.459 | 73.4209 | 78.6392 | 86.0826 | 92.5724 | 98.6935 | 105.0552 | 112.6802 | 115.2329 | 123.4557 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198 | 131.1198
98% | 0.8916 | 67.7358 | 63.5542 | 67.3784 | 58.0564 | 62.789 | 67.0012 | 72.7865 | 79.1103 | 85.5867 | 92.0046 | 97.7083 | 103.925 | 106.2983 | 114.334 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 122.646 | 98% | 0.8916 | 72.5377 | 68.3752 | 72.4165 | 63.1546 | 67.7675 | 72.6793 | 77.8448 | 85.2131 | 91.6373 | 97.6966 | 103.994 | 111.542 | 114.069 | 122.2086 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953 | 129.7953
97% | 1.486 | 67.0447 | 62.9057 | 66.6909 | 57.464 | 62.1483 | 66.3176 | 72.0438 | 78.3031 | 84.7134 | 91.0658 | 96.7113 | 102.8645 | 105.2136 | 113.1674 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 121.3945 | 97% | 1.486 | 71.7975 | 67.6774 | 71.6776 | 62.5101 | 67.0759 | 71.9376 | 77.0505 | 84.3436 | 90.7023 | 96.6997 | 102.9329 | 110.4038 | 112.905 | 120.9616 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709 | 128.4709
95% | 2.3776 | 65.6623 | 61.6087 | 65.3158 | 56.2791 | 60.8668 | 64.9502 | 70.5583 | 76.6886 | 82.9667 | 89.1881 | 94.7172 | 100.7436 | 103.0443 | 110.834 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 118.8915 | 95% | 2.3776 | 70.3171 | 66.282 | 70.1997 | 61.2213 | 65.6929 | 70.4544 | 75.4618 | 82.6045 | 88.8321 | 94.7059 | 100.8105 | 108.1274 | 110.5771 | 118.4675 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822 | 125.822
90% | 3.2692 | 62.2064 | 58.3661 | 61.8782 | 53.3171 | 57.6633 | 61.5317 | 66.8447 | 72.6523 | 78.6001 | 84.494 | 89.7321 | 95.4413 | 97.6209 | 105.0007 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 112.634 | 90% | 3.2692 | 66.6162 | 62.7935 | 66.505 | 57.9991 | 62.2354 | 66.7463 | 71.4901 | 78.2569 | 84.1567 | 89.7213 | 95.5047 | 102.4365 | 104.7572 | 112.2324 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998 | 119.1998
85% | 13.9683 | 58.7505 | 55.1235 | 58.4405 | 50.355 | 54.4598 | 58.1133 | 63.1311 | 68.6161 | 74.2334 | 79.7999 | 84.747 | 90.139 | 92.1975 | 99.1673 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 106.3766 | 85% | 13.9683 | 62.9153 | 59.305 | 62.8103 | 54.7769 | 58.7779 | 63.0381 | 67.5185 | 73.9093 | 79.4814 | 84.7368 | 90.1989 | 96.7456 | 98.9374 | 105.9973 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776 | 112.5776
80% | 41.3106 | 55.2946 | 51.881 | 55.0028 | 47.393 | 51.2563 | 54.6949 | 59.4175 | 64.5798 | 69.8667 | 75.1058 | 79.7619 | 84.8367 | 86.7741 | 93.3339 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 100.1192 | 80% | 41.3106 | 59.2144 | 55.8165 | 59.1156 | 51.5548 | 55.3204 | 59.33 | 63.5468 | 69.5617 | 74.806 | 79.7523 | 84.8931 | 91.0547 | 93.1175 | 99.7621 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554 | 105.9554
75% | 126.3094 | 51.8387 | 48.6384 | 51.5651 | 44.4309 | 48.0528 | 51.2765 | 55.704 | 60.5436 | 65.5 | 70.4117 | 74.7768 | 79.5344 | 81.3507 | 87.5005 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 93.8617 | 75% | 126.3094 | 55.5135 | 52.3279 | 55.4208 | 48.3326 | 51.8628 | 55.6219 | 59.5751 | 65.2141 | 70.1306 | 74.7678 | 79.5873 | 85.3638 | 87.2977 | 93.527 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332 | 99.3332
70% | 323.9464 | 48.3827 | 45.3959 | 48.1275 | 41.4688 | 44.8493 | 47.858 | 51.9904 | 56.5074 | 61.1334 | 65.7176 | 69.7917 | 74.2321 | 75.9273 | 81.6672 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 87.6043 | 70% | 323.9464 | 51.8126 | 48.8394 | 51.7261 | 45.1104 | 48.4053 | 51.9138 | 55.6034 | 60.8665 | 65.4552 | 69.7833 | 74.2814 | 79.6728 | 81.4778 | 87.2919 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711 | 92.711
65% | 549.5201 | 44.9268 | 42.1533 | 44.6898 | 38.5068 | 41.6457 | 44.4396 | 48.2768 | 52.4711 | 56.7667 | 61.0235 | 64.8065 | 68.9298 | 70.504 | 75.8338 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 81.3468 | 65% | 549.5201 | 48.1117 | 45.3509 | 48.0314 | 41.8882 | 44.9478 | 48.2056 | 51.6318 | 56.5189 | 60.7799 | 64.7987 | 68.9756 | 73.9819 | 75.658 | 81.0567 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887 | 86.0887
60% | 799.4641 | 41.4709 | 38.9107 | 41.2521 | 35.5447 | 38.4422 | 41.0212 | 44.5632 | 48.4349 | 52.4 | 56.3294 | 59.8214 | 63.6275 | 65.0806 | 70.0004 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 75.0894 | 60% | 799.4641 | 44.4108 | 41.8623 | 44.3367 | 38.6661 | 41.4903 | 44.4975 | 47.6601 | 52.1713 | 56.1045 | 59.8142 | 63.6698 | 68.291 | 69.8381 | 74.8216 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665 | 79.4665
55% | 1116.2777 | 38.015 | 35.6682 | 37.8144 | 32.5827 | 35.2387 | 37.6027 | 40.8496 | 44.3986 | 48.0334 | 51.6352 | 54.8363 | 58.3252 | 59.6572 | 64.1671 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 68.8319 | 55% | 1116.2777 | 40.7099 | 38.3738 | 40.6419 | 35.4439 | 38.0328 | 40.7894 | 43.6884 | 47.8237 | 51.4291 | 54.8297 | 58.364 | 62.6001 | 64.0183 | 68.5865 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443 | 72.8443
50% | 1494.9086 | 34.5591 | 32.4256 | 34.3768 | 29.6206 | 32.0352 | 34.1843 | 37.136 | 40.3624 | 43.6667 | 46.9411 | 49.8512 | 53.0229 | 54.2338 | 58.3337 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 62.5745 | 50% | 1494.9086 | 37.009 | 34.8853 | 36.9472 | 32.2217 | 34.5752 | 37.0813 | 39.7167 | 43.4761 | 46.7537 | 49.8452 | 53.0582 | 56.9092 | 58.1985 | 62.3513 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221 | 66.2221
45% | 2004.0097 | 31.1032 | 29.183 | 30.9391 | 26.6585 | 28.8317 | 30.7659 | 33.4224 | 36.3262 | 39.3 | 42.247 | 44.8661 | 47.7206 | 48.8104 | 52.5003 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 56.317 | 45% | 2004.0097 | 33.3081 | 31.3968 | 33.2525 | 28.9996 | 31.1177 | 33.3731 | 35.7451 | 39.1285 | 42.0784 | 44.8607 | 47.7524 | 51.2183 | 52.3786 | 56.1162 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999 | 59.5999
40% | 2877.179 | 27.6473 | 25.9405 | 27.5014 | 23.6965 | 25.6281 | 27.3474 | 29.7088 | 32.2899 | 34.9334 | 37.5529 | 39.8809 | 42.4184 | 43.3871 | 46.667 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 50.0596 | 40% | 2877.179 | 29.6072 | 27.9082 | 29.5578 | 25.7774 | 27.6602 | 29.665 | 31.7734 | 34.7808 | 37.403 | 39.8762 | 42.4465 | 45.5273 | 46.5588 | 49.8811 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777 | 52.9777
35% | 3454.933 | 24.1914 | 22.6979 | 24.0637 | 20.7344 | 22.4246 | 23.929 | 25.9952 | 28.2537 | 30.5667 | 32.8588 | 34.8958 | 37.1161 | 37.9637 | 40.8336 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 43.8021 | 35% | 3454.933 | 25.9063 | 24.4197 | 25.8631 | 22.5552 | 24.2027 | 25.9569 | 27.8017 | 30.4332 | 32.7276 | 34.8916 | 37.1407 | 39.8364 | 40.7389 | 43.6459 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555 | 46.3555
30% | 3663.5664 | 20.7355 | 19.4554 | 20.6261 | 17.7724 | 19.2211 | 20.5106 | 22.2816 | 24.2174 | 26.2 | 28.1647 | 29.9107 | 31.8138 | 32.5403 | 35.0002 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 37.5447 | 30% | 3663.5664 | 22.2054 | 20.9312 | 22.1683 | 19.333 | 20.7451 | 22.2488 | 23.83 | 26.0856 | 28.0522 | 29.9071 | 31.8349 | 34.1455 | 34.9191 | 37.4108 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333 | 39.7333
25% | 3862.6894 | 17.2796 | 16.2128 | 17.1884 | 14.8103 | 16.0176 | 17.0922 | 18.568 | 20.1812 | 21.8333 | 23.4706 | 24.9256 | 26.5115 | 27.1169 | 29.1668 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 31.2872 | 25% | 3862.6894 | 18.5045 | 17.4426 | 18.4736 | 16.1109 | 17.2876 | 18.5406 | 19.8584 | 21.738 | 23.3769 | 24.9226 | 26.5291 | 28.4546 | 29.0992 | 31.1757 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111 | 33.1111
20% | 4122.7381 | 13.8236 | 12.9702 | 13.7507 | 11.8482 | 12.8141 | 13.6737 | 14.8544 | 16.145 | 17.4667 | 18.7765 | 19.9405 | 21.2092 | 21.6935 | 23.3335 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 25.0298 | 20% | 4122.7381 | 14.8036 | 13.9541 | 14.7789 | 12.8887 | 13.8301 | 14.8325 | 15.8867 | 17.3904 | 18.7015 | 19.9381 | 21.2233 | 22.7637 | 23.2794 | 24.9405 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888 | 26.4888
15% | 4372.3849 | 10.3677 | 9.7277 | 10.313 | 8.8862 | 9.6106 | 10.2553 | 11.1408 | 12.1087 | 13.1 | 14.0823 | 14.9554 | 15.9069 | 16.2701 | 17.5001 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 18.7723 | 15% | 4372.3849 | 11.1027 | 10.4656 | 11.0842 | 9.6665 | 10.3726 | 11.1244 | 11.915 | 13.0428 | 14.0261 | 14.9536 | 15.9175 | 17.0728 | 17.4595 | 18.7054 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666 | 19.8666
10% | 4374.4653 | 6.9118 | 6.4851 | 6.8754 | 5.9241 | 6.407 | 6.8369 | 7.4272 | 8.0725 | 8.7333 | 9.3882 | 9.9702 | 10.6046 | 10.8468 | 11.6667 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 12.5149 | 10% | 4374.4653 | 7.4018 | 6.9771 | 7.3894 | 6.4443 | 6.915 | 7.4163 | 7.9433 | 8.6952 | 9.3507 | 9.969 | 10.6116 | 11.3818 | 11.6397 | 12.4703 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444 | 13.2444
5% | 4374.7625 | 3.4559 | 3.2426 | 3.4377 | 2.9621 | 3.2035 | 3.4184 | 3.7136 | 4.0362 | 4.3667 | 4.6941 | 4.9851 | 5.3023 | 5.4234 | 5.8334 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 6.2574 | 5% | 4374.7625 | 3.7009 | 3.4885 | 3.6947 | 3.2222 | 3.4575 | 3.7081 | 3.9717 | 4.3476 | 4.6754 | 4.9845 | 5.3058 | 5.6909 | 5.8198 | 6.2351 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222 | 6.6222
9.992e-14% | 4375.9513 | 6.9063e-14 | 6.4799e-14 | 6.8699e-14 | 5.9194e-14 | 6.4019e-14 | 6.8314e-14 | 7.4213e-14 | 8.066e-14 | 8.7264e-14 | 9.3807e-14 | 9.9623e-14 | 1.0596e-13 | 1.0838e-13 | 1.1657e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 1.2505e-13 | 9.992e-14% | 4375.9513 | 7.3959e-14 | 6.9715e-14 | 7.3835e-14 | 6.4392e-14 | 6.9095e-14 | 7.4103e-14 | 7.937e-14 | 8.6883e-14 | 9.3433e-14 | 9.9611e-14 | 1.0603e-13 | 1.1373e-13 | 1.163e-13 | 1.246e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13 | 1.3234e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 89.7351 | 84.6674 | 88.9468 | 77.8344 | 81.8506 | 85.9917 | 90.3894 | 95.4209 | 101.3428 | 106.8925 | 112.7246 | 122.6472 | 126.0234 | 132.3799 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 137.2432 | 100% | 0 | 104.9463 | 100.01 | 104.8547 | 94.4098 | 98.0019 | 103.6615 | 108.7773 | 115.8742 | 123.2735 | 129.3198 | 135.023 | 143.4876 | 149.6419 | 155.8428 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104 | 162.4104
99% | 0 | 88.8377 | 83.8207 | 88.0573 | 77.0561 | 81.0321 | 85.1318 | 89.4855 | 94.4666 | 100.3293 | 105.8236 | 111.5973 | 121.4207 | 124.7631 | 131.0561 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 135.8708 | 99% | 0.37816 | 103.8968 | 99.0099 | 103.8062 | 93.4657 | 97.0219 | 102.6249 | 107.6895 | 114.7155 | 122.0408 | 128.0266 | 133.6728 | 142.0527 | 148.1455 | 154.2844 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863 | 160.7863
98% | 0.37816 | 87.9404 | 82.9741 | 87.1679 | 76.2777 | 80.2136 | 84.2719 | 88.5816 | 93.5124 | 99.3159 | 104.7547 | 110.4701 | 120.1942 | 123.5029 | 129.7323 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 134.4983 | 98% | 1.1345 | 102.8473 | 98.0098 | 102.7576 | 92.5216 | 96.0419 | 101.5883 | 106.6017 | 113.5567 | 120.808 | 126.7334 | 132.3225 | 140.6178 | 146.6491 | 152.7259 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622 | 159.1622
97% | 0.75633 | 87.043 | 82.1274 | 86.2784 | 75.4994 | 79.3951 | 83.4119 | 87.6777 | 92.5582 | 98.3025 | 103.6857 | 109.3429 | 118.9678 | 122.2427 | 128.4085 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 133.1259 | 97% | 2.269 | 101.7979 | 97.0097 | 101.7091 | 91.5775 | 95.0618 | 100.5517 | 105.514 | 112.398 | 119.5753 | 125.4402 | 130.9723 | 139.1829 | 145.1526 | 151.1675 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381 | 157.5381
95% | 1.1345 | 85.2483 | 80.434 | 84.4994 | 73.9427 | 77.7581 | 81.6921 | 85.8699 | 90.6498 | 96.2756 | 101.5479 | 107.0884 | 116.5148 | 119.7222 | 125.7609 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 130.381 | 95% | 4.538 | 99.699 | 95.0095 | 99.612 | 89.6893 | 93.1018 | 98.4784 | 103.3384 | 110.0805 | 117.1098 | 122.8538 | 128.2718 | 136.3132 | 142.1598 | 148.0507 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899 | 154.2899
90% | 4.538 | 80.7616 | 76.2007 | 80.0521 | 70.051 | 73.6655 | 77.3925 | 81.3505 | 85.8788 | 91.2085 | 96.2033 | 101.4521 | 110.3825 | 113.421 | 119.1419 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 123.5189 | 90% | 7.9414 | 94.4516 | 90.009 | 94.3693 | 84.9688 | 88.2017 | 93.2954 | 97.8996 | 104.2868 | 110.9461 | 116.3878 | 121.5207 | 129.1388 | 134.6777 | 140.2585 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694 | 146.1694
85% | 7.9414 | 76.2748 | 71.9673 | 75.6048 | 66.1593 | 69.573 | 73.0929 | 76.831 | 81.1077 | 86.1413 | 90.8586 | 95.8159 | 104.2501 | 107.1199 | 112.5229 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 116.6567 | 85% | 14.3702 | 89.2043 | 85.0085 | 89.1265 | 80.2483 | 83.3016 | 88.1123 | 92.4607 | 98.4931 | 104.7825 | 109.9218 | 114.7695 | 121.9644 | 127.1956 | 132.4664 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488 | 138.0488
80% | 11.7231 | 71.788 | 67.7339 | 71.1574 | 62.2675 | 65.4805 | 68.7933 | 72.3115 | 76.3367 | 81.0742 | 85.514 | 90.1797 | 98.1177 | 100.8187 | 105.9039 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 109.7946 | 80% | 19.6645 | 83.957 | 80.008 | 83.8838 | 75.5278 | 78.4015 | 82.9292 | 87.0218 | 92.6994 | 98.6188 | 103.4559 | 108.0184 | 114.79 | 119.7135 | 124.6742 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283 | 129.9283
75% | 17.7737 | 67.3013 | 63.5006 | 66.7101 | 58.3758 | 61.3879 | 64.4938 | 67.7921 | 71.5656 | 76.0071 | 80.1694 | 84.5434 | 91.9854 | 94.5175 | 99.285 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 102.9324 | 75% | 25.7152 | 78.7097 | 75.0075 | 78.641 | 70.8073 | 73.5014 | 77.7461 | 81.583 | 86.9057 | 92.4551 | 96.9899 | 101.2672 | 107.6157 | 112.2314 | 116.8821 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078 | 121.8078
70% | 35.1693 | 62.8145 | 59.2672 | 62.2628 | 54.4841 | 57.2954 | 60.1942 | 63.2726 | 66.7946 | 70.9399 | 74.8248 | 78.9072 | 85.853 | 88.2164 | 92.666 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 96.0702 | 70% | 34.7911 | 73.4624 | 70.007 | 73.3983 | 66.0868 | 68.6013 | 72.5631 | 76.1441 | 81.112 | 86.2914 | 90.5239 | 94.5161 | 100.4413 | 104.7493 | 109.09 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873 | 113.6873
65% | 59.3718 | 58.3278 | 55.0338 | 57.8154 | 50.5924 | 53.2029 | 55.8946 | 58.7531 | 62.0236 | 65.8728 | 69.4801 | 73.271 | 79.7207 | 81.9152 | 86.047 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 89.2081 | 65% | 46.136 | 68.2151 | 65.0065 | 68.1556 | 61.3663 | 63.7012 | 67.38 | 70.7052 | 75.3182 | 80.1278 | 84.0579 | 87.7649 | 93.2669 | 97.2672 | 101.2978 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668 | 105.5668
60% | 156.9382 | 53.841 | 50.8005 | 53.3681 | 46.7007 | 49.1104 | 51.595 | 54.2336 | 57.2525 | 60.8057 | 64.1355 | 67.6348 | 73.5883 | 75.614 | 79.428 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 82.3459 | 60% | 76.7673 | 62.9678 | 60.006 | 62.9128 | 56.6459 | 58.8011 | 62.1969 | 65.2664 | 69.5245 | 73.9641 | 77.5919 | 81.0138 | 86.0925 | 89.7851 | 93.5057 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462 | 97.4462
55% | 363.794 | 49.3543 | 46.5671 | 48.9207 | 42.8089 | 45.0178 | 47.2954 | 49.7142 | 52.4815 | 55.7385 | 58.7909 | 61.9985 | 67.4559 | 69.3129 | 72.809 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 75.4838 | 55% | 106.2642 | 57.7205 | 55.0055 | 57.6701 | 51.9254 | 53.901 | 57.0138 | 59.8275 | 63.7308 | 67.8004 | 71.1259 | 74.2626 | 78.9182 | 82.303 | 85.7135 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257 | 89.3257
50% | 771.4551 | 44.8675 | 42.3337 | 44.4734 | 38.9172 | 40.9253 | 42.9958 | 45.1947 | 47.7104 | 50.6714 | 53.4463 | 56.3623 | 61.3236 | 63.0117 | 66.19 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 68.6216 | 50% | 178.4935 | 52.4731 | 50.005 | 52.4274 | 47.2049 | 49.001 | 51.8308 | 54.3886 | 57.9371 | 61.6367 | 64.6599 | 67.5115 | 71.7438 | 74.8209 | 77.9214 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052 | 81.2052
45% | 1255.5054 | 40.3808 | 38.1003 | 40.0261 | 35.0255 | 36.8328 | 38.6963 | 40.6752 | 42.9394 | 45.6042 | 48.1016 | 50.7261 | 55.1912 | 56.7105 | 59.571 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 61.7594 | 45% | 367.9538 | 47.2258 | 45.0045 | 47.1846 | 42.4844 | 44.1009 | 46.6477 | 48.9498 | 52.1434 | 55.4731 | 58.1939 | 60.7603 | 64.5694 | 67.3389 | 70.1293 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847 | 73.0847
40% | 2059.1045 | 35.894 | 33.867 | 35.5787 | 31.1338 | 32.7402 | 34.3967 | 36.1558 | 38.1683 | 40.5371 | 42.757 | 45.0898 | 49.0589 | 50.4094 | 52.952 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 54.8973 | 40% | 741.202 | 41.9785 | 40.004 | 41.9419 | 37.7639 | 39.2008 | 41.4646 | 43.5109 | 46.3497 | 49.3094 | 51.7279 | 54.0092 | 57.395 | 59.8568 | 62.3371 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642 | 64.9642
35% | 3060.4836 | 31.4073 | 29.6336 | 31.1314 | 27.242 | 28.6477 | 30.0971 | 31.6363 | 33.3973 | 35.47 | 37.4124 | 39.4536 | 42.9265 | 44.1082 | 46.333 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 48.0351 | 35% | 1167.7713 | 36.7312 | 35.0035 | 36.6992 | 33.0434 | 34.3007 | 36.2815 | 38.0721 | 40.556 | 43.1457 | 45.2619 | 47.258 | 50.2206 | 52.3747 | 54.545 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436 | 56.8436
30% | 3366.0403 | 26.9205 | 25.4002 | 26.684 | 23.3503 | 24.5552 | 25.7975 | 27.1168 | 28.6263 | 30.4028 | 32.0678 | 33.8174 | 36.7942 | 37.807 | 39.714 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 41.173 | 30% | 2002.3799 | 31.4839 | 30.003 | 31.4564 | 28.3229 | 29.4006 | 31.0985 | 32.6332 | 34.7623 | 36.982 | 38.7959 | 40.5069 | 43.0463 | 44.8926 | 46.7528 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231 | 48.7231
25% | 3686.3454 | 22.4338 | 21.1669 | 22.2367 | 19.4586 | 20.4626 | 21.4979 | 22.5974 | 23.8552 | 25.3357 | 26.7231 | 28.1811 | 30.6618 | 31.5058 | 33.095 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 34.3108 | 25% | 3173.5547 | 26.2366 | 25.0025 | 26.2137 | 23.6024 | 24.5005 | 25.9154 | 27.1943 | 28.9686 | 30.8184 | 32.33 | 33.7557 | 35.8719 | 37.4105 | 38.9607 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026 | 40.6026
20% | 4028.5841 | 17.947 | 16.9335 | 17.7894 | 15.5669 | 16.3701 | 17.1983 | 18.0779 | 19.0842 | 20.2686 | 21.3785 | 22.5449 | 24.5294 | 25.2047 | 26.476 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 27.4486 | 20% | 3477.5988 | 20.9893 | 20.002 | 20.9709 | 18.882 | 19.6004 | 20.7323 | 21.7555 | 23.1748 | 24.6547 | 25.864 | 27.0046 | 28.6975 | 29.9284 | 31.1686 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821 | 32.4821
15% | 4345.1076 | 13.4603 | 12.7001 | 13.342 | 11.6752 | 12.2776 | 12.8988 | 13.5584 | 14.3131 | 15.2014 | 16.0339 | 16.9087 | 18.3971 | 18.9035 | 19.857 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 20.5865 | 15% | 3788.4498 | 15.7419 | 15.0015 | 15.7282 | 14.1615 | 14.7003 | 15.5492 | 16.3166 | 17.3811 | 18.491 | 19.398 | 20.2534 | 21.5231 | 22.4463 | 23.3764 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616 | 24.3616
10% | 4381.0332 | 8.9735 | 8.4667 | 8.8947 | 7.7834 | 8.1851 | 8.5992 | 9.0389 | 9.5421 | 10.1343 | 10.6893 | 11.2725 | 12.2647 | 12.6023 | 13.238 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 13.7243 | 10% | 4317.5016 | 10.4946 | 10.001 | 10.4855 | 9.441 | 9.8002 | 10.3662 | 10.8777 | 11.5874 | 12.3273 | 12.932 | 13.5023 | 14.3488 | 14.9642 | 15.5843 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241 | 16.241
5% | 4391.6218 | 4.4868 | 4.2334 | 4.4473 | 3.8917 | 4.0925 | 4.2996 | 4.5195 | 4.771 | 5.0671 | 5.3446 | 5.6362 | 6.1324 | 6.3012 | 6.619 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 6.8622 | 5% | 4391.6218 | 5.2473 | 5.0005 | 5.2427 | 4.7205 | 4.9001 | 5.1831 | 5.4389 | 5.7937 | 6.1637 | 6.466 | 6.7511 | 7.1744 | 7.4821 | 7.7921 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205 | 8.1205
9.992e-14% | 4391.6218 | 8.9663e-14 | 8.46e-14 | 8.8876e-14 | 7.7772e-14 | 8.1785e-14 | 8.5923e-14 | 9.0317e-14 | 9.5345e-14 | 1.0126e-13 | 1.0681e-13 | 1.1263e-13 | 1.2255e-13 | 1.2592e-13 | 1.3227e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 1.3713e-13 | 9.992e-14% | 4391.6218 | 1.0486e-13 | 9.993e-14 | 1.0477e-13 | 9.4334e-14 | 9.7924e-14 | 1.0358e-13 | 1.0869e-13 | 1.1578e-13 | 1.2317e-13 | 1.2922e-13 | 1.3492e-13 | 1.4337e-13 | 1.4952e-13 | 1.5572e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13 | 1.6228e-13
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 100% | 0 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
99% | 0.5944 | 68.427 | 64.2027 | 68.066 | 73.0038 | 77.7847 | 82.0399 | 87.8842 | 94.2725 | 100.8151 | 107.2984 | 113.0603 | 119.3404 | 121.738 | 129.8557 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 99% | 0.5944 | 73.2778 | 69.0729 | 73.1555 | 78.154 | 82.814 | 87.7759 | 92.9942 | 100.4376 | 106.9274 | 113.0485 | 119.4102 | 127.0352 | 129.5879 | 137.8107 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748
98% | 0.8916 | 67.7358 | 63.5542 | 67.3784 | 72.2664 | 76.999 | 81.2112 | 86.9965 | 93.3203 | 99.7967 | 106.2146 | 111.9183 | 118.135 | 120.5083 | 128.544 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 98% | 0.8916 | 72.5377 | 68.3752 | 72.4165 | 77.3646 | 81.9775 | 86.8893 | 92.0548 | 99.4231 | 105.8473 | 111.9066 | 118.204 | 125.752 | 128.279 | 136.4186 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053
97% | 1.486 | 67.0447 | 62.9057 | 66.6909 | 71.529 | 76.2133 | 80.3826 | 86.1088 | 92.3681 | 98.7784 | 105.1308 | 110.7763 | 116.9295 | 119.2786 | 127.2324 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 97% | 1.486 | 71.7975 | 67.6774 | 71.6776 | 76.5751 | 81.1409 | 86.0026 | 91.1155 | 98.4086 | 104.7673 | 110.7647 | 116.9979 | 124.4688 | 126.97 | 135.0266 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359
95% | 2.3776 | 65.6623 | 61.6087 | 65.3158 | 70.0541 | 74.6418 | 78.7252 | 84.3333 | 90.4636 | 96.7417 | 102.9631 | 108.4922 | 114.5186 | 116.8193 | 124.609 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 95% | 2.3776 | 70.3171 | 66.282 | 70.1997 | 74.9963 | 79.4679 | 84.2294 | 89.2368 | 96.3795 | 102.6071 | 108.4809 | 114.5855 | 121.9024 | 124.3521 | 132.2425 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597
90% | 3.2692 | 62.2064 | 58.3661 | 61.8782 | 66.3671 | 70.7133 | 74.5817 | 79.8947 | 85.7023 | 91.6501 | 97.544 | 102.7821 | 108.4913 | 110.6709 | 118.0507 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 90% | 3.2692 | 66.6162 | 62.7935 | 66.505 | 71.0491 | 75.2854 | 79.7963 | 84.5401 | 91.3069 | 97.2067 | 102.7713 | 108.5547 | 115.4865 | 117.8072 | 125.2824 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498
85% | 13.9683 | 58.7505 | 55.1235 | 58.4405 | 62.68 | 66.7848 | 70.4383 | 75.4561 | 80.9411 | 86.5584 | 92.1249 | 97.072 | 102.464 | 104.5225 | 111.4923 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 85% | 13.9683 | 62.9153 | 59.305 | 62.8103 | 67.1019 | 71.1029 | 75.3631 | 79.8435 | 86.2343 | 91.8064 | 97.0618 | 102.5239 | 109.0706 | 111.2624 | 118.3223 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026
80% | 41.3106 | 55.2946 | 51.881 | 55.0028 | 58.993 | 62.8563 | 66.2949 | 71.0175 | 76.1798 | 81.4667 | 86.7058 | 91.3619 | 96.4367 | 98.3741 | 104.9339 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 80% | 41.3106 | 59.2144 | 55.8165 | 59.1156 | 63.1548 | 66.9204 | 70.93 | 75.1468 | 81.1617 | 86.406 | 91.3523 | 96.4931 | 102.6547 | 104.7175 | 111.3621 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554
75% | 126.3094 | 51.8387 | 48.6384 | 51.5651 | 55.3059 | 58.9278 | 62.1515 | 66.579 | 71.4186 | 76.375 | 81.2867 | 85.6518 | 90.4094 | 92.2257 | 98.3755 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 75% | 126.3094 | 55.5135 | 52.3279 | 55.4208 | 59.2076 | 62.7378 | 66.4969 | 70.4501 | 76.0891 | 81.0056 | 85.6428 | 90.4623 | 96.2388 | 98.1727 | 104.402 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082
70% | 323.9464 | 48.3827 | 45.3959 | 48.1275 | 51.6188 | 54.9993 | 58.008 | 62.1404 | 66.6574 | 71.2834 | 75.8676 | 79.9417 | 84.3821 | 86.0773 | 91.8172 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 70% | 323.9464 | 51.8126 | 48.8394 | 51.7261 | 55.2604 | 58.5553 | 62.0638 | 65.7534 | 71.0165 | 75.6052 | 79.9333 | 84.4314 | 89.8228 | 91.6278 | 97.4419 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861
65% | 549.5201 | 44.9268 | 42.1533 | 44.6898 | 47.9318 | 51.0707 | 53.8646 | 57.7018 | 61.8961 | 66.1917 | 70.4485 | 74.2315 | 78.3548 | 79.929 | 85.2588 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 65% | 549.5201 | 48.1117 | 45.3509 | 48.0314 | 51.3132 | 54.3728 | 57.6306 | 61.0568 | 65.9439 | 70.2049 | 74.2237 | 78.4006 | 83.4069 | 85.083 | 90.4817 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137
60% | 799.4641 | 41.4709 | 38.9107 | 41.2521 | 44.2447 | 47.1422 | 49.7212 | 53.2632 | 57.1349 | 61.1 | 65.0294 | 68.5214 | 72.3275 | 73.7806 | 78.7004 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 60% | 799.4641 | 44.4108 | 41.8623 | 44.3367 | 47.3661 | 50.1903 | 53.1975 | 56.3601 | 60.8713 | 64.8045 | 68.5142 | 72.3698 | 76.991 | 78.5381 | 83.5216 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665
55% | 1116.2777 | 38.015 | 35.6682 | 37.8144 | 40.5577 | 43.2137 | 45.5777 | 48.8246 | 52.3736 | 56.0084 | 59.6102 | 62.8113 | 66.3002 | 67.6322 | 72.1421 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 55% | 1116.2777 | 40.7099 | 38.3738 | 40.6419 | 43.4189 | 46.0078 | 48.7644 | 51.6634 | 55.7987 | 59.4041 | 62.8047 | 66.339 | 70.5751 | 71.9933 | 76.5615 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193
50% | 1494.9086 | 34.5591 | 32.4256 | 34.3768 | 36.8706 | 39.2852 | 41.4343 | 44.386 | 47.6124 | 50.9167 | 54.1911 | 57.1012 | 60.2729 | 61.4838 | 65.5837 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 50% | 1494.9086 | 37.009 | 34.8853 | 36.9472 | 39.4717 | 41.8252 | 44.3313 | 46.9667 | 50.7261 | 54.0037 | 57.0952 | 60.3082 | 64.1592 | 65.4485 | 69.6013 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721
45% | 2004.0097 | 31.1032 | 29.183 | 30.9391 | 33.1835 | 35.3567 | 37.2909 | 39.9474 | 42.8512 | 45.825 | 48.772 | 51.3911 | 54.2456 | 55.3354 | 59.0253 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 45% | 2004.0097 | 33.3081 | 31.3968 | 33.2525 | 35.5246 | 37.6427 | 39.8981 | 42.2701 | 45.6535 | 48.6034 | 51.3857 | 54.2774 | 57.7433 | 58.9036 | 62.6412 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249
40% | 2877.179 | 27.6473 | 25.9405 | 27.5014 | 29.4965 | 31.4281 | 33.1474 | 35.5088 | 38.0899 | 40.7334 | 43.3529 | 45.6809 | 48.2184 | 49.1871 | 52.467 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 40% | 2877.179 | 29.6072 | 27.9082 | 29.5578 | 31.5774 | 33.4602 | 35.465 | 37.5734 | 40.5808 | 43.203 | 45.6762 | 48.2465 | 51.3273 | 52.3588 | 55.6811 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777
35% | 3454.933 | 24.1914 | 22.6979 | 24.0637 | 25.8094 | 27.4996 | 29.004 | 31.0702 | 33.3287 | 35.6417 | 37.9338 | 39.9708 | 42.1911 | 43.0387 | 45.9086 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 35% | 3454.933 | 25.9063 | 24.4197 | 25.8631 | 27.6302 | 29.2777 | 31.0319 | 32.8767 | 35.5082 | 37.8026 | 39.9666 | 42.2157 | 44.9114 | 45.8139 | 48.7209 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305
30% | 3663.5664 | 20.7355 | 19.4554 | 20.6261 | 22.1224 | 23.5711 | 24.8606 | 26.6316 | 28.5674 | 30.55 | 32.5147 | 34.2607 | 36.1638 | 36.8903 | 39.3502 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 30% | 3663.5664 | 22.2054 | 20.9312 | 22.1683 | 23.683 | 25.0951 | 26.5988 | 28.18 | 30.4356 | 32.4022 | 34.2571 | 36.1849 | 38.4955 | 39.2691 | 41.7608 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833
25% | 3862.6894 | 17.2796 | 16.2128 | 17.1884 | 18.4353 | 19.6426 | 20.7172 | 22.193 | 23.8062 | 25.4583 | 27.0956 | 28.5506 | 30.1365 | 30.7419 | 32.7918 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 25% | 3862.6894 | 18.5045 | 17.4426 | 18.4736 | 19.7359 | 20.9126 | 22.1656 | 23.4834 | 25.363 | 27.0019 | 28.5476 | 30.1541 | 32.0796 | 32.7242 | 34.8007 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361
20% | 4122.7381 | 13.8236 | 12.9702 | 13.7507 | 14.7482 | 15.7141 | 16.5737 | 17.7544 | 19.045 | 20.3667 | 21.6765 | 22.8405 | 24.1092 | 24.5935 | 26.2335 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 20% | 4122.7381 | 14.8036 | 13.9541 | 14.7789 | 15.7887 | 16.7301 | 17.7325 | 18.7867 | 20.2904 | 21.6015 | 22.8381 | 24.1233 | 25.6637 | 26.1794 | 27.8405 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888
15% | 4372.3849 | 10.3677 | 9.7277 | 10.313 | 11.0612 | 11.7856 | 12.4303 | 13.3158 | 14.2837 | 15.275 | 16.2573 | 17.1304 | 18.0819 | 18.4451 | 19.6751 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 15% | 4372.3849 | 11.1027 | 10.4656 | 11.0842 | 11.8415 | 12.5476 | 13.2994 | 14.09 | 15.2178 | 16.2011 | 17.1286 | 18.0925 | 19.2478 | 19.6345 | 20.8804 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416
10% | 4374.4653 | 6.9118 | 6.4851 | 6.8754 | 7.3741 | 7.857 | 8.2869 | 8.8772 | 9.5225 | 10.1833 | 10.8382 | 11.4202 | 12.0546 | 12.2968 | 13.1167 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 10% | 4374.4653 | 7.4018 | 6.9771 | 7.3894 | 7.8943 | 8.365 | 8.8663 | 9.3933 | 10.1452 | 10.8007 | 11.419 | 12.0616 | 12.8318 | 13.0897 | 13.9203 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944
5% | 4374.7625 | 3.4559 | 3.2426 | 3.4377 | 3.6871 | 3.9285 | 4.1434 | 4.4386 | 4.7612 | 5.0917 | 5.4191 | 5.7101 | 6.0273 | 6.1484 | 6.5584 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 5% | 4374.7625 | 3.7009 | 3.4885 | 3.6947 | 3.9472 | 4.1825 | 4.4331 | 4.6967 | 5.0726 | 5.4004 | 5.7095 | 6.0308 | 6.4159 | 6.5448 | 6.9601 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472
9.992e-14% | 4375.9513 | 6.9063e-14 | 6.4799e-14 | 6.8699e-14 | 7.3682e-14 | 7.8508e-14 | 8.2802e-14 | 8.8701e-14 | 9.5149e-14 | 1.0175e-13 | 1.083e-13 | 1.1411e-13 | 1.2045e-13 | 1.2287e-13 | 1.3106e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 9.992e-14% | 4375.9513 | 7.3959e-14 | 6.9715e-14 | 7.3835e-14 | 7.888e-14 | 8.3584e-14 | 8.8592e-14 | 9.3858e-14 | 1.0137e-13 | 1.0792e-13 | 1.141e-13 | 1.2052e-13 | 1.2822e-13 | 1.3079e-13 | 1.3909e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 100% | 0 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104
99% | 0 | 88.8377 | 83.8207 | 88.0573 | 91.4111 | 95.3871 | 99.4868 | 103.8405 | 108.8216 | 114.6843 | 120.1786 | 125.9523 | 135.7757 | 139.1181 | 145.4111 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 99% | 0.37816 | 103.8968 | 99.0099 | 103.8062 | 107.8207 | 111.3769 | 116.9799 | 122.0445 | 129.0705 | 136.3958 | 142.3816 | 148.0278 | 156.4077 | 162.5005 | 168.6394 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413
98% | 0.37816 | 87.9404 | 82.9741 | 87.1679 | 90.4877 | 94.4236 | 98.4819 | 102.7916 | 107.7224 | 113.5259 | 118.9647 | 124.6801 | 134.4042 | 137.7129 | 143.9423 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 98% | 1.1345 | 102.8473 | 98.0098 | 102.7576 | 106.7316 | 110.2519 | 115.7983 | 120.8117 | 127.7667 | 135.018 | 140.9434 | 146.5325 | 154.8278 | 160.8591 | 166.9359 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722
97% | 0.75633 | 87.043 | 82.1274 | 86.2784 | 89.5644 | 93.4601 | 97.4769 | 101.7427 | 106.6232 | 112.3675 | 117.7507 | 123.4079 | 133.0328 | 136.3077 | 142.4735 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 97% | 2.269 | 101.7979 | 97.0097 | 101.7091 | 105.6425 | 109.1268 | 114.6167 | 119.579 | 126.463 | 133.6403 | 139.5052 | 145.0373 | 153.2479 | 159.2176 | 165.2325 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031
95% | 1.1345 | 85.2483 | 80.434 | 84.4994 | 87.7177 | 91.5331 | 95.4671 | 99.6449 | 104.4248 | 110.0506 | 115.3229 | 120.8634 | 130.2898 | 133.4972 | 139.5359 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 95% | 4.538 | 99.699 | 95.0095 | 99.612 | 103.4643 | 106.8768 | 112.2534 | 117.1134 | 123.8555 | 130.8848 | 136.6288 | 142.0468 | 150.0882 | 155.9348 | 161.8257 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649
90% | 4.538 | 80.7616 | 76.2007 | 80.0521 | 83.101 | 86.7155 | 90.4425 | 94.4005 | 98.9288 | 104.2585 | 109.2533 | 114.5021 | 123.4325 | 126.471 | 132.1919 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 90% | 7.9414 | 94.4516 | 90.009 | 94.3693 | 98.0188 | 101.2517 | 106.3454 | 110.9496 | 117.3368 | 123.9961 | 129.4378 | 134.5707 | 142.1888 | 147.7277 | 153.3085 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194
85% | 7.9414 | 76.2748 | 71.9673 | 75.6048 | 78.4843 | 81.898 | 85.4179 | 89.156 | 93.4327 | 98.4663 | 103.1836 | 108.1409 | 116.5751 | 119.4449 | 124.8479 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 85% | 14.3702 | 89.2043 | 85.0085 | 89.1265 | 92.5733 | 95.6266 | 100.4373 | 104.7857 | 110.8181 | 117.1075 | 122.2468 | 127.0945 | 134.2894 | 139.5206 | 144.7914 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738
80% | 11.7231 | 71.788 | 67.7339 | 71.1574 | 73.8675 | 77.0805 | 80.3933 | 83.9115 | 87.9367 | 92.6742 | 97.114 | 101.7797 | 109.7177 | 112.4187 | 117.5039 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 80% | 19.6645 | 83.957 | 80.008 | 83.8838 | 87.1278 | 90.0015 | 94.5292 | 98.6218 | 104.2994 | 110.2188 | 115.0559 | 119.6184 | 126.39 | 131.3135 | 136.2742 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283
75% | 17.7737 | 67.3013 | 63.5006 | 66.7101 | 69.2508 | 72.2629 | 75.3688 | 78.6671 | 82.4406 | 86.8821 | 91.0444 | 95.4184 | 102.8604 | 105.3925 | 110.16 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 75% | 25.7152 | 78.7097 | 75.0075 | 78.641 | 81.6823 | 84.3764 | 88.6211 | 92.458 | 97.7807 | 103.3301 | 107.8649 | 112.1422 | 118.4907 | 123.1064 | 127.7571 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828
70% | 35.1693 | 62.8145 | 59.2672 | 62.2628 | 64.6341 | 67.4454 | 70.3442 | 73.4226 | 76.9446 | 81.0899 | 84.9748 | 89.0572 | 96.003 | 98.3664 | 102.816 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 70% | 34.7911 | 73.4624 | 70.007 | 73.3983 | 76.2368 | 78.7513 | 82.7131 | 86.2941 | 91.262 | 96.4414 | 100.6739 | 104.6661 | 110.5913 | 114.8993 | 119.24 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373
65% | 59.3718 | 58.3278 | 55.0338 | 57.8154 | 60.0174 | 62.6279 | 65.3196 | 68.1781 | 71.4486 | 75.2978 | 78.9051 | 82.696 | 89.1457 | 91.3402 | 95.472 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 65% | 46.136 | 68.2151 | 65.0065 | 68.1556 | 70.7913 | 73.1262 | 76.805 | 80.1302 | 84.7432 | 89.5528 | 93.4829 | 97.1899 | 102.6919 | 106.6922 | 110.7228 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918
60% | 156.9382 | 53.841 | 50.8005 | 53.3681 | 55.4007 | 57.8104 | 60.295 | 62.9336 | 65.9525 | 69.5057 | 72.8355 | 76.3348 | 82.2883 | 84.314 | 88.128 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 60% | 76.7673 | 62.9678 | 60.006 | 62.9128 | 65.3459 | 67.5011 | 70.8969 | 73.9664 | 78.2245 | 82.6641 | 86.2919 | 89.7138 | 94.7925 | 98.4851 | 102.2057 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462
55% | 363.794 | 49.3543 | 46.5671 | 48.9207 | 50.7839 | 52.9928 | 55.2704 | 57.6892 | 60.4565 | 63.7135 | 66.7659 | 69.9735 | 75.4309 | 77.2879 | 80.784 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 55% | 106.2642 | 57.7205 | 55.0055 | 57.6701 | 59.9004 | 61.876 | 64.9888 | 67.8025 | 71.7058 | 75.7754 | 79.1009 | 82.2376 | 86.8932 | 90.278 | 93.6885 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007
50% | 771.4551 | 44.8675 | 42.3337 | 44.4734 | 46.1672 | 48.1753 | 50.2458 | 52.4447 | 54.9604 | 57.9214 | 60.6963 | 63.6123 | 68.5736 | 70.2617 | 73.44 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 50% | 178.4935 | 52.4731 | 50.005 | 52.4274 | 54.4549 | 56.251 | 59.0808 | 61.6386 | 65.1871 | 68.8867 | 71.9099 | 74.7615 | 78.9938 | 82.0709 | 85.1714 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552
45% | 1255.5054 | 40.3808 | 38.1003 | 40.0261 | 41.5505 | 43.3578 | 45.2213 | 47.2002 | 49.4644 | 52.1292 | 54.6266 | 57.2511 | 61.7162 | 63.2355 | 66.096 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 45% | 367.9538 | 47.2258 | 45.0045 | 47.1846 | 49.0094 | 50.6259 | 53.1727 | 55.4748 | 58.6684 | 61.9981 | 64.7189 | 67.2853 | 71.0944 | 73.8639 | 76.6543 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097
40% | 2059.1045 | 35.894 | 33.867 | 35.5787 | 36.9338 | 38.5402 | 40.1967 | 41.9558 | 43.9683 | 46.3371 | 48.557 | 50.8898 | 54.8589 | 56.2094 | 58.752 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 40% | 741.202 | 41.9785 | 40.004 | 41.9419 | 43.5639 | 45.0008 | 47.2646 | 49.3109 | 52.1497 | 55.1094 | 57.5279 | 59.8092 | 63.195 | 65.6568 | 68.1371 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642
35% | 3060.4836 | 31.4073 | 29.6336 | 31.1314 | 32.317 | 33.7227 | 35.1721 | 36.7113 | 38.4723 | 40.545 | 42.4874 | 44.5286 | 48.0015 | 49.1832 | 51.408 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 35% | 1167.7713 | 36.7312 | 35.0035 | 36.6992 | 38.1184 | 39.3757 | 41.3565 | 43.1471 | 45.631 | 48.2207 | 50.3369 | 52.333 | 55.2956 | 57.4497 | 59.62 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186
30% | 3366.0403 | 26.9205 | 25.4002 | 26.684 | 27.7003 | 28.9052 | 30.1475 | 31.4668 | 32.9763 | 34.7528 | 36.4178 | 38.1674 | 41.1442 | 42.157 | 44.064 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 30% | 2002.3799 | 31.4839 | 30.003 | 31.4564 | 32.6729 | 33.7506 | 35.4485 | 36.9832 | 39.1123 | 41.332 | 43.1459 | 44.8569 | 47.3963 | 49.2426 | 51.1028 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731
25% | 3686.3454 | 22.4338 | 21.1669 | 22.2367 | 23.0836 | 24.0876 | 25.1229 | 26.2224 | 27.4802 | 28.9607 | 30.3481 | 31.8061 | 34.2868 | 35.1308 | 36.72 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 25% | 3173.5547 | 26.2366 | 25.0025 | 26.2137 | 27.2274 | 28.1255 | 29.5404 | 30.8193 | 32.5936 | 34.4434 | 35.955 | 37.3807 | 39.4969 | 41.0355 | 42.5857 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276
20% | 4028.5841 | 17.947 | 16.9335 | 17.7894 | 18.4669 | 19.2701 | 20.0983 | 20.9779 | 21.9842 | 23.1686 | 24.2785 | 25.4449 | 27.4294 | 28.1047 | 29.376 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 20% | 3477.5988 | 20.9893 | 20.002 | 20.9709 | 21.782 | 22.5004 | 23.6323 | 24.6555 | 26.0748 | 27.5547 | 28.764 | 29.9046 | 31.5975 | 32.8284 | 34.0686 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821
15% | 4345.1076 | 13.4603 | 12.7001 | 13.342 | 13.8502 | 14.4526 | 15.0738 | 15.7334 | 16.4881 | 17.3764 | 18.2089 | 19.0837 | 20.5721 | 21.0785 | 22.032 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 15% | 3788.4498 | 15.7419 | 15.0015 | 15.7282 | 16.3365 | 16.8753 | 17.7242 | 18.4916 | 19.5561 | 20.666 | 21.573 | 22.4284 | 23.6981 | 24.6213 | 25.5514 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366
10% | 4381.0332 | 8.9735 | 8.4667 | 8.8947 | 9.2334 | 9.6351 | 10.0492 | 10.4889 | 10.9921 | 11.5843 | 12.1393 | 12.7225 | 13.7147 | 14.0523 | 14.688 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 10% | 4317.5016 | 10.4946 | 10.001 | 10.4855 | 10.891 | 11.2502 | 11.8162 | 12.3277 | 13.0374 | 13.7773 | 14.382 | 14.9523 | 15.7988 | 16.4142 | 17.0343 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691
5% | 4391.6218 | 4.4868 | 4.2334 | 4.4473 | 4.6167 | 4.8175 | 5.0246 | 5.2445 | 5.496 | 5.7921 | 6.0696 | 6.3612 | 6.8574 | 7.0262 | 7.344 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 5% | 4391.6218 | 5.2473 | 5.0005 | 5.2427 | 5.4455 | 5.6251 | 5.9081 | 6.1639 | 6.5187 | 6.8887 | 7.191 | 7.4761 | 7.8994 | 8.2071 | 8.5171 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455
9.992e-14% | 4391.6218 | 8.9663e-14 | 8.46e-14 | 8.8876e-14 | 9.2261e-14 | 9.6274e-14 | 1.0041e-13 | 1.0481e-13 | 1.0983e-13 | 1.1575e-13 | 1.213e-13 | 1.2712e-13 | 1.3704e-13 | 1.4041e-13 | 1.4676e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 9.992e-14% | 4391.6218 | 1.0486e-13 | 9.993e-14 | 1.0477e-13 | 1.0882e-13 | 1.1241e-13 | 1.1807e-13 | 1.2318e-13 | 1.3027e-13 | 1.3766e-13 | 1.437e-13 | 1.494e-13 | 1.5786e-13 | 1.6401e-13 | 1.7021e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 69.1182 | 64.8512 | 68.7535 | 54.4079 | 59.237 | 63.5353 | 69.4386 | 75.8915 | 82.5001 | 89.0489 | 94.869 | 101.2125 | 103.6343 | 111.8341 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 120.3156 | 100% | 0 | 74.018 | 69.7706 | 73.8944 | 59.6101 | 64.3171 | 69.3292 | 74.6002 | 82.1188 | 88.6742 | 94.857 | 101.283 | 108.985 | 111.5636 | 119.8693 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109 | 127.6109
99% | 0.5944 | 68.427 | 64.2027 | 68.066 | 53.8638 | 58.6447 | 62.8999 | 68.7442 | 75.1325 | 81.6751 | 88.1584 | 93.9203 | 100.2004 | 102.598 | 110.7157 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 119.1125 | 99% | 0.5944 | 73.2778 | 69.0729 | 73.1555 | 59.014 | 63.674 | 68.6359 | 73.8542 | 81.2976 | 87.7874 | 93.9085 | 100.2702 | 107.8952 | 110.4479 | 118.6707 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348 | 126.3348
98% | 0.8916 | 67.7358 | 63.5542 | 67.3784 | 53.3197 | 58.0523 | 62.2646 | 68.0498 | 74.3736 | 80.8501 | 87.2679 | 92.9717 | 99.1883 | 101.5616 | 109.5974 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 117.9093 | 98% | 0.8916 | 72.5377 | 68.3752 | 72.4165 | 58.4179 | 63.0308 | 67.9426 | 73.1082 | 80.4764 | 86.9007 | 92.9599 | 99.2574 | 106.8053 | 109.3323 | 117.472 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587 | 125.0587
97% | 1.486 | 67.0447 | 62.9057 | 66.6909 | 52.7756 | 57.4599 | 61.6292 | 67.3554 | 73.6147 | 80.0251 | 86.3775 | 92.023 | 98.1762 | 100.5253 | 108.479 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 116.7061 | 97% | 1.486 | 71.7975 | 67.6774 | 71.6776 | 57.8218 | 62.3876 | 67.2493 | 72.3621 | 79.6552 | 86.0139 | 92.0113 | 98.2445 | 105.7155 | 108.2167 | 116.2733 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826 | 123.7826
95% | 2.3776 | 65.6623 | 61.6087 | 65.3158 | 51.6875 | 56.2752 | 60.3585 | 65.9667 | 72.0969 | 78.3751 | 84.5965 | 90.1256 | 96.1519 | 98.4526 | 106.2424 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 114.2998 | 95% | 2.3776 | 70.3171 | 66.282 | 70.1997 | 56.6296 | 61.1013 | 65.8627 | 70.8701 | 78.0128 | 84.2404 | 90.1142 | 96.2189 | 103.5358 | 105.9854 | 113.8759 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303 | 121.2303
90% | 3.2692 | 62.2064 | 58.3661 | 61.8782 | 48.9671 | 53.3133 | 57.1817 | 62.4947 | 68.3023 | 74.2501 | 80.144 | 85.3821 | 91.0913 | 93.2709 | 100.6507 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 108.284 | 90% | 3.2692 | 66.6162 | 62.7935 | 66.505 | 53.6491 | 57.8854 | 62.3963 | 67.1401 | 73.9069 | 79.8067 | 85.3713 | 91.1547 | 98.0865 | 100.4072 | 107.8824 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498 | 114.8498
85% | 13.9683 | 58.7505 | 55.1235 | 58.4405 | 46.2467 | 50.3515 | 54.005 | 59.0228 | 64.5077 | 70.1251 | 75.6916 | 80.6387 | 86.0307 | 88.0892 | 95.0589 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 102.2683 | 85% | 13.9683 | 62.9153 | 59.305 | 62.8103 | 50.6686 | 54.6696 | 58.9298 | 63.4101 | 69.801 | 75.373 | 80.6285 | 86.0906 | 92.6373 | 94.829 | 101.8889 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693 | 108.4693
80% | 41.3106 | 55.2946 | 51.881 | 55.0028 | 43.5263 | 47.3896 | 50.8282 | 55.5509 | 60.7132 | 66.0001 | 71.2391 | 75.8952 | 80.97 | 82.9074 | 89.4672 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 96.2525 | 80% | 41.3106 | 59.2144 | 55.8165 | 59.1156 | 47.6881 | 51.4537 | 55.4633 | 59.6801 | 65.695 | 70.9393 | 75.8856 | 81.0264 | 87.188 | 89.2509 | 95.8955 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887 | 102.0887
75% | 126.3094 | 51.8387 | 48.6384 | 51.5651 | 40.8059 | 44.4278 | 47.6515 | 52.079 | 56.9186 | 61.875 | 66.7867 | 71.1518 | 75.9094 | 77.7257 | 83.8755 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 90.2367 | 75% | 126.3094 | 55.5135 | 52.3279 | 55.4208 | 44.7076 | 48.2378 | 51.9969 | 55.9501 | 61.5891 | 66.5056 | 71.1428 | 75.9623 | 81.7388 | 83.6727 | 89.902 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082 | 95.7082
70% | 323.9464 | 48.3827 | 45.3959 | 48.1275 | 38.0855 | 41.4659 | 44.4747 | 48.607 | 53.124 | 57.75 | 62.3342 | 66.4083 | 70.8488 | 72.544 | 78.2838 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 84.2209 | 70% | 323.9464 | 51.8126 | 48.8394 | 51.7261 | 41.7271 | 45.022 | 48.5304 | 52.2201 | 57.4831 | 62.0719 | 66.3999 | 70.8981 | 76.2895 | 78.0945 | 83.9085 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276 | 89.3276
65% | 549.5201 | 44.9268 | 42.1533 | 44.6898 | 35.3651 | 38.5041 | 41.2979 | 45.1351 | 49.3295 | 53.625 | 57.8818 | 61.6649 | 65.7882 | 67.3623 | 72.6921 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 78.2051 | 65% | 549.5201 | 48.1117 | 45.3509 | 48.0314 | 38.7466 | 41.8061 | 45.064 | 48.4901 | 53.3772 | 57.6382 | 61.6571 | 65.834 | 70.8403 | 72.5163 | 77.9151 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471 | 82.9471
60% | 799.4641 | 41.4709 | 38.9107 | 41.2521 | 32.6447 | 35.5422 | 38.1212 | 41.6632 | 45.5349 | 49.5 | 53.4294 | 56.9214 | 60.7275 | 62.1806 | 67.1004 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 72.1894 | 60% | 799.4641 | 44.4108 | 41.8623 | 44.3367 | 35.7661 | 38.5903 | 41.5975 | 44.7601 | 49.2713 | 53.2045 | 56.9142 | 60.7698 | 65.391 | 66.9381 | 71.9216 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665 | 76.5665
55% | 1116.2777 | 38.015 | 35.6682 | 37.8144 | 29.9243 | 32.5804 | 34.9444 | 38.1912 | 41.7403 | 45.375 | 48.9769 | 52.178 | 55.6669 | 56.9989 | 61.5087 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 66.1736 | 55% | 1116.2777 | 40.7099 | 38.3738 | 40.6419 | 32.7856 | 35.3744 | 38.131 | 41.0301 | 45.1653 | 48.7708 | 52.1714 | 55.7057 | 59.9418 | 61.36 | 65.9281 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186 | 70.186
50% | 1494.9086 | 34.5591 | 32.4256 | 34.3768 | 27.2039 | 29.6185 | 31.7676 | 34.7193 | 37.9457 | 41.25 | 44.5245 | 47.4345 | 50.6063 | 51.8172 | 55.917 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 60.1578 | 50% | 1494.9086 | 37.009 | 34.8853 | 36.9472 | 29.8051 | 32.1586 | 34.6646 | 37.3001 | 41.0594 | 44.3371 | 47.4285 | 50.6415 | 54.4925 | 55.7818 | 59.9347 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054 | 63.8054
45% | 2004.0097 | 31.1032 | 29.183 | 30.9391 | 24.4835 | 26.6567 | 28.5909 | 31.2474 | 34.1512 | 37.125 | 40.072 | 42.6911 | 45.5456 | 46.6354 | 50.3253 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 54.142 | 45% | 2004.0097 | 33.3081 | 31.3968 | 33.2525 | 26.8246 | 28.9427 | 31.1981 | 33.5701 | 36.9535 | 39.9034 | 42.6857 | 45.5774 | 49.0433 | 50.2036 | 53.9412 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249 | 57.4249
40% | 2877.179 | 27.6473 | 25.9405 | 27.5014 | 21.7631 | 23.6948 | 25.4141 | 27.7754 | 30.3566 | 33 | 35.6196 | 37.9476 | 40.485 | 41.4537 | 44.7336 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 48.1262 | 40% | 2877.179 | 29.6072 | 27.9082 | 29.5578 | 23.844 | 25.7269 | 27.7317 | 29.8401 | 32.8475 | 35.4697 | 37.9428 | 40.5132 | 43.594 | 44.6254 | 47.9477 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444 | 51.0444
35% | 3454.933 | 24.1914 | 22.6979 | 24.0637 | 19.0428 | 20.733 | 22.2373 | 24.3035 | 26.562 | 28.875 | 31.1671 | 33.2042 | 35.4244 | 36.272 | 39.1419 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 42.1105 | 35% | 3454.933 | 25.9063 | 24.4197 | 25.8631 | 20.8635 | 22.511 | 24.2652 | 26.1101 | 28.7416 | 31.036 | 33.2 | 35.4491 | 38.1448 | 39.0473 | 41.9543 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638 | 44.6638
30% | 3663.5664 | 20.7355 | 19.4554 | 20.6261 | 16.3224 | 17.7711 | 19.0606 | 20.8316 | 22.7674 | 24.75 | 26.7147 | 28.4607 | 30.3638 | 31.0903 | 33.5502 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 36.0947 | 30% | 3663.5664 | 22.2054 | 20.9312 | 22.1683 | 17.883 | 19.2951 | 20.7988 | 22.38 | 24.6356 | 26.6022 | 28.4571 | 30.3849 | 32.6955 | 33.4691 | 35.9608 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833 | 38.2833
25% | 3862.6894 | 17.2796 | 16.2128 | 17.1884 | 13.602 | 14.8093 | 15.8838 | 17.3597 | 18.9729 | 20.625 | 22.2622 | 23.7173 | 25.3031 | 25.9086 | 27.9585 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 30.0789 | 25% | 3862.6894 | 18.5045 | 17.4426 | 18.4736 | 14.9025 | 16.0793 | 17.3323 | 18.65 | 20.5297 | 22.1685 | 23.7143 | 25.3208 | 27.2463 | 27.8909 | 29.9673 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027 | 31.9027
20% | 4122.7381 | 13.8236 | 12.9702 | 13.7507 | 10.8816 | 11.8474 | 12.7071 | 13.8877 | 15.1783 | 16.5 | 17.8098 | 18.9738 | 20.2425 | 20.7269 | 22.3668 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 24.0631 | 20% | 4122.7381 | 14.8036 | 13.9541 | 14.7789 | 11.922 | 12.8634 | 13.8658 | 14.92 | 16.4238 | 17.7348 | 18.9714 | 20.2566 | 21.797 | 22.3127 | 23.9739 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222 | 25.5222
15% | 4372.3849 | 10.3677 | 9.7277 | 10.313 | 8.1612 | 8.8856 | 9.5303 | 10.4158 | 11.3837 | 12.375 | 13.3573 | 14.2304 | 15.1819 | 15.5451 | 16.7751 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 18.0473 | 15% | 4372.3849 | 11.1027 | 10.4656 | 11.0842 | 8.9415 | 9.6476 | 10.3994 | 11.19 | 12.3178 | 13.3011 | 14.2286 | 15.1925 | 16.3478 | 16.7345 | 17.9804 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416 | 19.1416
10% | 4374.4653 | 6.9118 | 6.4851 | 6.8754 | 5.4408 | 5.9237 | 6.3535 | 6.9439 | 7.5891 | 8.25 | 8.9049 | 9.4869 | 10.1213 | 10.3634 | 11.1834 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 12.0316 | 10% | 4374.4653 | 7.4018 | 6.9771 | 7.3894 | 5.961 | 6.4317 | 6.9329 | 7.46 | 8.2119 | 8.8674 | 9.4857 | 10.1283 | 10.8985 | 11.1564 | 11.9869 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611 | 12.7611
5% | 4374.7625 | 3.4559 | 3.2426 | 3.4377 | 2.7204 | 2.9619 | 3.1768 | 3.4719 | 3.7946 | 4.125 | 4.4524 | 4.7435 | 5.0606 | 5.1817 | 5.5917 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 6.0158 | 5% | 4374.7625 | 3.7009 | 3.4885 | 3.6947 | 2.9805 | 3.2159 | 3.4665 | 3.73 | 4.1059 | 4.4337 | 4.7429 | 5.0642 | 5.4493 | 5.5782 | 5.9935 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805 | 6.3805
9.992e-14% | 4375.9513 | 6.9063e-14 | 6.4799e-14 | 6.8699e-14 | 5.4364e-14 | 5.919e-14 | 6.3484e-14 | 6.9383e-14 | 7.5831e-14 | 8.2434e-14 | 8.8978e-14 | 9.4793e-14 | 1.0113e-13 | 1.0355e-13 | 1.1174e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 1.2022e-13 | 9.992e-14% | 4375.9513 | 7.3959e-14 | 6.9715e-14 | 7.3835e-14 | 5.9562e-14 | 6.4266e-14 | 6.9274e-14 | 7.4541e-14 | 8.2053e-14 | 8.8603e-14 | 9.4781e-14 | 1.012e-13 | 1.089e-13 | 1.1147e-13 | 1.1977e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13 | 1.2751e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 89.7351 | 84.6674 | 88.9468 | 73.0011 | 77.0173 | 81.1584 | 85.5561 | 90.5875 | 96.5094 | 102.0592 | 107.8913 | 117.8138 | 121.19 | 127.5466 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 132.4099 | 100% | 0 | 104.9463 | 100.01 | 104.8547 | 89.5764 | 93.1686 | 98.8282 | 103.944 | 111.0409 | 118.4402 | 124.4865 | 130.1896 | 138.6542 | 144.8086 | 151.0095 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771 | 157.5771
99% | 0 | 88.8377 | 83.8207 | 88.0573 | 72.2711 | 76.2471 | 80.3468 | 84.7005 | 89.6816 | 95.5443 | 101.0386 | 106.8123 | 116.6357 | 119.9781 | 126.2711 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 131.0858 | 99% | 0.37816 | 103.8968 | 99.0099 | 103.8062 | 88.6807 | 92.2369 | 97.8399 | 102.9045 | 109.9305 | 117.2558 | 123.2416 | 128.8878 | 137.2677 | 143.3605 | 149.4994 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013 | 156.0013
98% | 0.37816 | 87.9404 | 82.9741 | 87.1679 | 71.5411 | 75.4769 | 79.5352 | 83.845 | 88.7758 | 94.5792 | 100.018 | 105.7334 | 115.4576 | 118.7662 | 124.9957 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 129.7617 | 98% | 1.1345 | 102.8473 | 98.0098 | 102.7576 | 87.7849 | 91.3052 | 96.8516 | 101.8651 | 108.8201 | 116.0714 | 121.9968 | 127.5859 | 135.8811 | 141.9124 | 147.9893 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255 | 154.4255
97% | 0.75633 | 87.043 | 82.1274 | 86.2784 | 70.8111 | 74.7067 | 78.7236 | 82.9894 | 87.8699 | 93.6141 | 98.9974 | 104.6545 | 114.2794 | 117.5543 | 123.7202 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 128.4376 | 97% | 2.269 | 101.7979 | 97.0097 | 101.7091 | 86.8891 | 90.3735 | 95.8633 | 100.8256 | 107.7097 | 114.887 | 120.7519 | 126.284 | 134.4946 | 140.4643 | 146.4792 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497 | 152.8497
95% | 1.1345 | 85.2483 | 80.434 | 84.4994 | 69.351 | 73.1664 | 77.1004 | 81.2783 | 86.0581 | 91.684 | 96.9562 | 102.4967 | 111.9232 | 115.1305 | 121.1693 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 125.7894 | 95% | 4.538 | 99.699 | 95.0095 | 99.612 | 85.0976 | 88.5101 | 93.8868 | 98.7468 | 105.4888 | 112.5182 | 118.2622 | 123.6802 | 131.7215 | 137.5681 | 143.459 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982 | 149.6982
90% | 4.538 | 80.7616 | 76.2007 | 80.0521 | 65.701 | 69.3155 | 73.0425 | 77.0005 | 81.5288 | 86.8585 | 91.8533 | 97.1021 | 106.0325 | 109.071 | 114.7919 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 119.1689 | 90% | 7.9414 | 94.4516 | 90.009 | 94.3693 | 80.6188 | 83.8517 | 88.9454 | 93.5496 | 99.9368 | 106.5961 | 112.0378 | 117.1707 | 124.7888 | 130.3277 | 135.9085 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194 | 141.8194
85% | 7.9414 | 76.2748 | 71.9673 | 75.6048 | 62.0509 | 65.4647 | 68.9846 | 72.7227 | 76.9994 | 82.033 | 86.7503 | 91.7076 | 100.1418 | 103.0115 | 108.4146 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 112.5484 | 85% | 14.3702 | 89.2043 | 85.0085 | 89.1265 | 76.14 | 79.1933 | 84.004 | 88.3524 | 94.3848 | 100.6741 | 105.8135 | 110.6612 | 117.8561 | 123.0873 | 128.358 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405 | 133.9405
80% | 11.7231 | 71.788 | 67.7339 | 71.1574 | 58.4009 | 61.6138 | 64.9267 | 68.4449 | 72.47 | 77.2075 | 81.6473 | 86.313 | 94.2511 | 96.952 | 102.0373 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 105.9279 | 80% | 19.6645 | 83.957 | 80.008 | 83.8838 | 71.6611 | 74.5349 | 79.0625 | 83.1552 | 88.8327 | 94.7521 | 99.5892 | 104.1517 | 110.9234 | 115.8469 | 120.8076 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616 | 126.0616
75% | 17.7737 | 67.3013 | 63.5006 | 66.7101 | 54.7508 | 57.7629 | 60.8688 | 64.1671 | 67.9406 | 72.3821 | 76.5444 | 80.9184 | 88.3604 | 90.8925 | 95.66 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 99.3074 | 75% | 25.7152 | 78.7097 | 75.0075 | 78.641 | 67.1823 | 69.8764 | 74.1211 | 77.958 | 83.2807 | 88.8301 | 93.3649 | 97.6422 | 103.9907 | 108.6064 | 113.2571 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828 | 118.1828
70% | 35.1693 | 62.8145 | 59.2672 | 62.2628 | 51.1008 | 53.9121 | 56.8108 | 59.8893 | 63.4113 | 67.5566 | 71.4414 | 75.5239 | 82.4697 | 84.833 | 89.2826 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 92.6869 | 70% | 34.7911 | 73.4624 | 70.007 | 73.3983 | 62.7035 | 65.218 | 69.1797 | 72.7608 | 77.7286 | 82.9081 | 87.1405 | 91.1328 | 97.058 | 101.366 | 105.7066 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039 | 110.3039
65% | 59.3718 | 58.3278 | 55.0338 | 57.8154 | 47.4507 | 50.0612 | 52.7529 | 55.6114 | 58.8819 | 62.7311 | 66.3385 | 70.1293 | 76.579 | 78.7735 | 82.9053 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 86.0664 | 65% | 46.136 | 68.2151 | 65.0065 | 68.1556 | 58.2247 | 60.5596 | 64.2383 | 67.5636 | 72.1766 | 76.9861 | 80.9162 | 84.6233 | 90.1252 | 94.1256 | 98.1562 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251 | 102.4251
60% | 156.9382 | 53.841 | 50.8005 | 53.3681 | 43.8007 | 46.2104 | 48.695 | 51.3336 | 54.3525 | 57.9057 | 61.2355 | 64.7348 | 70.6883 | 72.714 | 76.528 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 79.4459 | 60% | 76.7673 | 62.9678 | 60.006 | 62.9128 | 53.7459 | 55.9011 | 59.2969 | 62.3664 | 66.6245 | 71.0641 | 74.6919 | 78.1138 | 83.1925 | 86.8851 | 90.6057 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462 | 94.5462
55% | 363.794 | 49.3543 | 46.5671 | 48.9207 | 40.1506 | 42.3595 | 44.6371 | 47.0558 | 49.8231 | 53.0802 | 56.1325 | 59.3402 | 64.7976 | 66.6545 | 70.1506 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 72.8254 | 55% | 106.2642 | 57.7205 | 55.0055 | 57.6701 | 49.267 | 51.2427 | 54.3555 | 57.1692 | 61.0725 | 65.1421 | 68.4676 | 71.6043 | 76.2598 | 79.6447 | 83.0552 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674 | 86.6674
50% | 771.4551 | 44.8675 | 42.3337 | 44.4734 | 36.5005 | 38.5086 | 40.5792 | 42.778 | 45.2938 | 48.2547 | 51.0296 | 53.9456 | 58.9069 | 60.595 | 63.7733 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 66.2049 | 50% | 178.4935 | 52.4731 | 50.005 | 52.4274 | 44.7882 | 46.5843 | 49.4141 | 51.972 | 55.5204 | 59.2201 | 62.2432 | 65.0948 | 69.3271 | 72.4043 | 75.5047 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885 | 78.7885
45% | 1255.5054 | 40.3808 | 38.1003 | 40.0261 | 32.8505 | 34.6578 | 36.5213 | 38.5002 | 40.7644 | 43.4292 | 45.9266 | 48.5511 | 53.0162 | 54.5355 | 57.396 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 59.5844 | 45% | 367.9538 | 47.2258 | 45.0045 | 47.1846 | 40.3094 | 41.9259 | 44.4727 | 46.7748 | 49.9684 | 53.2981 | 56.0189 | 58.5853 | 62.3944 | 65.1639 | 67.9543 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097 | 70.9097
40% | 2059.1045 | 35.894 | 33.867 | 35.5787 | 29.2004 | 30.8069 | 32.4633 | 34.2224 | 36.235 | 38.6038 | 40.8237 | 43.1565 | 47.1255 | 48.476 | 51.0186 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 52.964 | 40% | 741.202 | 41.9785 | 40.004 | 41.9419 | 35.8306 | 37.2674 | 39.5313 | 41.5776 | 44.4164 | 47.3761 | 49.7946 | 52.0759 | 55.4617 | 57.9234 | 60.4038 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308 | 63.0308
35% | 3060.4836 | 31.4073 | 29.6336 | 31.1314 | 25.5504 | 26.956 | 28.4054 | 29.9446 | 31.7056 | 33.7783 | 35.7207 | 37.7619 | 41.2348 | 42.4165 | 44.6413 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 46.3435 | 35% | 1167.7713 | 36.7312 | 35.0035 | 36.6992 | 31.3517 | 32.609 | 34.5899 | 36.3804 | 38.8643 | 41.4541 | 43.5703 | 45.5664 | 48.529 | 50.683 | 52.8533 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152 | 55.152
30% | 3366.0403 | 26.9205 | 25.4002 | 26.684 | 21.9003 | 23.1052 | 24.3475 | 25.6668 | 27.1763 | 28.9528 | 30.6178 | 32.3674 | 35.3442 | 36.357 | 38.264 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 39.723 | 30% | 2002.3799 | 31.4839 | 30.003 | 31.4564 | 26.8729 | 27.9506 | 29.6485 | 31.1832 | 33.3123 | 35.532 | 37.3459 | 39.0569 | 41.5963 | 43.4426 | 45.3028 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731 | 47.2731
25% | 3686.3454 | 22.4338 | 21.1669 | 22.2367 | 18.2503 | 19.2543 | 20.2896 | 21.389 | 22.6469 | 24.1274 | 25.5148 | 26.9728 | 29.4535 | 30.2975 | 31.8867 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 33.1025 | 25% | 3173.5547 | 26.2366 | 25.0025 | 26.2137 | 22.3941 | 23.2921 | 24.707 | 25.986 | 27.7602 | 29.61 | 31.1216 | 32.5474 | 34.6636 | 36.2021 | 37.7524 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943 | 39.3943
20% | 4028.5841 | 17.947 | 16.9335 | 17.7894 | 14.6002 | 15.4035 | 16.2317 | 17.1112 | 18.1175 | 19.3019 | 20.4118 | 21.5783 | 23.5628 | 24.238 | 25.5093 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 26.482 | 20% | 3477.5988 | 20.9893 | 20.002 | 20.9709 | 17.9153 | 18.6337 | 19.7656 | 20.7888 | 22.2082 | 23.688 | 24.8973 | 26.0379 | 27.7308 | 28.9617 | 30.2019 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154 | 31.5154
15% | 4345.1076 | 13.4603 | 12.7001 | 13.342 | 10.9502 | 11.5526 | 12.1738 | 12.8334 | 13.5881 | 14.4764 | 15.3089 | 16.1837 | 17.6721 | 18.1785 | 19.132 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 19.8615 | 15% | 3788.4498 | 15.7419 | 15.0015 | 15.7282 | 13.4365 | 13.9753 | 14.8242 | 15.5916 | 16.6561 | 17.766 | 18.673 | 19.5284 | 20.7981 | 21.7213 | 22.6514 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366 | 23.6366
10% | 4381.0332 | 8.9735 | 8.4667 | 8.8947 | 7.3001 | 7.7017 | 8.1158 | 8.5556 | 9.0588 | 9.6509 | 10.2059 | 10.7891 | 11.7814 | 12.119 | 12.7547 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 13.241 | 10% | 4317.5016 | 10.4946 | 10.001 | 10.4855 | 8.9576 | 9.3169 | 9.8828 | 10.3944 | 11.1041 | 11.844 | 12.4486 | 13.019 | 13.8654 | 14.4809 | 15.1009 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577 | 15.7577
5% | 4391.6218 | 4.4868 | 4.2334 | 4.4473 | 3.6501 | 3.8509 | 4.0579 | 4.2778 | 4.5294 | 4.8255 | 5.103 | 5.3946 | 5.8907 | 6.0595 | 6.3773 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 6.6205 | 5% | 4391.6218 | 5.2473 | 5.0005 | 5.2427 | 4.4788 | 4.6584 | 4.9414 | 5.1972 | 5.552 | 5.922 | 6.2243 | 6.5095 | 6.9327 | 7.2404 | 7.5505 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789 | 7.8789
9.992e-14% | 4391.6218 | 8.9663e-14 | 8.46e-14 | 8.8876e-14 | 7.2943e-14 | 7.6956e-14 | 8.1093e-14 | 8.5488e-14 | 9.0515e-14 | 9.6432e-14 | 1.0198e-13 | 1.0781e-13 | 1.1772e-13 | 1.2109e-13 | 1.2744e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 1.323e-13 | 9.992e-14% | 4391.6218 | 1.0486e-13 | 9.993e-14 | 1.0477e-13 | 8.9505e-14 | 9.3094e-14 | 9.8749e-14 | 1.0386e-13 | 1.1095e-13 | 1.1835e-13 | 1.2439e-13 | 1.3009e-13 | 1.3854e-13 | 1.4469e-13 | 1.5089e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 100% | 0 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
99% | 0.5944 | 68.427 | 64.2027 | 68.066 | 73.0038 | 77.7847 | 82.0399 | 87.8842 | 94.2725 | 100.8151 | 107.2984 | 113.0603 | 119.3404 | 121.738 | 129.8557 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 99% | 0.5944 | 73.2778 | 69.0729 | 73.1555 | 78.154 | 82.814 | 87.7759 | 92.9942 | 100.4376 | 106.9274 | 113.0485 | 119.4102 | 127.0352 | 129.5879 | 137.8107 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748
98% | 0.8916 | 67.7358 | 63.5542 | 67.3784 | 72.2664 | 76.999 | 81.2112 | 86.9965 | 93.3203 | 99.7967 | 106.2146 | 111.9183 | 118.135 | 120.5083 | 128.544 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 98% | 0.8916 | 72.5377 | 68.3752 | 72.4165 | 77.3646 | 81.9775 | 86.8893 | 92.0548 | 99.4231 | 105.8473 | 111.9066 | 118.204 | 125.752 | 128.279 | 136.4186 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053
97% | 1.486 | 67.0447 | 62.9057 | 66.6909 | 71.529 | 76.2133 | 80.3826 | 86.1088 | 92.3681 | 98.7784 | 105.1308 | 110.7763 | 116.9295 | 119.2786 | 127.2324 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 97% | 1.486 | 71.7975 | 67.6774 | 71.6776 | 76.5751 | 81.1409 | 86.0026 | 91.1155 | 98.4086 | 104.7673 | 110.7647 | 116.9979 | 124.4688 | 126.97 | 135.0266 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359
95% | 2.3776 | 65.6623 | 61.6087 | 65.3158 | 70.0541 | 74.6418 | 78.7252 | 84.3333 | 90.4636 | 96.7417 | 102.9631 | 108.4922 | 114.5186 | 116.8193 | 124.609 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 95% | 2.3776 | 70.3171 | 66.282 | 70.1997 | 74.9963 | 79.4679 | 84.2294 | 89.2368 | 96.3795 | 102.6071 | 108.4809 | 114.5855 | 121.9024 | 124.3521 | 132.2425 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597
90% | 3.2692 | 62.2064 | 58.3661 | 61.8782 | 66.3671 | 70.7133 | 74.5817 | 79.8947 | 85.7023 | 91.6501 | 97.544 | 102.7821 | 108.4913 | 110.6709 | 118.0507 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 90% | 3.2692 | 66.6162 | 62.7935 | 66.505 | 71.0491 | 75.2854 | 79.7963 | 84.5401 | 91.3069 | 97.2067 | 102.7713 | 108.5547 | 115.4865 | 117.8072 | 125.2824 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498
85% | 13.9683 | 58.7505 | 55.1235 | 58.4405 | 62.68 | 66.7848 | 70.4383 | 75.4561 | 80.9411 | 86.5584 | 92.1249 | 97.072 | 102.464 | 104.5225 | 111.4923 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 85% | 13.9683 | 62.9153 | 59.305 | 62.8103 | 67.1019 | 71.1029 | 75.3631 | 79.8435 | 86.2343 | 91.8064 | 97.0618 | 102.5239 | 109.0706 | 111.2624 | 118.3223 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026
80% | 41.3106 | 55.2946 | 51.881 | 55.0028 | 58.993 | 62.8563 | 66.2949 | 71.0175 | 76.1798 | 81.4667 | 86.7058 | 91.3619 | 96.4367 | 98.3741 | 104.9339 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 80% | 41.3106 | 59.2144 | 55.8165 | 59.1156 | 63.1548 | 66.9204 | 70.93 | 75.1468 | 81.1617 | 86.406 | 91.3523 | 96.4931 | 102.6547 | 104.7175 | 111.3621 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554
75% | 126.3094 | 51.8387 | 48.6384 | 51.5651 | 55.3059 | 58.9278 | 62.1515 | 66.579 | 71.4186 | 76.375 | 81.2867 | 85.6518 | 90.4094 | 92.2257 | 98.3755 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 75% | 126.3094 | 55.5135 | 52.3279 | 55.4208 | 59.2076 | 62.7378 | 66.4969 | 70.4501 | 76.0891 | 81.0056 | 85.6428 | 90.4623 | 96.2388 | 98.1727 | 104.402 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082
70% | 323.9464 | 48.3827 | 45.3959 | 48.1275 | 51.6188 | 54.9993 | 58.008 | 62.1404 | 66.6574 | 71.2834 | 75.8676 | 79.9417 | 84.3821 | 86.0773 | 91.8172 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 70% | 323.9464 | 51.8126 | 48.8394 | 51.7261 | 55.2604 | 58.5553 | 62.0638 | 65.7534 | 71.0165 | 75.6052 | 79.9333 | 84.4314 | 89.8228 | 91.6278 | 97.4419 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861
65% | 549.5201 | 44.9268 | 42.1533 | 44.6898 | 47.9318 | 51.0707 | 53.8646 | 57.7018 | 61.8961 | 66.1917 | 70.4485 | 74.2315 | 78.3548 | 79.929 | 85.2588 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 65% | 549.5201 | 48.1117 | 45.3509 | 48.0314 | 51.3132 | 54.3728 | 57.6306 | 61.0568 | 65.9439 | 70.2049 | 74.2237 | 78.4006 | 83.4069 | 85.083 | 90.4817 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137
60% | 799.4641 | 41.4709 | 38.9107 | 41.2521 | 44.2447 | 47.1422 | 49.7212 | 53.2632 | 57.1349 | 61.1 | 65.0294 | 68.5214 | 72.3275 | 73.7806 | 78.7004 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 60% | 799.4641 | 44.4108 | 41.8623 | 44.3367 | 47.3661 | 50.1903 | 53.1975 | 56.3601 | 60.8713 | 64.8045 | 68.5142 | 72.3698 | 76.991 | 78.5381 | 83.5216 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665
55% | 1116.2777 | 38.015 | 35.6682 | 37.8144 | 40.5577 | 43.2137 | 45.5777 | 48.8246 | 52.3736 | 56.0084 | 59.6102 | 62.8113 | 66.3002 | 67.6322 | 72.1421 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 55% | 1116.2777 | 40.7099 | 38.3738 | 40.6419 | 43.4189 | 46.0078 | 48.7644 | 51.6634 | 55.7987 | 59.4041 | 62.8047 | 66.339 | 70.5751 | 71.9933 | 76.5615 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193
50% | 1494.9086 | 34.5591 | 32.4256 | 34.3768 | 36.8706 | 39.2852 | 41.4343 | 44.386 | 47.6124 | 50.9167 | 54.1911 | 57.1012 | 60.2729 | 61.4838 | 65.5837 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 50% | 1494.9086 | 37.009 | 34.8853 | 36.9472 | 39.4717 | 41.8252 | 44.3313 | 46.9667 | 50.7261 | 54.0037 | 57.0952 | 60.3082 | 64.1592 | 65.4485 | 69.6013 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721
45% | 2004.0097 | 31.1032 | 29.183 | 30.9391 | 33.1835 | 35.3567 | 37.2909 | 39.9474 | 42.8512 | 45.825 | 48.772 | 51.3911 | 54.2456 | 55.3354 | 59.0253 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 45% | 2004.0097 | 33.3081 | 31.3968 | 33.2525 | 35.5246 | 37.6427 | 39.8981 | 42.2701 | 45.6535 | 48.6034 | 51.3857 | 54.2774 | 57.7433 | 58.9036 | 62.6412 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249
40% | 2877.179 | 27.6473 | 25.9405 | 27.5014 | 29.4965 | 31.4281 | 33.1474 | 35.5088 | 38.0899 | 40.7334 | 43.3529 | 45.6809 | 48.2184 | 49.1871 | 52.467 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 40% | 2877.179 | 29.6072 | 27.9082 | 29.5578 | 31.5774 | 33.4602 | 35.465 | 37.5734 | 40.5808 | 43.203 | 45.6762 | 48.2465 | 51.3273 | 52.3588 | 55.6811 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777
35% | 3454.933 | 24.1914 | 22.6979 | 24.0637 | 25.8094 | 27.4996 | 29.004 | 31.0702 | 33.3287 | 35.6417 | 37.9338 | 39.9708 | 42.1911 | 43.0387 | 45.9086 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 35% | 3454.933 | 25.9063 | 24.4197 | 25.8631 | 27.6302 | 29.2777 | 31.0319 | 32.8767 | 35.5082 | 37.8026 | 39.9666 | 42.2157 | 44.9114 | 45.8139 | 48.7209 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305
30% | 3663.5664 | 20.7355 | 19.4554 | 20.6261 | 22.1224 | 23.5711 | 24.8606 | 26.6316 | 28.5674 | 30.55 | 32.5147 | 34.2607 | 36.1638 | 36.8903 | 39.3502 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 30% | 3663.5664 | 22.2054 | 20.9312 | 22.1683 | 23.683 | 25.0951 | 26.5988 | 28.18 | 30.4356 | 32.4022 | 34.2571 | 36.1849 | 38.4955 | 39.2691 | 41.7608 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833
25% | 3862.6894 | 17.2796 | 16.2128 | 17.1884 | 18.4353 | 19.6426 | 20.7172 | 22.193 | 23.8062 | 25.4583 | 27.0956 | 28.5506 | 30.1365 | 30.7419 | 32.7918 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 25% | 3862.6894 | 18.5045 | 17.4426 | 18.4736 | 19.7359 | 20.9126 | 22.1656 | 23.4834 | 25.363 | 27.0019 | 28.5476 | 30.1541 | 32.0796 | 32.7242 | 34.8007 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361
20% | 4122.7381 | 13.8236 | 12.9702 | 13.7507 | 14.7482 | 15.7141 | 16.5737 | 17.7544 | 19.045 | 20.3667 | 21.6765 | 22.8405 | 24.1092 | 24.5935 | 26.2335 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 20% | 4122.7381 | 14.8036 | 13.9541 | 14.7789 | 15.7887 | 16.7301 | 17.7325 | 18.7867 | 20.2904 | 21.6015 | 22.8381 | 24.1233 | 25.6637 | 26.1794 | 27.8405 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888
15% | 4372.3849 | 10.3677 | 9.7277 | 10.313 | 11.0612 | 11.7856 | 12.4303 | 13.3158 | 14.2837 | 15.275 | 16.2573 | 17.1304 | 18.0819 | 18.4451 | 19.6751 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 15% | 4372.3849 | 11.1027 | 10.4656 | 11.0842 | 11.8415 | 12.5476 | 13.2994 | 14.09 | 15.2178 | 16.2011 | 17.1286 | 18.0925 | 19.2478 | 19.6345 | 20.8804 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416
10% | 4374.4653 | 6.9118 | 6.4851 | 6.8754 | 7.3741 | 7.857 | 8.2869 | 8.8772 | 9.5225 | 10.1833 | 10.8382 | 11.4202 | 12.0546 | 12.2968 | 13.1167 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 10% | 4374.4653 | 7.4018 | 6.9771 | 7.3894 | 7.8943 | 8.365 | 8.8663 | 9.3933 | 10.1452 | 10.8007 | 11.419 | 12.0616 | 12.8318 | 13.0897 | 13.9203 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944
5% | 4374.7625 | 3.4559 | 3.2426 | 3.4377 | 3.6871 | 3.9285 | 4.1434 | 4.4386 | 4.7612 | 5.0917 | 5.4191 | 5.7101 | 6.0273 | 6.1484 | 6.5584 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 5% | 4374.7625 | 3.7009 | 3.4885 | 3.6947 | 3.9472 | 4.1825 | 4.4331 | 4.6967 | 5.0726 | 5.4004 | 5.7095 | 6.0308 | 6.4159 | 6.5448 | 6.9601 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472
9.992e-14% | 4375.9513 | 6.9063e-14 | 6.4799e-14 | 6.8699e-14 | 7.3682e-14 | 7.8508e-14 | 8.2802e-14 | 8.8701e-14 | 9.5149e-14 | 1.0175e-13 | 1.083e-13 | 1.1411e-13 | 1.2045e-13 | 1.2287e-13 | 1.3106e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 9.992e-14% | 4375.9513 | 7.3959e-14 | 6.9715e-14 | 7.3835e-14 | 7.888e-14 | 8.3584e-14 | 8.8592e-14 | 9.3858e-14 | 1.0137e-13 | 1.0792e-13 | 1.141e-13 | 1.2052e-13 | 1.2822e-13 | 1.3079e-13 | 1.3909e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 100% | 0 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104
99% | 0 | 88.8377 | 83.8207 | 88.0573 | 91.4111 | 95.3871 | 99.4868 | 103.8405 | 108.8216 | 114.6843 | 120.1786 | 125.9523 | 135.7757 | 139.1181 | 145.4111 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 99% | 0.37816 | 103.8968 | 99.0099 | 103.8062 | 107.8207 | 111.3769 | 116.9799 | 122.0445 | 129.0705 | 136.3958 | 142.3816 | 148.0278 | 156.4077 | 162.5005 | 168.6394 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413
98% | 0.37816 | 87.9404 | 82.9741 | 87.1679 | 90.4877 | 94.4236 | 98.4819 | 102.7916 | 107.7224 | 113.5259 | 118.9647 | 124.6801 | 134.4042 | 137.7129 | 143.9423 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 98% | 1.1345 | 102.8473 | 98.0098 | 102.7576 | 106.7316 | 110.2519 | 115.7983 | 120.8117 | 127.7667 | 135.018 | 140.9434 | 146.5325 | 154.8278 | 160.8591 | 166.9359 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722
97% | 0.75633 | 87.043 | 82.1274 | 86.2784 | 89.5644 | 93.4601 | 97.4769 | 101.7427 | 106.6232 | 112.3675 | 117.7507 | 123.4079 | 133.0328 | 136.3077 | 142.4735 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 97% | 2.269 | 101.7979 | 97.0097 | 101.7091 | 105.6425 | 109.1268 | 114.6167 | 119.579 | 126.463 | 133.6403 | 139.5052 | 145.0373 | 153.2479 | 159.2176 | 165.2325 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031
95% | 1.1345 | 85.2483 | 80.434 | 84.4994 | 87.7177 | 91.5331 | 95.4671 | 99.6449 | 104.4248 | 110.0506 | 115.3229 | 120.8634 | 130.2898 | 133.4972 | 139.5359 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 95% | 4.538 | 99.699 | 95.0095 | 99.612 | 103.4643 | 106.8768 | 112.2534 | 117.1134 | 123.8555 | 130.8848 | 136.6288 | 142.0468 | 150.0882 | 155.9348 | 161.8257 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649
90% | 4.538 | 80.7616 | 76.2007 | 80.0521 | 83.101 | 86.7155 | 90.4425 | 94.4005 | 98.9288 | 104.2585 | 109.2533 | 114.5021 | 123.4325 | 126.471 | 132.1919 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 90% | 7.9414 | 94.4516 | 90.009 | 94.3693 | 98.0188 | 101.2517 | 106.3454 | 110.9496 | 117.3368 | 123.9961 | 129.4378 | 134.5707 | 142.1888 | 147.7277 | 153.3085 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194
85% | 7.9414 | 76.2748 | 71.9673 | 75.6048 | 78.4843 | 81.898 | 85.4179 | 89.156 | 93.4327 | 98.4663 | 103.1836 | 108.1409 | 116.5751 | 119.4449 | 124.8479 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 85% | 14.3702 | 89.2043 | 85.0085 | 89.1265 | 92.5733 | 95.6266 | 100.4373 | 104.7857 | 110.8181 | 117.1075 | 122.2468 | 127.0945 | 134.2894 | 139.5206 | 144.7914 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738
80% | 11.7231 | 71.788 | 67.7339 | 71.1574 | 73.8675 | 77.0805 | 80.3933 | 83.9115 | 87.9367 | 92.6742 | 97.114 | 101.7797 | 109.7177 | 112.4187 | 117.5039 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 80% | 19.6645 | 83.957 | 80.008 | 83.8838 | 87.1278 | 90.0015 | 94.5292 | 98.6218 | 104.2994 | 110.2188 | 115.0559 | 119.6184 | 126.39 | 131.3135 | 136.2742 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283
75% | 17.7737 | 67.3013 | 63.5006 | 66.7101 | 69.2508 | 72.2629 | 75.3688 | 78.6671 | 82.4406 | 86.8821 | 91.0444 | 95.4184 | 102.8604 | 105.3925 | 110.16 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 75% | 25.7152 | 78.7097 | 75.0075 | 78.641 | 81.6823 | 84.3764 | 88.6211 | 92.458 | 97.7807 | 103.3301 | 107.8649 | 112.1422 | 118.4907 | 123.1064 | 127.7571 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828
70% | 35.1693 | 62.8145 | 59.2672 | 62.2628 | 64.6341 | 67.4454 | 70.3442 | 73.4226 | 76.9446 | 81.0899 | 84.9748 | 89.0572 | 96.003 | 98.3664 | 102.816 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 70% | 34.7911 | 73.4624 | 70.007 | 73.3983 | 76.2368 | 78.7513 | 82.7131 | 86.2941 | 91.262 | 96.4414 | 100.6739 | 104.6661 | 110.5913 | 114.8993 | 119.24 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373
65% | 59.3718 | 58.3278 | 55.0338 | 57.8154 | 60.0174 | 62.6279 | 65.3196 | 68.1781 | 71.4486 | 75.2978 | 78.9051 | 82.696 | 89.1457 | 91.3402 | 95.472 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 65% | 46.136 | 68.2151 | 65.0065 | 68.1556 | 70.7913 | 73.1262 | 76.805 | 80.1302 | 84.7432 | 89.5528 | 93.4829 | 97.1899 | 102.6919 | 106.6922 | 110.7228 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918
60% | 156.9382 | 53.841 | 50.8005 | 53.3681 | 55.4007 | 57.8104 | 60.295 | 62.9336 | 65.9525 | 69.5057 | 72.8355 | 76.3348 | 82.2883 | 84.314 | 88.128 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 60% | 76.7673 | 62.9678 | 60.006 | 62.9128 | 65.3459 | 67.5011 | 70.8969 | 73.9664 | 78.2245 | 82.6641 | 86.2919 | 89.7138 | 94.7925 | 98.4851 | 102.2057 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462
55% | 363.794 | 49.3543 | 46.5671 | 48.9207 | 50.7839 | 52.9928 | 55.2704 | 57.6892 | 60.4565 | 63.7135 | 66.7659 | 69.9735 | 75.4309 | 77.2879 | 80.784 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 55% | 106.2642 | 57.7205 | 55.0055 | 57.6701 | 59.9004 | 61.876 | 64.9888 | 67.8025 | 71.7058 | 75.7754 | 79.1009 | 82.2376 | 86.8932 | 90.278 | 93.6885 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007
50% | 771.4551 | 44.8675 | 42.3337 | 44.4734 | 46.1672 | 48.1753 | 50.2458 | 52.4447 | 54.9604 | 57.9214 | 60.6963 | 63.6123 | 68.5736 | 70.2617 | 73.44 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 50% | 178.4935 | 52.4731 | 50.005 | 52.4274 | 54.4549 | 56.251 | 59.0808 | 61.6386 | 65.1871 | 68.8867 | 71.9099 | 74.7615 | 78.9938 | 82.0709 | 85.1714 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552
45% | 1255.5054 | 40.3808 | 38.1003 | 40.0261 | 41.5505 | 43.3578 | 45.2213 | 47.2002 | 49.4644 | 52.1292 | 54.6266 | 57.2511 | 61.7162 | 63.2355 | 66.096 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 45% | 367.9538 | 47.2258 | 45.0045 | 47.1846 | 49.0094 | 50.6259 | 53.1727 | 55.4748 | 58.6684 | 61.9981 | 64.7189 | 67.2853 | 71.0944 | 73.8639 | 76.6543 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097
40% | 2059.1045 | 35.894 | 33.867 | 35.5787 | 36.9338 | 38.5402 | 40.1967 | 41.9558 | 43.9683 | 46.3371 | 48.557 | 50.8898 | 54.8589 | 56.2094 | 58.752 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 40% | 741.202 | 41.9785 | 40.004 | 41.9419 | 43.5639 | 45.0008 | 47.2646 | 49.3109 | 52.1497 | 55.1094 | 57.5279 | 59.8092 | 63.195 | 65.6568 | 68.1371 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642
35% | 3060.4836 | 31.4073 | 29.6336 | 31.1314 | 32.317 | 33.7227 | 35.1721 | 36.7113 | 38.4723 | 40.545 | 42.4874 | 44.5286 | 48.0015 | 49.1832 | 51.408 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 35% | 1167.7713 | 36.7312 | 35.0035 | 36.6992 | 38.1184 | 39.3757 | 41.3565 | 43.1471 | 45.631 | 48.2207 | 50.3369 | 52.333 | 55.2956 | 57.4497 | 59.62 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186
30% | 3366.0403 | 26.9205 | 25.4002 | 26.684 | 27.7003 | 28.9052 | 30.1475 | 31.4668 | 32.9763 | 34.7528 | 36.4178 | 38.1674 | 41.1442 | 42.157 | 44.064 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 30% | 2002.3799 | 31.4839 | 30.003 | 31.4564 | 32.6729 | 33.7506 | 35.4485 | 36.9832 | 39.1123 | 41.332 | 43.1459 | 44.8569 | 47.3963 | 49.2426 | 51.1028 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731
25% | 3686.3454 | 22.4338 | 21.1669 | 22.2367 | 23.0836 | 24.0876 | 25.1229 | 26.2224 | 27.4802 | 28.9607 | 30.3481 | 31.8061 | 34.2868 | 35.1308 | 36.72 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 25% | 3173.5547 | 26.2366 | 25.0025 | 26.2137 | 27.2274 | 28.1255 | 29.5404 | 30.8193 | 32.5936 | 34.4434 | 35.955 | 37.3807 | 39.4969 | 41.0355 | 42.5857 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276
20% | 4028.5841 | 17.947 | 16.9335 | 17.7894 | 18.4669 | 19.2701 | 20.0983 | 20.9779 | 21.9842 | 23.1686 | 24.2785 | 25.4449 | 27.4294 | 28.1047 | 29.376 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 20% | 3477.5988 | 20.9893 | 20.002 | 20.9709 | 21.782 | 22.5004 | 23.6323 | 24.6555 | 26.0748 | 27.5547 | 28.764 | 29.9046 | 31.5975 | 32.8284 | 34.0686 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821
15% | 4345.1076 | 13.4603 | 12.7001 | 13.342 | 13.8502 | 14.4526 | 15.0738 | 15.7334 | 16.4881 | 17.3764 | 18.2089 | 19.0837 | 20.5721 | 21.0785 | 22.032 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 15% | 3788.4498 | 15.7419 | 15.0015 | 15.7282 | 16.3365 | 16.8753 | 17.7242 | 18.4916 | 19.5561 | 20.666 | 21.573 | 22.4284 | 23.6981 | 24.6213 | 25.5514 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366
10% | 4381.0332 | 8.9735 | 8.4667 | 8.8947 | 9.2334 | 9.6351 | 10.0492 | 10.4889 | 10.9921 | 11.5843 | 12.1393 | 12.7225 | 13.7147 | 14.0523 | 14.688 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 10% | 4317.5016 | 10.4946 | 10.001 | 10.4855 | 10.891 | 11.2502 | 11.8162 | 12.3277 | 13.0374 | 13.7773 | 14.382 | 14.9523 | 15.7988 | 16.4142 | 17.0343 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691
5% | 4391.6218 | 4.4868 | 4.2334 | 4.4473 | 4.6167 | 4.8175 | 5.0246 | 5.2445 | 5.496 | 5.7921 | 6.0696 | 6.3612 | 6.8574 | 7.0262 | 7.344 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 5% | 4391.6218 | 5.2473 | 5.0005 | 5.2427 | 5.4455 | 5.6251 | 5.9081 | 6.1639 | 6.5187 | 6.8887 | 7.191 | 7.4761 | 7.8994 | 8.2071 | 8.5171 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455
9.992e-14% | 4391.6218 | 8.9663e-14 | 8.46e-14 | 8.8876e-14 | 9.2261e-14 | 9.6274e-14 | 1.0041e-13 | 1.0481e-13 | 1.0983e-13 | 1.1575e-13 | 1.213e-13 | 1.2712e-13 | 1.3704e-13 | 1.4041e-13 | 1.4676e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 9.992e-14% | 4391.6218 | 1.0486e-13 | 9.993e-14 | 1.0477e-13 | 1.0882e-13 | 1.1241e-13 | 1.1807e-13 | 1.2318e-13 | 1.3027e-13 | 1.3766e-13 | 1.437e-13 | 1.494e-13 | 1.5786e-13 | 1.6401e-13 | 1.7021e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.2334 | 57.0001 | 60.6023 | 65.3416 | 69.9522 | 73.8962 | 79.4803 | 85.484 | 91.6236 | 97.7916 | 103.2533 | 109.0566 | 111.0903 | 118.8984 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 126.9635 | 100% | 0 | 67.1333 | 61.9194 | 65.7432 | 70.5439 | 75.0323 | 79.6901 | 84.6419 | 91.7113 | 97.7977 | 103.5997 | 109.6673 | 116.829 | 119.0196 | 126.9337 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588 | 134.2588
99% | 0.5944 | 61.6111 | 56.4301 | 59.9962 | 64.6882 | 69.2527 | 73.1573 | 78.6855 | 84.6292 | 90.7074 | 96.8136 | 102.2207 | 107.966 | 109.9794 | 117.7094 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 125.6939 | 99% | 0.5944 | 66.4619 | 61.3002 | 65.0858 | 69.8385 | 74.282 | 78.8932 | 83.7955 | 90.7942 | 96.8197 | 102.5637 | 108.5706 | 115.6607 | 117.8294 | 125.6643 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162 | 132.9162
98% | 0.8916 | 60.9888 | 55.8601 | 59.3902 | 64.0348 | 68.5532 | 72.4183 | 77.8907 | 83.7743 | 89.7911 | 95.8357 | 101.1882 | 106.8754 | 108.8685 | 116.5204 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 124.4242 | 98% | 0.8916 | 65.7906 | 60.6811 | 64.4283 | 69.133 | 73.5317 | 78.0963 | 82.9491 | 89.8771 | 95.8418 | 101.5277 | 107.4739 | 114.4925 | 116.6392 | 124.395 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736 | 131.5736
97% | 1.486 | 60.3664 | 55.2901 | 58.7842 | 63.3814 | 67.8536 | 71.6793 | 77.0959 | 82.9195 | 88.8749 | 94.8578 | 100.1557 | 105.7849 | 107.7576 | 115.3314 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 123.1546 | 97% | 1.486 | 65.1193 | 60.0619 | 63.7709 | 68.4276 | 72.7813 | 77.2994 | 82.1026 | 88.96 | 94.8638 | 100.4917 | 106.3772 | 113.3242 | 115.449 | 123.1257 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231 | 130.231
95% | 2.3776 | 59.1218 | 54.1501 | 57.5721 | 62.0746 | 66.4546 | 70.2014 | 75.5063 | 81.2098 | 87.0424 | 92.902 | 98.0906 | 103.6037 | 105.5358 | 112.9535 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 120.6153 | 95% | 2.3776 | 63.7766 | 58.8235 | 62.456 | 67.0167 | 71.2807 | 75.7056 | 80.4098 | 87.1258 | 92.9078 | 98.4197 | 104.1839 | 110.9876 | 113.0686 | 120.587 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459 | 127.5459
90% | 3.2692 | 56.0101 | 51.3001 | 54.542 | 58.8075 | 62.957 | 66.5066 | 71.5323 | 76.9356 | 82.4613 | 88.0124 | 92.9279 | 98.1509 | 99.9813 | 107.0085 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 114.2672 | 90% | 3.2692 | 60.4199 | 55.7275 | 59.1689 | 63.4895 | 67.5291 | 71.7211 | 76.1777 | 82.5402 | 88.0179 | 93.2397 | 98.7005 | 105.1461 | 107.1177 | 114.2403 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329 | 120.8329
85% | 13.9683 | 52.8984 | 48.4501 | 51.5119 | 55.5404 | 59.4594 | 62.8118 | 67.5583 | 72.6614 | 77.8801 | 83.1228 | 87.7653 | 92.6981 | 94.4268 | 101.0636 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 107.919 | 85% | 13.9683 | 57.0633 | 52.6315 | 55.8817 | 59.9623 | 63.7775 | 67.7366 | 71.9456 | 77.9546 | 83.1281 | 88.0597 | 93.2172 | 99.3047 | 101.1667 | 107.8936 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12 | 114.12
80% | 41.3106 | 49.7867 | 45.6001 | 48.4818 | 52.2733 | 55.9618 | 59.117 | 63.5843 | 68.3872 | 73.2989 | 78.2333 | 82.6026 | 87.2453 | 88.8723 | 95.1187 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 101.5708 | 80% | 41.3106 | 53.7066 | 49.5356 | 52.5946 | 56.4351 | 60.0258 | 63.7521 | 67.7135 | 73.3691 | 78.2382 | 82.8797 | 87.7338 | 93.4632 | 95.2157 | 101.5469 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407 | 107.407
75% | 126.3094 | 46.6751 | 42.7501 | 45.4517 | 49.0062 | 52.4642 | 55.4222 | 59.6103 | 64.113 | 68.7177 | 73.3437 | 77.44 | 81.7924 | 83.3178 | 89.1738 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 95.2226 | 75% | 126.3094 | 50.3499 | 46.4396 | 49.3074 | 52.9079 | 56.2742 | 59.7676 | 63.4814 | 68.7835 | 73.3483 | 77.6998 | 82.2504 | 87.6218 | 89.2647 | 95.2003 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941 | 100.6941
70% | 323.9464 | 43.5634 | 39.9001 | 42.4216 | 45.7392 | 48.9665 | 51.7274 | 55.6362 | 59.8388 | 64.1365 | 68.4541 | 72.2773 | 76.3396 | 77.7632 | 83.2289 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 88.8745 | 70% | 323.9464 | 46.9933 | 43.3436 | 46.0202 | 49.3807 | 52.5226 | 55.7831 | 59.2493 | 64.1979 | 68.4584 | 72.5198 | 76.7671 | 81.7803 | 83.3137 | 88.8536 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812 | 93.9812
65% | 549.5201 | 40.4517 | 37.0501 | 39.3915 | 42.4721 | 45.4689 | 48.0325 | 51.6622 | 55.5646 | 59.5554 | 63.5645 | 67.1146 | 70.8868 | 72.2087 | 77.2839 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 82.5263 | 65% | 549.5201 | 43.6366 | 40.2476 | 42.7331 | 45.8535 | 48.771 | 51.7986 | 55.0172 | 59.6124 | 63.5685 | 67.3398 | 71.2837 | 75.9389 | 77.3627 | 82.5069 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682 | 87.2682
60% | 799.4641 | 37.3401 | 34.2001 | 36.3614 | 39.205 | 41.9713 | 44.3377 | 47.6882 | 51.2904 | 54.9742 | 58.6749 | 61.952 | 65.4339 | 66.6542 | 71.339 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 76.1781 | 60% | 799.4641 | 40.28 | 37.1517 | 39.4459 | 42.3263 | 45.0194 | 47.8141 | 50.7851 | 55.0268 | 58.6786 | 62.1598 | 65.8004 | 70.0974 | 71.4118 | 76.1602 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553 | 80.5553
55% | 1116.2777 | 34.2284 | 31.3501 | 33.3312 | 35.9379 | 38.4737 | 40.6429 | 43.7142 | 47.0162 | 50.393 | 53.7854 | 56.7893 | 59.9811 | 61.0997 | 65.3941 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 69.8299 | 55% | 1116.2777 | 36.9233 | 34.0557 | 36.1588 | 38.7991 | 41.2678 | 43.8296 | 46.553 | 50.4412 | 53.7887 | 56.9798 | 60.317 | 64.256 | 65.4608 | 69.8135 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423 | 73.8423
50% | 1494.9086 | 31.1167 | 28.5 | 30.3011 | 32.6708 | 34.9761 | 36.9481 | 39.7402 | 42.742 | 45.8118 | 48.8958 | 51.6266 | 54.5283 | 55.5452 | 59.4492 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 63.4818 | 50% | 1494.9086 | 33.5666 | 30.9597 | 32.8716 | 35.2719 | 37.5162 | 39.8451 | 42.3209 | 45.8557 | 48.8989 | 51.7998 | 54.8336 | 58.4145 | 59.5098 | 63.4668 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294 | 67.1294
45% | 2004.0097 | 28.005 | 25.65 | 27.271 | 29.4037 | 31.4785 | 33.2533 | 35.7662 | 38.4678 | 41.2306 | 44.0062 | 46.464 | 49.0755 | 49.9907 | 53.5043 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 57.1336 | 45% | 2004.0097 | 30.21 | 27.8637 | 29.5844 | 31.7448 | 33.7645 | 35.8606 | 38.0889 | 41.2701 | 44.009 | 46.6199 | 49.3503 | 52.5731 | 53.5588 | 57.1202 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165 | 60.4165
40% | 2877.179 | 24.8934 | 22.8 | 24.2409 | 26.1367 | 27.9809 | 29.5585 | 31.7921 | 34.1936 | 36.6494 | 39.1166 | 41.3013 | 43.6226 | 44.4361 | 47.5594 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 50.7854 | 40% | 2877.179 | 26.8533 | 24.7678 | 26.2973 | 28.2176 | 30.0129 | 31.8761 | 33.8568 | 36.6845 | 39.1191 | 41.4399 | 43.8669 | 46.7316 | 47.6078 | 50.7735 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035 | 53.7035
35% | 3454.933 | 21.7817 | 19.95 | 21.2108 | 22.8696 | 24.4833 | 25.8637 | 27.8181 | 29.9194 | 32.0683 | 34.227 | 36.1386 | 38.1698 | 38.8816 | 41.6144 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 44.4372 | 35% | 3454.933 | 23.4966 | 21.6718 | 23.0101 | 24.6904 | 26.2613 | 27.8915 | 29.6247 | 32.099 | 34.2292 | 36.2599 | 38.3835 | 40.8902 | 41.6569 | 44.4268 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906 | 46.9906
30% | 3663.5664 | 18.67 | 17.1 | 18.1807 | 19.6025 | 20.9857 | 22.1689 | 23.8441 | 25.6452 | 27.4871 | 29.3375 | 30.976 | 32.717 | 33.3271 | 35.6695 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 38.0891 | 30% | 3663.5664 | 20.14 | 18.5758 | 19.723 | 21.1632 | 22.5097 | 23.907 | 25.3926 | 27.5134 | 29.3393 | 31.0799 | 32.9002 | 35.0487 | 35.7059 | 38.0801 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776 | 40.2776
25% | 3862.6894 | 15.5584 | 14.25 | 15.1506 | 16.3354 | 17.4881 | 18.4741 | 19.8701 | 21.371 | 22.9059 | 24.4479 | 25.8133 | 27.2641 | 27.7726 | 29.7246 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 31.7409 | 25% | 3862.6894 | 16.7833 | 15.4799 | 16.4358 | 17.636 | 18.7581 | 19.9225 | 21.1605 | 22.9278 | 24.4494 | 25.8999 | 27.4168 | 29.2073 | 29.7549 | 31.7334 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647 | 33.5647
20% | 4122.7381 | 12.4467 | 11.4 | 12.1205 | 13.0683 | 13.9904 | 14.7792 | 15.8961 | 17.0968 | 18.3247 | 19.5583 | 20.6507 | 21.8113 | 22.2181 | 23.7797 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 25.3927 | 20% | 4122.7381 | 13.4267 | 12.3839 | 13.1486 | 14.1088 | 15.0065 | 15.938 | 16.9284 | 18.3423 | 19.5595 | 20.7199 | 21.9335 | 23.3658 | 23.8039 | 25.3867 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518 | 26.8518
15% | 4372.3849 | 9.335 | 8.55 | 9.0903 | 9.8012 | 10.4928 | 11.0844 | 11.9221 | 12.8226 | 13.7435 | 14.6687 | 15.488 | 16.3585 | 16.6636 | 17.8348 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 19.0445 | 15% | 4372.3849 | 10.07 | 9.2879 | 9.8615 | 10.5816 | 11.2548 | 11.9535 | 12.6963 | 13.7567 | 14.6697 | 15.54 | 16.4501 | 17.5244 | 17.8529 | 19.0401 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388 | 20.1388
10% | 4374.4653 | 6.2233 | 5.7 | 6.0602 | 6.5342 | 6.9952 | 7.3896 | 7.948 | 8.5484 | 9.1624 | 9.7792 | 10.3253 | 10.9057 | 11.109 | 11.8898 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 12.6964 | 10% | 4374.4653 | 6.7133 | 6.1919 | 6.5743 | 7.0544 | 7.5032 | 7.969 | 8.4642 | 9.1711 | 9.7798 | 10.36 | 10.9667 | 11.6829 | 11.902 | 12.6934 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259 | 13.4259
5% | 4374.7625 | 3.1117 | 2.85 | 3.0301 | 3.2671 | 3.4976 | 3.6948 | 3.974 | 4.2742 | 4.5812 | 4.8896 | 5.1627 | 5.4528 | 5.5545 | 5.9449 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 6.3482 | 5% | 4374.7625 | 3.3567 | 3.096 | 3.2872 | 3.5272 | 3.7516 | 3.9845 | 4.2321 | 4.5856 | 4.8899 | 5.18 | 5.4834 | 5.8415 | 5.951 | 6.3467 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129 | 6.7129
9.992e-14% | 4375.9513 | 6.2184e-14 | 5.6955e-14 | 6.0554e-14 | 6.5289e-14 | 6.9896e-14 | 7.3837e-14 | 7.9417e-14 | 8.5416e-14 | 9.155e-14 | 9.7713e-14 | 1.0317e-13 | 1.0897e-13 | 1.11e-13 | 1.188e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 1.2686e-13 | 9.992e-14% | 4375.9513 | 6.708e-14 | 6.187e-14 | 6.5691e-14 | 7.0488e-14 | 7.4972e-14 | 7.9626e-14 | 8.4574e-14 | 9.1638e-14 | 9.772e-14 | 1.0352e-13 | 1.0958e-13 | 1.1674e-13 | 1.1892e-13 | 1.2683e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13 | 1.3415e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 82.8503 | 76.8163 | 80.7955 | 83.9349 | 87.7324 | 91.5193 | 95.5978 | 100.1801 | 105.633 | 110.8018 | 116.2755 | 125.6579 | 128.6461 | 134.6109 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 139.0578 | 100% | 0 | 98.0615 | 92.1588 | 96.7035 | 100.5102 | 103.8837 | 109.1891 | 113.9857 | 120.6335 | 127.5637 | 133.2291 | 138.5739 | 146.4983 | 152.2646 | 158.0738 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225 | 164.225
99% | 0 | 82.0218 | 76.0481 | 79.9876 | 83.0955 | 86.8551 | 90.6041 | 94.6418 | 99.1783 | 104.5767 | 109.6938 | 115.1127 | 124.4013 | 127.3596 | 133.2648 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 137.6672 | 99% | 0.37816 | 97.0809 | 91.2373 | 95.7365 | 99.5051 | 102.8449 | 108.0972 | 112.8458 | 119.4271 | 126.2881 | 131.8968 | 137.1882 | 145.0333 | 150.742 | 156.4931 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827 | 162.5827
98% | 0.37816 | 81.1933 | 75.28 | 79.1796 | 82.2562 | 85.9778 | 89.6889 | 93.6859 | 98.1765 | 103.5203 | 108.5858 | 113.95 | 123.1447 | 126.0732 | 131.9187 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 136.2766 | 98% | 1.1345 | 96.1003 | 90.3157 | 94.7694 | 98.5 | 101.8061 | 107.0054 | 111.706 | 118.2208 | 125.0124 | 130.5645 | 135.8024 | 143.5683 | 149.2193 | 154.9123 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405 | 160.9405
97% | 0.75633 | 80.3648 | 74.5118 | 78.3717 | 81.4168 | 85.1005 | 88.7737 | 92.7299 | 97.1747 | 102.464 | 107.4778 | 112.7872 | 121.8881 | 124.7867 | 130.5726 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 134.886 | 97% | 2.269 | 95.1197 | 89.3941 | 93.8024 | 97.4949 | 100.7672 | 105.9135 | 110.5661 | 117.0145 | 123.7368 | 129.2323 | 134.4167 | 142.1033 | 147.6967 | 153.3316 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982 | 159.2982
95% | 1.1345 | 78.7078 | 72.9755 | 76.7558 | 79.7381 | 83.3458 | 86.9433 | 90.8179 | 95.1711 | 100.3513 | 105.2617 | 110.4617 | 119.375 | 122.2138 | 127.8804 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 132.1049 | 95% | 4.538 | 93.1584 | 87.5509 | 91.8683 | 95.4847 | 98.6896 | 103.7297 | 108.2864 | 114.6018 | 121.1855 | 126.5677 | 131.6452 | 139.1733 | 144.6514 | 150.1701 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137 | 156.0137
90% | 4.538 | 74.5653 | 69.1347 | 72.716 | 75.5414 | 78.9592 | 82.3674 | 86.038 | 90.1621 | 95.0697 | 99.7216 | 104.648 | 113.0921 | 115.7815 | 121.1498 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 125.152 | 90% | 7.9414 | 88.2553 | 82.943 | 87.0331 | 90.4592 | 93.4954 | 98.2702 | 102.5871 | 108.5701 | 114.8073 | 119.9062 | 124.7165 | 131.8484 | 137.0381 | 142.2664 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025 | 147.8025
85% | 7.9414 | 70.4227 | 65.2938 | 68.6762 | 71.3446 | 74.5726 | 77.7914 | 81.2581 | 85.1531 | 89.788 | 94.1815 | 98.8342 | 106.8092 | 109.3492 | 114.4193 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 118.1991 | 85% | 14.3702 | 83.3523 | 78.335 | 82.198 | 85.4337 | 88.3012 | 92.8108 | 96.8878 | 102.5384 | 108.4292 | 113.2448 | 117.7878 | 124.5235 | 129.4249 | 134.3627 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912 | 139.5912
80% | 11.7231 | 66.2802 | 61.453 | 64.6364 | 67.1479 | 70.186 | 73.2154 | 76.4783 | 80.1441 | 84.5064 | 88.6415 | 93.0204 | 100.5263 | 102.9169 | 107.6887 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 111.2462 | 80% | 19.6645 | 78.4492 | 73.7271 | 77.3628 | 80.4082 | 83.107 | 87.3513 | 91.1886 | 96.5068 | 102.051 | 106.5833 | 110.8591 | 117.1986 | 121.8117 | 126.459 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38 | 131.38
75% | 17.7737 | 62.1377 | 57.6122 | 60.5967 | 62.9512 | 65.7993 | 68.6395 | 71.6984 | 75.1351 | 79.2247 | 83.1014 | 87.2066 | 94.2434 | 96.4846 | 100.9582 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 104.2933 | 75% | 25.7152 | 73.5461 | 69.1191 | 72.5276 | 75.3826 | 77.9128 | 81.8919 | 85.4893 | 90.4751 | 95.6728 | 99.9218 | 103.9304 | 109.8737 | 114.1984 | 118.5553 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687 | 123.1687
70% | 35.1693 | 57.9952 | 53.7714 | 56.5569 | 58.7544 | 61.4127 | 64.0635 | 66.9185 | 70.1261 | 73.9431 | 77.5613 | 81.3929 | 87.9605 | 90.0523 | 94.2276 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 97.3404 | 70% | 34.7911 | 68.643 | 64.5112 | 67.6924 | 70.3571 | 72.7186 | 76.4324 | 79.79 | 84.4434 | 89.2946 | 93.2604 | 97.0017 | 102.5488 | 106.5852 | 110.6517 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575 | 114.9575
65% | 59.3718 | 53.8527 | 49.9306 | 52.5171 | 54.5577 | 57.0261 | 59.4875 | 62.1386 | 65.1171 | 68.6614 | 72.0212 | 75.5791 | 81.6776 | 83.6199 | 87.4971 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 90.3876 | 65% | 46.136 | 63.74 | 59.9032 | 62.8573 | 65.3316 | 67.5244 | 70.9729 | 74.0907 | 78.4117 | 82.9164 | 86.5989 | 90.073 | 95.2239 | 98.972 | 102.748 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462 | 106.7462
60% | 156.9382 | 49.7102 | 46.0898 | 48.4773 | 50.3609 | 52.6395 | 54.9116 | 57.3587 | 60.1081 | 63.3798 | 66.4811 | 69.7653 | 75.3947 | 77.1876 | 80.7666 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 83.4347 | 60% | 76.7673 | 58.8369 | 55.2953 | 58.0221 | 60.3061 | 62.3302 | 65.5135 | 68.3914 | 72.3801 | 76.5382 | 79.9375 | 83.1443 | 87.899 | 91.3588 | 94.8443 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535 | 98.535
55% | 363.794 | 45.5677 | 42.249 | 44.4375 | 46.1642 | 48.2528 | 50.3356 | 52.5788 | 55.099 | 58.0981 | 60.941 | 63.9515 | 69.1118 | 70.7553 | 74.036 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 76.4818 | 55% | 106.2642 | 53.9338 | 50.6874 | 53.1869 | 55.2806 | 57.1361 | 60.054 | 62.6921 | 66.3484 | 70.16 | 73.276 | 76.2156 | 80.574 | 83.7455 | 86.9406 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237 | 90.3237
50% | 771.4551 | 41.4251 | 38.4081 | 40.3978 | 41.9674 | 43.8662 | 45.7597 | 47.7989 | 50.09 | 52.8165 | 55.4009 | 58.1378 | 62.8289 | 64.323 | 67.3055 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 69.5289 | 50% | 178.4935 | 49.0307 | 46.0794 | 48.3517 | 50.2551 | 51.9419 | 54.5946 | 56.9929 | 60.3167 | 63.7819 | 66.6146 | 69.2869 | 73.2491 | 76.1323 | 79.0369 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125 | 82.1125
45% | 1255.5054 | 37.2826 | 34.5673 | 36.358 | 37.7707 | 39.4796 | 41.1837 | 43.019 | 45.081 | 47.5348 | 49.8608 | 52.324 | 56.546 | 57.8907 | 60.5749 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 62.576 | 45% | 367.9538 | 44.1277 | 41.4715 | 43.5166 | 45.2296 | 46.7477 | 49.1351 | 51.2936 | 54.2851 | 57.4037 | 59.9531 | 62.3583 | 65.9242 | 68.5191 | 71.1332 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012 | 73.9012
40% | 2059.1045 | 33.1401 | 30.7265 | 32.3182 | 33.574 | 35.093 | 36.6077 | 38.2391 | 40.072 | 42.2532 | 44.3207 | 46.5102 | 50.2632 | 51.4584 | 53.8444 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 55.6231 | 40% | 741.202 | 39.2246 | 36.8635 | 38.6814 | 40.2041 | 41.5535 | 43.6757 | 45.5943 | 48.2534 | 51.0255 | 53.2917 | 55.4296 | 58.5993 | 60.9058 | 63.2295 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69 | 65.69
35% | 3060.4836 | 28.9976 | 26.8857 | 28.2784 | 29.3772 | 30.7064 | 32.0318 | 33.4592 | 35.063 | 36.9715 | 38.7806 | 40.6964 | 43.9803 | 45.0261 | 47.1138 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 48.6702 | 35% | 1167.7713 | 34.3215 | 32.2556 | 33.8462 | 35.1786 | 36.3593 | 38.2162 | 39.895 | 42.2217 | 44.6473 | 46.6302 | 48.5009 | 51.2744 | 53.2926 | 55.3258 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787 | 57.4787
30% | 3366.0403 | 24.8551 | 23.0449 | 24.2387 | 25.1805 | 26.3197 | 27.4558 | 28.6793 | 30.054 | 31.6899 | 33.2405 | 34.8827 | 37.6974 | 38.5938 | 40.3833 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 41.7173 | 30% | 2002.3799 | 29.4184 | 27.6477 | 29.011 | 30.1531 | 31.1651 | 32.7567 | 34.1957 | 36.19 | 38.2691 | 39.9687 | 41.5722 | 43.9495 | 45.6794 | 47.4221 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675 | 49.2675
25% | 3686.3454 | 20.7126 | 19.2041 | 20.1989 | 20.9837 | 21.9331 | 22.8798 | 23.8995 | 25.045 | 26.4082 | 27.7005 | 29.0689 | 31.4145 | 32.1615 | 33.6527 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 34.7644 | 25% | 3173.5547 | 24.5154 | 23.0397 | 24.1759 | 25.1275 | 25.9709 | 27.2973 | 28.4964 | 30.1584 | 31.8909 | 33.3073 | 34.6435 | 36.6246 | 38.0661 | 39.5184 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562 | 41.0562
20% | 4028.5841 | 16.5701 | 15.3633 | 16.1591 | 16.787 | 17.5465 | 18.3039 | 19.1196 | 20.036 | 21.1266 | 22.1604 | 23.2551 | 25.1316 | 25.7292 | 26.9222 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 27.8116 | 20% | 3477.5988 | 19.6123 | 18.4318 | 19.3407 | 20.102 | 20.7767 | 21.8378 | 22.7971 | 24.1267 | 25.5127 | 26.6458 | 27.7148 | 29.2997 | 30.4529 | 31.6148 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845 | 32.845
15% | 4345.1076 | 12.4275 | 11.5224 | 12.1193 | 12.5902 | 13.1599 | 13.7279 | 14.3397 | 15.027 | 15.8449 | 16.6203 | 17.4413 | 18.8487 | 19.2969 | 20.1916 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 20.8587 | 15% | 3788.4498 | 14.7092 | 13.8238 | 14.5055 | 15.0765 | 15.5826 | 16.3784 | 17.0979 | 18.095 | 19.1346 | 19.9844 | 20.7861 | 21.9747 | 22.8397 | 23.7111 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337 | 24.6337
10% | 4381.0332 | 8.285 | 7.6816 | 8.0796 | 8.3935 | 8.7732 | 9.1519 | 9.5598 | 10.018 | 10.5633 | 11.0802 | 11.6276 | 12.5658 | 12.8646 | 13.4611 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 13.9058 | 10% | 4317.5016 | 9.8061 | 9.2159 | 9.6703 | 10.051 | 10.3884 | 10.9189 | 11.3986 | 12.0633 | 12.7564 | 13.3229 | 13.8574 | 14.6498 | 15.2265 | 15.8074 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225 | 16.4225
5% | 4391.6218 | 4.1425 | 3.8408 | 4.0398 | 4.1967 | 4.3866 | 4.576 | 4.7799 | 5.009 | 5.2816 | 5.5401 | 5.8138 | 6.2829 | 6.4323 | 6.7305 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 6.9529 | 5% | 4391.6218 | 4.9031 | 4.6079 | 4.8352 | 5.0255 | 5.1942 | 5.4595 | 5.6993 | 6.0317 | 6.3782 | 6.6615 | 6.9287 | 7.3249 | 7.6132 | 7.9037 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112 | 8.2112
9.992e-14% | 4391.6218 | 8.2784e-14 | 7.6755e-14 | 8.0731e-14 | 8.3868e-14 | 8.7662e-14 | 9.1446e-14 | 9.5521e-14 | 1.001e-13 | 1.0555e-13 | 1.1071e-13 | 1.1618e-13 | 1.2556e-13 | 1.2854e-13 | 1.345e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 1.3895e-13 | 9.992e-14% | 4391.6218 | 9.7983e-14 | 9.2085e-14 | 9.6626e-14 | 1.0043e-13 | 1.038e-13 | 1.091e-13 | 1.1389e-13 | 1.2054e-13 | 1.2746e-13 | 1.3312e-13 | 1.3846e-13 | 1.4638e-13 | 1.5214e-13 | 1.5795e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13 | 1.6409e-13
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 100% | 0 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
99% | 0.5944 | 68.427 | 64.2027 | 68.066 | 73.0038 | 77.7847 | 82.0399 | 87.8842 | 94.2725 | 100.8151 | 107.2984 | 113.0603 | 119.3404 | 121.738 | 129.8557 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 99% | 0.5944 | 73.2778 | 69.0729 | 73.1555 | 78.154 | 82.814 | 87.7759 | 92.9942 | 100.4376 | 106.9274 | 113.0485 | 119.4102 | 127.0352 | 129.5879 | 137.8107 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748
98% | 0.8916 | 67.7358 | 63.5542 | 67.3784 | 72.2664 | 76.999 | 81.2112 | 86.9965 | 93.3203 | 99.7967 | 106.2146 | 111.9183 | 118.135 | 120.5083 | 128.544 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 98% | 0.8916 | 72.5377 | 68.3752 | 72.4165 | 77.3646 | 81.9775 | 86.8893 | 92.0548 | 99.4231 | 105.8473 | 111.9066 | 118.204 | 125.752 | 128.279 | 136.4186 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053
97% | 1.486 | 67.0447 | 62.9057 | 66.6909 | 71.529 | 76.2133 | 80.3826 | 86.1088 | 92.3681 | 98.7784 | 105.1308 | 110.7763 | 116.9295 | 119.2786 | 127.2324 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 97% | 1.486 | 71.7975 | 67.6774 | 71.6776 | 76.5751 | 81.1409 | 86.0026 | 91.1155 | 98.4086 | 104.7673 | 110.7647 | 116.9979 | 124.4688 | 126.97 | 135.0266 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359
95% | 2.3776 | 65.6623 | 61.6087 | 65.3158 | 70.0541 | 74.6418 | 78.7252 | 84.3333 | 90.4636 | 96.7417 | 102.9631 | 108.4922 | 114.5186 | 116.8193 | 124.609 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 95% | 2.3776 | 70.3171 | 66.282 | 70.1997 | 74.9963 | 79.4679 | 84.2294 | 89.2368 | 96.3795 | 102.6071 | 108.4809 | 114.5855 | 121.9024 | 124.3521 | 132.2425 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597
90% | 3.2692 | 62.2064 | 58.3661 | 61.8782 | 66.3671 | 70.7133 | 74.5817 | 79.8947 | 85.7023 | 91.6501 | 97.544 | 102.7821 | 108.4913 | 110.6709 | 118.0507 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 90% | 3.2692 | 66.6162 | 62.7935 | 66.505 | 71.0491 | 75.2854 | 79.7963 | 84.5401 | 91.3069 | 97.2067 | 102.7713 | 108.5547 | 115.4865 | 117.8072 | 125.2824 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498
85% | 13.9683 | 58.7505 | 55.1235 | 58.4405 | 62.68 | 66.7848 | 70.4383 | 75.4561 | 80.9411 | 86.5584 | 92.1249 | 97.072 | 102.464 | 104.5225 | 111.4923 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 85% | 13.9683 | 62.9153 | 59.305 | 62.8103 | 67.1019 | 71.1029 | 75.3631 | 79.8435 | 86.2343 | 91.8064 | 97.0618 | 102.5239 | 109.0706 | 111.2624 | 118.3223 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026
80% | 41.3106 | 55.2946 | 51.881 | 55.0028 | 58.993 | 62.8563 | 66.2949 | 71.0175 | 76.1798 | 81.4667 | 86.7058 | 91.3619 | 96.4367 | 98.3741 | 104.9339 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 80% | 41.3106 | 59.2144 | 55.8165 | 59.1156 | 63.1548 | 66.9204 | 70.93 | 75.1468 | 81.1617 | 86.406 | 91.3523 | 96.4931 | 102.6547 | 104.7175 | 111.3621 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554
75% | 126.3094 | 51.8387 | 48.6384 | 51.5651 | 55.3059 | 58.9278 | 62.1515 | 66.579 | 71.4186 | 76.375 | 81.2867 | 85.6518 | 90.4094 | 92.2257 | 98.3755 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 75% | 126.3094 | 55.5135 | 52.3279 | 55.4208 | 59.2076 | 62.7378 | 66.4969 | 70.4501 | 76.0891 | 81.0056 | 85.6428 | 90.4623 | 96.2388 | 98.1727 | 104.402 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082
70% | 323.9464 | 48.3827 | 45.3959 | 48.1275 | 51.6188 | 54.9993 | 58.008 | 62.1404 | 66.6574 | 71.2834 | 75.8676 | 79.9417 | 84.3821 | 86.0773 | 91.8172 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 70% | 323.9464 | 51.8126 | 48.8394 | 51.7261 | 55.2604 | 58.5553 | 62.0638 | 65.7534 | 71.0165 | 75.6052 | 79.9333 | 84.4314 | 89.8228 | 91.6278 | 97.4419 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861
65% | 549.5201 | 44.9268 | 42.1533 | 44.6898 | 47.9318 | 51.0707 | 53.8646 | 57.7018 | 61.8961 | 66.1917 | 70.4485 | 74.2315 | 78.3548 | 79.929 | 85.2588 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 65% | 549.5201 | 48.1117 | 45.3509 | 48.0314 | 51.3132 | 54.3728 | 57.6306 | 61.0568 | 65.9439 | 70.2049 | 74.2237 | 78.4006 | 83.4069 | 85.083 | 90.4817 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137
60% | 799.4641 | 41.4709 | 38.9107 | 41.2521 | 44.2447 | 47.1422 | 49.7212 | 53.2632 | 57.1349 | 61.1 | 65.0294 | 68.5214 | 72.3275 | 73.7806 | 78.7004 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 60% | 799.4641 | 44.4108 | 41.8623 | 44.3367 | 47.3661 | 50.1903 | 53.1975 | 56.3601 | 60.8713 | 64.8045 | 68.5142 | 72.3698 | 76.991 | 78.5381 | 83.5216 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665
55% | 1116.2777 | 38.015 | 35.6682 | 37.8144 | 40.5577 | 43.2137 | 45.5777 | 48.8246 | 52.3736 | 56.0084 | 59.6102 | 62.8113 | 66.3002 | 67.6322 | 72.1421 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 55% | 1116.2777 | 40.7099 | 38.3738 | 40.6419 | 43.4189 | 46.0078 | 48.7644 | 51.6634 | 55.7987 | 59.4041 | 62.8047 | 66.339 | 70.5751 | 71.9933 | 76.5615 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193
50% | 1494.9086 | 34.5591 | 32.4256 | 34.3768 | 36.8706 | 39.2852 | 41.4343 | 44.386 | 47.6124 | 50.9167 | 54.1911 | 57.1012 | 60.2729 | 61.4838 | 65.5837 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 50% | 1494.9086 | 37.009 | 34.8853 | 36.9472 | 39.4717 | 41.8252 | 44.3313 | 46.9667 | 50.7261 | 54.0037 | 57.0952 | 60.3082 | 64.1592 | 65.4485 | 69.6013 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721
45% | 2004.0097 | 31.1032 | 29.183 | 30.9391 | 33.1835 | 35.3567 | 37.2909 | 39.9474 | 42.8512 | 45.825 | 48.772 | 51.3911 | 54.2456 | 55.3354 | 59.0253 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 45% | 2004.0097 | 33.3081 | 31.3968 | 33.2525 | 35.5246 | 37.6427 | 39.8981 | 42.2701 | 45.6535 | 48.6034 | 51.3857 | 54.2774 | 57.7433 | 58.9036 | 62.6412 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249
40% | 2877.179 | 27.6473 | 25.9405 | 27.5014 | 29.4965 | 31.4281 | 33.1474 | 35.5088 | 38.0899 | 40.7334 | 43.3529 | 45.6809 | 48.2184 | 49.1871 | 52.467 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 40% | 2877.179 | 29.6072 | 27.9082 | 29.5578 | 31.5774 | 33.4602 | 35.465 | 37.5734 | 40.5808 | 43.203 | 45.6762 | 48.2465 | 51.3273 | 52.3588 | 55.6811 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777
35% | 3454.933 | 24.1914 | 22.6979 | 24.0637 | 25.8094 | 27.4996 | 29.004 | 31.0702 | 33.3287 | 35.6417 | 37.9338 | 39.9708 | 42.1911 | 43.0387 | 45.9086 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 35% | 3454.933 | 25.9063 | 24.4197 | 25.8631 | 27.6302 | 29.2777 | 31.0319 | 32.8767 | 35.5082 | 37.8026 | 39.9666 | 42.2157 | 44.9114 | 45.8139 | 48.7209 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305
30% | 3663.5664 | 20.7355 | 19.4554 | 20.6261 | 22.1224 | 23.5711 | 24.8606 | 26.6316 | 28.5674 | 30.55 | 32.5147 | 34.2607 | 36.1638 | 36.8903 | 39.3502 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 30% | 3663.5664 | 22.2054 | 20.9312 | 22.1683 | 23.683 | 25.0951 | 26.5988 | 28.18 | 30.4356 | 32.4022 | 34.2571 | 36.1849 | 38.4955 | 39.2691 | 41.7608 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833
25% | 3862.6894 | 17.2796 | 16.2128 | 17.1884 | 18.4353 | 19.6426 | 20.7172 | 22.193 | 23.8062 | 25.4583 | 27.0956 | 28.5506 | 30.1365 | 30.7419 | 32.7918 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 25% | 3862.6894 | 18.5045 | 17.4426 | 18.4736 | 19.7359 | 20.9126 | 22.1656 | 23.4834 | 25.363 | 27.0019 | 28.5476 | 30.1541 | 32.0796 | 32.7242 | 34.8007 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361
20% | 4122.7381 | 13.8236 | 12.9702 | 13.7507 | 14.7482 | 15.7141 | 16.5737 | 17.7544 | 19.045 | 20.3667 | 21.6765 | 22.8405 | 24.1092 | 24.5935 | 26.2335 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 20% | 4122.7381 | 14.8036 | 13.9541 | 14.7789 | 15.7887 | 16.7301 | 17.7325 | 18.7867 | 20.2904 | 21.6015 | 22.8381 | 24.1233 | 25.6637 | 26.1794 | 27.8405 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888
15% | 4372.3849 | 10.3677 | 9.7277 | 10.313 | 11.0612 | 11.7856 | 12.4303 | 13.3158 | 14.2837 | 15.275 | 16.2573 | 17.1304 | 18.0819 | 18.4451 | 19.6751 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 15% | 4372.3849 | 11.1027 | 10.4656 | 11.0842 | 11.8415 | 12.5476 | 13.2994 | 14.09 | 15.2178 | 16.2011 | 17.1286 | 18.0925 | 19.2478 | 19.6345 | 20.8804 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416
10% | 4374.4653 | 6.9118 | 6.4851 | 6.8754 | 7.3741 | 7.857 | 8.2869 | 8.8772 | 9.5225 | 10.1833 | 10.8382 | 11.4202 | 12.0546 | 12.2968 | 13.1167 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 10% | 4374.4653 | 7.4018 | 6.9771 | 7.3894 | 7.8943 | 8.365 | 8.8663 | 9.3933 | 10.1452 | 10.8007 | 11.419 | 12.0616 | 12.8318 | 13.0897 | 13.9203 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944
5% | 4374.7625 | 3.4559 | 3.2426 | 3.4377 | 3.6871 | 3.9285 | 4.1434 | 4.4386 | 4.7612 | 5.0917 | 5.4191 | 5.7101 | 6.0273 | 6.1484 | 6.5584 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 5% | 4374.7625 | 3.7009 | 3.4885 | 3.6947 | 3.9472 | 4.1825 | 4.4331 | 4.6967 | 5.0726 | 5.4004 | 5.7095 | 6.0308 | 6.4159 | 6.5448 | 6.9601 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472
9.992e-14% | 4375.9513 | 6.9063e-14 | 6.4799e-14 | 6.8699e-14 | 7.3682e-14 | 7.8508e-14 | 8.2802e-14 | 8.8701e-14 | 9.5149e-14 | 1.0175e-13 | 1.083e-13 | 1.1411e-13 | 1.2045e-13 | 1.2287e-13 | 1.3106e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 9.992e-14% | 4375.9513 | 7.3959e-14 | 6.9715e-14 | 7.3835e-14 | 7.888e-14 | 8.3584e-14 | 8.8592e-14 | 9.3858e-14 | 1.0137e-13 | 1.0792e-13 | 1.141e-13 | 1.2052e-13 | 1.2822e-13 | 1.3079e-13 | 1.3909e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 100% | 0 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104
99% | 0 | 88.8377 | 83.8207 | 88.0573 | 91.4111 | 95.3871 | 99.4868 | 103.8405 | 108.8216 | 114.6843 | 120.1786 | 125.9523 | 135.7757 | 139.1181 | 145.4111 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 99% | 0.37816 | 103.8968 | 99.0099 | 103.8062 | 107.8207 | 111.3769 | 116.9799 | 122.0445 | 129.0705 | 136.3958 | 142.3816 | 148.0278 | 156.4077 | 162.5005 | 168.6394 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413
98% | 0.37816 | 87.9404 | 82.9741 | 87.1679 | 90.4877 | 94.4236 | 98.4819 | 102.7916 | 107.7224 | 113.5259 | 118.9647 | 124.6801 | 134.4042 | 137.7129 | 143.9423 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 98% | 1.1345 | 102.8473 | 98.0098 | 102.7576 | 106.7316 | 110.2519 | 115.7983 | 120.8117 | 127.7667 | 135.018 | 140.9434 | 146.5325 | 154.8278 | 160.8591 | 166.9359 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722
97% | 0.75633 | 87.043 | 82.1274 | 86.2784 | 89.5644 | 93.4601 | 97.4769 | 101.7427 | 106.6232 | 112.3675 | 117.7507 | 123.4079 | 133.0328 | 136.3077 | 142.4735 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 97% | 2.269 | 101.7979 | 97.0097 | 101.7091 | 105.6425 | 109.1268 | 114.6167 | 119.579 | 126.463 | 133.6403 | 139.5052 | 145.0373 | 153.2479 | 159.2176 | 165.2325 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031
95% | 1.1345 | 85.2483 | 80.434 | 84.4994 | 87.7177 | 91.5331 | 95.4671 | 99.6449 | 104.4248 | 110.0506 | 115.3229 | 120.8634 | 130.2898 | 133.4972 | 139.5359 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 95% | 4.538 | 99.699 | 95.0095 | 99.612 | 103.4643 | 106.8768 | 112.2534 | 117.1134 | 123.8555 | 130.8848 | 136.6288 | 142.0468 | 150.0882 | 155.9348 | 161.8257 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649
90% | 4.538 | 80.7616 | 76.2007 | 80.0521 | 83.101 | 86.7155 | 90.4425 | 94.4005 | 98.9288 | 104.2585 | 109.2533 | 114.5021 | 123.4325 | 126.471 | 132.1919 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 90% | 7.9414 | 94.4516 | 90.009 | 94.3693 | 98.0188 | 101.2517 | 106.3454 | 110.9496 | 117.3368 | 123.9961 | 129.4378 | 134.5707 | 142.1888 | 147.7277 | 153.3085 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194
85% | 7.9414 | 76.2748 | 71.9673 | 75.6048 | 78.4843 | 81.898 | 85.4179 | 89.156 | 93.4327 | 98.4663 | 103.1836 | 108.1409 | 116.5751 | 119.4449 | 124.8479 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 85% | 14.3702 | 89.2043 | 85.0085 | 89.1265 | 92.5733 | 95.6266 | 100.4373 | 104.7857 | 110.8181 | 117.1075 | 122.2468 | 127.0945 | 134.2894 | 139.5206 | 144.7914 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738
80% | 11.7231 | 71.788 | 67.7339 | 71.1574 | 73.8675 | 77.0805 | 80.3933 | 83.9115 | 87.9367 | 92.6742 | 97.114 | 101.7797 | 109.7177 | 112.4187 | 117.5039 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 80% | 19.6645 | 83.957 | 80.008 | 83.8838 | 87.1278 | 90.0015 | 94.5292 | 98.6218 | 104.2994 | 110.2188 | 115.0559 | 119.6184 | 126.39 | 131.3135 | 136.2742 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283
75% | 17.7737 | 67.3013 | 63.5006 | 66.7101 | 69.2508 | 72.2629 | 75.3688 | 78.6671 | 82.4406 | 86.8821 | 91.0444 | 95.4184 | 102.8604 | 105.3925 | 110.16 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 75% | 25.7152 | 78.7097 | 75.0075 | 78.641 | 81.6823 | 84.3764 | 88.6211 | 92.458 | 97.7807 | 103.3301 | 107.8649 | 112.1422 | 118.4907 | 123.1064 | 127.7571 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828
70% | 35.1693 | 62.8145 | 59.2672 | 62.2628 | 64.6341 | 67.4454 | 70.3442 | 73.4226 | 76.9446 | 81.0899 | 84.9748 | 89.0572 | 96.003 | 98.3664 | 102.816 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 70% | 34.7911 | 73.4624 | 70.007 | 73.3983 | 76.2368 | 78.7513 | 82.7131 | 86.2941 | 91.262 | 96.4414 | 100.6739 | 104.6661 | 110.5913 | 114.8993 | 119.24 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373
65% | 59.3718 | 58.3278 | 55.0338 | 57.8154 | 60.0174 | 62.6279 | 65.3196 | 68.1781 | 71.4486 | 75.2978 | 78.9051 | 82.696 | 89.1457 | 91.3402 | 95.472 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 65% | 46.136 | 68.2151 | 65.0065 | 68.1556 | 70.7913 | 73.1262 | 76.805 | 80.1302 | 84.7432 | 89.5528 | 93.4829 | 97.1899 | 102.6919 | 106.6922 | 110.7228 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918
60% | 156.9382 | 53.841 | 50.8005 | 53.3681 | 55.4007 | 57.8104 | 60.295 | 62.9336 | 65.9525 | 69.5057 | 72.8355 | 76.3348 | 82.2883 | 84.314 | 88.128 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 60% | 76.7673 | 62.9678 | 60.006 | 62.9128 | 65.3459 | 67.5011 | 70.8969 | 73.9664 | 78.2245 | 82.6641 | 86.2919 | 89.7138 | 94.7925 | 98.4851 | 102.2057 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462
55% | 363.794 | 49.3543 | 46.5671 | 48.9207 | 50.7839 | 52.9928 | 55.2704 | 57.6892 | 60.4565 | 63.7135 | 66.7659 | 69.9735 | 75.4309 | 77.2879 | 80.784 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 55% | 106.2642 | 57.7205 | 55.0055 | 57.6701 | 59.9004 | 61.876 | 64.9888 | 67.8025 | 71.7058 | 75.7754 | 79.1009 | 82.2376 | 86.8932 | 90.278 | 93.6885 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007
50% | 771.4551 | 44.8675 | 42.3337 | 44.4734 | 46.1672 | 48.1753 | 50.2458 | 52.4447 | 54.9604 | 57.9214 | 60.6963 | 63.6123 | 68.5736 | 70.2617 | 73.44 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 50% | 178.4935 | 52.4731 | 50.005 | 52.4274 | 54.4549 | 56.251 | 59.0808 | 61.6386 | 65.1871 | 68.8867 | 71.9099 | 74.7615 | 78.9938 | 82.0709 | 85.1714 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552
45% | 1255.5054 | 40.3808 | 38.1003 | 40.0261 | 41.5505 | 43.3578 | 45.2213 | 47.2002 | 49.4644 | 52.1292 | 54.6266 | 57.2511 | 61.7162 | 63.2355 | 66.096 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 45% | 367.9538 | 47.2258 | 45.0045 | 47.1846 | 49.0094 | 50.6259 | 53.1727 | 55.4748 | 58.6684 | 61.9981 | 64.7189 | 67.2853 | 71.0944 | 73.8639 | 76.6543 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097
40% | 2059.1045 | 35.894 | 33.867 | 35.5787 | 36.9338 | 38.5402 | 40.1967 | 41.9558 | 43.9683 | 46.3371 | 48.557 | 50.8898 | 54.8589 | 56.2094 | 58.752 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 40% | 741.202 | 41.9785 | 40.004 | 41.9419 | 43.5639 | 45.0008 | 47.2646 | 49.3109 | 52.1497 | 55.1094 | 57.5279 | 59.8092 | 63.195 | 65.6568 | 68.1371 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642
35% | 3060.4836 | 31.4073 | 29.6336 | 31.1314 | 32.317 | 33.7227 | 35.1721 | 36.7113 | 38.4723 | 40.545 | 42.4874 | 44.5286 | 48.0015 | 49.1832 | 51.408 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 35% | 1167.7713 | 36.7312 | 35.0035 | 36.6992 | 38.1184 | 39.3757 | 41.3565 | 43.1471 | 45.631 | 48.2207 | 50.3369 | 52.333 | 55.2956 | 57.4497 | 59.62 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186
30% | 3366.0403 | 26.9205 | 25.4002 | 26.684 | 27.7003 | 28.9052 | 30.1475 | 31.4668 | 32.9763 | 34.7528 | 36.4178 | 38.1674 | 41.1442 | 42.157 | 44.064 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 30% | 2002.3799 | 31.4839 | 30.003 | 31.4564 | 32.6729 | 33.7506 | 35.4485 | 36.9832 | 39.1123 | 41.332 | 43.1459 | 44.8569 | 47.3963 | 49.2426 | 51.1028 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731
25% | 3686.3454 | 22.4338 | 21.1669 | 22.2367 | 23.0836 | 24.0876 | 25.1229 | 26.2224 | 27.4802 | 28.9607 | 30.3481 | 31.8061 | 34.2868 | 35.1308 | 36.72 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 25% | 3173.5547 | 26.2366 | 25.0025 | 26.2137 | 27.2274 | 28.1255 | 29.5404 | 30.8193 | 32.5936 | 34.4434 | 35.955 | 37.3807 | 39.4969 | 41.0355 | 42.5857 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276
20% | 4028.5841 | 17.947 | 16.9335 | 17.7894 | 18.4669 | 19.2701 | 20.0983 | 20.9779 | 21.9842 | 23.1686 | 24.2785 | 25.4449 | 27.4294 | 28.1047 | 29.376 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 20% | 3477.5988 | 20.9893 | 20.002 | 20.9709 | 21.782 | 22.5004 | 23.6323 | 24.6555 | 26.0748 | 27.5547 | 28.764 | 29.9046 | 31.5975 | 32.8284 | 34.0686 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821
15% | 4345.1076 | 13.4603 | 12.7001 | 13.342 | 13.8502 | 14.4526 | 15.0738 | 15.7334 | 16.4881 | 17.3764 | 18.2089 | 19.0837 | 20.5721 | 21.0785 | 22.032 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 15% | 3788.4498 | 15.7419 | 15.0015 | 15.7282 | 16.3365 | 16.8753 | 17.7242 | 18.4916 | 19.5561 | 20.666 | 21.573 | 22.4284 | 23.6981 | 24.6213 | 25.5514 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366
10% | 4381.0332 | 8.9735 | 8.4667 | 8.8947 | 9.2334 | 9.6351 | 10.0492 | 10.4889 | 10.9921 | 11.5843 | 12.1393 | 12.7225 | 13.7147 | 14.0523 | 14.688 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 10% | 4317.5016 | 10.4946 | 10.001 | 10.4855 | 10.891 | 11.2502 | 11.8162 | 12.3277 | 13.0374 | 13.7773 | 14.382 | 14.9523 | 15.7988 | 16.4142 | 17.0343 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691
5% | 4391.6218 | 4.4868 | 4.2334 | 4.4473 | 4.6167 | 4.8175 | 5.0246 | 5.2445 | 5.496 | 5.7921 | 6.0696 | 6.3612 | 6.8574 | 7.0262 | 7.344 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 5% | 4391.6218 | 5.2473 | 5.0005 | 5.2427 | 5.4455 | 5.6251 | 5.9081 | 6.1639 | 6.5187 | 6.8887 | 7.191 | 7.4761 | 7.8994 | 8.2071 | 8.5171 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455
9.992e-14% | 4391.6218 | 8.9663e-14 | 8.46e-14 | 8.8876e-14 | 9.2261e-14 | 9.6274e-14 | 1.0041e-13 | 1.0481e-13 | 1.0983e-13 | 1.1575e-13 | 1.213e-13 | 1.2712e-13 | 1.3704e-13 | 1.4041e-13 | 1.4676e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 9.992e-14% | 4391.6218 | 1.0486e-13 | 9.993e-14 | 1.0477e-13 | 1.0882e-13 | 1.1241e-13 | 1.1807e-13 | 1.2318e-13 | 1.3027e-13 | 1.3766e-13 | 1.437e-13 | 1.494e-13 | 1.5786e-13 | 1.6401e-13 | 1.7021e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 69.1182 | 64.8512 | 68.7535 | 73.7412 | 78.5704 | 82.8686 | 88.7719 | 95.2248 | 101.8334 | 108.3823 | 114.2024 | 120.5459 | 122.9676 | 131.1674 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 139.6489 | 100% | 0 | 74.018 | 69.7706 | 73.8944 | 78.9434 | 83.6505 | 88.6625 | 93.9335 | 101.4521 | 108.0075 | 114.1904 | 120.6164 | 128.3183 | 130.8969 | 139.2027 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442 | 146.9442
99% | 0.5944 | 68.427 | 64.2027 | 68.066 | 73.0038 | 77.7847 | 82.0399 | 87.8842 | 94.2725 | 100.8151 | 107.2984 | 113.0603 | 119.3404 | 121.738 | 129.8557 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 138.2525 | 99% | 0.5944 | 73.2778 | 69.0729 | 73.1555 | 78.154 | 82.814 | 87.7759 | 92.9942 | 100.4376 | 106.9274 | 113.0485 | 119.4102 | 127.0352 | 129.5879 | 137.8107 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748 | 145.4748
98% | 0.8916 | 67.7358 | 63.5542 | 67.3784 | 72.2664 | 76.999 | 81.2112 | 86.9965 | 93.3203 | 99.7967 | 106.2146 | 111.9183 | 118.135 | 120.5083 | 128.544 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 136.856 | 98% | 0.8916 | 72.5377 | 68.3752 | 72.4165 | 77.3646 | 81.9775 | 86.8893 | 92.0548 | 99.4231 | 105.8473 | 111.9066 | 118.204 | 125.752 | 128.279 | 136.4186 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053 | 144.0053
97% | 1.486 | 67.0447 | 62.9057 | 66.6909 | 71.529 | 76.2133 | 80.3826 | 86.1088 | 92.3681 | 98.7784 | 105.1308 | 110.7763 | 116.9295 | 119.2786 | 127.2324 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 135.4595 | 97% | 1.486 | 71.7975 | 67.6774 | 71.6776 | 76.5751 | 81.1409 | 86.0026 | 91.1155 | 98.4086 | 104.7673 | 110.7647 | 116.9979 | 124.4688 | 126.97 | 135.0266 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359 | 142.5359
95% | 2.3776 | 65.6623 | 61.6087 | 65.3158 | 70.0541 | 74.6418 | 78.7252 | 84.3333 | 90.4636 | 96.7417 | 102.9631 | 108.4922 | 114.5186 | 116.8193 | 124.609 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 132.6665 | 95% | 2.3776 | 70.3171 | 66.282 | 70.1997 | 74.9963 | 79.4679 | 84.2294 | 89.2368 | 96.3795 | 102.6071 | 108.4809 | 114.5855 | 121.9024 | 124.3521 | 132.2425 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597 | 139.597
90% | 3.2692 | 62.2064 | 58.3661 | 61.8782 | 66.3671 | 70.7133 | 74.5817 | 79.8947 | 85.7023 | 91.6501 | 97.544 | 102.7821 | 108.4913 | 110.6709 | 118.0507 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 125.684 | 90% | 3.2692 | 66.6162 | 62.7935 | 66.505 | 71.0491 | 75.2854 | 79.7963 | 84.5401 | 91.3069 | 97.2067 | 102.7713 | 108.5547 | 115.4865 | 117.8072 | 125.2824 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498 | 132.2498
85% | 13.9683 | 58.7505 | 55.1235 | 58.4405 | 62.68 | 66.7848 | 70.4383 | 75.4561 | 80.9411 | 86.5584 | 92.1249 | 97.072 | 102.464 | 104.5225 | 111.4923 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 118.7016 | 85% | 13.9683 | 62.9153 | 59.305 | 62.8103 | 67.1019 | 71.1029 | 75.3631 | 79.8435 | 86.2343 | 91.8064 | 97.0618 | 102.5239 | 109.0706 | 111.2624 | 118.3223 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026 | 124.9026
80% | 41.3106 | 55.2946 | 51.881 | 55.0028 | 58.993 | 62.8563 | 66.2949 | 71.0175 | 76.1798 | 81.4667 | 86.7058 | 91.3619 | 96.4367 | 98.3741 | 104.9339 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 111.7192 | 80% | 41.3106 | 59.2144 | 55.8165 | 59.1156 | 63.1548 | 66.9204 | 70.93 | 75.1468 | 81.1617 | 86.406 | 91.3523 | 96.4931 | 102.6547 | 104.7175 | 111.3621 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554 | 117.5554
75% | 126.3094 | 51.8387 | 48.6384 | 51.5651 | 55.3059 | 58.9278 | 62.1515 | 66.579 | 71.4186 | 76.375 | 81.2867 | 85.6518 | 90.4094 | 92.2257 | 98.3755 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 104.7367 | 75% | 126.3094 | 55.5135 | 52.3279 | 55.4208 | 59.2076 | 62.7378 | 66.4969 | 70.4501 | 76.0891 | 81.0056 | 85.6428 | 90.4623 | 96.2388 | 98.1727 | 104.402 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082 | 110.2082
70% | 323.9464 | 48.3827 | 45.3959 | 48.1275 | 51.6188 | 54.9993 | 58.008 | 62.1404 | 66.6574 | 71.2834 | 75.8676 | 79.9417 | 84.3821 | 86.0773 | 91.8172 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 97.7543 | 70% | 323.9464 | 51.8126 | 48.8394 | 51.7261 | 55.2604 | 58.5553 | 62.0638 | 65.7534 | 71.0165 | 75.6052 | 79.9333 | 84.4314 | 89.8228 | 91.6278 | 97.4419 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861 | 102.861
65% | 549.5201 | 44.9268 | 42.1533 | 44.6898 | 47.9318 | 51.0707 | 53.8646 | 57.7018 | 61.8961 | 66.1917 | 70.4485 | 74.2315 | 78.3548 | 79.929 | 85.2588 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 90.7718 | 65% | 549.5201 | 48.1117 | 45.3509 | 48.0314 | 51.3132 | 54.3728 | 57.6306 | 61.0568 | 65.9439 | 70.2049 | 74.2237 | 78.4006 | 83.4069 | 85.083 | 90.4817 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137 | 95.5137
60% | 799.4641 | 41.4709 | 38.9107 | 41.2521 | 44.2447 | 47.1422 | 49.7212 | 53.2632 | 57.1349 | 61.1 | 65.0294 | 68.5214 | 72.3275 | 73.7806 | 78.7004 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 83.7894 | 60% | 799.4641 | 44.4108 | 41.8623 | 44.3367 | 47.3661 | 50.1903 | 53.1975 | 56.3601 | 60.8713 | 64.8045 | 68.5142 | 72.3698 | 76.991 | 78.5381 | 83.5216 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665 | 88.1665
55% | 1116.2777 | 38.015 | 35.6682 | 37.8144 | 40.5577 | 43.2137 | 45.5777 | 48.8246 | 52.3736 | 56.0084 | 59.6102 | 62.8113 | 66.3002 | 67.6322 | 72.1421 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 76.8069 | 55% | 1116.2777 | 40.7099 | 38.3738 | 40.6419 | 43.4189 | 46.0078 | 48.7644 | 51.6634 | 55.7987 | 59.4041 | 62.8047 | 66.339 | 70.5751 | 71.9933 | 76.5615 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193 | 80.8193
50% | 1494.9086 | 34.5591 | 32.4256 | 34.3768 | 36.8706 | 39.2852 | 41.4343 | 44.386 | 47.6124 | 50.9167 | 54.1911 | 57.1012 | 60.2729 | 61.4838 | 65.5837 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 69.8245 | 50% | 1494.9086 | 37.009 | 34.8853 | 36.9472 | 39.4717 | 41.8252 | 44.3313 | 46.9667 | 50.7261 | 54.0037 | 57.0952 | 60.3082 | 64.1592 | 65.4485 | 69.6013 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721 | 73.4721
45% | 2004.0097 | 31.1032 | 29.183 | 30.9391 | 33.1835 | 35.3567 | 37.2909 | 39.9474 | 42.8512 | 45.825 | 48.772 | 51.3911 | 54.2456 | 55.3354 | 59.0253 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 62.842 | 45% | 2004.0097 | 33.3081 | 31.3968 | 33.2525 | 35.5246 | 37.6427 | 39.8981 | 42.2701 | 45.6535 | 48.6034 | 51.3857 | 54.2774 | 57.7433 | 58.9036 | 62.6412 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249 | 66.1249
40% | 2877.179 | 27.6473 | 25.9405 | 27.5014 | 29.4965 | 31.4281 | 33.1474 | 35.5088 | 38.0899 | 40.7334 | 43.3529 | 45.6809 | 48.2184 | 49.1871 | 52.467 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 55.8596 | 40% | 2877.179 | 29.6072 | 27.9082 | 29.5578 | 31.5774 | 33.4602 | 35.465 | 37.5734 | 40.5808 | 43.203 | 45.6762 | 48.2465 | 51.3273 | 52.3588 | 55.6811 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777 | 58.7777
35% | 3454.933 | 24.1914 | 22.6979 | 24.0637 | 25.8094 | 27.4996 | 29.004 | 31.0702 | 33.3287 | 35.6417 | 37.9338 | 39.9708 | 42.1911 | 43.0387 | 45.9086 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 48.8771 | 35% | 3454.933 | 25.9063 | 24.4197 | 25.8631 | 27.6302 | 29.2777 | 31.0319 | 32.8767 | 35.5082 | 37.8026 | 39.9666 | 42.2157 | 44.9114 | 45.8139 | 48.7209 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305 | 51.4305
30% | 3663.5664 | 20.7355 | 19.4554 | 20.6261 | 22.1224 | 23.5711 | 24.8606 | 26.6316 | 28.5674 | 30.55 | 32.5147 | 34.2607 | 36.1638 | 36.8903 | 39.3502 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 41.8947 | 30% | 3663.5664 | 22.2054 | 20.9312 | 22.1683 | 23.683 | 25.0951 | 26.5988 | 28.18 | 30.4356 | 32.4022 | 34.2571 | 36.1849 | 38.4955 | 39.2691 | 41.7608 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833 | 44.0833
25% | 3862.6894 | 17.2796 | 16.2128 | 17.1884 | 18.4353 | 19.6426 | 20.7172 | 22.193 | 23.8062 | 25.4583 | 27.0956 | 28.5506 | 30.1365 | 30.7419 | 32.7918 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 34.9122 | 25% | 3862.6894 | 18.5045 | 17.4426 | 18.4736 | 19.7359 | 20.9126 | 22.1656 | 23.4834 | 25.363 | 27.0019 | 28.5476 | 30.1541 | 32.0796 | 32.7242 | 34.8007 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361 | 36.7361
20% | 4122.7381 | 13.8236 | 12.9702 | 13.7507 | 14.7482 | 15.7141 | 16.5737 | 17.7544 | 19.045 | 20.3667 | 21.6765 | 22.8405 | 24.1092 | 24.5935 | 26.2335 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 27.9298 | 20% | 4122.7381 | 14.8036 | 13.9541 | 14.7789 | 15.7887 | 16.7301 | 17.7325 | 18.7867 | 20.2904 | 21.6015 | 22.8381 | 24.1233 | 25.6637 | 26.1794 | 27.8405 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888 | 29.3888
15% | 4372.3849 | 10.3677 | 9.7277 | 10.313 | 11.0612 | 11.7856 | 12.4303 | 13.3158 | 14.2837 | 15.275 | 16.2573 | 17.1304 | 18.0819 | 18.4451 | 19.6751 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 20.9473 | 15% | 4372.3849 | 11.1027 | 10.4656 | 11.0842 | 11.8415 | 12.5476 | 13.2994 | 14.09 | 15.2178 | 16.2011 | 17.1286 | 18.0925 | 19.2478 | 19.6345 | 20.8804 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416 | 22.0416
10% | 4374.4653 | 6.9118 | 6.4851 | 6.8754 | 7.3741 | 7.857 | 8.2869 | 8.8772 | 9.5225 | 10.1833 | 10.8382 | 11.4202 | 12.0546 | 12.2968 | 13.1167 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 13.9649 | 10% | 4374.4653 | 7.4018 | 6.9771 | 7.3894 | 7.8943 | 8.365 | 8.8663 | 9.3933 | 10.1452 | 10.8007 | 11.419 | 12.0616 | 12.8318 | 13.0897 | 13.9203 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944 | 14.6944
5% | 4374.7625 | 3.4559 | 3.2426 | 3.4377 | 3.6871 | 3.9285 | 4.1434 | 4.4386 | 4.7612 | 5.0917 | 5.4191 | 5.7101 | 6.0273 | 6.1484 | 6.5584 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 6.9824 | 5% | 4374.7625 | 3.7009 | 3.4885 | 3.6947 | 3.9472 | 4.1825 | 4.4331 | 4.6967 | 5.0726 | 5.4004 | 5.7095 | 6.0308 | 6.4159 | 6.5448 | 6.9601 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472 | 7.3472
9.992e-14% | 4375.9513 | 6.9063e-14 | 6.4799e-14 | 6.8699e-14 | 7.3682e-14 | 7.8508e-14 | 8.2802e-14 | 8.8701e-14 | 9.5149e-14 | 1.0175e-13 | 1.083e-13 | 1.1411e-13 | 1.2045e-13 | 1.2287e-13 | 1.3106e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 1.3954e-13 | 9.992e-14% | 4375.9513 | 7.3959e-14 | 6.9715e-14 | 7.3835e-14 | 7.888e-14 | 8.3584e-14 | 8.8592e-14 | 9.3858e-14 | 1.0137e-13 | 1.0792e-13 | 1.141e-13 | 1.2052e-13 | 1.2822e-13 | 1.3079e-13 | 1.3909e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13 | 1.4683e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 89.7351 | 84.6674 | 88.9468 | 92.3344 | 96.3506 | 100.4917 | 104.8894 | 109.9209 | 115.8428 | 121.3925 | 127.2246 | 137.1472 | 140.5234 | 146.8799 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 151.7432 | 100% | 0 | 104.9463 | 100.01 | 104.8547 | 108.9098 | 112.5019 | 118.1615 | 123.2773 | 130.3742 | 137.7735 | 143.8198 | 149.523 | 157.9876 | 164.1419 | 170.3428 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104 | 176.9104
99% | 0 | 88.8377 | 83.8207 | 88.0573 | 91.4111 | 95.3871 | 99.4868 | 103.8405 | 108.8216 | 114.6843 | 120.1786 | 125.9523 | 135.7757 | 139.1181 | 145.4111 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 150.2258 | 99% | 0.37816 | 103.8968 | 99.0099 | 103.8062 | 107.8207 | 111.3769 | 116.9799 | 122.0445 | 129.0705 | 136.3958 | 142.3816 | 148.0278 | 156.4077 | 162.5005 | 168.6394 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413 | 175.1413
98% | 0.37816 | 87.9404 | 82.9741 | 87.1679 | 90.4877 | 94.4236 | 98.4819 | 102.7916 | 107.7224 | 113.5259 | 118.9647 | 124.6801 | 134.4042 | 137.7129 | 143.9423 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 148.7083 | 98% | 1.1345 | 102.8473 | 98.0098 | 102.7576 | 106.7316 | 110.2519 | 115.7983 | 120.8117 | 127.7667 | 135.018 | 140.9434 | 146.5325 | 154.8278 | 160.8591 | 166.9359 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722 | 173.3722
97% | 0.75633 | 87.043 | 82.1274 | 86.2784 | 89.5644 | 93.4601 | 97.4769 | 101.7427 | 106.6232 | 112.3675 | 117.7507 | 123.4079 | 133.0328 | 136.3077 | 142.4735 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 147.1909 | 97% | 2.269 | 101.7979 | 97.0097 | 101.7091 | 105.6425 | 109.1268 | 114.6167 | 119.579 | 126.463 | 133.6403 | 139.5052 | 145.0373 | 153.2479 | 159.2176 | 165.2325 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031 | 171.6031
95% | 1.1345 | 85.2483 | 80.434 | 84.4994 | 87.7177 | 91.5331 | 95.4671 | 99.6449 | 104.4248 | 110.0506 | 115.3229 | 120.8634 | 130.2898 | 133.4972 | 139.5359 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 144.156 | 95% | 4.538 | 99.699 | 95.0095 | 99.612 | 103.4643 | 106.8768 | 112.2534 | 117.1134 | 123.8555 | 130.8848 | 136.6288 | 142.0468 | 150.0882 | 155.9348 | 161.8257 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649 | 168.0649
90% | 4.538 | 80.7616 | 76.2007 | 80.0521 | 83.101 | 86.7155 | 90.4425 | 94.4005 | 98.9288 | 104.2585 | 109.2533 | 114.5021 | 123.4325 | 126.471 | 132.1919 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 136.5689 | 90% | 7.9414 | 94.4516 | 90.009 | 94.3693 | 98.0188 | 101.2517 | 106.3454 | 110.9496 | 117.3368 | 123.9961 | 129.4378 | 134.5707 | 142.1888 | 147.7277 | 153.3085 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194 | 159.2194
85% | 7.9414 | 76.2748 | 71.9673 | 75.6048 | 78.4843 | 81.898 | 85.4179 | 89.156 | 93.4327 | 98.4663 | 103.1836 | 108.1409 | 116.5751 | 119.4449 | 124.8479 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 128.9817 | 85% | 14.3702 | 89.2043 | 85.0085 | 89.1265 | 92.5733 | 95.6266 | 100.4373 | 104.7857 | 110.8181 | 117.1075 | 122.2468 | 127.0945 | 134.2894 | 139.5206 | 144.7914 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738 | 150.3738
80% | 11.7231 | 71.788 | 67.7339 | 71.1574 | 73.8675 | 77.0805 | 80.3933 | 83.9115 | 87.9367 | 92.6742 | 97.114 | 101.7797 | 109.7177 | 112.4187 | 117.5039 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 121.3946 | 80% | 19.6645 | 83.957 | 80.008 | 83.8838 | 87.1278 | 90.0015 | 94.5292 | 98.6218 | 104.2994 | 110.2188 | 115.0559 | 119.6184 | 126.39 | 131.3135 | 136.2742 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283 | 141.5283
75% | 17.7737 | 67.3013 | 63.5006 | 66.7101 | 69.2508 | 72.2629 | 75.3688 | 78.6671 | 82.4406 | 86.8821 | 91.0444 | 95.4184 | 102.8604 | 105.3925 | 110.16 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 113.8074 | 75% | 25.7152 | 78.7097 | 75.0075 | 78.641 | 81.6823 | 84.3764 | 88.6211 | 92.458 | 97.7807 | 103.3301 | 107.8649 | 112.1422 | 118.4907 | 123.1064 | 127.7571 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828 | 132.6828
70% | 35.1693 | 62.8145 | 59.2672 | 62.2628 | 64.6341 | 67.4454 | 70.3442 | 73.4226 | 76.9446 | 81.0899 | 84.9748 | 89.0572 | 96.003 | 98.3664 | 102.816 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 106.2202 | 70% | 34.7911 | 73.4624 | 70.007 | 73.3983 | 76.2368 | 78.7513 | 82.7131 | 86.2941 | 91.262 | 96.4414 | 100.6739 | 104.6661 | 110.5913 | 114.8993 | 119.24 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373 | 123.8373
65% | 59.3718 | 58.3278 | 55.0338 | 57.8154 | 60.0174 | 62.6279 | 65.3196 | 68.1781 | 71.4486 | 75.2978 | 78.9051 | 82.696 | 89.1457 | 91.3402 | 95.472 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 98.6331 | 65% | 46.136 | 68.2151 | 65.0065 | 68.1556 | 70.7913 | 73.1262 | 76.805 | 80.1302 | 84.7432 | 89.5528 | 93.4829 | 97.1899 | 102.6919 | 106.6922 | 110.7228 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918 | 114.9918
60% | 156.9382 | 53.841 | 50.8005 | 53.3681 | 55.4007 | 57.8104 | 60.295 | 62.9336 | 65.9525 | 69.5057 | 72.8355 | 76.3348 | 82.2883 | 84.314 | 88.128 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 91.0459 | 60% | 76.7673 | 62.9678 | 60.006 | 62.9128 | 65.3459 | 67.5011 | 70.8969 | 73.9664 | 78.2245 | 82.6641 | 86.2919 | 89.7138 | 94.7925 | 98.4851 | 102.2057 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462 | 106.1462
55% | 363.794 | 49.3543 | 46.5671 | 48.9207 | 50.7839 | 52.9928 | 55.2704 | 57.6892 | 60.4565 | 63.7135 | 66.7659 | 69.9735 | 75.4309 | 77.2879 | 80.784 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 83.4588 | 55% | 106.2642 | 57.7205 | 55.0055 | 57.6701 | 59.9004 | 61.876 | 64.9888 | 67.8025 | 71.7058 | 75.7754 | 79.1009 | 82.2376 | 86.8932 | 90.278 | 93.6885 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007 | 97.3007
50% | 771.4551 | 44.8675 | 42.3337 | 44.4734 | 46.1672 | 48.1753 | 50.2458 | 52.4447 | 54.9604 | 57.9214 | 60.6963 | 63.6123 | 68.5736 | 70.2617 | 73.44 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 75.8716 | 50% | 178.4935 | 52.4731 | 50.005 | 52.4274 | 54.4549 | 56.251 | 59.0808 | 61.6386 | 65.1871 | 68.8867 | 71.9099 | 74.7615 | 78.9938 | 82.0709 | 85.1714 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552 | 88.4552
45% | 1255.5054 | 40.3808 | 38.1003 | 40.0261 | 41.5505 | 43.3578 | 45.2213 | 47.2002 | 49.4644 | 52.1292 | 54.6266 | 57.2511 | 61.7162 | 63.2355 | 66.096 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 68.2844 | 45% | 367.9538 | 47.2258 | 45.0045 | 47.1846 | 49.0094 | 50.6259 | 53.1727 | 55.4748 | 58.6684 | 61.9981 | 64.7189 | 67.2853 | 71.0944 | 73.8639 | 76.6543 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097 | 79.6097
40% | 2059.1045 | 35.894 | 33.867 | 35.5787 | 36.9338 | 38.5402 | 40.1967 | 41.9558 | 43.9683 | 46.3371 | 48.557 | 50.8898 | 54.8589 | 56.2094 | 58.752 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 60.6973 | 40% | 741.202 | 41.9785 | 40.004 | 41.9419 | 43.5639 | 45.0008 | 47.2646 | 49.3109 | 52.1497 | 55.1094 | 57.5279 | 59.8092 | 63.195 | 65.6568 | 68.1371 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642 | 70.7642
35% | 3060.4836 | 31.4073 | 29.6336 | 31.1314 | 32.317 | 33.7227 | 35.1721 | 36.7113 | 38.4723 | 40.545 | 42.4874 | 44.5286 | 48.0015 | 49.1832 | 51.408 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 53.1101 | 35% | 1167.7713 | 36.7312 | 35.0035 | 36.6992 | 38.1184 | 39.3757 | 41.3565 | 43.1471 | 45.631 | 48.2207 | 50.3369 | 52.333 | 55.2956 | 57.4497 | 59.62 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186 | 61.9186
30% | 3366.0403 | 26.9205 | 25.4002 | 26.684 | 27.7003 | 28.9052 | 30.1475 | 31.4668 | 32.9763 | 34.7528 | 36.4178 | 38.1674 | 41.1442 | 42.157 | 44.064 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 45.523 | 30% | 2002.3799 | 31.4839 | 30.003 | 31.4564 | 32.6729 | 33.7506 | 35.4485 | 36.9832 | 39.1123 | 41.332 | 43.1459 | 44.8569 | 47.3963 | 49.2426 | 51.1028 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731 | 53.0731
25% | 3686.3454 | 22.4338 | 21.1669 | 22.2367 | 23.0836 | 24.0876 | 25.1229 | 26.2224 | 27.4802 | 28.9607 | 30.3481 | 31.8061 | 34.2868 | 35.1308 | 36.72 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 37.9358 | 25% | 3173.5547 | 26.2366 | 25.0025 | 26.2137 | 27.2274 | 28.1255 | 29.5404 | 30.8193 | 32.5936 | 34.4434 | 35.955 | 37.3807 | 39.4969 | 41.0355 | 42.5857 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276 | 44.2276
20% | 4028.5841 | 17.947 | 16.9335 | 17.7894 | 18.4669 | 19.2701 | 20.0983 | 20.9779 | 21.9842 | 23.1686 | 24.2785 | 25.4449 | 27.4294 | 28.1047 | 29.376 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 30.3486 | 20% | 3477.5988 | 20.9893 | 20.002 | 20.9709 | 21.782 | 22.5004 | 23.6323 | 24.6555 | 26.0748 | 27.5547 | 28.764 | 29.9046 | 31.5975 | 32.8284 | 34.0686 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821 | 35.3821
15% | 4345.1076 | 13.4603 | 12.7001 | 13.342 | 13.8502 | 14.4526 | 15.0738 | 15.7334 | 16.4881 | 17.3764 | 18.2089 | 19.0837 | 20.5721 | 21.0785 | 22.032 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 22.7615 | 15% | 3788.4498 | 15.7419 | 15.0015 | 15.7282 | 16.3365 | 16.8753 | 17.7242 | 18.4916 | 19.5561 | 20.666 | 21.573 | 22.4284 | 23.6981 | 24.6213 | 25.5514 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366 | 26.5366
10% | 4381.0332 | 8.9735 | 8.4667 | 8.8947 | 9.2334 | 9.6351 | 10.0492 | 10.4889 | 10.9921 | 11.5843 | 12.1393 | 12.7225 | 13.7147 | 14.0523 | 14.688 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 15.1743 | 10% | 4317.5016 | 10.4946 | 10.001 | 10.4855 | 10.891 | 11.2502 | 11.8162 | 12.3277 | 13.0374 | 13.7773 | 14.382 | 14.9523 | 15.7988 | 16.4142 | 17.0343 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691 | 17.691
5% | 4391.6218 | 4.4868 | 4.2334 | 4.4473 | 4.6167 | 4.8175 | 5.0246 | 5.2445 | 5.496 | 5.7921 | 6.0696 | 6.3612 | 6.8574 | 7.0262 | 7.344 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 7.5872 | 5% | 4391.6218 | 5.2473 | 5.0005 | 5.2427 | 5.4455 | 5.6251 | 5.9081 | 6.1639 | 6.5187 | 6.8887 | 7.191 | 7.4761 | 7.8994 | 8.2071 | 8.5171 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455 | 8.8455
9.992e-14% | 4391.6218 | 8.9663e-14 | 8.46e-14 | 8.8876e-14 | 9.2261e-14 | 9.6274e-14 | 1.0041e-13 | 1.0481e-13 | 1.0983e-13 | 1.1575e-13 | 1.213e-13 | 1.2712e-13 | 1.3704e-13 | 1.4041e-13 | 1.4676e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 1.5162e-13 | 9.992e-14% | 4391.6218 | 1.0486e-13 | 9.993e-14 | 1.0477e-13 | 1.0882e-13 | 1.1241e-13 | 1.1807e-13 | 1.2318e-13 | 1.3027e-13 | 1.3766e-13 | 1.437e-13 | 1.494e-13 | 1.5786e-13 | 1.6401e-13 | 1.7021e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13 | 1.7677e-13

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 162349945.5089 | 67.2% | 33.0819
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 70185987.1383 | 29.05% | 9.9906
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 3438927.3871 | 1.423% | 0.4767
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 5622421.9462 | 2.327% | 0.5178
|  | 241597281.9805 |  | 44.0669 | KW/h
|  |  |  | 44066.9381 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [45 empty] | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374
98% | [45 empty] | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532
97% | [45 empty] | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2.3199 | 4.595 | 6.7409 | 9.9259 | 12.2416 | 14.5749 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461
98% | [11 empty] | 1.5656 | 2.8232 | 5.191 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | [9 empty] | 3.5978 | 8.1022 | 12.3509 | 18.6569 | 23.2418 | 27.8614 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541
97% | [11 empty] | 1.0469 | 2.2918 | 4.6355 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | [9 empty] | 3.8336 | 10.5217 | 16.8301 | 26.193 | 33.0005 | 39.8595 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241
95% | [11 empty] | 0.29903 | 1.4947 | 3.8023 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | [9 empty] | 2.9799 | 16.1484 | 28.5712 | 47.009 | 60.4145 | 73.9215 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272
90% | [12 empty] | 1.5715 | 16.7245 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | [10 empty] | 7.6317 | 25.0454 | 51.6937 | 71.0689 | 90.5907 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669
85% | FY38: 0.35741; FY39: 7.0813; FY40: 7.0813; FY41: 7.0813; FY42: 7.0813; FY43: 7.0813; FY44: 7.0813; FY45: 7.0813; FY46: 7.0813; FY47: 7.0813; FY48: 7.0813; FY49: 7.0813; FY50: 7.0813; FY51: 7.0813; FY52: 7.0813; FY53: 7.0813; FY54: 7.0813 | [11 empty] | 5.6364 | 46.8602 | 81.4796 | 116.3608 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048
80% | [42 empty] | 3.7371 | 23.65 | 50.7343 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202
75% | [43 empty] | 0.048712 | 10.0691 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245
70% | [45 empty] | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9116 | 8.1811 | 30.7107 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7312 | 46.999 | 95.175 | 204.0758 | 305.1456 | 423.9721 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0381 | 5.7268 | 21.4975 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8194 | 14.0997 | 28.5525 | 61.2227 | 91.5437 | 127.1916 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY38: 0; FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 1.285 | 4.4699 | 6.7857 | 9.1189 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901 | 11.5901
98% | FY38: 0.0016089; FY39: 1.6014; FY40: 1.6014; FY41: 1.6014; FY42: 1.6014; FY43: 1.6014; FY44: 1.6014; FY45: 1.6014; FY46: 1.6014; FY47: 1.6014; FY48: 1.6014; FY49: 1.6014; FY50: 1.6014; FY51: 1.6014; FY52: 1.6014; FY53: 1.6014; FY54: 1.6014 | [11 empty] | 1.5487 | 7.8547 | 12.4395 | 17.0591 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519 | 21.9519
97% | FY39: 1.0824; FY40: 1.0824; FY41: 1.0824; FY42: 1.0824; FY43: 1.0824; FY44: 1.0824; FY45: 1.0824; FY46: 1.0824; FY47: 1.0824; FY48: 1.0824; FY49: 1.0824; FY50: 1.0824; FY51: 1.0824; FY52: 1.0824; FY53: 1.0824; FY54: 1.0824 | [11 empty] | 0.7912 | 10.1541 | 16.9616 | 23.8206 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853 | 31.0853
95% | FY39: 0.32615; FY40: 0.32615; FY41: 0.32615; FY42: 0.32615; FY43: 0.32615; FY44: 0.32615; FY45: 0.32615; FY46: 0.32615; FY47: 0.32615; FY48: 0.32615; FY49: 0.32615; FY50: 0.32615; FY51: 0.32615; FY52: 0.32615; FY53: 0.32615; FY54: 0.32615 | [11 empty] | 0.00020876 | 15.4247 | 28.8302 | 42.3372 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429 | 56.6429
90% | [42 empty] | 6.8227 | 25.4198 | 44.9415 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177 | 65.6177
85% | [43 empty] | 5.9698 | 34.7955 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395 | 71.7395
80% | [44 empty] | 0.78115 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274 | 16.4274
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016089 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | 3.0099 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.625 | 44.7261 | 96.4066 | 172.854 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548 | 275.0548
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011263 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | 2.1069 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0875 | 13.4178 | 28.922 | 51.8562 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164 | 82.5164
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [45 empty] | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374
98% | [45 empty] | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532
97% | [45 empty] | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2.3199 | 4.595 | 6.7409 | 9.9259 | 12.2416 | 14.5749 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461
98% | [11 empty] | 1.5656 | 2.8232 | 5.191 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | [9 empty] | 3.5978 | 8.1022 | 12.3509 | 18.6569 | 23.2418 | 27.8614 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541
97% | [11 empty] | 1.0469 | 2.2918 | 4.6355 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | [9 empty] | 3.8336 | 10.5217 | 16.8301 | 26.193 | 33.0005 | 39.8595 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241
95% | [11 empty] | 0.29903 | 1.4947 | 3.8023 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | [9 empty] | 2.9799 | 16.1484 | 28.5712 | 47.009 | 60.4145 | 73.9215 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272
90% | [12 empty] | 1.5715 | 16.7245 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | [10 empty] | 7.6317 | 25.0454 | 51.6937 | 71.0689 | 90.5907 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669
85% | FY38: 0.35741; FY39: 7.0813; FY40: 7.0813; FY41: 7.0813; FY42: 7.0813; FY43: 7.0813; FY44: 7.0813; FY45: 7.0813; FY46: 7.0813; FY47: 7.0813; FY48: 7.0813; FY49: 7.0813; FY50: 7.0813; FY51: 7.0813; FY52: 7.0813; FY53: 7.0813; FY54: 7.0813 | [11 empty] | 5.6364 | 46.8602 | 81.4796 | 116.3608 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048
80% | [42 empty] | 3.7371 | 23.65 | 50.7343 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202
75% | [43 empty] | 0.048712 | 10.0691 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245
70% | [45 empty] | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9116 | 8.1811 | 30.7107 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7312 | 46.999 | 95.175 | 204.0758 | 305.1456 | 423.9721 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0381 | 5.7268 | 21.4975 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8194 | 14.0997 | 28.5525 | 61.2227 | 91.5437 | 127.1916 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [12 empty] | 2.6513 | 4.967 | 7.3002 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715 | 9.7715
98% | FY39: 0.0026326; FY40: 0.0026326; FY41: 0.0026326; FY42: 0.0026326; FY43: 0.0026326; FY44: 0.0026326; FY45: 0.0026326; FY46: 0.0026326; FY47: 0.0026326; FY48: 0.0026326; FY49: 0.0026326; FY50: 0.0026326; FY51: 0.0026326; FY52: 0.0026326; FY53: 0.0026326; FY54: 0.0026326 | [12 empty] | 4.2539 | 8.8388 | 13.4584 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511 | 18.3511
97% | [42 empty] | 4.8078 | 11.6153 | 18.4743 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739 | 25.739
95% | [42 empty] | 4.8966 | 18.3021 | 31.8091 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148 | 46.1148
90% | [42 empty] | 0.14611 | 10.2944 | 29.7251 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014 | 50.4014
85% | [44 empty] | 10.4672 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511 | 44.5511
80% | [45 empty] | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047 | 3.0047
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | 0.0026326 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.7557 | 54.0177 | 111.2344 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335 | 197.9335
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | 0.0018428 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0267 | 16.2053 | 33.3703 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38 | 59.38
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [45 empty] | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374
98% | [45 empty] | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532
97% | [45 empty] | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2.3199 | 4.595 | 6.7409 | 9.9259 | 12.2416 | 14.5749 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461
98% | [11 empty] | 1.5656 | 2.8232 | 5.191 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | [9 empty] | 3.5978 | 8.1022 | 12.3509 | 18.6569 | 23.2418 | 27.8614 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541
97% | [11 empty] | 1.0469 | 2.2918 | 4.6355 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | [9 empty] | 3.8336 | 10.5217 | 16.8301 | 26.193 | 33.0005 | 39.8595 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241
95% | [11 empty] | 0.29903 | 1.4947 | 3.8023 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | [9 empty] | 2.9799 | 16.1484 | 28.5712 | 47.009 | 60.4145 | 73.9215 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272
90% | [12 empty] | 1.5715 | 16.7245 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | [10 empty] | 7.6317 | 25.0454 | 51.6937 | 71.0689 | 90.5907 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669
85% | FY38: 0.35741; FY39: 7.0813; FY40: 7.0813; FY41: 7.0813; FY42: 7.0813; FY43: 7.0813; FY44: 7.0813; FY45: 7.0813; FY46: 7.0813; FY47: 7.0813; FY48: 7.0813; FY49: 7.0813; FY50: 7.0813; FY51: 7.0813; FY52: 7.0813; FY53: 7.0813; FY54: 7.0813 | [11 empty] | 5.6364 | 46.8602 | 81.4796 | 116.3608 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048
80% | [42 empty] | 3.7371 | 23.65 | 50.7343 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202
75% | [43 empty] | 0.048712 | 10.0691 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245
70% | [45 empty] | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9116 | 8.1811 | 30.7107 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7312 | 46.999 | 95.175 | 204.0758 | 305.1456 | 423.9721 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0381 | 5.7268 | 21.4975 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8194 | 14.0997 | 28.5525 | 61.2227 | 91.5437 | 127.1916 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY38: 0; FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [10 empty] | 0.60997 | 2.6211 | 5.6028 | 7.7725 | 9.9584 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729 | 12.2729
98% | FY38: 0.62086; FY39: 2.2773; FY40: 2.2773; FY41: 2.2773; FY42: 2.2773; FY43: 2.2773; FY44: 2.2773; FY45: 2.2773; FY46: 2.2773; FY47: 2.2773; FY48: 2.2773; FY49: 2.2773; FY50: 2.2773; FY51: 2.2773; FY52: 2.2773; FY53: 2.2773; FY54: 2.2773 | [10 empty] | 0.25447 | 4.1941 | 10.0976 | 14.3934 | 18.7212 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037 | 23.3037
97% | FY38: 0.13181; FY39: 1.7514; FY40: 1.7514; FY41: 1.7514; FY42: 1.7514; FY43: 1.7514; FY44: 1.7514; FY45: 1.7514; FY46: 1.7514; FY47: 1.7514; FY48: 1.7514; FY49: 1.7514; FY50: 1.7514; FY51: 1.7514; FY52: 1.7514; FY53: 1.7514; FY54: 1.7514 | [11 empty] | 4.719 | 13.4844 | 19.8627 | 26.2884 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924 | 33.0924
95% | FY39: 0.96261; FY40: 0.96261; FY41: 0.96261; FY42: 0.96261; FY43: 0.96261; FY44: 0.96261; FY45: 0.96261; FY46: 0.96261; FY47: 0.96261; FY48: 0.96261; FY49: 0.96261; FY50: 0.96261; FY51: 0.96261; FY52: 0.96261; FY53: 0.96261; FY54: 0.96261 | [11 empty] | 4.7216 | 21.9827 | 34.5431 | 47.1968 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955 | 60.5955
90% | FY39: 0.32645; FY40: 0.32645; FY41: 0.32645; FY42: 0.32645; FY43: 0.32645; FY44: 0.32645; FY45: 0.32645; FY46: 0.32645; FY47: 0.32645; FY48: 0.32645; FY49: 0.32645; FY50: 0.32645; FY51: 0.32645; FY52: 0.32645; FY53: 0.32645; FY54: 0.32645 | [11 empty] | 0.1187 | 15.5229 | 33.6766 | 51.9652 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304 | 71.3304
85% | [42 empty] | 0.35422 | 15.6495 | 47.3453 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468 | 81.9468
80% | [44 empty] | 3.9008 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128 | 24.0128
75% | [45 empty] | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115 | 0.068115
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75267 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | 5.3177 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.86444 | 16.3744 | 67.0445 | 125.8977 | 205.376 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226 | 306.6226
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52687 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | 3.7224 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25933 | 4.9123 | 20.1134 | 37.7693 | 61.6128 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868 | 91.9868
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [45 empty] | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374
98% | [45 empty] | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532
97% | [45 empty] | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2.3199 | 4.595 | 6.7409 | 9.9259 | 12.2416 | 14.5749 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461
98% | [11 empty] | 1.5656 | 2.8232 | 5.191 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | [9 empty] | 3.5978 | 8.1022 | 12.3509 | 18.6569 | 23.2418 | 27.8614 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541
97% | [11 empty] | 1.0469 | 2.2918 | 4.6355 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | [9 empty] | 3.8336 | 10.5217 | 16.8301 | 26.193 | 33.0005 | 39.8595 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241
95% | [11 empty] | 0.29903 | 1.4947 | 3.8023 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | [9 empty] | 2.9799 | 16.1484 | 28.5712 | 47.009 | 60.4145 | 73.9215 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272
90% | [12 empty] | 1.5715 | 16.7245 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | [10 empty] | 7.6317 | 25.0454 | 51.6937 | 71.0689 | 90.5907 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669
85% | FY38: 0.35741; FY39: 7.0813; FY40: 7.0813; FY41: 7.0813; FY42: 7.0813; FY43: 7.0813; FY44: 7.0813; FY45: 7.0813; FY46: 7.0813; FY47: 7.0813; FY48: 7.0813; FY49: 7.0813; FY50: 7.0813; FY51: 7.0813; FY52: 7.0813; FY53: 7.0813; FY54: 7.0813 | [11 empty] | 5.6364 | 46.8602 | 81.4796 | 116.3608 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048
80% | [42 empty] | 3.7371 | 23.65 | 50.7343 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202
75% | [43 empty] | 0.048712 | 10.0691 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245
70% | [45 empty] | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9116 | 8.1811 | 30.7107 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7312 | 46.999 | 95.175 | 204.0758 | 305.1456 | 423.9721 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0381 | 5.7268 | 21.4975 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8194 | 14.0997 | 28.5525 | 61.2227 | 91.5437 | 127.1916 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [45 empty] | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374 | 1.9374
98% | [45 empty] | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532 | 0.532
97% | [45 empty] | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526 | 0.22526
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947 | 2.6947
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841 | 0.80841
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2.3199 | 4.595 | 6.7409 | 9.9259 | 12.2416 | 14.5749 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461 | 17.0461
98% | [11 empty] | 1.5656 | 2.8232 | 5.191 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | 7.0025 | [9 empty] | 3.5978 | 8.1022 | 12.3509 | 18.6569 | 23.2418 | 27.8614 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541 | 32.7541
97% | [11 empty] | 1.0469 | 2.2918 | 4.6355 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | 6.4287 | [9 empty] | 3.8336 | 10.5217 | 16.8301 | 26.193 | 33.0005 | 39.8595 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241 | 47.1241
95% | [11 empty] | 0.29903 | 1.4947 | 3.8023 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | 5.5679 | [9 empty] | 2.9799 | 16.1484 | 28.5712 | 47.009 | 60.4145 | 73.9215 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272 | 88.2272
90% | [12 empty] | 1.5715 | 16.7245 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | 32.0351 | [10 empty] | 7.6317 | 25.0454 | 51.6937 | 71.0689 | 90.5907 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669 | 111.2669
85% | FY38: 0.35741; FY39: 7.0813; FY40: 7.0813; FY41: 7.0813; FY42: 7.0813; FY43: 7.0813; FY44: 7.0813; FY45: 7.0813; FY46: 7.0813; FY47: 7.0813; FY48: 7.0813; FY49: 7.0813; FY50: 7.0813; FY51: 7.0813; FY52: 7.0813; FY53: 7.0813; FY54: 7.0813 | [11 empty] | 5.6364 | 46.8602 | 81.4796 | 116.3608 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048 | 153.3048
80% | [42 empty] | 3.7371 | 23.65 | 50.7343 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202 | 79.4202
75% | [43 empty] | 0.048712 | 10.0691 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245 | 37.245
70% | [45 empty] | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404 | 1.5404
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9116 | 8.1811 | 30.7107 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | 58.1155 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7312 | 46.999 | 95.175 | 204.0758 | 305.1456 | 423.9721 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288 | 567.9288
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0381 | 5.7268 | 21.4975 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | 40.6809 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8194 | 14.0997 | 28.5525 | 61.2227 | 91.5437 | 127.1916 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786 | 170.3786

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 2.0948 | 5.968 | 9.4101 | 13.1618 | 14.5941 | 19.4437 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | [8 empty] | 1.8693 | 5.7463 | 9.403 | 13.2035 | 17.7587 | 19.2837 | 24.1959 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745
98% | [8 empty] | 0.74475 | 2.6619 | 4.3656 | 6.2227 | 6.9316 | 9.332 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | [8 empty] | 0.63313 | 2.5522 | 4.3621 | 6.2433 | 8.498 | 9.2528 | 11.6843 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505
97% | [8 empty] | 0.8842 | 4.6795 | 8.0525 | 11.7288 | 13.1323 | 17.8843 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | [8 empty] | 0.66324 | 4.4623 | 8.0455 | 11.7696 | 16.2332 | 17.7276 | 22.5411 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276
95% | [8 empty] | 0.20953 | 5.5698 | 10.5514 | 15.981 | 18.0539 | 25.0723 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | [8 empty] | 0.081366 | 5.249 | 10.5411 | 16.0413 | 22.6337 | 24.8408 | 31.9499 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762
90% | [9 empty] | 2.193 | 6.9876 | 12.2193 | 14.2166 | 20.9791 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | [9 empty] | 1.9076 | 6.9777 | 12.2774 | 18.6294 | 20.756 | 27.606 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907
85% | [10 empty] | 23.2543 | 82.1442 | 104.8162 | 181.5802 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | [10 empty] | 23.1561 | 82.804 | 154.9081 | 179.0481 | 256.8046 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279
80% | [11 empty] | 49.3399 | 99.7529 | 284.7177 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | [11 empty] | 50.5859 | 220.4506 | 278.6164 | 465.9727 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014
75% | [12 empty] | 2.2783 | 327.6472 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | [12 empty] | 156.1147 | 309.8297 | 856.9643 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309
70% | FY38: 4.9911; FY39: 680.9849; FY40: 680.9849; FY41: 680.9849; FY42: 680.9849; FY43: 680.9849; FY44: 680.9849; FY45: 680.9849; FY46: 680.9849; FY47: 680.9849; FY48: 680.9849; FY49: 680.9849; FY50: 680.9849; FY51: 680.9849; FY52: 680.9849; FY53: 680.9849; FY54: 680.9849 | [13 empty] | 2.0971 | 618.8325 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723
65% | [45 empty] | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9333 | 21.0721 | 62.6215 | 190.7976 | 273.7758 | 891.6476 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.247 | 19.9174 | 62.4857 | 192.925 | 615.2263 | 861.4523 | 2316.5514 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7533 | 14.7505 | 43.8351 | 133.5583 | 191.6431 | 624.1533 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97411 | 5.9752 | 18.7457 | 57.8775 | 184.5679 | 258.4357 | 694.9654 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.7562 | 3.8988 | 5.7218 | 7.2476 | 8.5992 | 10.7288 | 12.6537 | 15.3241 | 18.1083 | 20.3833 | 22.5293 | 25.7143 | 28.03 | 30.3632 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344
98% |  |  |  | 0.66157 | 2.1576 | 3.7001 | 5.3382 | 7.2124 | 9.4182 | 11.4855 | 13.6579 | 17.3539 | 18.6116 | 20.9793 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 |  | 10.7187 | 7.0413 | 10.6506 | 13.6715 | 16.3476 | 20.5639 | 24.3751 | 29.6622 | 35.1745 | 39.6789 | 43.9277 | 50.2336 | 54.8185 | 59.4381 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308
97% |  |  |  | 0.31239 | 1.7932 | 3.3201 | 4.9415 | 6.7967 | 8.9802 | 11.0264 | 13.1767 | 16.8353 | 18.0801 | 20.4239 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 |  | 14.8875 | 9.4273 | 14.7863 | 19.2716 | 23.245 | 29.5053 | 35.164 | 43.0141 | 51.1987 | 57.8867 | 64.1952 | 73.5581 | 80.3656 | 87.2246 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892
95% |  |  |  | 0.013596 | 1.2466 | 2.75 | 4.3466 | 6.1732 | 8.323 | 10.3378 | 12.4551 | 16.0573 | 17.283 | 19.5907 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 |  | 26.2032 | 15.4508 | 26.0038 | 34.8366 | 42.6611 | 54.989 | 66.1323 | 81.591 | 97.7083 | 110.8786 | 123.3014 | 141.7391 | 155.1447 | 168.6516 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573
90% |  |  |  |  | 1.9227 | 12.7794 | 26.6244 | 42.4645 | 61.1079 | 78.5798 | 96.9404 | 128.1789 | 138.8079 | 158.8197 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 |  | 26.8034 | 11.2629 | 26.5152 | 39.2813 | 50.5902 | 68.4079 | 84.5135 | 106.8561 | 130.1507 | 149.1858 | 167.1406 | 193.7889 | 213.1641 | 232.6859 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621
85% | [5 empty] | 0.52287 | 8.7756 | 23.7588 | 41.3945 | 57.9219 | 75.2901 | 104.84 | 114.8945 | 133.8246 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 |  | 16.8948 | 0.42068 | 16.3832 | 39.1901 | 59.3967 | 91.2331 | 120.0103 | 159.9319 | 201.5543 | 235.566 | 267.6474 | 315.2623 | 349.8817 | 384.7629 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069
80% | [7 empty] | 6.1637 | 24.0901 | 41.4045 | 59.5998 | 90.5568 | 101.0901 | 120.9216 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 |  | 9.4684e-06 |  |  | 5.5316 | 19.134 | 43.854 | 66.1987 | 97.1966 | 129.5152 | 155.9243 | 180.8345 | 217.8061 | 244.687 | 271.7713 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572
75% | [8 empty] | 6.3044 | 29.5222 | 56.8702 | 103.3996 | 119.2314 | 149.0388 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | [5 empty] | 0.34552 | 14.5429 | 38.3604 | 71.6396 | 106.3365 | 134.6892 | 161.4326 | 201.1251 | 229.9842 | 259.0617 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587
70% | [9 empty] | 4.8747 | 52.8726 | 177.9862 | 220.566 | 300.7336 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | [7 empty] | 7.8145 | 48.2959 | 96.9835 | 136.7688 | 174.2959 | 229.9933 | 270.4892 | 311.2915 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066
65% | [11 empty] | 81.6729 | 136.8236 | 240.6687 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | [8 empty] | 3.6997 | 43.0779 | 89.3797 | 133.0535 | 197.8737 | 245.0026 | 292.488 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815
60% | [12 empty] | 31.8023 | 261.3027 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | [9 empty] | 0.27668 | 39.0679 | 130.2401 | 292.2908 | 410.113 | 528.8265 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602
55% | FY39: 46.4501; FY40: 46.4501; FY41: 46.4501; FY42: 46.4501; FY43: 46.4501; FY44: 46.4501; FY45: 46.4501; FY46: 46.4501; FY47: 46.4501; FY48: 46.4501; FY49: 46.4501; FY50: 46.4501; FY51: 46.4501; FY52: 46.4501; FY53: 46.4501; FY54: 46.4501 | [11 empty] | 0.52076 | 58.3942 | 152.8404 | 258.0119 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026
50% | [43 empty] | 5.1141 | 85.428 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0.98755 | 7.1201 | 23.0724 | 50.0263 | 92.5692 | 159.6184 | 245.1528 | 380.8629 | 736.8809 | 917.1904 | 1426.3035 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | E @ R (MWh) | 101.2639 | 47.5018 | 100.0608 | 159.0303 | 220.3192 | 333.8249 | 455.2225 | 657.2114 | 910.0845 | 1169.4092 | 1469.1189 | 1997.7796 | 2439.6351 | 2970.0052 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691
Option 1 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0.69129 | 4.9841 | 16.1507 | 35.0184 | 64.7985 | 111.7329 | 171.607 | 266.604 | 515.8167 | 642.0333 | 998.4125 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 30.3792 | 14.2505 | 30.0182 | 47.7091 | 66.0958 | 100.1475 | 136.5668 | 197.1634 | 273.0253 | 350.8228 | 440.7357 | 599.3339 | 731.8905 | 891.0016 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [10 empty] | 0.83445 | 4.5862 | 6.0185 | 10.868 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | 15.8842 | [10 empty] | 0.82736 | 4.6278 | 9.183 | 10.708 | 15.6203 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988 | 20.1988
98% | [10 empty] | 0.12216 | 1.9779 | 2.6869 | 5.0873 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | 7.5702 | [10 empty] | 0.11899 | 1.9985 | 4.2532 | 5.0081 | 7.4395 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058 | 9.7058
97% | [11 empty] | 3.3255 | 4.729 | 9.4811 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | 14.3964 | [11 empty] | 3.3663 | 7.8299 | 9.3243 | 14.1378 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243 | 18.6243
95% | [11 empty] | 3.57 | 5.6429 | 12.6613 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | 19.9209 | [11 empty] | 3.6303 | 10.2227 | 12.4298 | 19.5389 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652 | 26.1652
90% | [11 empty] | 0.72849 | 2.2607 | 9.0206 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | 16.0155 | [11 empty] | 0.7615 | 6.6709 | 8.7975 | 15.6475 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321 | 22.0321
85% | FY38: 45.8348; FY39: 125.237; FY40: 125.237; FY41: 125.237; FY42: 125.237; FY43: 125.237; FY44: 125.237; FY45: 125.237; FY46: 125.237; FY47: 125.237; FY48: 125.237; FY49: 125.237; FY50: 125.237; FY51: 125.237; FY52: 125.237; FY53: 125.237; FY54: 125.237 | [12 empty] | 20.2078 | 43.3027 | 121.0592 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336 | 193.5336
80% | FY38: 4.3813; FY39: 148.9573; FY40: 148.9573; FY41: 148.9573; FY42: 148.9573; FY43: 148.9573; FY44: 148.9573; FY45: 148.9573; FY46: 148.9573; FY47: 148.9573; FY48: 148.9573; FY49: 148.9573; FY50: 148.9573; FY51: 148.9573; FY52: 148.9573; FY53: 148.9573; FY54: 148.9573 | [13 empty] | 3.0388 | 138.8908 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196 | 313.5196
75% | FY39: 36.5296; FY40: 36.5296; FY41: 36.5296; FY42: 36.5296; FY43: 36.5296; FY44: 36.5296; FY45: 36.5296; FY46: 36.5296; FY47: 36.5296; FY48: 36.5296; FY49: 36.5296; FY50: 36.5296; FY51: 36.5296; FY52: 36.5296; FY53: 36.5296; FY54: 36.5296 | [14 empty] | 26.2421 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571 | 411.7571
70% | [45 empty] | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762 | 35.0762
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95661 | 14.188 | 21.3378 | 97.3342 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | 384.5112 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94635 | 14.3845 | 58.3675 | 92.6091 | 358.5761 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127 | 1050.6127
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66963 | 9.9316 | 14.9365 | 68.134 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | 269.1578 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2839 | 4.3154 | 17.5102 | 27.7827 | 107.5728 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838 | 315.1838
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.7562 | 3.8988 | 5.7218 | 1.7916 | 3.1433 | 5.2728 | 7.1978 | 9.8681 | 12.6523 | 14.9274 | 17.0733 | 20.2583 | 22.574 | 24.9073 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785 | 27.3785
98% | [6 empty] | 0.017053 | 1.8112 | 4.0171 | 6.0843 | 8.2567 | 11.9528 | 13.2104 | 15.5782 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 | 17.3897 |  | 10.7187 | 7.0413 | 10.6506 | 2.8692 | 5.5453 | 9.7616 | 13.5728 | 18.8599 | 24.3722 | 28.8766 | 33.1254 | 39.4314 | 44.0163 | 48.6358 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286 | 53.5286
97% | [7 empty] | 1.4504 | 3.6339 | 5.6801 | 7.8305 | 11.489 | 12.7338 | 15.0776 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 | 16.8707 |  | 14.8875 | 9.4273 | 14.7863 | 3.2327 | 7.2061 | 13.4664 | 19.1251 | 26.9753 | 35.1598 | 41.8478 | 48.1563 | 57.5192 | 64.3267 | 71.1857 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503 | 78.4503
95% | [7 empty] | 0.90911 | 3.059 | 5.0738 | 7.191 | 10.7933 | 12.019 | 14.3267 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 | 16.0922 |  | 26.2032 | 15.4508 | 26.0038 | 3.2523 | 11.0768 | 23.4047 | 34.548 | 50.0068 | 66.124 | 79.2943 | 91.7171 | 110.1548 | 123.5604 | 137.0674 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731 | 151.3731
90% | [7 empty] | 0.74973 | 15.4588 | 32.9306 | 51.2913 | 82.5297 | 93.1587 | 113.1706 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 | 128.4812 |  | 26.8034 | 11.2629 | 26.5152 | 0.086296 | 5.2871 | 22.7587 | 38.8643 | 61.207 | 84.5015 | 103.5367 | 121.4914 | 148.1398 | 167.515 | 187.0368 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713 | 207.713
85% | [8 empty] | 1.3548 | 14.7403 | 32.1085 | 61.6584 | 71.7128 | 90.6429 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 | 105.126 |  | 16.8948 | 0.42068 | 16.3832 |  |  | 10.4015 | 38.445 | 78.3666 | 119.989 | 154.0007 | 186.0821 | 233.697 | 268.3163 | 303.1976 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416 | 340.1416
80% | [9 empty] | 0.97327 | 14.3619 | 45.3189 | 55.8522 | 75.6837 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 | 90.8564 |  | 9.4684e-06 | [5 empty] | 5.1748 | 33.8636 | 66.1821 | 92.5912 | 117.5015 | 154.473 | 181.354 | 208.4382 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241 | 237.1241
75% | [10 empty] | 0.51516 | 35.4056 | 51.2374 | 81.0448 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | 103.8499 | [8 empty] | 6.3943 | 38.3426 | 66.6952 | 93.4387 | 133.1311 | 161.9903 | 191.0678 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648 | 221.8648
70% | [11 empty] | 11.004 | 39.0308 | 117.8628 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | 179.1973 | [9 empty] | 7.8011 | 41.3579 | 78.885 | 134.5824 | 175.0784 | 215.8806 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958 | 259.0958
65% | FY38: 21.9626; FY39: 83.2365; FY40: 83.2365; FY41: 83.2365; FY42: 83.2365; FY43: 83.2365; FY44: 83.2365; FY45: 83.2365; FY46: 83.2365; FY47: 83.2365; FY48: 83.2365; FY49: 83.2365; FY50: 83.2365; FY51: 83.2365; FY52: 83.2365; FY53: 83.2365; FY54: 83.2365 | [10 empty] | 1.5376 | 23.7453 | 86.8353 | 133.9641 | 181.4495 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743 | 231.743
60% | FY39: 0.00046484; FY40: 0.00046484; FY41: 0.00046484; FY42: 0.00046484; FY43: 0.00046484; FY44: 0.00046484; FY45: 0.00046484; FY46: 0.00046484; FY47: 0.00046484; FY48: 0.00046484; FY49: 0.00046484; FY50: 0.00046484; FY51: 0.00046484; FY52: 0.00046484; FY53: 0.00046484; FY54: 0.00046484 | [12 empty] | 35.3087 | 132.5168 | 251.2303 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964 | 376.964
55% | [43 empty] | 0.6749 | 35.0891 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729 | 123.4729
50% | [45 empty] | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287 | 0.070287
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.017053 | 4.9205 | 27.5235 | 65.4824 | 121.555 | 270.1518 | 348.9552 | 545.3498 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | 741.1004 | E @ R (MWh) | 101.2639 | 47.5018 | 100.0608 | 11.2322 | 32.2586 | 85.0658 | 156.9278 | 285.5416 | 455.1246 | 624.6655 | 811.2162 | 1153.5311 | 1475.8871 | 1855.186 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92 | 2308.92
Option 2 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011937 | 3.4443 | 19.2665 | 45.8377 | 85.0885 | 189.1063 | 244.2686 | 381.7449 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | 518.7703 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 30.3792 | 14.2505 | 30.0182 | 3.3696 | 9.6776 | 25.5197 | 47.0784 | 85.6625 | 136.5374 | 187.3996 | 243.3648 | 346.0593 | 442.7661 | 556.5558 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676 | 692.676
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 2.0948 | 5.968 | 9.4101 | 13.1618 | 14.5941 | 19.4437 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | [8 empty] | 1.8693 | 5.7463 | 9.403 | 13.2035 | 17.7587 | 19.2837 | 24.1959 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745
98% | [8 empty] | 0.74475 | 2.6619 | 4.3656 | 6.2227 | 6.9316 | 9.332 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | [8 empty] | 0.63313 | 2.5522 | 4.3621 | 6.2433 | 8.498 | 9.2528 | 11.6843 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505
97% | [8 empty] | 0.8842 | 4.6795 | 8.0525 | 11.7288 | 13.1323 | 17.8843 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | [8 empty] | 0.66324 | 4.4623 | 8.0455 | 11.7696 | 16.2332 | 17.7276 | 22.5411 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276
95% | [8 empty] | 0.20953 | 5.5698 | 10.5514 | 15.981 | 18.0539 | 25.0723 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | [8 empty] | 0.081366 | 5.249 | 10.5411 | 16.0413 | 22.6337 | 24.8408 | 31.9499 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762
90% | [9 empty] | 2.193 | 6.9876 | 12.2193 | 14.2166 | 20.9791 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | [9 empty] | 1.9076 | 6.9777 | 12.2774 | 18.6294 | 20.756 | 27.606 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907
85% | [10 empty] | 23.2543 | 82.1442 | 104.8162 | 181.5802 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | [10 empty] | 23.1561 | 82.804 | 154.9081 | 179.0481 | 256.8046 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279
80% | [11 empty] | 49.3399 | 99.7529 | 284.7177 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | [11 empty] | 50.5859 | 220.4506 | 278.6164 | 465.9727 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014
75% | [12 empty] | 2.2783 | 327.6472 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | [12 empty] | 156.1147 | 309.8297 | 856.9643 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309
70% | FY38: 4.9911; FY39: 680.9849; FY40: 680.9849; FY41: 680.9849; FY42: 680.9849; FY43: 680.9849; FY44: 680.9849; FY45: 680.9849; FY46: 680.9849; FY47: 680.9849; FY48: 680.9849; FY49: 680.9849; FY50: 680.9849; FY51: 680.9849; FY52: 680.9849; FY53: 680.9849; FY54: 680.9849 | [13 empty] | 2.0971 | 618.8325 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723
65% | [45 empty] | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9333 | 21.0721 | 62.6215 | 190.7976 | 273.7758 | 891.6476 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.247 | 19.9174 | 62.4857 | 192.925 | 615.2263 | 861.4523 | 2316.5514 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7533 | 14.7505 | 43.8351 | 133.5583 | 191.6431 | 624.1533 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97411 | 5.9752 | 18.7457 | 57.8775 | 184.5679 | 258.4357 | 694.9654 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.7562 | 3.8988 | 5.7218 | 7.2476 | 8.5992 | 10.7288 | 12.6537 | 15.3241 | 18.1083 | 20.3833 | 22.5293 | 25.7143 | 28.03 | 30.3632 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344
98% |  |  |  | 0.66157 | 2.1576 | 3.7001 | 5.3382 | 7.2124 | 9.4182 | 11.4855 | 13.6579 | 17.3539 | 18.6116 | 20.9793 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 |  | 10.7187 | 7.0413 | 10.6506 | 13.6715 | 16.3476 | 20.5639 | 24.3751 | 29.6622 | 35.1745 | 39.6789 | 43.9277 | 50.2336 | 54.8185 | 59.4381 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308
97% |  |  |  | 0.31239 | 1.7932 | 3.3201 | 4.9415 | 6.7967 | 8.9802 | 11.0264 | 13.1767 | 16.8353 | 18.0801 | 20.4239 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 |  | 14.8875 | 9.4273 | 14.7863 | 19.2716 | 23.245 | 29.5053 | 35.164 | 43.0141 | 51.1987 | 57.8867 | 64.1952 | 73.5581 | 80.3656 | 87.2246 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892
95% |  |  |  | 0.013596 | 1.2466 | 2.75 | 4.3466 | 6.1732 | 8.323 | 10.3378 | 12.4551 | 16.0573 | 17.283 | 19.5907 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 |  | 26.2032 | 15.4508 | 26.0038 | 34.8366 | 42.6611 | 54.989 | 66.1323 | 81.591 | 97.7083 | 110.8786 | 123.3014 | 141.7391 | 155.1447 | 168.6516 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573
90% |  |  |  |  | 1.9227 | 12.7794 | 26.6244 | 42.4645 | 61.1079 | 78.5798 | 96.9404 | 128.1789 | 138.8079 | 158.8197 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 |  | 26.8034 | 11.2629 | 26.5152 | 39.2813 | 50.5902 | 68.4079 | 84.5135 | 106.8561 | 130.1507 | 149.1858 | 167.1406 | 193.7889 | 213.1641 | 232.6859 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621
85% | [5 empty] | 0.52287 | 8.7756 | 23.7588 | 41.3945 | 57.9219 | 75.2901 | 104.84 | 114.8945 | 133.8246 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 |  | 16.8948 | 0.42068 | 16.3832 | 39.1901 | 59.3967 | 91.2331 | 120.0103 | 159.9319 | 201.5543 | 235.566 | 267.6474 | 315.2623 | 349.8817 | 384.7629 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069
80% | [7 empty] | 6.1637 | 24.0901 | 41.4045 | 59.5998 | 90.5568 | 101.0901 | 120.9216 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 |  | 9.4684e-06 |  |  | 5.5316 | 19.134 | 43.854 | 66.1987 | 97.1966 | 129.5152 | 155.9243 | 180.8345 | 217.8061 | 244.687 | 271.7713 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572
75% | [8 empty] | 6.3044 | 29.5222 | 56.8702 | 103.3996 | 119.2314 | 149.0388 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | [5 empty] | 0.34552 | 14.5429 | 38.3604 | 71.6396 | 106.3365 | 134.6892 | 161.4326 | 201.1251 | 229.9842 | 259.0617 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587
70% | [9 empty] | 4.8747 | 52.8726 | 177.9862 | 220.566 | 300.7336 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | [7 empty] | 7.8145 | 48.2959 | 96.9835 | 136.7688 | 174.2959 | 229.9933 | 270.4892 | 311.2915 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066
65% | [11 empty] | 81.6729 | 136.8236 | 240.6687 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | [8 empty] | 3.6997 | 43.0779 | 89.3797 | 133.0535 | 197.8737 | 245.0026 | 292.488 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815
60% | [12 empty] | 31.8023 | 261.3027 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | [9 empty] | 0.27668 | 39.0679 | 130.2401 | 292.2908 | 410.113 | 528.8265 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602
55% | FY39: 46.4501; FY40: 46.4501; FY41: 46.4501; FY42: 46.4501; FY43: 46.4501; FY44: 46.4501; FY45: 46.4501; FY46: 46.4501; FY47: 46.4501; FY48: 46.4501; FY49: 46.4501; FY50: 46.4501; FY51: 46.4501; FY52: 46.4501; FY53: 46.4501; FY54: 46.4501 | [11 empty] | 0.52076 | 58.3942 | 152.8404 | 258.0119 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026
50% | [43 empty] | 5.1141 | 85.428 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0.98755 | 7.1201 | 23.0724 | 50.0263 | 92.5692 | 159.6184 | 245.1528 | 380.8629 | 736.8809 | 917.1904 | 1426.3035 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | E @ R (MWh) | 101.2639 | 47.5018 | 100.0608 | 159.0303 | 220.3192 | 333.8249 | 455.2225 | 657.2114 | 910.0845 | 1169.4092 | 1469.1189 | 1997.7796 | 2439.6351 | 2970.0052 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691
Option 3 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0.69129 | 4.9841 | 16.1507 | 35.0184 | 64.7985 | 111.7329 | 171.607 | 266.604 | 515.8167 | 642.0333 | 998.4125 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 30.3792 | 14.2505 | 30.0182 | 47.7091 | 66.0958 | 100.1475 | 136.5668 | 197.1634 | 273.0253 | 350.8228 | 440.7357 | 599.3339 | 731.8905 | 891.0016 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [11 empty] | 1.7276 | 3.1599 | 8.0094 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | 13.0256 | [11 empty] | 1.7693 | 6.3244 | 7.8495 | 12.7617 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402 | 17.3402
98% | [11 empty] | 0.563 | 1.2719 | 3.6723 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | 6.1552 | [11 empty] | 0.58363 | 2.8383 | 3.5932 | 6.0246 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909 | 8.2909
97% | [11 empty] | 0.52439 | 1.9279 | 6.68 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | 11.5953 | [11 empty] | 0.56524 | 5.0288 | 6.5232 | 11.3367 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232 | 15.8232
95% | [11 empty] | 0.031163 | 1.5058 | 8.5243 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | 15.7839 | [11 empty] | 0.043488 | 6.0857 | 8.2928 | 15.4019 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282 | 22.0282
90% | [12 empty] | 0.036639 | 5.0344 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | 12.0294 | [12 empty] | 2.6847 | 4.8113 | 11.6613 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046 | 18.046
85% | FY38: 7.7743; FY39: 79.9885; FY40: 79.9885; FY41: 79.9885; FY42: 79.9885; FY43: 79.9885; FY44: 79.9885; FY45: 79.9885; FY46: 79.9885; FY47: 79.9885; FY48: 79.9885; FY49: 79.9885; FY50: 79.9885; FY51: 79.9885; FY52: 79.9885; FY53: 79.9885; FY54: 79.9885 | [12 empty] | 0.080584 | 6.519 | 75.8107 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851 | 148.2851
80% | FY39: 45.3723; FY40: 45.3723; FY41: 45.3723; FY42: 45.3723; FY43: 45.3723; FY44: 45.3723; FY45: 45.3723; FY46: 45.3723; FY47: 45.3723; FY48: 45.3723; FY49: 45.3723; FY50: 45.3723; FY51: 45.3723; FY52: 45.3723; FY53: 45.3723; FY54: 45.3723 | [14 empty] | 38.1372 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923 | 204.4923
75% | [45 empty] | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119 | 122.5119
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8462 | 7.9022 | 39.6947 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | 183.9503 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9616 | 23.0426 | 37.589 | 171.1342 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177 | 556.8177
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9923 | 5.5316 | 27.7863 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | 128.7652 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88849 | 6.9128 | 11.2767 | 51.3403 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453 | 167.0453
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.7562 | 3.8988 | 5.7218 | 0.029909 | 1.3246 | 3.4542 | 5.3791 | 8.0495 | 10.8336 | 13.1087 | 15.2547 | 18.4397 | 20.7554 | 23.0886 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598 | 25.5598
98% | [7 empty] | 0.048421 | 2.2167 | 4.284 | 6.4564 | 10.1524 | 11.41 | 13.7778 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 | 15.5893 |  | 10.7187 | 7.0413 | 10.6506 |  | 1.9446 | 6.1609 | 9.972 | 15.2591 | 20.7715 | 25.2759 | 29.5246 | 35.8306 | 40.4155 | 45.0351 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278 | 49.9278
97% | [8 empty] | 1.8518 | 3.898 | 6.0484 | 9.7069 | 10.9517 | 13.2955 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 | 15.0886 |  | 14.8875 | 9.4273 | 14.7863 |  | 1.8598 | 8.1201 | 13.7788 | 21.629 | 29.8135 | 36.5015 | 42.81 | 52.1729 | 58.9804 | 65.8394 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104 | 73.104
95% | [8 empty] | 1.3043 | 3.3191 | 5.4363 | 9.0386 | 10.2643 | 12.572 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 | 14.3375 |  | 26.2032 | 15.4508 | 26.0038 |  | 0.83845 | 12.8766 | 24.0199 | 39.4787 | 55.5959 | 68.7662 | 81.189 | 99.6268 | 113.0323 | 126.5393 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845 | 140.845
90% | [8 empty] | 2.1759 | 17.7142 | 36.0749 | 67.3133 | 77.9423 | 97.9542 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 | 113.2648 |  | 26.8034 | 11.2629 | 26.5152 |  |  | 7.5647 | 23.6479 | 45.9906 | 69.2851 | 88.3203 | 106.2751 | 132.9234 | 152.2986 | 171.8204 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966 | 192.4966
85% | [9 empty] | 2.3476 | 17.7146 | 47.2645 | 57.319 | 76.2491 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 | 90.7321 |  | 16.8948 | 0.42068 | 16.3832 |  |  |  | 11.701 | 51.1782 | 92.8005 | 126.8123 | 158.8937 | 206.5086 | 241.1279 | 276.0092 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532 | 312.9532
80% | [10 empty] | 2.2039 | 30.2396 | 40.7729 | 60.6044 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 | 75.7771 |  | 9.4684e-06 | [6 empty] | 12.8169 | 45.0711 | 71.4802 | 96.3905 | 133.362 | 160.2429 | 187.3272 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131 | 216.0131
75% | [11 empty] | 13.103 | 28.5728 | 58.3802 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | 81.1852 | [9 empty] | 15.7478 | 44.0306 | 70.7741 | 110.4665 | 139.3256 | 168.4031 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001 | 199.2001
70% | [12 empty] | 4.1119 | 56.9058 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | 118.2404 | [10 empty] | 12.6465 | 47.0814 | 102.7788 | 143.2747 | 184.077 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922 | 227.2922
65% | FY38: 0.012953; FY39: 22.224; FY40: 22.224; FY41: 22.224; FY42: 22.224; FY43: 22.224; FY44: 22.224; FY45: 22.224; FY46: 22.224; FY47: 22.224; FY48: 22.224; FY49: 22.224; FY50: 22.224; FY51: 22.224; FY52: 22.224; FY53: 22.224; FY54: 22.224 | [11 empty] | 3.2552 | 49.8224 | 96.9513 | 144.4367 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302 | 194.7302
60% | [42 empty] | 1.8912 | 51.3197 | 158.6982 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432 | 284.432
55% | [44 empty] | 3.8596 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503 | 53.503
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.048421 | 7.5487 | 31.5629 | 73.9345 | 186.8185 | 241.345 | 389.7519 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | 546.4392 | E @ R (MWh) | 101.2639 | 47.5018 | 100.0608 | 0.029909 | 5.9674 | 38.1764 | 88.4988 | 194.4019 | 339.9191 | 486.9423 | 651.4481 | 943.8229 | 1217.7243 | 1555.1338 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057 | 1970.057
Option 4 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033895 | 5.2841 | 22.094 | 51.7541 | 130.7729 | 168.9415 | 272.8263 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | 382.5074 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 30.3792 | 14.2505 | 30.0182 | 0.0089726 | 1.7902 | 11.4529 | 26.5496 | 58.3206 | 101.9757 | 146.0827 | 195.4344 | 283.1469 | 365.3173 | 466.5401 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171 | 591.0171
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 2.0948 | 5.968 | 9.4101 | 13.1618 | 14.5941 | 19.4437 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | [8 empty] | 1.8693 | 5.7463 | 9.403 | 13.2035 | 17.7587 | 19.2837 | 24.1959 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745
98% | [8 empty] | 0.74475 | 2.6619 | 4.3656 | 6.2227 | 6.9316 | 9.332 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | [8 empty] | 0.63313 | 2.5522 | 4.3621 | 6.2433 | 8.498 | 9.2528 | 11.6843 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505
97% | [8 empty] | 0.8842 | 4.6795 | 8.0525 | 11.7288 | 13.1323 | 17.8843 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | [8 empty] | 0.66324 | 4.4623 | 8.0455 | 11.7696 | 16.2332 | 17.7276 | 22.5411 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276
95% | [8 empty] | 0.20953 | 5.5698 | 10.5514 | 15.981 | 18.0539 | 25.0723 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | [8 empty] | 0.081366 | 5.249 | 10.5411 | 16.0413 | 22.6337 | 24.8408 | 31.9499 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762
90% | [9 empty] | 2.193 | 6.9876 | 12.2193 | 14.2166 | 20.9791 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | [9 empty] | 1.9076 | 6.9777 | 12.2774 | 18.6294 | 20.756 | 27.606 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907
85% | [10 empty] | 23.2543 | 82.1442 | 104.8162 | 181.5802 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | [10 empty] | 23.1561 | 82.804 | 154.9081 | 179.0481 | 256.8046 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279
80% | [11 empty] | 49.3399 | 99.7529 | 284.7177 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | [11 empty] | 50.5859 | 220.4506 | 278.6164 | 465.9727 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014
75% | [12 empty] | 2.2783 | 327.6472 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | [12 empty] | 156.1147 | 309.8297 | 856.9643 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309
70% | FY38: 4.9911; FY39: 680.9849; FY40: 680.9849; FY41: 680.9849; FY42: 680.9849; FY43: 680.9849; FY44: 680.9849; FY45: 680.9849; FY46: 680.9849; FY47: 680.9849; FY48: 680.9849; FY49: 680.9849; FY50: 680.9849; FY51: 680.9849; FY52: 680.9849; FY53: 680.9849; FY54: 680.9849 | [13 empty] | 2.0971 | 618.8325 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723
65% | [45 empty] | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9333 | 21.0721 | 62.6215 | 190.7976 | 273.7758 | 891.6476 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.247 | 19.9174 | 62.4857 | 192.925 | 615.2263 | 861.4523 | 2316.5514 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7533 | 14.7505 | 43.8351 | 133.5583 | 191.6431 | 624.1533 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97411 | 5.9752 | 18.7457 | 57.8775 | 184.5679 | 258.4357 | 694.9654 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.7562 | 3.8988 | 5.7218 | 7.2476 | 8.5992 | 10.7288 | 12.6537 | 15.3241 | 18.1083 | 20.3833 | 22.5293 | 25.7143 | 28.03 | 30.3632 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344
98% |  |  |  | 0.66157 | 2.1576 | 3.7001 | 5.3382 | 7.2124 | 9.4182 | 11.4855 | 13.6579 | 17.3539 | 18.6116 | 20.9793 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 |  | 10.7187 | 7.0413 | 10.6506 | 13.6715 | 16.3476 | 20.5639 | 24.3751 | 29.6622 | 35.1745 | 39.6789 | 43.9277 | 50.2336 | 54.8185 | 59.4381 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308
97% |  |  |  | 0.31239 | 1.7932 | 3.3201 | 4.9415 | 6.7967 | 8.9802 | 11.0264 | 13.1767 | 16.8353 | 18.0801 | 20.4239 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 |  | 14.8875 | 9.4273 | 14.7863 | 19.2716 | 23.245 | 29.5053 | 35.164 | 43.0141 | 51.1987 | 57.8867 | 64.1952 | 73.5581 | 80.3656 | 87.2246 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892
95% |  |  |  | 0.013596 | 1.2466 | 2.75 | 4.3466 | 6.1732 | 8.323 | 10.3378 | 12.4551 | 16.0573 | 17.283 | 19.5907 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 |  | 26.2032 | 15.4508 | 26.0038 | 34.8366 | 42.6611 | 54.989 | 66.1323 | 81.591 | 97.7083 | 110.8786 | 123.3014 | 141.7391 | 155.1447 | 168.6516 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573
90% |  |  |  |  | 1.9227 | 12.7794 | 26.6244 | 42.4645 | 61.1079 | 78.5798 | 96.9404 | 128.1789 | 138.8079 | 158.8197 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 |  | 26.8034 | 11.2629 | 26.5152 | 39.2813 | 50.5902 | 68.4079 | 84.5135 | 106.8561 | 130.1507 | 149.1858 | 167.1406 | 193.7889 | 213.1641 | 232.6859 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621
85% | [5 empty] | 0.52287 | 8.7756 | 23.7588 | 41.3945 | 57.9219 | 75.2901 | 104.84 | 114.8945 | 133.8246 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 |  | 16.8948 | 0.42068 | 16.3832 | 39.1901 | 59.3967 | 91.2331 | 120.0103 | 159.9319 | 201.5543 | 235.566 | 267.6474 | 315.2623 | 349.8817 | 384.7629 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069
80% | [7 empty] | 6.1637 | 24.0901 | 41.4045 | 59.5998 | 90.5568 | 101.0901 | 120.9216 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 |  | 9.4684e-06 |  |  | 5.5316 | 19.134 | 43.854 | 66.1987 | 97.1966 | 129.5152 | 155.9243 | 180.8345 | 217.8061 | 244.687 | 271.7713 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572
75% | [8 empty] | 6.3044 | 29.5222 | 56.8702 | 103.3996 | 119.2314 | 149.0388 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | [5 empty] | 0.34552 | 14.5429 | 38.3604 | 71.6396 | 106.3365 | 134.6892 | 161.4326 | 201.1251 | 229.9842 | 259.0617 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587
70% | [9 empty] | 4.8747 | 52.8726 | 177.9862 | 220.566 | 300.7336 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | [7 empty] | 7.8145 | 48.2959 | 96.9835 | 136.7688 | 174.2959 | 229.9933 | 270.4892 | 311.2915 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066
65% | [11 empty] | 81.6729 | 136.8236 | 240.6687 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | [8 empty] | 3.6997 | 43.0779 | 89.3797 | 133.0535 | 197.8737 | 245.0026 | 292.488 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815
60% | [12 empty] | 31.8023 | 261.3027 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | [9 empty] | 0.27668 | 39.0679 | 130.2401 | 292.2908 | 410.113 | 528.8265 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602
55% | FY39: 46.4501; FY40: 46.4501; FY41: 46.4501; FY42: 46.4501; FY43: 46.4501; FY44: 46.4501; FY45: 46.4501; FY46: 46.4501; FY47: 46.4501; FY48: 46.4501; FY49: 46.4501; FY50: 46.4501; FY51: 46.4501; FY52: 46.4501; FY53: 46.4501; FY54: 46.4501 | [11 empty] | 0.52076 | 58.3942 | 152.8404 | 258.0119 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026
50% | [43 empty] | 5.1141 | 85.428 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0.98755 | 7.1201 | 23.0724 | 50.0263 | 92.5692 | 159.6184 | 245.1528 | 380.8629 | 736.8809 | 917.1904 | 1426.3035 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | E @ R (MWh) | 101.2639 | 47.5018 | 100.0608 | 159.0303 | 220.3192 | 333.8249 | 455.2225 | 657.2114 | 910.0845 | 1169.4092 | 1469.1189 | 1997.7796 | 2439.6351 | 2970.0052 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691
Option 5 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0.69129 | 4.9841 | 16.1507 | 35.0184 | 64.7985 | 111.7329 | 171.607 | 266.604 | 515.8167 | 642.0333 | 998.4125 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 30.3792 | 14.2505 | 30.0182 | 47.7091 | 66.0958 | 100.1475 | 136.5668 | 197.1634 | 273.0253 | 350.8228 | 440.7357 | 599.3339 | 731.8905 | 891.0016 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [10 empty] | 2.9345 | 6.3668 | 7.5696 | 12.1875 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | 16.9574 | [10 empty] | 3.1394 | 6.7279 | 10.9636 | 12.2592 | 16.9397 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272 | 21.272
98% | [10 empty] | 1.1604 | 2.8593 | 3.4546 | 5.7404 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | 8.1014 | [10 empty] | 1.2618 | 3.038 | 5.1346 | 5.7759 | 8.0926 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237 | 10.237
97% | [10 empty] | 1.7071 | 5.0703 | 6.2489 | 10.774 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | 15.448 | [10 empty] | 1.9078 | 5.4242 | 9.5747 | 10.8443 | 15.4307 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759 | 19.6759
95% | [10 empty] | 1.1797 | 6.1469 | 7.8877 | 14.5709 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | 21.4741 | [10 empty] | 1.4762 | 6.6696 | 12.7996 | 14.6746 | 21.4485 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183 | 27.7183
90% | [10 empty] | 0.0072927 | 2.7437 | 4.421 | 10.8605 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | 17.5121 | [10 empty] | 0.03305 | 3.2474 | 9.1539 | 10.9605 | 17.4874 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287 | 23.5287
85% | [11 empty] | 0.12081 | 4.5825 | 66.7208 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | 142.2246 | [11 empty] | 0.79117 | 47.3481 | 67.8557 | 141.9452 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212 | 210.5212
80% | FY38: 24.494; FY39: 189.8893; FY40: 189.8893; FY41: 189.8893; FY42: 189.8893; FY43: 189.8893; FY44: 189.8893; FY45: 189.8893; FY46: 189.8893; FY47: 189.8893; FY48: 189.8893; FY49: 189.8893; FY50: 189.8893; FY51: 189.8893; FY52: 189.8893; FY53: 189.8893; FY54: 189.8893 | [12 empty] | 5.2987 | 26.0386 | 189.2161 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516 | 354.4516
75% | FY39: 95.1927; FY40: 95.1927; FY41: 95.1927; FY42: 95.1927; FY43: 95.1927; FY44: 95.1927; FY45: 95.1927; FY46: 95.1927; FY47: 95.1927; FY48: 95.1927; FY49: 95.1927; FY50: 95.1927; FY51: 95.1927; FY52: 95.1927; FY53: 95.1927; FY54: 95.1927 | [14 empty] | 94.0132 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903 | 531.2903
70% | [45 empty] | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965 | 123.2965
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.989 | 23.3078 | 34.1644 | 145.348 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | 506.7995 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8183 | 25.8984 | 100.2733 | 148.4087 | 504.5736 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914 | 1321.9914
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8923 | 16.3155 | 23.9151 | 101.7436 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | 354.7597 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3455 | 7.7695 | 30.082 | 44.5226 | 151.3721 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974 | 396.5974
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3.1657 | 0.94467 | 2.6547 | 4.0871 | 5.3564 | 7.3527 | 9.1575 | 11.6589 | 14.2666 | 16.3983 | 18.4094 | 21.3912 | 23.5609 | 25.7467 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612 | 28.0612
98% | [5 empty] | 0.35794 | 1.8772 | 3.584 | 5.6152 | 7.5405 | 9.5794 | 13.0743 | 14.1874 | 16.4092 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 | 18.0656 |  | 5.5897 | 1.1923 | 4.578 | 7.4139 | 9.9272 | 13.8796 | 17.453 | 22.4054 | 27.5684 | 31.789 | 35.7708 | 41.6743 | 45.9701 | 50.2979 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804 | 54.8804
97% | [5 empty] | 0.049386 | 1.5156 | 3.2052 | 5.2157 | 7.1215 | 9.1397 | 12.5991 | 13.7009 | 15.9002 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 | 17.5398 |  | 7.2721 | 0.74295 | 5.7699 | 9.9806 | 13.7122 | 19.5807 | 24.8863 | 32.2396 | 39.9054 | 46.172 | 52.084 | 60.8494 | 67.2278 | 73.6535 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575 | 80.4575
95% | [6 empty] | 0.97336 | 2.6369 | 4.6165 | 6.493 | 8.4801 | 11.8863 | 12.9711 | 15.1366 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 | 16.751 |  | 11.2066 | 0.023184 | 8.2485 | 16.5404 | 23.8888 | 35.4451 | 45.8931 | 60.3734 | 75.4691 | 87.8097 | 99.4518 | 116.7128 | 129.2732 | 141.927 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256 | 155.3256
90% | [6 empty] | 0.93195 | 11.7984 | 28.9653 | 45.238 | 62.4703 | 92.0081 | 101.4156 | 120.1942 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 | 134.1939 |  | 5.4384 |  | 2.5058 | 12.8377 | 23.4584 | 40.1609 | 55.2615 | 76.1901 | 98.008 | 115.844 | 132.6705 | 157.6181 | 175.7718 | 194.0604 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256 | 213.4256
85% | [7 empty] | 0.31446 | 10.9894 | 26.3824 | 42.6832 | 70.6244 | 79.5234 | 97.2869 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 | 110.5299 |  |  |  |  | 1.0141 | 11.4178 | 40.7617 | 67.7433 | 105.1382 | 144.1223 | 175.9913 | 206.0567 | 250.6328 | 283.0695 | 315.7474 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489 | 350.3489
80% | [8 empty] | 0.12379 | 8.4696 | 25.4402 | 54.7119 | 64.0346 | 82.6441 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | 96.5176 | [6 empty] | 6.3216 | 25.6149 | 54.6509 | 84.9209 | 109.6663 | 133.0111 | 167.6232 | 192.8094 | 218.1827 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498 | 245.0498
75% | [10 empty] | 7.595 | 49.5235 | 63.5359 | 91.5065 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | 112.3588 | [7 empty] | 2.0991 | 25.9628 | 58.4604 | 85.0269 | 110.0898 | 147.249 | 174.2887 | 201.5294 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737 | 230.3737
70% | [11 empty] | 35.2125 | 70.7722 | 145.9995 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | 202.0823 | [8 empty] | 1.2232 | 29.8026 | 67.0814 | 102.2502 | 154.393 | 192.3359 | 230.5607 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358 | 271.0358
65% | [12 empty] | 1.3665 | 45.4475 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | 112.8806 | [9 empty] | 0.0079587 | 14.0391 | 49.2072 | 109.8907 | 154.0483 | 198.5341 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387 | 245.6387
60% | FY39: 9.895; FY40: 9.895; FY41: 9.895; FY42: 9.895; FY43: 9.895; FY44: 9.895; FY45: 9.895; FY46: 9.895; FY47: 9.895; FY48: 9.895; FY49: 9.895; FY50: 9.895; FY51: 9.895; FY52: 9.895; FY53: 9.895; FY54: 9.895 | [11 empty] | 1.6848 | 75.8724 | 182.7272 | 293.9417 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032 | 411.7032
55% | [43 empty] | 9.0279 | 59.4472 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493 | 154.2493
50% | [45 empty] | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539 | 5.5539
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0.40732 | 5.2981 | 21.539 | 55.5258 | 101.2449 | 165.3881 | 339.6399 | 421.5074 | 630.5247 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | 830.8145 | E @ R (MWh) | 32.6724 | 2.9031 | 23.757 | 51.8739 | 87.7609 | 163.5023 | 248.1088 | 389.8427 | 572.5316 | 749.8181 | 940.6863 | 1303.9068 | 1630.1107 | 2003.6287 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038 | 2446.1038
Option 6 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0.28513 | 3.7087 | 15.0773 | 38.8681 | 70.8715 | 115.7717 | 237.748 | 295.0552 | 441.3673 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | 581.5701 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 9.8017 | 0.87094 | 7.1271 | 15.5622 | 26.3283 | 49.0507 | 74.4326 | 116.9528 | 171.7595 | 224.9454 | 282.2059 | 391.172 | 489.0332 | 601.0886 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311 | 733.8311
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 2.0948 | 5.968 | 9.4101 | 13.1618 | 14.5941 | 19.4437 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | [8 empty] | 1.8693 | 5.7463 | 9.403 | 13.2035 | 17.7587 | 19.2837 | 24.1959 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745
98% | [8 empty] | 0.74475 | 2.6619 | 4.3656 | 6.2227 | 6.9316 | 9.332 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | [8 empty] | 0.63313 | 2.5522 | 4.3621 | 6.2433 | 8.498 | 9.2528 | 11.6843 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505
97% | [8 empty] | 0.8842 | 4.6795 | 8.0525 | 11.7288 | 13.1323 | 17.8843 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | [8 empty] | 0.66324 | 4.4623 | 8.0455 | 11.7696 | 16.2332 | 17.7276 | 22.5411 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276
95% | [8 empty] | 0.20953 | 5.5698 | 10.5514 | 15.981 | 18.0539 | 25.0723 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | [8 empty] | 0.081366 | 5.249 | 10.5411 | 16.0413 | 22.6337 | 24.8408 | 31.9499 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762
90% | [9 empty] | 2.193 | 6.9876 | 12.2193 | 14.2166 | 20.9791 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | [9 empty] | 1.9076 | 6.9777 | 12.2774 | 18.6294 | 20.756 | 27.606 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907
85% | [10 empty] | 23.2543 | 82.1442 | 104.8162 | 181.5802 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | [10 empty] | 23.1561 | 82.804 | 154.9081 | 179.0481 | 256.8046 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279
80% | [11 empty] | 49.3399 | 99.7529 | 284.7177 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | [11 empty] | 50.5859 | 220.4506 | 278.6164 | 465.9727 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014
75% | [12 empty] | 2.2783 | 327.6472 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | [12 empty] | 156.1147 | 309.8297 | 856.9643 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309
70% | FY38: 4.9911; FY39: 680.9849; FY40: 680.9849; FY41: 680.9849; FY42: 680.9849; FY43: 680.9849; FY44: 680.9849; FY45: 680.9849; FY46: 680.9849; FY47: 680.9849; FY48: 680.9849; FY49: 680.9849; FY50: 680.9849; FY51: 680.9849; FY52: 680.9849; FY53: 680.9849; FY54: 680.9849 | [13 empty] | 2.0971 | 618.8325 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723
65% | [45 empty] | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9333 | 21.0721 | 62.6215 | 190.7976 | 273.7758 | 891.6476 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.247 | 19.9174 | 62.4857 | 192.925 | 615.2263 | 861.4523 | 2316.5514 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7533 | 14.7505 | 43.8351 | 133.5583 | 191.6431 | 624.1533 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97411 | 5.9752 | 18.7457 | 57.8775 | 184.5679 | 258.4357 | 694.9654 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.7562 | 3.8988 | 5.7218 | 7.2476 | 8.5992 | 10.7288 | 12.6537 | 15.3241 | 18.1083 | 20.3833 | 22.5293 | 25.7143 | 28.03 | 30.3632 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344
98% |  |  |  | 0.66157 | 2.1576 | 3.7001 | 5.3382 | 7.2124 | 9.4182 | 11.4855 | 13.6579 | 17.3539 | 18.6116 | 20.9793 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 |  | 10.7187 | 7.0413 | 10.6506 | 13.6715 | 16.3476 | 20.5639 | 24.3751 | 29.6622 | 35.1745 | 39.6789 | 43.9277 | 50.2336 | 54.8185 | 59.4381 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308
97% |  |  |  | 0.31239 | 1.7932 | 3.3201 | 4.9415 | 6.7967 | 8.9802 | 11.0264 | 13.1767 | 16.8353 | 18.0801 | 20.4239 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 |  | 14.8875 | 9.4273 | 14.7863 | 19.2716 | 23.245 | 29.5053 | 35.164 | 43.0141 | 51.1987 | 57.8867 | 64.1952 | 73.5581 | 80.3656 | 87.2246 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892
95% |  |  |  | 0.013596 | 1.2466 | 2.75 | 4.3466 | 6.1732 | 8.323 | 10.3378 | 12.4551 | 16.0573 | 17.283 | 19.5907 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 |  | 26.2032 | 15.4508 | 26.0038 | 34.8366 | 42.6611 | 54.989 | 66.1323 | 81.591 | 97.7083 | 110.8786 | 123.3014 | 141.7391 | 155.1447 | 168.6516 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573
90% |  |  |  |  | 1.9227 | 12.7794 | 26.6244 | 42.4645 | 61.1079 | 78.5798 | 96.9404 | 128.1789 | 138.8079 | 158.8197 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 |  | 26.8034 | 11.2629 | 26.5152 | 39.2813 | 50.5902 | 68.4079 | 84.5135 | 106.8561 | 130.1507 | 149.1858 | 167.1406 | 193.7889 | 213.1641 | 232.6859 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621
85% | [5 empty] | 0.52287 | 8.7756 | 23.7588 | 41.3945 | 57.9219 | 75.2901 | 104.84 | 114.8945 | 133.8246 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 |  | 16.8948 | 0.42068 | 16.3832 | 39.1901 | 59.3967 | 91.2331 | 120.0103 | 159.9319 | 201.5543 | 235.566 | 267.6474 | 315.2623 | 349.8817 | 384.7629 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069
80% | [7 empty] | 6.1637 | 24.0901 | 41.4045 | 59.5998 | 90.5568 | 101.0901 | 120.9216 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 |  | 9.4684e-06 |  |  | 5.5316 | 19.134 | 43.854 | 66.1987 | 97.1966 | 129.5152 | 155.9243 | 180.8345 | 217.8061 | 244.687 | 271.7713 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572
75% | [8 empty] | 6.3044 | 29.5222 | 56.8702 | 103.3996 | 119.2314 | 149.0388 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | [5 empty] | 0.34552 | 14.5429 | 38.3604 | 71.6396 | 106.3365 | 134.6892 | 161.4326 | 201.1251 | 229.9842 | 259.0617 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587
70% | [9 empty] | 4.8747 | 52.8726 | 177.9862 | 220.566 | 300.7336 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | [7 empty] | 7.8145 | 48.2959 | 96.9835 | 136.7688 | 174.2959 | 229.9933 | 270.4892 | 311.2915 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066
65% | [11 empty] | 81.6729 | 136.8236 | 240.6687 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | [8 empty] | 3.6997 | 43.0779 | 89.3797 | 133.0535 | 197.8737 | 245.0026 | 292.488 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815
60% | [12 empty] | 31.8023 | 261.3027 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | [9 empty] | 0.27668 | 39.0679 | 130.2401 | 292.2908 | 410.113 | 528.8265 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602
55% | FY39: 46.4501; FY40: 46.4501; FY41: 46.4501; FY42: 46.4501; FY43: 46.4501; FY44: 46.4501; FY45: 46.4501; FY46: 46.4501; FY47: 46.4501; FY48: 46.4501; FY49: 46.4501; FY50: 46.4501; FY51: 46.4501; FY52: 46.4501; FY53: 46.4501; FY54: 46.4501 | [11 empty] | 0.52076 | 58.3942 | 152.8404 | 258.0119 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026
50% | [43 empty] | 5.1141 | 85.428 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0.98755 | 7.1201 | 23.0724 | 50.0263 | 92.5692 | 159.6184 | 245.1528 | 380.8629 | 736.8809 | 917.1904 | 1426.3035 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | E @ R (MWh) | 101.2639 | 47.5018 | 100.0608 | 159.0303 | 220.3192 | 333.8249 | 455.2225 | 657.2114 | 910.0845 | 1169.4092 | 1469.1189 | 1997.7796 | 2439.6351 | 2970.0052 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691
Option 7 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0.69129 | 4.9841 | 16.1507 | 35.0184 | 64.7985 | 111.7329 | 171.607 | 266.604 | 515.8167 | 642.0333 | 998.4125 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 30.3792 | 14.2505 | 30.0182 | 47.7091 | 66.0958 | 100.1475 | 136.5668 | 197.1634 | 273.0253 | 350.8228 | 440.7357 | 599.3339 | 731.8905 | 891.0016 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [8 empty] | 2.0948 | 5.968 | 9.4101 | 13.1618 | 14.5941 | 19.4437 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | 24.4599 | [8 empty] | 1.8693 | 5.7463 | 9.403 | 13.2035 | 17.7587 | 19.2837 | 24.1959 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745 | 28.7745
98% | [8 empty] | 0.74475 | 2.6619 | 4.3656 | 6.2227 | 6.9316 | 9.332 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | 11.8149 | [8 empty] | 0.63313 | 2.5522 | 4.3621 | 6.2433 | 8.498 | 9.2528 | 11.6843 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505 | 13.9505
97% | [8 empty] | 0.8842 | 4.6795 | 8.0525 | 11.7288 | 13.1323 | 17.8843 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | 22.7997 | [8 empty] | 0.66324 | 4.4623 | 8.0455 | 11.7696 | 16.2332 | 17.7276 | 22.5411 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276 | 27.0276
95% | [8 empty] | 0.20953 | 5.5698 | 10.5514 | 15.981 | 18.0539 | 25.0723 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | 32.3319 | [8 empty] | 0.081366 | 5.249 | 10.5411 | 16.0413 | 22.6337 | 24.8408 | 31.9499 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762 | 38.5762
90% | [9 empty] | 2.193 | 6.9876 | 12.2193 | 14.2166 | 20.9791 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | 27.9741 | [9 empty] | 1.9076 | 6.9777 | 12.2774 | 18.6294 | 20.756 | 27.606 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907 | 33.9907
85% | [10 empty] | 23.2543 | 82.1442 | 104.8162 | 181.5802 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | 260.9824 | [10 empty] | 23.1561 | 82.804 | 154.9081 | 179.0481 | 256.8046 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279 | 329.279
80% | [11 empty] | 49.3399 | 99.7529 | 284.7177 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | 476.0392 | [11 empty] | 50.5859 | 220.4506 | 278.6164 | 465.9727 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014 | 640.6014
75% | [12 empty] | 2.2783 | 327.6472 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | 886.3615 | [12 empty] | 156.1147 | 309.8297 | 856.9643 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309 | 1366.9309
70% | FY38: 4.9911; FY39: 680.9849; FY40: 680.9849; FY41: 680.9849; FY42: 680.9849; FY43: 680.9849; FY44: 680.9849; FY45: 680.9849; FY46: 680.9849; FY47: 680.9849; FY48: 680.9849; FY49: 680.9849; FY50: 680.9849; FY51: 680.9849; FY52: 680.9849; FY53: 680.9849; FY54: 680.9849 | [13 empty] | 2.0971 | 618.8325 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723 | 1726.2723
65% | [45 empty] | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884 | 393.1884
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9333 | 21.0721 | 62.6215 | 190.7976 | 273.7758 | 891.6476 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | 2423.7485 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.247 | 19.9174 | 62.4857 | 192.925 | 615.2263 | 861.4523 | 2316.5514 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915 | 4598.5915
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7533 | 14.7505 | 43.8351 | 133.5583 | 191.6431 | 624.1533 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | 1696.6239 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97411 | 5.9752 | 18.7457 | 57.8775 | 184.5679 | 258.4357 | 694.9654 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774 | 1379.5774
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.7562 | 3.8988 | 5.7218 | 7.2476 | 8.5992 | 10.7288 | 12.6537 | 15.3241 | 18.1083 | 20.3833 | 22.5293 | 25.7143 | 28.03 | 30.3632 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344 | 32.8344
98% |  |  |  | 0.66157 | 2.1576 | 3.7001 | 5.3382 | 7.2124 | 9.4182 | 11.4855 | 13.6579 | 17.3539 | 18.6116 | 20.9793 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 | 22.7909 |  | 10.7187 | 7.0413 | 10.6506 | 13.6715 | 16.3476 | 20.5639 | 24.3751 | 29.6622 | 35.1745 | 39.6789 | 43.9277 | 50.2336 | 54.8185 | 59.4381 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308 | 64.3308
97% |  |  |  | 0.31239 | 1.7932 | 3.3201 | 4.9415 | 6.7967 | 8.9802 | 11.0264 | 13.1767 | 16.8353 | 18.0801 | 20.4239 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 | 22.217 |  | 14.8875 | 9.4273 | 14.7863 | 19.2716 | 23.245 | 29.5053 | 35.164 | 43.0141 | 51.1987 | 57.8867 | 64.1952 | 73.5581 | 80.3656 | 87.2246 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892 | 94.4892
95% |  |  |  | 0.013596 | 1.2466 | 2.75 | 4.3466 | 6.1732 | 8.323 | 10.3378 | 12.4551 | 16.0573 | 17.283 | 19.5907 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 | 21.3563 |  | 26.2032 | 15.4508 | 26.0038 | 34.8366 | 42.6611 | 54.989 | 66.1323 | 81.591 | 97.7083 | 110.8786 | 123.3014 | 141.7391 | 155.1447 | 168.6516 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573 | 182.9573
90% |  |  |  |  | 1.9227 | 12.7794 | 26.6244 | 42.4645 | 61.1079 | 78.5798 | 96.9404 | 128.1789 | 138.8079 | 158.8197 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 | 174.1304 |  | 26.8034 | 11.2629 | 26.5152 | 39.2813 | 50.5902 | 68.4079 | 84.5135 | 106.8561 | 130.1507 | 149.1858 | 167.1406 | 193.7889 | 213.1641 | 232.6859 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621 | 253.3621
85% | [5 empty] | 0.52287 | 8.7756 | 23.7588 | 41.3945 | 57.9219 | 75.2901 | 104.84 | 114.8945 | 133.8246 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 | 148.3076 |  | 16.8948 | 0.42068 | 16.3832 | 39.1901 | 59.3967 | 91.2331 | 120.0103 | 159.9319 | 201.5543 | 235.566 | 267.6474 | 315.2623 | 349.8817 | 384.7629 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069 | 421.7069
80% | [7 empty] | 6.1637 | 24.0901 | 41.4045 | 59.5998 | 90.5568 | 101.0901 | 120.9216 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 | 136.0943 |  | 9.4684e-06 |  |  | 5.5316 | 19.134 | 43.854 | 66.1987 | 97.1966 | 129.5152 | 155.9243 | 180.8345 | 217.8061 | 244.687 | 271.7713 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572 | 300.4572
75% | [8 empty] | 6.3044 | 29.5222 | 56.8702 | 103.3996 | 119.2314 | 149.0388 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | 171.8438 | [5 empty] | 0.34552 | 14.5429 | 38.3604 | 71.6396 | 106.3365 | 134.6892 | 161.4326 | 201.1251 | 229.9842 | 259.0617 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587 | 289.8587
70% | [9 empty] | 4.8747 | 52.8726 | 177.9862 | 220.566 | 300.7336 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | 362.0681 | [7 empty] | 7.8145 | 48.2959 | 96.9835 | 136.7688 | 174.2959 | 229.9933 | 270.4892 | 311.2915 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066 | 354.5066
65% | [11 empty] | 81.6729 | 136.8236 | 240.6687 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | 320.1186 | [8 empty] | 3.6997 | 43.0779 | 89.3797 | 133.0535 | 197.8737 | 245.0026 | 292.488 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815 | 342.7815
60% | [12 empty] | 31.8023 | 261.3027 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | 550.2262 | [9 empty] | 0.27668 | 39.0679 | 130.2401 | 292.2908 | 410.113 | 528.8265 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602 | 654.5602
55% | FY39: 46.4501; FY40: 46.4501; FY41: 46.4501; FY42: 46.4501; FY43: 46.4501; FY44: 46.4501; FY45: 46.4501; FY46: 46.4501; FY47: 46.4501; FY48: 46.4501; FY49: 46.4501; FY50: 46.4501; FY51: 46.4501; FY52: 46.4501; FY53: 46.4501; FY54: 46.4501 | [11 empty] | 0.52076 | 58.3942 | 152.8404 | 258.0119 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026 | 369.4026
50% | [43 empty] | 5.1141 | 85.428 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213 | 267.9213
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0.98755 | 7.1201 | 23.0724 | 50.0263 | 92.5692 | 159.6184 | 245.1528 | 380.8629 | 736.8809 | 917.1904 | 1426.3035 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | 1975.6033 | E @ R (MWh) | 101.2639 | 47.5018 | 100.0608 | 159.0303 | 220.3192 | 333.8249 | 455.2225 | 657.2114 | 910.0845 | 1169.4092 | 1469.1189 | 1997.7796 | 2439.6351 | 2970.0052 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691 | 3629.1691
Option 8 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0.69129 | 4.9841 | 16.1507 | 35.0184 | 64.7985 | 111.7329 | 171.607 | 266.604 | 515.8167 | 642.0333 | 998.4125 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | 1382.9223 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 30.3792 | 14.2505 | 30.0182 | 47.7091 | 66.0958 | 100.1475 | 136.5668 | 197.1634 | 273.0253 | 350.8228 | 440.7357 | 599.3339 | 731.8905 | 891.0016 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507 | 1088.7507

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 11.8122 | 9.2886 | 11.5965 | 14.5464 | 17.4025 | 19.9446 | 23.4359 | 27.2523 | 31.1608 | 35.034 | 38.4761 | 42.2278 | 43.6601 | 48.5097 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 |  | 14.7101 | 12.198 | 14.637 | 17.6231 | 20.407 | 23.3712 | 26.4886 | 30.9353 | 34.8123 | 38.469 | 42.2695 | 46.8247 | 48.3497 | 53.2619 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405
98% | 5.7007 | 4.4516 | 5.5939 | 7.054 | 8.4677 | 9.726 | 11.4541 | 13.3432 | 15.2778 | 17.1949 | 18.8987 | 20.7557 | 21.4646 | 23.865 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 |  | 7.1351 | 5.8917 | 7.0989 | 8.5769 | 9.9549 | 11.4221 | 12.9651 | 15.1661 | 17.0852 | 18.8951 | 20.7763 | 23.031 | 23.7858 | 26.2173 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835
97% | 10.9905 | 8.5177 | 10.7792 | 13.6697 | 16.4684 | 18.9594 | 22.3806 | 26.1203 | 29.9502 | 33.7455 | 37.1185 | 40.7948 | 42.1983 | 46.9504 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 |  | 13.8302 | 11.3686 | 13.7586 | 16.6846 | 19.4125 | 22.3172 | 25.3719 | 29.7293 | 33.5283 | 37.1115 | 40.8356 | 45.2992 | 46.7936 | 51.6071 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936
95% | 15.5614 | 11.9092 | 15.2493 | 19.5184 | 23.6518 | 27.3309 | 32.3837 | 37.9069 | 43.5634 | 49.1688 | 54.1504 | 59.58 | 61.6529 | 68.6713 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 |  | 19.7554 | 16.1198 | 19.6496 | 23.9712 | 28.0001 | 32.29 | 36.8016 | 43.2371 | 48.848 | 54.1401 | 59.6403 | 66.2327 | 68.4398 | 75.549 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752
90% | 13.4045 | 9.8855 | 13.1038 | 17.2173 | 21.2 | 24.7449 | 29.6135 | 34.9353 | 40.3856 | 45.7866 | 50.5866 | 55.8183 | 57.8156 | 64.5781 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 |  | 17.4456 | 13.9426 | 17.3436 | 21.5077 | 25.3897 | 29.5233 | 33.8704 | 40.0712 | 45.4776 | 50.5767 | 55.8764 | 62.2284 | 64.3551 | 71.205 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897
85% | 123.8793 | 83.9329 | 120.4651 | 167.1587 | 212.3681 | 252.6072 | 307.8727 | 368.2828 | 430.1509 | 491.4597 | 545.9461 | 605.3325 | 628.0045 | 704.7685 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 |  | 169.7502 | 129.9866 | 168.5932 | 215.8608 | 259.9267 | 306.8483 | 356.1939 | 426.5814 | 487.9512 | 545.8339 | 605.9923 | 678.0964 | 702.2364 | 779.9929 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673
80% | 222.088 | 125.8361 | 213.8613 | 326.3707 | 435.3039 | 532.261 | 665.4245 | 810.9841 | 960.0568 | 1107.7818 | 1239.0681 | 1382.161 | 1436.7897 | 1621.7545 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 |  | 332.6151 | 236.8036 | 329.8273 | 443.7197 | 549.8975 | 662.9563 | 781.8556 | 951.456 | 1099.328 | 1238.7977 | 1383.7507 | 1557.4874 | 1615.6532 | 1803.0095 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382
75% | 396.6559 | 116.4694 | 372.6315 | 701.1915 | 1019.3082 | 1302.451 | 1691.327 | 2116.4032 | 2551.7386 | 2983.1384 | 3366.5325 | 3784.4054 | 3943.9368 | 4484.0876 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 |  | 719.4271 | 439.6298 | 711.2859 | 1043.8848 | 1353.9548 | 1684.119 | 2031.3394 | 2526.6219 | 2958.451 | 3365.7428 | 3789.0478 | 4296.4091 | 4466.2702 | 5013.4048 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713
70% | 246.929 |  | 204.178 | 901.6933 | 1593.649 | 2209.5309 | 3055.3998 | 3980.0102 | 4926.9358 | 5865.3009 | 6699.2458 | 7608.1877 | 7955.1946 | 9130.111 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 |  | 941.3587 | 332.8577 | 923.6502 | 1647.1071 | 2321.5601 | 3039.7213 | 3794.9824 | 4872.3028 | 5811.6018 | 6697.5281 | 7618.2856 | 8721.8795 | 9091.3551 | 10281.4623 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723
65% |  |  |  | 226.1234 | 932.7463 | 1587.2067 | 2486.0603 | 3468.5876 | 4474.828 | 5471.9717 | 6358.1545 | 7324.0318 | 7692.7751 | 8941.2875 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 |  | 258.5342 |  | 243.8113 | 989.553 | 1706.2533 | 2469.3997 | 3271.9699 | 4416.7729 | 5414.9089 | 6356.3291 | 7334.7623 | 8507.4846 | 8900.1039 | 10164.7587 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028
60% |  |  |  |  | 149.8988 | 723.0581 | 1645.246 | 2653.2798 | 3685.6423 | 4708.672 | 5617.8601 | 6608.8117 | 6987.1276 | 8268.0514 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 |  |  |  |  | 184.3862 | 845.1952 | 1628.1529 | 2451.5579 | 3626.0801 | 4650.1278 | 5615.9873 | 6619.8207 | 7822.987 | 8225.7988 | 9523.2841 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284
55% | [5 empty] | 25.7795 | 679.408 | 1854.709 | 3058.5836 | 4251.5748 | 5311.8114 | 6467.3953 | 6908.5629 | 8402.2937 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | [5 empty] | 63.0524 | 659.9292 | 1619.4738 | 2989.126 | 4183.3044 | 5309.6275 | 6480.2334 | 7883.2883 | 8353.0214 | 9866.0651 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246
50% | [7 empty] | 479.7725 | 1727.5166 | 3029.3066 | 4186.235 | 5447.2062 | 5928.6075 | 7558.5641 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | [7 empty] | 307.8144 | 1651.7246 | 2954.8101 | 4183.852 | 5461.2151 | 6992.2262 | 7504.7982 | 9155.829 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017
45% | [8 empty] | 203.3275 | 1315.0503 | 2721.7171 | 4255.7243 | 4841.3627 | 6824.2511 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | [8 empty] | 167.3292 | 1227.8012 | 2718.8181 | 4272.7665 | 6135.285 | 6758.8434 | 8767.3691 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515
40% | [10 empty] | 474.4529 | 2069.885 | 2934.9379 | 5977.8403 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | [10 empty] | 472.4498 | 2093.2934 | 4920.5663 | 5877.4669 | 8959.7119 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735
35% | [12 empty] | 3.8716 | 560.4187 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | [12 empty] | 265.2858 | 528.0265 | 1908.4996 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332
30% | [45 empty] | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1047.0217 | 370.2909 | 967.4586 | 2394.5434 | 4430.4648 | 6733.6002 | 10650.0061 | 15871.5872 | 22179.118 | 29405.186 | 36720.2539 | 45772.3176 | 49487.9623 | 62726.003 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | E @ R (MWh) | 2494.5618 | 1198.7985 | 2449.6557 | 4612.8752 | 7203.004 | 10570.0505 | 14750.6849 | 21787.1338 | 28968.0357 | 36704.1588 | 45878.566 | 58024.6116 | 62275.2981 | 76501.2272 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131
Option 1 Winter POE50 W E @ R (MWh) N 2 | 732.9152 | 259.2037 | 677.221 | 1676.1804 | 3101.3253 | 4713.5201 | 7455.0043 | 11110.111 | 15525.3826 | 20583.6302 | 25704.1777 | 32040.6223 | 34641.5736 | 43908.2021 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 748.3685 | 359.6395 | 734.8967 | 1383.8626 | 2160.9012 | 3171.0152 | 4425.2055 | 6536.1402 | 8690.4107 | 11011.2476 | 13763.5698 | 17407.3835 | 18682.5894 | 22950.3682 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.6224 | 20.765 | 22.5879 | 24.1137 | 25.4654 | 27.5949 | 29.5198 | 32.1902 | 34.9744 | 37.2495 | 39.3954 | 42.5804 | 44.8961 | 47.2293 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006
98% | 16.5594 | 14.6718 | 16.2658 | 17.5277 | 19.0237 | 20.5662 | 22.2043 | 24.0785 | 26.2844 | 28.3516 | 30.524 | 34.2201 | 35.4777 | 37.8454 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 |  | 44.451 | 40.7735 | 44.3828 | 47.4037 | 50.0798 | 54.2961 | 58.1073 | 63.3944 | 68.9067 | 73.4112 | 77.6599 | 83.9659 | 88.5508 | 93.1703 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631
97% | 16.2201 | 14.3516 | 15.9295 | 17.1785 | 18.6593 | 20.1862 | 21.8077 | 23.6628 | 25.8463 | 27.8925 | 30.0429 | 33.7014 | 34.9463 | 37.29 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 |  | 65.4859 | 60.0257 | 65.3846 | 69.87 | 73.8434 | 80.1037 | 85.7624 | 93.6125 | 101.7971 | 108.4851 | 114.7936 | 124.1565 | 130.964 | 137.823 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876
95% | 15.7111 | 13.8713 | 15.4249 | 16.6548 | 18.1128 | 19.6161 | 21.2127 | 23.0393 | 25.1892 | 27.2039 | 29.3212 | 32.9235 | 34.1492 | 36.4568 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 |  | 127.4 | 116.6476 | 127.2006 | 136.0333 | 143.8578 | 156.1858 | 167.3291 | 182.7878 | 198.9051 | 212.0754 | 224.4981 | 242.9359 | 256.3414 | 269.8484 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541
90% | 130.7104 | 114.7563 | 128.2287 | 138.8937 | 151.5375 | 164.5746 | 178.4195 | 194.2596 | 212.9031 | 230.3749 | 248.7356 | 279.974 | 290.603 | 310.6149 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 |  | 178.5986 | 163.058 | 178.3104 | 191.0765 | 202.3853 | 220.203 | 236.3086 | 258.6513 | 281.9458 | 300.981 | 318.9357 | 345.5841 | 364.9593 | 384.4811 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573
85% | 115.4398 | 100.3481 | 113.0923 | 123.1808 | 135.1411 | 147.4735 | 160.5701 | 175.554 | 193.1897 | 209.7171 | 227.0853 | 256.6352 | 266.6896 | 285.6197 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 |  | 303.619 | 275.8513 | 303.104 | 325.9143 | 346.1208 | 377.9573 | 406.7345 | 446.6561 | 488.2784 | 522.2902 | 554.3716 | 601.9865 | 636.6058 | 671.4871 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311
80% | 111.2991 | 95.4888 | 108.8398 | 119.4088 | 131.9386 | 144.8582 | 158.5785 | 174.2759 | 192.7514 | 210.0658 | 228.2611 | 259.2181 | 269.7513 | 289.5829 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 |  | 222.2583 | 200.6975 | 221.8584 | 239.57 | 255.2597 | 279.9798 | 302.3245 | 333.3224 | 365.6409 | 392.0501 | 416.9603 | 453.9319 | 480.8128 | 507.8971 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583
75% | 150.9309 | 127.1676 | 147.2345 | 163.12 | 181.9528 | 201.3713 | 221.9933 | 245.5869 | 273.3561 | 299.3802 | 326.7283 | 373.2576 | 389.0894 | 418.8968 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 |  | 222.2599 | 199.1124 | 221.8307 | 240.8456 | 257.6901 | 284.2293 | 308.2184 | 341.4976 | 376.1945 | 404.5472 | 431.2907 | 470.9831 | 499.8423 | 528.9197 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167
70% | 355.8769 | 291.9649 | 345.9354 | 388.6595 | 439.3106 | 491.5371 | 547.0002 | 610.4557 | 685.1415 | 755.1337 | 828.6866 | 953.828 | 996.4079 | 1076.5754 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 |  | 285.7656 | 253.2844 | 285.1632 | 311.8455 | 335.482 | 372.7226 | 406.3848 | 453.083 | 501.7706 | 541.5558 | 579.0829 | 634.7803 | 675.2763 | 716.0785 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937
65% | 386.5423 | 303.7538 | 373.6646 | 429.0075 | 494.6183 | 562.2701 | 634.1144 | 716.3116 | 813.056 | 903.7206 | 998.9975 | 1161.0998 | 1216.2557 | 1320.1009 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 |  | 297.6766 | 259.8752 | 296.9755 | 328.0282 | 355.5363 | 398.8766 | 438.0523 | 492.3994 | 549.0617 | 595.3635 | 639.0373 | 703.8576 | 750.9864 | 798.4718 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653
60% | 1120.4925 | 811.4729 | 1072.4245 | 1278.9995 | 1523.9013 | 1776.4207 | 2044.5895 | 2351.402 | 2712.5139 | 3050.9321 | 3406.5666 | 4011.6358 | 4217.5128 | 4605.1294 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 |  | 642.9947 | 548.4913 | 641.2421 | 718.8737 | 787.6439 | 895.9948 | 993.9341 | 1129.8017 | 1271.4575 | 1387.2119 | 1496.3964 | 1658.4471 | 1776.2693 | 1894.9828 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165
55% | 1447.5067 | 844.7507 | 1353.748 | 1756.6813 | 2234.3727 | 2726.9226 | 3249.9973 | 3848.4481 | 4552.8123 | 5212.9114 | 5906.5916 | 7086.8049 | 7488.3769 | 8244.4394 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 |  | 464.401 | 380.678 | 462.8484 | 531.6242 | 592.5495 | 688.5403 | 775.3074 | 895.676 | 1021.1726 | 1123.7224 | 1220.4518 | 1364.0167 | 1468.3984 | 1573.5698 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605
50% | 1023.5986 | 186.306 | 855.6256 | 1579.9211 | 2439.4694 | 3325.7539 | 4266.9641 | 5343.8046 | 6611.2235 | 7798.9926 | 9047.1869 | 11170.839 | 11893.4197 | 13253.8635 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 |  | 758.1769 | 570.9902 | 754.7055 | 908.4736 | 1044.6895 | 1259.3045 | 1453.2969 | 1722.4155 | 2002.9989 | 2232.2783 | 2448.5445 | 2769.5249 | 3002.9001 | 3238.0408 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867
45% | 3.8607 |  |  | 128.7608 | 642.1854 | 1516.7957 | 2527.9377 | 3684.7872 | 5046.3752 | 6322.3953 | 7663.3303 | 9944.7695 | 10721.0378 | 12182.5623 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 |  | 994.5681 | 550.3323 | 986.3297 | 1351.2559 | 1674.5265 | 2183.8559 | 2644.2434 | 3282.9219 | 3948.8091 | 4492.9405 | 5006.1885 | 5767.9468 | 6321.7982 | 6879.8398 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814
40% | [5 empty] | 30.864 | 518.0035 | 1729.8767 | 3723.2143 | 5618.6184 | 7610.4472 | 10999.3037 | 12152.3749 | 14323.3278 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 |  | 245.2232 | 6.1061 | 237.7967 | 666.3272 | 1199.3612 | 2097.1486 | 2908.6668 | 4034.4559 | 5208.2054 | 6167.3376 | 7072.0323 | 8414.7724 | 9391.038 | 10374.6896 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51
35% | [8 empty] | 260.8444 | 1291.6349 | 3113.9117 | 6839.6111 | 8107.4308 | 10494.4273 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | [5 empty] | 6.0897 | 256.3183 | 767.9228 | 1830.1246 | 3013.7375 | 3980.9297 | 4893.2269 | 6247.2505 | 7231.72 | 8223.6376 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128
30% | [11 empty] | 257.78 | 456.7488 | 964.1965 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | [8 empty] | 68.044 | 794.1592 | 1909.9605 | 3334.2353 | 5630.2335 | 7299.5843 | 8981.5646 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098
25% | FY39: 17.9814; FY40: 17.9814; FY41: 17.9814; FY42: 17.9814; FY43: 17.9814; FY44: 17.9814; FY45: 17.9814; FY46: 17.9814; FY47: 17.9814; FY48: 17.9814; FY49: 17.9814; FY50: 17.9814; FY51: 17.9814; FY52: 17.9814; FY53: 17.9814; FY54: 17.9814 | [11 empty] | 5.1692 | 579.6374 | 1537.8682 | 2907.3948 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 4894.7486 | 2918.9038 | 4546.4136 | 6157.9939 | 8430.2235 | 11149.2101 | 14573.3927 | 19145.5429 | 25354.7011 | 31987.3251 | 39696.4168 | 53695.6017 | 58570.2717 | 67880.9291 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | E @ R (MWh) | 4875.5009 | 3646.6886 | 4849.7207 | 6091.2554 | 7350.5809 | 9633.3116 | 11982.1132 | 15661.0344 | 20228.0154 | 24482.3898 | 28872.2704 | 36136.5914 | 41958.8115 | 48229.1261 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882
Option 1 Summer POE50 W E @ R (MWh) N 2 | 3426.324 | 2043.2327 | 3182.4895 | 4310.5957 | 5901.1564 | 7804.447 | 10201.3749 | 13401.88 | 17748.2908 | 22391.1276 | 27787.4917 | 37586.9212 | 40999.1902 | 47516.6503 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 1462.6503 | 1094.0066 | 1454.9162 | 1827.3766 | 2205.1743 | 2889.9935 | 3594.634 | 4698.3103 | 6068.4046 | 7344.7169 | 8661.6811 | 10840.9774 | 12587.6434 | 14468.7378 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 11.8122 | 9.2886 | 11.5965 | 5.9707 | 8.8268 | 11.3689 | 14.8603 | 18.6767 | 22.5851 | 26.4583 | 29.9005 | 33.6522 | 35.0845 | 39.934 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 | 44.9502 |  | 14.7101 | 12.198 | 14.637 | 9.0475 | 11.8313 | 14.7956 | 17.9129 | 22.3596 | 26.2367 | 29.8934 | 33.6939 | 38.249 | 39.774 | 44.6863 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648 | 49.2648
98% | 5.7007 | 4.4516 | 5.5939 | 2.8093 | 4.223 | 5.4813 | 7.2094 | 9.0984 | 11.033 | 12.9501 | 14.6539 | 16.5109 | 17.2199 | 19.6203 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 | 22.1032 |  | 7.1351 | 5.8917 | 7.0989 | 4.3322 | 5.7101 | 7.1774 | 8.7204 | 10.9214 | 12.8404 | 14.6504 | 16.5316 | 18.7862 | 19.5411 | 21.9725 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388 | 24.2388
97% | 10.9905 | 8.5177 | 10.7792 | 5.2665 | 8.0651 | 10.5561 | 13.9773 | 17.717 | 21.5469 | 25.3422 | 28.7152 | 32.3915 | 33.795 | 38.5471 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 | 43.4624 |  | 13.8302 | 11.3686 | 13.7586 | 8.2814 | 11.0092 | 13.9139 | 16.9686 | 21.326 | 25.125 | 28.7083 | 32.4323 | 36.8959 | 38.3903 | 43.2038 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903 | 47.6903
95% | 15.5614 | 11.9092 | 15.2493 | 7.1074 | 11.2408 | 14.9198 | 19.9727 | 25.4959 | 31.1524 | 36.7578 | 41.7394 | 47.169 | 49.2419 | 56.2603 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 | 63.5199 |  | 19.7554 | 16.1198 | 19.6496 | 11.5602 | 15.5891 | 19.879 | 24.3906 | 30.8261 | 36.437 | 41.7291 | 47.2293 | 53.8217 | 56.0288 | 63.138 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642 | 69.7642
90% | 13.4045 | 9.8855 | 13.1038 | 5.2587 | 9.2415 | 12.7863 | 17.655 | 22.9768 | 28.4271 | 33.8281 | 38.6281 | 43.8598 | 45.8571 | 52.6196 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 | 59.6146 |  | 17.4456 | 13.9426 | 17.3436 | 9.5492 | 13.4312 | 17.5647 | 21.9118 | 28.1126 | 33.519 | 38.6182 | 43.9179 | 50.2699 | 52.3965 | 59.2465 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312 | 65.6312
85% | 123.8793 | 83.9329 | 120.4651 | 31.4132 | 76.6227 | 116.8618 | 172.1273 | 232.5374 | 294.4055 | 355.7143 | 410.2007 | 469.5871 | 492.2591 | 569.0231 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 | 648.4253 |  | 169.7502 | 129.9866 | 168.5932 | 80.1154 | 124.1813 | 171.1029 | 220.4485 | 290.836 | 352.2058 | 410.0885 | 470.2469 | 542.351 | 566.491 | 644.2475 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219 | 716.7219
80% | 222.088 | 125.8361 | 213.8613 | 9.7712 | 108.2221 | 205.1792 | 338.3427 | 483.9023 | 632.9749 | 780.6999 | 911.9862 | 1055.0792 | 1109.7078 | 1294.6726 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 | 1485.9941 |  | 332.6151 | 236.8036 | 329.8273 | 116.6379 | 222.8157 | 335.8744 | 454.7737 | 624.3742 | 772.2462 | 911.7158 | 1056.6689 | 1230.4055 | 1288.5714 | 1475.9276 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564 | 1650.5564
75% | 396.6559 | 116.4694 | 372.6315 |  | 73.6569 | 347.2772 | 736.1532 | 1161.2294 | 1596.5648 | 2027.9646 | 2411.3587 | 2829.2316 | 2988.763 | 3528.9138 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 | 4087.6281 |  | 719.4271 | 439.6298 | 711.2859 | 92.9575 | 398.7809 | 728.9452 | 1076.1656 | 1571.448 | 2003.2772 | 2410.569 | 2833.8739 | 3341.2353 | 3511.0964 | 4058.2309 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975 | 4568.1975
70% | 246.929 |  | 204.178 |  |  | 163.2569 | 977.7406 | 1902.3509 | 2849.2765 | 3787.6416 | 4621.5866 | 5530.5284 | 5877.5354 | 7052.4517 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 | 8267.7467 |  | 941.3587 | 332.8577 | 923.6502 |  | 250.8947 | 962.0621 | 1717.3232 | 2794.6436 | 3733.9425 | 4619.8688 | 5540.6264 | 6644.2202 | 7013.6959 | 8203.8031 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638 | 9313.0638
65% | [6 empty] | 290.0549 | 1260.7851 | 2267.0255 | 3264.1692 | 4150.352 | 5116.2293 | 5484.9726 | 6733.485 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 | 8024.9052 |  | 258.5342 |  | 243.8113 |  |  | 276.2621 | 1064.1674 | 2208.9704 | 3207.1064 | 4148.5266 | 5126.9598 | 6299.6821 | 6692.3014 | 7956.9562 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003 | 9135.7003
60% | [7 empty] | 394.861 | 1420.5251 | 2443.5547 | 3352.7429 | 4343.6945 | 4722.0103 | 6002.9342 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | 7327.8798 | [7 empty] | 234.8153 | 1360.9629 | 2385.0106 | 3350.8701 | 4354.7035 | 5557.8698 | 5960.6815 | 7258.1668 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112 | 8467.5112
55% | [8 empty] | 444.3952 | 1610.1411 | 2670.3777 | 3825.9616 | 4267.1292 | 5760.86 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | 7305.9262 | [8 empty] | 389.9027 | 1541.8707 | 2668.1938 | 3838.7996 | 5241.8546 | 5711.5877 | 7224.6314 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909 | 8634.8909
50% | [9 empty] | 301.7336 | 1303.907 | 2564.8782 | 3046.2795 | 4676.2361 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | 6362.2097 | [9 empty] | 259.0051 | 1301.5239 | 2578.887 | 4109.8982 | 4622.4702 | 6273.5009 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737 | 7812.3737
45% | [10 empty] | 46.1983 | 816.0634 | 1335.3054 | 3317.8173 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | 5368.8521 | [10 empty] | 45.6234 | 829.5208 | 2628.8512 | 3252.4096 | 5260.9353 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177 | 7133.0177
40% | FY38: 970.136; FY39: 3744.413; FY40: 3744.413; FY41: 3744.413; FY42: 3744.413; FY43: 3744.413; FY44: 3744.413; FY45: 3744.413; FY46: 3744.413; FY47: 3744.413; FY48: 3744.413; FY49: 3744.413; FY50: 3744.413; FY51: 3744.413; FY52: 3744.413; FY53: 3744.413; FY54: 3744.413 | [12 empty] | 412.2948 | 907.7552 | 3578.806 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676 | 6451.6676
35% | FY39: 62.0748; FY40: 62.0748; FY41: 62.0748; FY42: 62.0748; FY43: 62.0748; FY44: 62.0748; FY45: 62.0748; FY46: 62.0748; FY47: 62.0748; FY48: 62.0748; FY49: 62.0748; FY50: 62.0748; FY51: 62.0748; FY52: 62.0748; FY53: 62.0748; FY54: 62.0748 | [14 empty] | 44.5933 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338 | 725.3338
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1047.0217 | 370.2909 | 967.4586 | 67.597 | 300.0989 | 887.6874 | 2588.0932 | 5529.6308 | 9619.9121 | 14706.9556 | 20032.3471 | 26724.8365 | 29505.1605 | 40113.511 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | 52919.7055 | E @ R (MWh) | 2494.5618 | 1198.7985 | 2449.6557 | 332.4811 | 1054.2435 | 2547.5773 | 4857.598 | 9354.6834 | 14388.8225 | 20020.5793 | 26804.0918 | 36206.6856 | 39733.191 | 52212.0462 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239 | 64865.6239
Option 2 Winter POE50 W E @ R (MWh) N 2 | 732.9152 | 259.2037 | 677.221 | 47.3179 | 210.0692 | 621.3812 | 1811.6653 | 3870.7416 | 6733.9385 | 10294.8689 | 14022.643 | 18707.3856 | 20653.6123 | 28079.4577 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | 37043.7938 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 748.3685 | 359.6395 | 734.8967 | 99.7443 | 316.273 | 764.2732 | 1457.2794 | 2806.405 | 4316.6468 | 6006.1738 | 8041.2275 | 10862.0057 | 11919.9573 | 15663.6138 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872 | 19459.6872
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.6224 | 20.765 | 22.5879 | 18.6578 | 20.0094 | 22.139 | 24.0639 | 26.7343 | 29.5184 | 31.7935 | 33.9394 | 37.1244 | 39.4401 | 41.7734 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446 | 44.2446
98% | 16.5594 | 14.6718 | 16.2658 | 12.1266 | 13.6225 | 15.1651 | 16.8032 | 18.6774 | 20.8832 | 22.9505 | 25.1229 | 28.8189 | 30.0765 | 32.4443 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 | 34.2558 |  | 44.451 | 40.7735 | 44.3828 | 36.6015 | 39.2776 | 43.4939 | 47.3051 | 52.5921 | 58.1045 | 62.6089 | 66.8577 | 73.1636 | 77.7485 | 82.3681 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608 | 87.2608
97% | 16.2201 | 14.3516 | 15.9295 | 11.8322 | 13.313 | 14.8399 | 16.4614 | 18.3165 | 20.5 | 22.5462 | 24.6966 | 28.3551 | 29.6 | 31.9437 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 | 33.7368 |  | 65.4859 | 60.0257 | 65.3846 | 53.8311 | 57.8045 | 64.0648 | 69.7235 | 77.5736 | 85.7582 | 92.4462 | 98.7547 | 108.1176 | 114.9251 | 121.7841 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487 | 129.0487
95% | 15.7111 | 13.8713 | 15.4249 | 11.3907 | 12.8487 | 14.3521 | 15.9486 | 17.7752 | 19.9251 | 21.9399 | 24.0572 | 27.6594 | 28.8851 | 31.1928 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 | 32.9583 |  | 127.4 | 116.6476 | 127.2006 | 104.449 | 112.2736 | 124.6015 | 135.7448 | 151.2035 | 167.3208 | 180.4911 | 192.9138 | 211.3516 | 224.7572 | 238.2641 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698 | 252.5698
90% | 130.7104 | 114.7563 | 128.2287 | 93.2446 | 105.8883 | 118.9254 | 132.7704 | 148.6105 | 167.2539 | 184.7258 | 203.0864 | 234.3249 | 244.9539 | 264.9657 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 | 280.2764 |  | 178.5986 | 163.058 | 178.3104 | 145.4273 | 156.7362 | 174.5539 | 190.6595 | 213.0021 | 236.2966 | 255.3318 | 273.2866 | 299.9349 | 319.3101 | 338.8319 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081 | 359.5081
85% | 115.4398 | 100.3481 | 113.0923 | 79.9992 | 91.9595 | 104.2919 | 117.3885 | 132.3723 | 150.008 | 166.5354 | 183.9036 | 213.4535 | 223.508 | 242.4381 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 | 256.9211 |  | 303.619 | 275.8513 | 303.104 | 244.349 | 264.5555 | 296.3919 | 325.1692 | 365.0908 | 406.7131 | 440.7249 | 472.8063 | 520.4212 | 555.0405 | 589.9218 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658 | 626.8658
80% | 111.2991 | 95.4888 | 108.8398 | 74.1709 | 86.7007 | 99.6203 | 113.3406 | 129.038 | 147.5135 | 164.8279 | 183.0232 | 213.9802 | 224.5134 | 244.345 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 | 259.5177 |  | 222.2583 | 200.6975 | 221.8584 | 176.2369 | 191.9267 | 216.6467 | 238.9914 | 269.9894 | 302.3079 | 328.717 | 353.6273 | 390.5988 | 417.4797 | 444.564 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499 | 473.2499
75% | 150.9309 | 127.1676 | 147.2345 | 95.1261 | 113.9588 | 133.3774 | 153.9993 | 177.593 | 205.3622 | 231.3863 | 258.7343 | 305.2637 | 321.0955 | 350.9029 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 | 373.7079 |  | 222.2599 | 199.1124 | 221.8307 | 172.8517 | 189.6961 | 216.2354 | 240.2245 | 273.5037 | 308.2006 | 336.5533 | 363.2967 | 402.9892 | 431.8483 | 460.9258 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228 | 491.7228
70% | 355.8769 | 291.9649 | 345.9354 | 205.7888 | 256.4398 | 308.6663 | 364.1294 | 427.5849 | 502.2707 | 572.2629 | 645.8158 | 770.9573 | 813.5371 | 893.7046 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 | 955.0392 |  | 285.7656 | 253.2844 | 285.1632 | 216.4346 | 240.0712 | 277.3118 | 310.9739 | 357.6721 | 406.3597 | 446.145 | 483.6721 | 539.3695 | 579.8654 | 620.6677 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828 | 663.8828
65% | 386.5423 | 303.7538 | 373.6646 | 192.1253 | 257.7362 | 325.388 | 397.2323 | 479.4295 | 576.1739 | 666.8385 | 762.1154 | 924.2177 | 979.3736 | 1083.2187 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 | 1162.6686 |  | 297.6766 | 259.8752 | 296.9755 | 216.9897 | 244.4978 | 287.8381 | 327.0139 | 381.3609 | 438.0232 | 484.325 | 527.9988 | 592.8191 | 639.9479 | 687.4333 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268 | 737.7268
60% | 1120.4925 | 811.4729 | 1072.4245 | 394.8041 | 639.7059 | 892.2253 | 1160.3941 | 1467.2066 | 1828.3186 | 2166.7367 | 2522.3712 | 3127.4404 | 3333.3175 | 3720.934 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 | 4017.4916 |  | 642.9947 | 548.4913 | 641.2421 | 441.2775 | 510.0476 | 618.3985 | 716.3379 | 852.2055 | 993.8613 | 1109.6157 | 1218.8002 | 1380.8509 | 1498.673 | 1617.3866 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203 | 1743.1203
55% | 1447.5067 | 844.7507 | 1353.748 | 117.2753 | 509.7119 | 1002.2618 | 1525.3365 | 2123.7874 | 2828.1516 | 3488.2507 | 4181.9309 | 5362.1441 | 5763.7161 | 6519.7787 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 | 7098.227 |  | 464.401 | 380.678 | 462.8484 | 285.6945 | 346.6198 | 442.6107 | 529.3777 | 649.7463 | 775.2429 | 877.7927 | 974.5221 | 1118.087 | 1222.4687 | 1327.6401 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308 | 1439.0308
50% | 1023.5986 | 186.306 | 855.6256 |  | 8.695 | 344.4274 | 1163.644 | 2240.4845 | 3507.9033 | 4695.6725 | 5943.8668 | 8067.5189 | 8790.0996 | 10150.5434 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 | 11191.3918 |  | 758.1769 | 570.9902 | 754.7055 | 358.6275 | 494.8433 | 709.4583 | 903.4508 | 1172.5693 | 1453.1527 | 1682.4322 | 1898.6984 | 2219.6788 | 2453.0539 | 2688.1947 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406 | 2937.2406
45% | 3.8607 | [5 empty] | 18.9398 | 490.7805 | 1712.4788 | 2988.499 | 4329.434 | 6610.8732 | 7387.1414 | 8848.666 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 | 9966.8493 |  | 994.5681 | 550.3323 | 986.3297 | 136.1681 | 374.4352 | 878.9481 | 1339.3356 | 1978.0141 | 2643.9012 | 3188.0326 | 3701.2806 | 4463.0389 | 5016.8903 | 5574.9319 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736 | 6165.9736
40% | [8 empty] | 79.9695 | 921.7917 | 2658.2677 | 6047.1243 | 7200.1954 | 9371.1484 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 | 11032.1011 |  | 245.2232 | 6.1061 | 237.7967 |  |  | 150.9751 | 649.2239 | 1734.3142 | 2908.0636 | 3867.1959 | 4771.8906 | 6114.6307 | 7090.8963 | 8074.5479 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683 | 9116.3683
35% | [10 empty] | 21.3149 | 1623.2703 | 2681.6525 | 5049.4289 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | 6875.6723 | [8 empty] | 112.7002 | 767.4506 | 1661.4591 | 2573.7563 | 3927.7798 | 4912.2494 | 5904.1669 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421 | 6954.7421
30% | FY38: 69.3195; FY39: 262.7155; FY40: 262.7155; FY41: 262.7155; FY42: 262.7155; FY43: 262.7155; FY44: 262.7155; FY45: 262.7155; FY46: 262.7155; FY47: 262.7155; FY48: 262.7155; FY49: 262.7155; FY50: 262.7155; FY51: 262.7155; FY52: 262.7155; FY53: 262.7155; FY54: 262.7155 | [10 empty] | 28.2782 | 436.7162 | 1837.558 | 3366.4914 | 5048.4717 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169 | 6829.9169
25% | [43 empty] | 6.6993 | 348.3039 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121 | 1225.9121
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 4894.7486 | 2918.9038 | 4546.4136 | 1287.8837 | 2110.5805 | 3373.5407 | 5196.3881 | 7871.6562 | 11766.7123 | 16314.9639 | 21967.7409 | 33585.4019 | 38051.6656 | 46904.9745 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | 53833.5305 | E @ R (MWh) | 4875.5009 | 3646.6886 | 4849.7207 | 2607.5962 | 3242.7944 | 4523.6676 | 6047.5954 | 8668.2721 | 11980.2755 | 15073.943 | 18442.8176 | 24237.514 | 28967.7852 | 34210.1778 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849 | 40278.3849
Option 2 Summer POE50 W E @ R (MWh) N 2 | 3426.324 | 2043.2327 | 3182.4895 | 901.5186 | 1477.4064 | 2361.4785 | 3637.4717 | 5510.1593 | 8236.6986 | 11420.4747 | 15377.4186 | 23509.7813 | 26636.1659 | 32833.4822 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | 37683.4714 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 1462.6503 | 1094.0066 | 1454.9162 | 782.2789 | 972.8383 | 1357.1003 | 1814.2786 | 2600.4816 | 3594.0827 | 4522.1829 | 5532.8453 | 7271.2542 | 8690.3355 | 10263.0533 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155 | 12083.5155
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 11.8122 | 9.2886 | 11.5965 | 14.5464 | 17.4025 | 19.9446 | 23.4359 | 27.2523 | 31.1608 | 35.034 | 38.4761 | 42.2278 | 43.6601 | 48.5097 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 |  | 14.7101 | 12.198 | 14.637 | 17.6231 | 20.407 | 23.3712 | 26.4886 | 30.9353 | 34.8123 | 38.469 | 42.2695 | 46.8247 | 48.3497 | 53.2619 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405
98% | 5.7007 | 4.4516 | 5.5939 | 7.054 | 8.4677 | 9.726 | 11.4541 | 13.3432 | 15.2778 | 17.1949 | 18.8987 | 20.7557 | 21.4646 | 23.865 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 |  | 7.1351 | 5.8917 | 7.0989 | 8.5769 | 9.9549 | 11.4221 | 12.9651 | 15.1661 | 17.0852 | 18.8951 | 20.7763 | 23.031 | 23.7858 | 26.2173 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835
97% | 10.9905 | 8.5177 | 10.7792 | 13.6697 | 16.4684 | 18.9594 | 22.3806 | 26.1203 | 29.9502 | 33.7455 | 37.1185 | 40.7948 | 42.1983 | 46.9504 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 |  | 13.8302 | 11.3686 | 13.7586 | 16.6846 | 19.4125 | 22.3172 | 25.3719 | 29.7293 | 33.5283 | 37.1115 | 40.8356 | 45.2992 | 46.7936 | 51.6071 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936
95% | 15.5614 | 11.9092 | 15.2493 | 19.5184 | 23.6518 | 27.3309 | 32.3837 | 37.9069 | 43.5634 | 49.1688 | 54.1504 | 59.58 | 61.6529 | 68.6713 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 |  | 19.7554 | 16.1198 | 19.6496 | 23.9712 | 28.0001 | 32.29 | 36.8016 | 43.2371 | 48.848 | 54.1401 | 59.6403 | 66.2327 | 68.4398 | 75.549 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752
90% | 13.4045 | 9.8855 | 13.1038 | 17.2173 | 21.2 | 24.7449 | 29.6135 | 34.9353 | 40.3856 | 45.7866 | 50.5866 | 55.8183 | 57.8156 | 64.5781 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 |  | 17.4456 | 13.9426 | 17.3436 | 21.5077 | 25.3897 | 29.5233 | 33.8704 | 40.0712 | 45.4776 | 50.5767 | 55.8764 | 62.2284 | 64.3551 | 71.205 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897
85% | 123.8793 | 83.9329 | 120.4651 | 167.1587 | 212.3681 | 252.6072 | 307.8727 | 368.2828 | 430.1509 | 491.4597 | 545.9461 | 605.3325 | 628.0045 | 704.7685 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 |  | 169.7502 | 129.9866 | 168.5932 | 215.8608 | 259.9267 | 306.8483 | 356.1939 | 426.5814 | 487.9512 | 545.8339 | 605.9923 | 678.0964 | 702.2364 | 779.9929 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673
80% | 222.088 | 125.8361 | 213.8613 | 326.3707 | 435.3039 | 532.261 | 665.4245 | 810.9841 | 960.0568 | 1107.7818 | 1239.0681 | 1382.161 | 1436.7897 | 1621.7545 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 |  | 332.6151 | 236.8036 | 329.8273 | 443.7197 | 549.8975 | 662.9563 | 781.8556 | 951.456 | 1099.328 | 1238.7977 | 1383.7507 | 1557.4874 | 1615.6532 | 1803.0095 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382
75% | 396.6559 | 116.4694 | 372.6315 | 701.1915 | 1019.3082 | 1302.451 | 1691.327 | 2116.4032 | 2551.7386 | 2983.1384 | 3366.5325 | 3784.4054 | 3943.9368 | 4484.0876 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 |  | 719.4271 | 439.6298 | 711.2859 | 1043.8848 | 1353.9548 | 1684.119 | 2031.3394 | 2526.6219 | 2958.451 | 3365.7428 | 3789.0478 | 4296.4091 | 4466.2702 | 5013.4048 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713
70% | 246.929 |  | 204.178 | 901.6933 | 1593.649 | 2209.5309 | 3055.3998 | 3980.0102 | 4926.9358 | 5865.3009 | 6699.2458 | 7608.1877 | 7955.1946 | 9130.111 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 |  | 941.3587 | 332.8577 | 923.6502 | 1647.1071 | 2321.5601 | 3039.7213 | 3794.9824 | 4872.3028 | 5811.6018 | 6697.5281 | 7618.2856 | 8721.8795 | 9091.3551 | 10281.4623 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723
65% |  |  |  | 226.1234 | 932.7463 | 1587.2067 | 2486.0603 | 3468.5876 | 4474.828 | 5471.9717 | 6358.1545 | 7324.0318 | 7692.7751 | 8941.2875 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 |  | 258.5342 |  | 243.8113 | 989.553 | 1706.2533 | 2469.3997 | 3271.9699 | 4416.7729 | 5414.9089 | 6356.3291 | 7334.7623 | 8507.4846 | 8900.1039 | 10164.7587 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028
60% |  |  |  |  | 149.8988 | 723.0581 | 1645.246 | 2653.2798 | 3685.6423 | 4708.672 | 5617.8601 | 6608.8117 | 6987.1276 | 8268.0514 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 |  |  |  |  | 184.3862 | 845.1952 | 1628.1529 | 2451.5579 | 3626.0801 | 4650.1278 | 5615.9873 | 6619.8207 | 7822.987 | 8225.7988 | 9523.2841 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284
55% | [5 empty] | 25.7795 | 679.408 | 1854.709 | 3058.5836 | 4251.5748 | 5311.8114 | 6467.3953 | 6908.5629 | 8402.2937 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | [5 empty] | 63.0524 | 659.9292 | 1619.4738 | 2989.126 | 4183.3044 | 5309.6275 | 6480.2334 | 7883.2883 | 8353.0214 | 9866.0651 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246
50% | [7 empty] | 479.7725 | 1727.5166 | 3029.3066 | 4186.235 | 5447.2062 | 5928.6075 | 7558.5641 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | [7 empty] | 307.8144 | 1651.7246 | 2954.8101 | 4183.852 | 5461.2151 | 6992.2262 | 7504.7982 | 9155.829 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017
45% | [8 empty] | 203.3275 | 1315.0503 | 2721.7171 | 4255.7243 | 4841.3627 | 6824.2511 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | [8 empty] | 167.3292 | 1227.8012 | 2718.8181 | 4272.7665 | 6135.285 | 6758.8434 | 8767.3691 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515
40% | [10 empty] | 474.4529 | 2069.885 | 2934.9379 | 5977.8403 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | [10 empty] | 472.4498 | 2093.2934 | 4920.5663 | 5877.4669 | 8959.7119 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735
35% | [12 empty] | 3.8716 | 560.4187 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | [12 empty] | 265.2858 | 528.0265 | 1908.4996 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332
30% | [45 empty] | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1047.0217 | 370.2909 | 967.4586 | 2394.5434 | 4430.4648 | 6733.6002 | 10650.0061 | 15871.5872 | 22179.118 | 29405.186 | 36720.2539 | 45772.3176 | 49487.9623 | 62726.003 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | E @ R (MWh) | 2494.5618 | 1198.7985 | 2449.6557 | 4612.8752 | 7203.004 | 10570.0505 | 14750.6849 | 21787.1338 | 28968.0357 | 36704.1588 | 45878.566 | 58024.6116 | 62275.2981 | 76501.2272 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131
Option 3 Winter POE50 W E @ R (MWh) N 2 | 732.9152 | 259.2037 | 677.221 | 1676.1804 | 3101.3253 | 4713.5201 | 7455.0043 | 11110.111 | 15525.3826 | 20583.6302 | 25704.1777 | 32040.6223 | 34641.5736 | 43908.2021 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 748.3685 | 359.6395 | 734.8967 | 1383.8626 | 2160.9012 | 3171.0152 | 4425.2055 | 6536.1402 | 8690.4107 | 11011.2476 | 13763.5698 | 17407.3835 | 18682.5894 | 22950.3682 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.6224 | 20.765 | 22.5879 | 24.1137 | 25.4654 | 27.5949 | 29.5198 | 32.1902 | 34.9744 | 37.2495 | 39.3954 | 42.5804 | 44.8961 | 47.2293 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006
98% | 16.5594 | 14.6718 | 16.2658 | 17.5277 | 19.0237 | 20.5662 | 22.2043 | 24.0785 | 26.2844 | 28.3516 | 30.524 | 34.2201 | 35.4777 | 37.8454 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 |  | 44.451 | 40.7735 | 44.3828 | 47.4037 | 50.0798 | 54.2961 | 58.1073 | 63.3944 | 68.9067 | 73.4112 | 77.6599 | 83.9659 | 88.5508 | 93.1703 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631
97% | 16.2201 | 14.3516 | 15.9295 | 17.1785 | 18.6593 | 20.1862 | 21.8077 | 23.6628 | 25.8463 | 27.8925 | 30.0429 | 33.7014 | 34.9463 | 37.29 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 |  | 65.4859 | 60.0257 | 65.3846 | 69.87 | 73.8434 | 80.1037 | 85.7624 | 93.6125 | 101.7971 | 108.4851 | 114.7936 | 124.1565 | 130.964 | 137.823 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876
95% | 15.7111 | 13.8713 | 15.4249 | 16.6548 | 18.1128 | 19.6161 | 21.2127 | 23.0393 | 25.1892 | 27.2039 | 29.3212 | 32.9235 | 34.1492 | 36.4568 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 |  | 127.4 | 116.6476 | 127.2006 | 136.0333 | 143.8578 | 156.1858 | 167.3291 | 182.7878 | 198.9051 | 212.0754 | 224.4981 | 242.9359 | 256.3414 | 269.8484 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541
90% | 130.7104 | 114.7563 | 128.2287 | 138.8937 | 151.5375 | 164.5746 | 178.4195 | 194.2596 | 212.9031 | 230.3749 | 248.7356 | 279.974 | 290.603 | 310.6149 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 |  | 178.5986 | 163.058 | 178.3104 | 191.0765 | 202.3853 | 220.203 | 236.3086 | 258.6513 | 281.9458 | 300.981 | 318.9357 | 345.5841 | 364.9593 | 384.4811 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573
85% | 115.4398 | 100.3481 | 113.0923 | 123.1808 | 135.1411 | 147.4735 | 160.5701 | 175.554 | 193.1897 | 209.7171 | 227.0853 | 256.6352 | 266.6896 | 285.6197 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 |  | 303.619 | 275.8513 | 303.104 | 325.9143 | 346.1208 | 377.9573 | 406.7345 | 446.6561 | 488.2784 | 522.2902 | 554.3716 | 601.9865 | 636.6058 | 671.4871 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311
80% | 111.2991 | 95.4888 | 108.8398 | 119.4088 | 131.9386 | 144.8582 | 158.5785 | 174.2759 | 192.7514 | 210.0658 | 228.2611 | 259.2181 | 269.7513 | 289.5829 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 |  | 222.2583 | 200.6975 | 221.8584 | 239.57 | 255.2597 | 279.9798 | 302.3245 | 333.3224 | 365.6409 | 392.0501 | 416.9603 | 453.9319 | 480.8128 | 507.8971 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583
75% | 150.9309 | 127.1676 | 147.2345 | 163.12 | 181.9528 | 201.3713 | 221.9933 | 245.5869 | 273.3561 | 299.3802 | 326.7283 | 373.2576 | 389.0894 | 418.8968 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 |  | 222.2599 | 199.1124 | 221.8307 | 240.8456 | 257.6901 | 284.2293 | 308.2184 | 341.4976 | 376.1945 | 404.5472 | 431.2907 | 470.9831 | 499.8423 | 528.9197 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167
70% | 355.8769 | 291.9649 | 345.9354 | 388.6595 | 439.3106 | 491.5371 | 547.0002 | 610.4557 | 685.1415 | 755.1337 | 828.6866 | 953.828 | 996.4079 | 1076.5754 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 |  | 285.7656 | 253.2844 | 285.1632 | 311.8455 | 335.482 | 372.7226 | 406.3848 | 453.083 | 501.7706 | 541.5558 | 579.0829 | 634.7803 | 675.2763 | 716.0785 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937
65% | 386.5423 | 303.7538 | 373.6646 | 429.0075 | 494.6183 | 562.2701 | 634.1144 | 716.3116 | 813.056 | 903.7206 | 998.9975 | 1161.0998 | 1216.2557 | 1320.1009 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 |  | 297.6766 | 259.8752 | 296.9755 | 328.0282 | 355.5363 | 398.8766 | 438.0523 | 492.3994 | 549.0617 | 595.3635 | 639.0373 | 703.8576 | 750.9864 | 798.4718 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653
60% | 1120.4925 | 811.4729 | 1072.4245 | 1278.9995 | 1523.9013 | 1776.4207 | 2044.5895 | 2351.402 | 2712.5139 | 3050.9321 | 3406.5666 | 4011.6358 | 4217.5128 | 4605.1294 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 |  | 642.9947 | 548.4913 | 641.2421 | 718.8737 | 787.6439 | 895.9948 | 993.9341 | 1129.8017 | 1271.4575 | 1387.2119 | 1496.3964 | 1658.4471 | 1776.2693 | 1894.9828 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165
55% | 1447.5067 | 844.7507 | 1353.748 | 1756.6813 | 2234.3727 | 2726.9226 | 3249.9973 | 3848.4481 | 4552.8123 | 5212.9114 | 5906.5916 | 7086.8049 | 7488.3769 | 8244.4394 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 |  | 464.401 | 380.678 | 462.8484 | 531.6242 | 592.5495 | 688.5403 | 775.3074 | 895.676 | 1021.1726 | 1123.7224 | 1220.4518 | 1364.0167 | 1468.3984 | 1573.5698 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605
50% | 1023.5986 | 186.306 | 855.6256 | 1579.9211 | 2439.4694 | 3325.7539 | 4266.9641 | 5343.8046 | 6611.2235 | 7798.9926 | 9047.1869 | 11170.839 | 11893.4197 | 13253.8635 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 |  | 758.1769 | 570.9902 | 754.7055 | 908.4736 | 1044.6895 | 1259.3045 | 1453.2969 | 1722.4155 | 2002.9989 | 2232.2783 | 2448.5445 | 2769.5249 | 3002.9001 | 3238.0408 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867
45% | 3.8607 |  |  | 128.7608 | 642.1854 | 1516.7957 | 2527.9377 | 3684.7872 | 5046.3752 | 6322.3953 | 7663.3303 | 9944.7695 | 10721.0378 | 12182.5623 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 |  | 994.5681 | 550.3323 | 986.3297 | 1351.2559 | 1674.5265 | 2183.8559 | 2644.2434 | 3282.9219 | 3948.8091 | 4492.9405 | 5006.1885 | 5767.9468 | 6321.7982 | 6879.8398 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814
40% | [5 empty] | 30.864 | 518.0035 | 1729.8767 | 3723.2143 | 5618.6184 | 7610.4472 | 10999.3037 | 12152.3749 | 14323.3278 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 |  | 245.2232 | 6.1061 | 237.7967 | 666.3272 | 1199.3612 | 2097.1486 | 2908.6668 | 4034.4559 | 5208.2054 | 6167.3376 | 7072.0323 | 8414.7724 | 9391.038 | 10374.6896 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51
35% | [8 empty] | 260.8444 | 1291.6349 | 3113.9117 | 6839.6111 | 8107.4308 | 10494.4273 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | [5 empty] | 6.0897 | 256.3183 | 767.9228 | 1830.1246 | 3013.7375 | 3980.9297 | 4893.2269 | 6247.2505 | 7231.72 | 8223.6376 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128
30% | [11 empty] | 257.78 | 456.7488 | 964.1965 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | [8 empty] | 68.044 | 794.1592 | 1909.9605 | 3334.2353 | 5630.2335 | 7299.5843 | 8981.5646 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098
25% | FY39: 17.9814; FY40: 17.9814; FY41: 17.9814; FY42: 17.9814; FY43: 17.9814; FY44: 17.9814; FY45: 17.9814; FY46: 17.9814; FY47: 17.9814; FY48: 17.9814; FY49: 17.9814; FY50: 17.9814; FY51: 17.9814; FY52: 17.9814; FY53: 17.9814; FY54: 17.9814 | [11 empty] | 5.1692 | 579.6374 | 1537.8682 | 2907.3948 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 4894.7486 | 2918.9038 | 4546.4136 | 6157.9939 | 8430.2235 | 11149.2101 | 14573.3927 | 19145.5429 | 25354.7011 | 31987.3251 | 39696.4168 | 53695.6017 | 58570.2717 | 67880.9291 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | E @ R (MWh) | 4875.5009 | 3646.6886 | 4849.7207 | 6091.2554 | 7350.5809 | 9633.3116 | 11982.1132 | 15661.0344 | 20228.0154 | 24482.3898 | 28872.2704 | 36136.5914 | 41958.8115 | 48229.1261 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882
Option 3 Summer POE50 W E @ R (MWh) N 2 | 3426.324 | 2043.2327 | 3182.4895 | 4310.5957 | 5901.1564 | 7804.447 | 10201.3749 | 13401.88 | 17748.2908 | 22391.1276 | 27787.4917 | 37586.9212 | 40999.1902 | 47516.6503 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 1462.6503 | 1094.0066 | 1454.9162 | 1827.3766 | 2205.1743 | 2889.9935 | 3594.634 | 4698.3103 | 6068.4046 | 7344.7169 | 8661.6811 | 10840.9774 | 12587.6434 | 14468.7378 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 11.8122 | 9.2886 | 11.5965 | 3.1122 | 5.9682 | 8.5103 | 12.0017 | 15.8181 | 19.7266 | 23.5998 | 27.0419 | 30.7936 | 32.2259 | 37.0755 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 | 42.0917 |  | 14.7101 | 12.198 | 14.637 | 6.1889 | 8.9727 | 11.937 | 15.0544 | 19.5011 | 23.3781 | 27.0348 | 30.8353 | 35.3905 | 36.9155 | 41.8277 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063 | 46.4063
98% | 5.7007 | 4.4516 | 5.5939 | 1.3944 | 2.8081 | 4.0663 | 5.7945 | 7.6835 | 9.6181 | 11.5352 | 13.239 | 15.096 | 15.805 | 18.2054 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 | 20.6883 |  | 7.1351 | 5.8917 | 7.0989 | 2.9173 | 4.2952 | 5.7625 | 7.3055 | 9.5065 | 11.4255 | 13.2355 | 15.1166 | 17.3713 | 18.1262 | 20.5576 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239 | 22.8239
97% | 10.9905 | 8.5177 | 10.7792 | 2.4654 | 5.264 | 7.755 | 11.1762 | 14.9159 | 18.7458 | 22.5411 | 25.9141 | 29.5904 | 30.9939 | 35.746 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 | 40.6613 |  | 13.8302 | 11.3686 | 13.7586 | 5.4803 | 8.2081 | 11.1128 | 14.1675 | 18.5249 | 22.324 | 25.9072 | 29.6313 | 34.0948 | 35.5892 | 40.4027 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892 | 44.8892
95% | 15.5614 | 11.9092 | 15.2493 | 2.9704 | 7.1038 | 10.7828 | 15.8357 | 21.3589 | 27.0154 | 32.6208 | 37.6024 | 43.032 | 45.1049 | 52.1233 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 | 59.3829 |  | 19.7554 | 16.1198 | 19.6496 | 7.4232 | 11.452 | 15.742 | 20.2536 | 26.6891 | 32.3 | 37.5921 | 43.0923 | 49.6847 | 51.8918 | 59.001 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272 | 65.6272
90% | 13.4045 | 9.8855 | 13.1038 | 1.2726 | 5.2553 | 8.8002 | 13.6688 | 18.9906 | 24.4409 | 29.8419 | 34.6419 | 39.8736 | 41.8709 | 48.6334 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 | 55.6284 |  | 17.4456 | 13.9426 | 17.3436 | 5.563 | 9.445 | 13.5785 | 17.9257 | 24.1265 | 29.5329 | 34.632 | 39.9317 | 46.2837 | 48.4104 | 55.2603 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645 | 61.645
85% | 123.8793 | 83.9329 | 120.4651 | 0.0088486 | 31.3742 | 71.6133 | 126.8788 | 187.2889 | 249.157 | 310.4658 | 364.9522 | 424.3386 | 447.0106 | 523.7746 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 | 603.1768 |  | 169.7502 | 129.9866 | 168.5932 | 34.8669 | 78.9328 | 125.8544 | 175.2 | 245.5875 | 306.9573 | 364.84 | 424.9984 | 497.1025 | 521.2425 | 598.999 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734 | 671.4734
80% | 222.088 | 125.8361 | 213.8613 |  | 9.7244 | 96.1519 | 229.3154 | 374.875 | 523.9476 | 671.6726 | 802.959 | 946.0519 | 1000.6805 | 1185.6453 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 | 1376.9668 |  | 332.6151 | 236.8036 | 329.8273 | 14.3474 | 113.7884 | 226.8471 | 345.7464 | 515.3469 | 663.2189 | 802.6885 | 947.6416 | 1121.3782 | 1179.5441 | 1366.9003 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291 | 1541.5291
75% | 396.6559 | 116.4694 | 372.6315 |  |  | 49.7406 | 417.7619 | 842.8381 | 1278.1735 | 1709.5733 | 2092.9674 | 2510.8403 | 2670.3717 | 3210.5225 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 | 3769.2368 |  | 719.4271 | 439.6298 | 711.2859 |  | 86.184 | 410.5539 | 757.7743 | 1253.0568 | 1684.8859 | 2092.1777 | 2515.4827 | 3022.844 | 3192.7051 | 3739.8397 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062 | 4249.8062
70% | 246.929 |  | 204.178 |  |  |  | 287.6306 | 1209.7978 | 2156.7234 | 3095.0885 | 3929.0335 | 4837.9753 | 5184.9823 | 6359.8987 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 | 7575.1936 |  | 941.3587 | 332.8577 | 923.6502 |  |  | 273.4026 | 1024.7701 | 2102.0905 | 3041.3894 | 3927.3157 | 4848.0733 | 5951.6672 | 6321.1428 | 7511.25 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107 | 8620.5107
65% | [7 empty] | 524.8509 | 1531.0914 | 2528.2351 | 3414.4178 | 4380.2952 | 4749.0384 | 5997.5508 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 | 7288.9711 |  | 258.5342 |  | 243.8113 |  |  |  | 333.3137 | 1473.0363 | 2471.1723 | 3412.5924 | 4391.0256 | 5563.7479 | 5956.3673 | 7221.022 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661 | 8399.7661
60% | [7 empty] | 6.0741 | 665.486 | 1688.5157 | 2597.7038 | 3588.6554 | 3966.9712 | 5247.8951 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | 6572.8408 | [8 empty] | 605.9238 | 1629.9715 | 2595.831 | 3599.6644 | 4802.8307 | 5205.6425 | 6503.1277 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721 | 7712.4721
55% | [8 empty] | 13.8264 | 729.6632 | 1789.8998 | 2945.4837 | 3386.6512 | 4880.3821 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | 6425.4483 | [8 empty] | 5.3179 | 661.9893 | 1787.7159 | 2958.3217 | 4361.3767 | 4831.1098 | 6344.1535 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413 | 7754.413
50% | [9 empty] | 0.25149 | 428.8454 | 1604.1022 | 2085.5035 | 3715.4601 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | 5401.4337 | [10 empty] | 427.1759 | 1618.111 | 3149.1222 | 3661.6942 | 5312.7249 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977 | 6851.5977
45% | [11 empty] | 146.4421 | 418.0412 | 2149.006 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | 4200.0408 | [11 empty] | 152.4469 | 1460.04 | 2083.5983 | 4092.1241 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064 | 5964.2064
40% | FY38: 158.6181; FY39: 1994.2272; FY40: 1994.2272; FY41: 1994.2272; FY42: 1994.2272; FY43: 1994.2272; FY44: 1994.2272; FY45: 1994.2272; FY46: 1994.2272; FY47: 1994.2272; FY48: 1994.2272; FY49: 1994.2272; FY50: 1994.2272; FY51: 1994.2272; FY52: 1994.2272; FY53: 1994.2272; FY54: 1994.2272 | [12 empty] | 1.6441 | 133.0063 | 1851.2252 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323 | 4658.0323
35% | [45 empty] | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845 | 208.1845
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1047.0217 | 370.2909 | 967.4586 | 11.2237 | 67.4981 | 257.4205 | 1120.0635 | 3224.4919 | 6517.9522 | 10853.6044 | 15559.2182 | 21542.5702 | 24075.2513 | 33620.5369 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | 45425.9885 | E @ R (MWh) | 2494.5618 | 1198.7985 | 2449.6557 | 76.7869 | 321.2784 | 1094.7909 | 2711.5112 | 6298.7075 | 10578.545 | 15548.7389 | 21614.3729 | 30114.5786 | 33276.9858 | 44758.4158 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831 | 56873.3831
Option 4 Winter POE50 W E @ R (MWh) N 2 | 732.9152 | 259.2037 | 677.221 | 7.8566 | 47.2486 | 180.1944 | 784.0445 | 2257.1443 | 4562.5666 | 7597.5231 | 10891.4528 | 15079.7992 | 16852.6759 | 23534.3758 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | 31798.192 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 748.3685 | 359.6395 | 734.8967 | 23.0361 | 96.3835 | 328.4373 | 813.4533 | 1889.6123 | 3173.5635 | 4664.6217 | 6484.3119 | 9034.3736 | 9983.0957 | 13427.5248 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149 | 17062.0149
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.6224 | 20.765 | 22.5879 | 16.8391 | 18.1907 | 20.3203 | 22.2452 | 24.9156 | 27.6998 | 29.9748 | 32.1208 | 35.3058 | 37.6215 | 39.9547 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259 | 42.4259
98% | 16.5594 | 14.6718 | 16.2658 | 10.3262 | 11.8222 | 13.3647 | 15.0028 | 16.877 | 19.0828 | 21.1501 | 23.3225 | 27.0186 | 28.2762 | 30.6439 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 |  | 44.451 | 40.7735 | 44.3828 | 33.0007 | 35.6768 | 39.8931 | 43.7043 | 48.9914 | 54.5037 | 59.0081 | 63.2569 | 69.5629 | 74.1478 | 78.7673 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601 | 83.6601
97% | 16.2201 | 14.3516 | 15.9295 | 10.0501 | 11.5309 | 13.0578 | 14.6793 | 16.5344 | 18.7179 | 20.7641 | 22.9145 | 26.573 | 27.8179 | 30.1616 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 | 31.9547 |  | 65.4859 | 60.0257 | 65.3846 | 48.4848 | 52.4582 | 58.7185 | 64.3772 | 72.2273 | 80.4119 | 87.0999 | 93.4084 | 102.7713 | 109.5788 | 116.4378 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024 | 123.7024
95% | 15.7111 | 13.8713 | 15.4249 | 9.636 | 11.094 | 12.5974 | 14.194 | 16.0206 | 18.1704 | 20.1852 | 22.3025 | 25.9047 | 27.1304 | 29.4381 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 | 31.2037 |  | 127.4 | 116.6476 | 127.2006 | 93.9209 | 101.7455 | 114.0734 | 125.2167 | 140.6754 | 156.7927 | 169.963 | 182.3857 | 200.8235 | 214.2291 | 227.736 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417 | 242.0417
90% | 130.7104 | 114.7563 | 128.2287 | 78.0282 | 90.672 | 103.709 | 117.554 | 133.3941 | 152.0375 | 169.5094 | 187.87 | 219.1085 | 229.7375 | 249.7493 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 | 265.06 |  | 178.5986 | 163.058 | 178.3104 | 130.2109 | 141.5198 | 159.3375 | 175.4431 | 197.7857 | 221.0803 | 240.1154 | 258.0702 | 284.7185 | 304.0937 | 323.6155 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917 | 344.2917
85% | 115.4398 | 100.3481 | 113.0923 | 65.6053 | 77.5656 | 89.898 | 102.9946 | 117.9785 | 135.6142 | 152.1416 | 169.5098 | 199.0596 | 209.1141 | 228.0442 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 | 242.5273 |  | 303.619 | 275.8513 | 303.104 | 217.1605 | 237.3671 | 269.2035 | 297.9808 | 337.9024 | 379.5247 | 413.5365 | 445.6178 | 493.2327 | 527.8521 | 562.7333 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773 | 599.6773
80% | 111.2991 | 95.4888 | 108.8398 | 59.0916 | 71.6214 | 84.541 | 98.2613 | 113.9587 | 132.4342 | 149.7486 | 167.9439 | 198.9009 | 209.4341 | 229.2657 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 | 244.4384 |  | 222.2583 | 200.6975 | 221.8584 | 155.1259 | 170.8157 | 195.5357 | 217.8804 | 248.8783 | 281.1968 | 307.606 | 332.5162 | 369.4878 | 396.3687 | 423.453 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389 | 452.1389
75% | 150.9309 | 127.1676 | 147.2345 | 72.4614 | 91.2942 | 110.7127 | 131.3347 | 154.9283 | 182.6976 | 208.7217 | 236.0697 | 282.599 | 298.4308 | 328.2382 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 | 351.0433 |  | 222.2599 | 199.1124 | 221.8307 | 150.187 | 167.0315 | 193.5707 | 217.5598 | 250.839 | 285.536 | 313.8886 | 340.6321 | 380.3245 | 409.1837 | 438.2612 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582 | 469.0582
70% | 355.8769 | 291.9649 | 345.9354 | 144.8318 | 195.4828 | 247.7093 | 303.1725 | 366.6279 | 441.3137 | 511.306 | 584.8589 | 710.0003 | 752.5802 | 832.7477 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 | 894.0822 |  | 285.7656 | 253.2844 | 285.1632 | 184.631 | 208.2676 | 245.5082 | 279.1703 | 325.8685 | 374.5561 | 414.3413 | 451.8685 | 507.5659 | 548.0618 | 588.8641 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792 | 632.0792
65% | 386.5423 | 303.7538 | 373.6646 | 113.1646 | 178.7755 | 246.4273 | 318.2716 | 400.4688 | 497.2132 | 587.8778 | 683.1547 | 845.257 | 900.4129 | 1004.258 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 | 1083.7079 |  | 297.6766 | 259.8752 | 296.9755 | 179.9769 | 207.4849 | 250.8253 | 290.001 | 344.3481 | 401.0104 | 447.3122 | 490.986 | 555.8062 | 602.9351 | 650.4205 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714 | 700.714
60% | 1120.4925 | 811.4729 | 1072.4245 | 108.6119 | 344.9741 | 597.4935 | 865.6624 | 1172.4748 | 1533.5868 | 1872.0049 | 2227.6394 | 2832.7086 | 3038.5857 | 3426.2022 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 | 3722.7599 |  | 642.9947 | 548.4913 | 641.2421 | 348.7454 | 417.5156 | 525.8665 | 623.8058 | 759.6734 | 901.3292 | 1017.0836 | 1126.2681 | 1288.3188 | 1406.141 | 1524.8545 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882 | 1650.5882
55% | 1447.5067 | 844.7507 | 1353.748 |  | 69.6505 | 427.3749 | 950.4496 | 1548.9004 | 2253.2647 | 2913.3637 | 3607.044 | 4787.2572 | 5188.8292 | 5944.8917 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 | 6523.3401 |  | 464.401 | 380.678 | 462.8484 | 203.718 | 264.6432 | 360.6341 | 447.4011 | 567.7698 | 693.2663 | 795.8161 | 892.5455 | 1036.1104 | 1140.4921 | 1245.6635 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543 | 1357.0543
50% | 1023.5986 | 186.306 | 855.6256 |  |  | 0.069111 | 287.3751 | 1206.0444 | 2473.4633 | 3661.2324 | 4909.4267 | 7033.0789 | 7755.6595 | 9116.1033 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 | 10156.9517 |  | 758.1769 | 570.9902 | 754.7055 | 175.3454 | 311.5613 | 526.1763 | 720.1688 | 989.2873 | 1269.8707 | 1499.1501 | 1715.4163 | 2036.3967 | 2269.7719 | 2504.9126 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585 | 2753.9585
45% | 3.8607 | [6 empty] | 25.7182 | 669.9272 | 1877.2002 | 3218.1352 | 5499.5744 | 6275.8427 | 7737.3672 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 | 8855.5505 |  | 994.5681 | 550.3323 | 986.3297 | 0.74921 | 80.0675 | 444.2895 | 904.3663 | 1543.0448 | 2208.932 | 2753.0633 | 3266.3114 | 4028.0697 | 4581.921 | 5139.9626 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043 | 5731.0043
40% | [9 empty] | 138.5758 | 1162.7385 | 4396.3978 | 5549.4689 | 7720.4219 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 | 9381.3746 |  | 245.2232 | 6.1061 | 237.7967 |  |  |  | 169.8361 | 968.7339 | 2141.3497 | 3100.482 | 4005.1767 | 5347.9168 | 6324.1824 | 7307.834 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543 | 8349.6543
35% | [11 empty] | 542.1382 | 1241.3747 | 3234.4294 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | 5060.6728 | [9 empty] | 277.5552 | 924.6362 | 1800.5994 | 3154.623 | 4139.0925 | 5131.0101 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852 | 6181.5852
30% | FY38: 0.040882; FY39: 70.1445; FY40: 70.1445; FY41: 70.1445; FY42: 70.1445; FY43: 70.1445; FY44: 70.1445; FY45: 70.1445; FY46: 70.1445; FY47: 70.1445; FY48: 70.1445; FY49: 70.1445; FY50: 70.1445; FY51: 70.1445; FY52: 70.1445; FY53: 70.1445; FY54: 70.1445 | [11 empty] | 59.8686 | 929.2 | 2132.6713 | 3737.4408 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859 | 5518.8859
25% | [44 empty] | 38.3116 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086 | 531.086
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 4894.7486 | 2918.9038 | 4546.4136 | 671.8072 | 1154.4833 | 1946.9547 | 3218.9517 | 5289.9262 | 8527.5234 | 12303.7814 | 17222.9302 | 27625.5768 | 31732.6947 | 40142.0034 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | 46947.267 | E @ R (MWh) | 4875.5009 | 3646.6886 | 4849.7207 | 1938.0959 | 2414.3453 | 3403.9526 | 4599.1569 | 6820.941 | 9754.6155 | 12573.0773 | 15557.0486 | 20820.2345 | 25218.3443 | 30080.233 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064 | 35763.6064
Option 4 Summer POE50 W E @ R (MWh) N 2 | 3426.324 | 2043.2327 | 3182.4895 | 470.265 | 808.1383 | 1362.8683 | 2253.2662 | 3702.9483 | 5969.2664 | 8612.647 | 12056.0512 | 19337.9038 | 22212.8863 | 28099.4024 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | 32863.0869 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 1462.6503 | 1094.0066 | 1454.9162 | 581.4288 | 724.3036 | 1021.1858 | 1379.7471 | 2046.2823 | 2926.3846 | 3771.9232 | 4667.1146 | 6246.0704 | 7565.5033 | 9024.0699 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819 | 10729.0819
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 11.8122 | 9.2886 | 11.5965 | 14.5464 | 17.4025 | 19.9446 | 23.4359 | 27.2523 | 31.1608 | 35.034 | 38.4761 | 42.2278 | 43.6601 | 48.5097 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 |  | 14.7101 | 12.198 | 14.637 | 17.6231 | 20.407 | 23.3712 | 26.4886 | 30.9353 | 34.8123 | 38.469 | 42.2695 | 46.8247 | 48.3497 | 53.2619 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405
98% | 5.7007 | 4.4516 | 5.5939 | 7.054 | 8.4677 | 9.726 | 11.4541 | 13.3432 | 15.2778 | 17.1949 | 18.8987 | 20.7557 | 21.4646 | 23.865 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 |  | 7.1351 | 5.8917 | 7.0989 | 8.5769 | 9.9549 | 11.4221 | 12.9651 | 15.1661 | 17.0852 | 18.8951 | 20.7763 | 23.031 | 23.7858 | 26.2173 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835
97% | 10.9905 | 8.5177 | 10.7792 | 13.6697 | 16.4684 | 18.9594 | 22.3806 | 26.1203 | 29.9502 | 33.7455 | 37.1185 | 40.7948 | 42.1983 | 46.9504 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 |  | 13.8302 | 11.3686 | 13.7586 | 16.6846 | 19.4125 | 22.3172 | 25.3719 | 29.7293 | 33.5283 | 37.1115 | 40.8356 | 45.2992 | 46.7936 | 51.6071 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936
95% | 15.5614 | 11.9092 | 15.2493 | 19.5184 | 23.6518 | 27.3309 | 32.3837 | 37.9069 | 43.5634 | 49.1688 | 54.1504 | 59.58 | 61.6529 | 68.6713 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 |  | 19.7554 | 16.1198 | 19.6496 | 23.9712 | 28.0001 | 32.29 | 36.8016 | 43.2371 | 48.848 | 54.1401 | 59.6403 | 66.2327 | 68.4398 | 75.549 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752
90% | 13.4045 | 9.8855 | 13.1038 | 17.2173 | 21.2 | 24.7449 | 29.6135 | 34.9353 | 40.3856 | 45.7866 | 50.5866 | 55.8183 | 57.8156 | 64.5781 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 |  | 17.4456 | 13.9426 | 17.3436 | 21.5077 | 25.3897 | 29.5233 | 33.8704 | 40.0712 | 45.4776 | 50.5767 | 55.8764 | 62.2284 | 64.3551 | 71.205 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897
85% | 123.8793 | 83.9329 | 120.4651 | 167.1587 | 212.3681 | 252.6072 | 307.8727 | 368.2828 | 430.1509 | 491.4597 | 545.9461 | 605.3325 | 628.0045 | 704.7685 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 |  | 169.7502 | 129.9866 | 168.5932 | 215.8608 | 259.9267 | 306.8483 | 356.1939 | 426.5814 | 487.9512 | 545.8339 | 605.9923 | 678.0964 | 702.2364 | 779.9929 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673
80% | 222.088 | 125.8361 | 213.8613 | 326.3707 | 435.3039 | 532.261 | 665.4245 | 810.9841 | 960.0568 | 1107.7818 | 1239.0681 | 1382.161 | 1436.7897 | 1621.7545 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 |  | 332.6151 | 236.8036 | 329.8273 | 443.7197 | 549.8975 | 662.9563 | 781.8556 | 951.456 | 1099.328 | 1238.7977 | 1383.7507 | 1557.4874 | 1615.6532 | 1803.0095 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382
75% | 396.6559 | 116.4694 | 372.6315 | 701.1915 | 1019.3082 | 1302.451 | 1691.327 | 2116.4032 | 2551.7386 | 2983.1384 | 3366.5325 | 3784.4054 | 3943.9368 | 4484.0876 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 |  | 719.4271 | 439.6298 | 711.2859 | 1043.8848 | 1353.9548 | 1684.119 | 2031.3394 | 2526.6219 | 2958.451 | 3365.7428 | 3789.0478 | 4296.4091 | 4466.2702 | 5013.4048 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713
70% | 246.929 |  | 204.178 | 901.6933 | 1593.649 | 2209.5309 | 3055.3998 | 3980.0102 | 4926.9358 | 5865.3009 | 6699.2458 | 7608.1877 | 7955.1946 | 9130.111 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 |  | 941.3587 | 332.8577 | 923.6502 | 1647.1071 | 2321.5601 | 3039.7213 | 3794.9824 | 4872.3028 | 5811.6018 | 6697.5281 | 7618.2856 | 8721.8795 | 9091.3551 | 10281.4623 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723
65% |  |  |  | 226.1234 | 932.7463 | 1587.2067 | 2486.0603 | 3468.5876 | 4474.828 | 5471.9717 | 6358.1545 | 7324.0318 | 7692.7751 | 8941.2875 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 |  | 258.5342 |  | 243.8113 | 989.553 | 1706.2533 | 2469.3997 | 3271.9699 | 4416.7729 | 5414.9089 | 6356.3291 | 7334.7623 | 8507.4846 | 8900.1039 | 10164.7587 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028
60% |  |  |  |  | 149.8988 | 723.0581 | 1645.246 | 2653.2798 | 3685.6423 | 4708.672 | 5617.8601 | 6608.8117 | 6987.1276 | 8268.0514 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 |  |  |  |  | 184.3862 | 845.1952 | 1628.1529 | 2451.5579 | 3626.0801 | 4650.1278 | 5615.9873 | 6619.8207 | 7822.987 | 8225.7988 | 9523.2841 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284
55% | [5 empty] | 25.7795 | 679.408 | 1854.709 | 3058.5836 | 4251.5748 | 5311.8114 | 6467.3953 | 6908.5629 | 8402.2937 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | [5 empty] | 63.0524 | 659.9292 | 1619.4738 | 2989.126 | 4183.3044 | 5309.6275 | 6480.2334 | 7883.2883 | 8353.0214 | 9866.0651 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246
50% | [7 empty] | 479.7725 | 1727.5166 | 3029.3066 | 4186.235 | 5447.2062 | 5928.6075 | 7558.5641 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | [7 empty] | 307.8144 | 1651.7246 | 2954.8101 | 4183.852 | 5461.2151 | 6992.2262 | 7504.7982 | 9155.829 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017
45% | [8 empty] | 203.3275 | 1315.0503 | 2721.7171 | 4255.7243 | 4841.3627 | 6824.2511 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | [8 empty] | 167.3292 | 1227.8012 | 2718.8181 | 4272.7665 | 6135.285 | 6758.8434 | 8767.3691 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515
40% | [10 empty] | 474.4529 | 2069.885 | 2934.9379 | 5977.8403 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | [10 empty] | 472.4498 | 2093.2934 | 4920.5663 | 5877.4669 | 8959.7119 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735
35% | [12 empty] | 3.8716 | 560.4187 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | [12 empty] | 265.2858 | 528.0265 | 1908.4996 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332
30% | [45 empty] | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1047.0217 | 370.2909 | 967.4586 | 2394.5434 | 4430.4648 | 6733.6002 | 10650.0061 | 15871.5872 | 22179.118 | 29405.186 | 36720.2539 | 45772.3176 | 49487.9623 | 62726.003 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | E @ R (MWh) | 2494.5618 | 1198.7985 | 2449.6557 | 4612.8752 | 7203.004 | 10570.0505 | 14750.6849 | 21787.1338 | 28968.0357 | 36704.1588 | 45878.566 | 58024.6116 | 62275.2981 | 76501.2272 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131
Option 5 Winter POE50 W E @ R (MWh) N 2 | 732.9152 | 259.2037 | 677.221 | 1676.1804 | 3101.3253 | 4713.5201 | 7455.0043 | 11110.111 | 15525.3826 | 20583.6302 | 25704.1777 | 32040.6223 | 34641.5736 | 43908.2021 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 748.3685 | 359.6395 | 734.8967 | 1383.8626 | 2160.9012 | 3171.0152 | 4425.2055 | 6536.1402 | 8690.4107 | 11011.2476 | 13763.5698 | 17407.3835 | 18682.5894 | 22950.3682 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.6224 | 20.765 | 22.5879 | 24.1137 | 25.4654 | 27.5949 | 29.5198 | 32.1902 | 34.9744 | 37.2495 | 39.3954 | 42.5804 | 44.8961 | 47.2293 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006
98% | 16.5594 | 14.6718 | 16.2658 | 17.5277 | 19.0237 | 20.5662 | 22.2043 | 24.0785 | 26.2844 | 28.3516 | 30.524 | 34.2201 | 35.4777 | 37.8454 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 |  | 44.451 | 40.7735 | 44.3828 | 47.4037 | 50.0798 | 54.2961 | 58.1073 | 63.3944 | 68.9067 | 73.4112 | 77.6599 | 83.9659 | 88.5508 | 93.1703 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631
97% | 16.2201 | 14.3516 | 15.9295 | 17.1785 | 18.6593 | 20.1862 | 21.8077 | 23.6628 | 25.8463 | 27.8925 | 30.0429 | 33.7014 | 34.9463 | 37.29 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 |  | 65.4859 | 60.0257 | 65.3846 | 69.87 | 73.8434 | 80.1037 | 85.7624 | 93.6125 | 101.7971 | 108.4851 | 114.7936 | 124.1565 | 130.964 | 137.823 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876
95% | 15.7111 | 13.8713 | 15.4249 | 16.6548 | 18.1128 | 19.6161 | 21.2127 | 23.0393 | 25.1892 | 27.2039 | 29.3212 | 32.9235 | 34.1492 | 36.4568 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 |  | 127.4 | 116.6476 | 127.2006 | 136.0333 | 143.8578 | 156.1858 | 167.3291 | 182.7878 | 198.9051 | 212.0754 | 224.4981 | 242.9359 | 256.3414 | 269.8484 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541
90% | 130.7104 | 114.7563 | 128.2287 | 138.8937 | 151.5375 | 164.5746 | 178.4195 | 194.2596 | 212.9031 | 230.3749 | 248.7356 | 279.974 | 290.603 | 310.6149 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 |  | 178.5986 | 163.058 | 178.3104 | 191.0765 | 202.3853 | 220.203 | 236.3086 | 258.6513 | 281.9458 | 300.981 | 318.9357 | 345.5841 | 364.9593 | 384.4811 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573
85% | 115.4398 | 100.3481 | 113.0923 | 123.1808 | 135.1411 | 147.4735 | 160.5701 | 175.554 | 193.1897 | 209.7171 | 227.0853 | 256.6352 | 266.6896 | 285.6197 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 |  | 303.619 | 275.8513 | 303.104 | 325.9143 | 346.1208 | 377.9573 | 406.7345 | 446.6561 | 488.2784 | 522.2902 | 554.3716 | 601.9865 | 636.6058 | 671.4871 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311
80% | 111.2991 | 95.4888 | 108.8398 | 119.4088 | 131.9386 | 144.8582 | 158.5785 | 174.2759 | 192.7514 | 210.0658 | 228.2611 | 259.2181 | 269.7513 | 289.5829 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 |  | 222.2583 | 200.6975 | 221.8584 | 239.57 | 255.2597 | 279.9798 | 302.3245 | 333.3224 | 365.6409 | 392.0501 | 416.9603 | 453.9319 | 480.8128 | 507.8971 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583
75% | 150.9309 | 127.1676 | 147.2345 | 163.12 | 181.9528 | 201.3713 | 221.9933 | 245.5869 | 273.3561 | 299.3802 | 326.7283 | 373.2576 | 389.0894 | 418.8968 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 |  | 222.2599 | 199.1124 | 221.8307 | 240.8456 | 257.6901 | 284.2293 | 308.2184 | 341.4976 | 376.1945 | 404.5472 | 431.2907 | 470.9831 | 499.8423 | 528.9197 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167
70% | 355.8769 | 291.9649 | 345.9354 | 388.6595 | 439.3106 | 491.5371 | 547.0002 | 610.4557 | 685.1415 | 755.1337 | 828.6866 | 953.828 | 996.4079 | 1076.5754 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 |  | 285.7656 | 253.2844 | 285.1632 | 311.8455 | 335.482 | 372.7226 | 406.3848 | 453.083 | 501.7706 | 541.5558 | 579.0829 | 634.7803 | 675.2763 | 716.0785 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937
65% | 386.5423 | 303.7538 | 373.6646 | 429.0075 | 494.6183 | 562.2701 | 634.1144 | 716.3116 | 813.056 | 903.7206 | 998.9975 | 1161.0998 | 1216.2557 | 1320.1009 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 |  | 297.6766 | 259.8752 | 296.9755 | 328.0282 | 355.5363 | 398.8766 | 438.0523 | 492.3994 | 549.0617 | 595.3635 | 639.0373 | 703.8576 | 750.9864 | 798.4718 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653
60% | 1120.4925 | 811.4729 | 1072.4245 | 1278.9995 | 1523.9013 | 1776.4207 | 2044.5895 | 2351.402 | 2712.5139 | 3050.9321 | 3406.5666 | 4011.6358 | 4217.5128 | 4605.1294 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 |  | 642.9947 | 548.4913 | 641.2421 | 718.8737 | 787.6439 | 895.9948 | 993.9341 | 1129.8017 | 1271.4575 | 1387.2119 | 1496.3964 | 1658.4471 | 1776.2693 | 1894.9828 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165
55% | 1447.5067 | 844.7507 | 1353.748 | 1756.6813 | 2234.3727 | 2726.9226 | 3249.9973 | 3848.4481 | 4552.8123 | 5212.9114 | 5906.5916 | 7086.8049 | 7488.3769 | 8244.4394 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 |  | 464.401 | 380.678 | 462.8484 | 531.6242 | 592.5495 | 688.5403 | 775.3074 | 895.676 | 1021.1726 | 1123.7224 | 1220.4518 | 1364.0167 | 1468.3984 | 1573.5698 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605
50% | 1023.5986 | 186.306 | 855.6256 | 1579.9211 | 2439.4694 | 3325.7539 | 4266.9641 | 5343.8046 | 6611.2235 | 7798.9926 | 9047.1869 | 11170.839 | 11893.4197 | 13253.8635 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 |  | 758.1769 | 570.9902 | 754.7055 | 908.4736 | 1044.6895 | 1259.3045 | 1453.2969 | 1722.4155 | 2002.9989 | 2232.2783 | 2448.5445 | 2769.5249 | 3002.9001 | 3238.0408 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867
45% | 3.8607 |  |  | 128.7608 | 642.1854 | 1516.7957 | 2527.9377 | 3684.7872 | 5046.3752 | 6322.3953 | 7663.3303 | 9944.7695 | 10721.0378 | 12182.5623 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 |  | 994.5681 | 550.3323 | 986.3297 | 1351.2559 | 1674.5265 | 2183.8559 | 2644.2434 | 3282.9219 | 3948.8091 | 4492.9405 | 5006.1885 | 5767.9468 | 6321.7982 | 6879.8398 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814
40% | [5 empty] | 30.864 | 518.0035 | 1729.8767 | 3723.2143 | 5618.6184 | 7610.4472 | 10999.3037 | 12152.3749 | 14323.3278 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 |  | 245.2232 | 6.1061 | 237.7967 | 666.3272 | 1199.3612 | 2097.1486 | 2908.6668 | 4034.4559 | 5208.2054 | 6167.3376 | 7072.0323 | 8414.7724 | 9391.038 | 10374.6896 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51
35% | [8 empty] | 260.8444 | 1291.6349 | 3113.9117 | 6839.6111 | 8107.4308 | 10494.4273 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | [5 empty] | 6.0897 | 256.3183 | 767.9228 | 1830.1246 | 3013.7375 | 3980.9297 | 4893.2269 | 6247.2505 | 7231.72 | 8223.6376 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128
30% | [11 empty] | 257.78 | 456.7488 | 964.1965 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | [8 empty] | 68.044 | 794.1592 | 1909.9605 | 3334.2353 | 5630.2335 | 7299.5843 | 8981.5646 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098
25% | FY39: 17.9814; FY40: 17.9814; FY41: 17.9814; FY42: 17.9814; FY43: 17.9814; FY44: 17.9814; FY45: 17.9814; FY46: 17.9814; FY47: 17.9814; FY48: 17.9814; FY49: 17.9814; FY50: 17.9814; FY51: 17.9814; FY52: 17.9814; FY53: 17.9814; FY54: 17.9814 | [11 empty] | 5.1692 | 579.6374 | 1537.8682 | 2907.3948 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 4894.7486 | 2918.9038 | 4546.4136 | 6157.9939 | 8430.2235 | 11149.2101 | 14573.3927 | 19145.5429 | 25354.7011 | 31987.3251 | 39696.4168 | 53695.6017 | 58570.2717 | 67880.9291 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | E @ R (MWh) | 4875.5009 | 3646.6886 | 4849.7207 | 6091.2554 | 7350.5809 | 9633.3116 | 11982.1132 | 15661.0344 | 20228.0154 | 24482.3898 | 28872.2704 | 36136.5914 | 41958.8115 | 48229.1261 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882
Option 5 Summer POE50 W E @ R (MWh) N 2 | 3426.324 | 2043.2327 | 3182.4895 | 4310.5957 | 5901.1564 | 7804.447 | 10201.3749 | 13401.88 | 17748.2908 | 22391.1276 | 27787.4917 | 37586.9212 | 40999.1902 | 47516.6503 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 1462.6503 | 1094.0066 | 1454.9162 | 1827.3766 | 2205.1743 | 2889.9935 | 3594.634 | 4698.3103 | 6068.4046 | 7344.7169 | 8661.6811 | 10840.9774 | 12587.6434 | 14468.7378 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.7404 | 4.6453 | 6.7757 | 9.5787 | 12.3055 | 14.6381 | 17.9407 | 21.4914 | 25.1225 | 28.7704 | 32.0006 | 35.4328 | 36.6356 | 41.2535 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 | 46.0234 |  | 10.6383 | 7.5547 | 9.8162 | 12.6554 | 15.31 | 18.0647 | 20.9933 | 25.1744 | 28.774 | 32.2054 | 35.794 | 40.0296 | 41.3252 | 46.0057 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338 | 50.338
98% | 3.6852 | 2.1532 | 3.2077 | 4.5951 | 5.9448 | 7.0994 | 8.7341 | 10.4916 | 12.2889 | 14.0945 | 15.6934 | 17.3923 | 17.9876 | 20.2734 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 | 22.6344 |  | 5.1196 | 3.5933 | 4.7127 | 6.1181 | 7.432 | 8.7955 | 10.2451 | 12.3146 | 14.0963 | 15.7948 | 17.571 | 19.6676 | 20.3089 | 22.6256 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77 | 24.77
97% | 7.0006 | 3.9677 | 6.0552 | 8.8019 | 11.4739 | 13.7596 | 16.9958 | 20.4752 | 24.0333 | 27.6078 | 30.7731 | 34.1363 | 35.315 | 39.84 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 | 44.5141 |  | 9.8402 | 6.8186 | 9.0346 | 11.8168 | 14.418 | 17.1174 | 19.9871 | 24.0841 | 27.6114 | 30.9738 | 34.4902 | 38.6408 | 39.9103 | 44.4968 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419 | 48.7419
95% | 9.6685 | 5.1892 | 8.2724 | 12.329 | 16.2753 | 19.6511 | 24.4307 | 29.5695 | 34.8245 | 40.1039 | 44.7787 | 49.746 | 51.4867 | 58.1699 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 | 65.0731 |  | 13.8625 | 9.3998 | 12.6727 | 16.7817 | 20.6235 | 24.6103 | 28.8487 | 34.8996 | 40.1091 | 45.0752 | 50.2687 | 56.3987 | 58.2736 | 65.0475 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173 | 71.3173
90% | 7.7265 | 3.4104 | 6.3812 | 10.2899 | 14.0924 | 17.3451 | 21.9505 | 26.9019 | 31.9653 | 37.0522 | 41.5566 | 46.3428 | 48.0201 | 54.4596 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 | 61.1111 |  | 11.7675 | 7.4675 | 10.6211 | 14.5804 | 18.2821 | 22.1235 | 26.2073 | 32.0377 | 37.0573 | 41.8423 | 46.8464 | 52.7529 | 54.5595 | 61.0865 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277 | 67.1277
85% | 59.4257 | 10.8125 | 44.1551 | 88.5241 | 131.6871 | 168.61 | 220.8871 | 277.0921 | 334.5695 | 392.3123 | 443.4434 | 497.7725 | 516.8121 | 589.9091 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 | 665.4129 |  | 105.2967 | 56.4863 | 92.2833 | 137.2263 | 179.2457 | 222.8511 | 269.2083 | 335.3908 | 392.3698 | 446.6864 | 503.4896 | 570.5364 | 591.044 | 665.1335 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095 | 733.7095
80% | 66.7856 |  | 30.7797 | 136.8989 | 240.9011 | 329.8677 | 455.8307 | 591.258 | 729.751 | 868.8836 | 992.0854 | 1122.9926 | 1168.869 | 1344.9979 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 | 1526.9261 |  | 177.3128 | 59.7029 | 145.9567 | 254.2479 | 355.4947 | 460.563 | 572.2617 | 731.7299 | 869.0222 | 999.8995 | 1136.7681 | 1298.3189 | 1347.7326 | 1526.2529 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883 | 1691.4883
75% | 10.7395 |  |  | 147.8789 | 451.5956 | 711.4038 | 1079.2523 | 1474.7393 | 1879.179 | 2285.4865 | 2645.2715 | 3027.5584 | 3161.5309 | 3675.8783 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 | 4207.1613 |  | 265.8992 | 5.5448 | 174.3304 | 490.5722 | 786.2422 | 1093.0719 | 1419.2647 | 1884.958 | 2285.8913 | 2668.091 | 3067.7868 | 3539.5622 | 3683.8643 | 4205.1955 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307 | 4687.7307
70% |  |  |  | 0.34137 | 358.7813 | 923.9068 | 1724.0372 | 2584.2863 | 3464.0086 | 4347.7941 | 5130.3852 | 5961.9218 | 6253.3338 | 7372.1236 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 | 8527.751 |  | 61.8914 |  | 4.9894 | 443.5618 | 1086.6924 | 1754.0972 | 2463.6198 | 3476.5789 | 4348.6746 | 5180.0213 | 6049.425 | 7075.6136 | 7389.4943 | 8523.4749 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681 | 9573.0681
65% |  |  |  |  | 0.14282 | 244.0216 | 1071.302 | 1985.4365 | 2920.2641 | 3859.4093 | 4691.0214 | 5574.6449 | 5884.3108 | 7073.1809 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 | 8301.1961 |  |  |  |  | 7.3897 | 394.5346 | 1103.2449 | 1857.2116 | 2933.6218 | 3860.3449 | 4743.7666 | 5667.6292 | 6758.0977 | 7091.6397 | 8296.6521 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911 | 9411.9911
60% | [6 empty] | 239.939 | 1131.626 | 2090.7217 | 3054.2472 | 3907.4481 | 4814.0106 | 5131.7154 | 6351.4486 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | 7611.3432 | [6 empty] | 263.5183 | 1000.0724 | 2104.4263 | 3055.2072 | 3961.5626 | 4909.4088 | 6028.1859 | 6370.3866 | 7606.6813 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746 | 8750.9746
55% | [7 empty] | 211.771 | 1198.69 | 2322.2913 | 3317.2392 | 4374.4139 | 4744.9008 | 6167.2751 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | 7636.4829 | [7 empty] | 133.0164 | 1214.6713 | 2323.4108 | 3380.344 | 4485.6611 | 5790.3069 | 6189.3594 | 7631.0465 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476 | 8965.4476
50% | [8 empty] | 92.1134 | 924.0764 | 2009.7612 | 3163.3484 | 3567.6231 | 5119.7155 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | 6722.9126 | [8 empty] | 98.0695 | 925.2974 | 2078.6211 | 3284.7412 | 4708.3684 | 5143.8138 | 6716.9804 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766 | 8173.0766
45% | [10 empty] | 366.5682 | 1477.3466 | 1969.1582 | 3857.3226 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | 5807.6574 | [10 empty] | 413.2323 | 1625.0244 | 3356.9073 | 3886.6389 | 5800.4407 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823 | 7571.823
40% | [11 empty] | 2.4649 | 93.4966 | 1556.8421 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | 4417.7952 | [11 empty] | 16.1421 | 1008.3362 | 1592.3295 | 4406.7205 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498 | 7125.0498
35% | FY39: 161.7611; FY40: 161.7611; FY41: 161.7611; FY42: 161.7611; FY43: 161.7611; FY44: 161.7611; FY45: 161.7611; FY46: 161.7611; FY47: 161.7611; FY48: 161.7611; FY49: 161.7611; FY50: 161.7611; FY51: 161.7611; FY52: 161.7611; FY53: 161.7611; FY54: 161.7611 | [14 empty] | 159.7567 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304 | 992.9304
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 172.7722 | 30.1783 | 105.6271 | 419.2379 | 1243.1999 | 2450.3032 | 4881.3001 | 8365.1388 | 12837.5318 | 18202.1296 | 23668.0261 | 30199.5246 | 32681.1959 | 43322.69 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | 55825.7559 | E @ R (MWh) | 661.6281 | 156.5679 | 464.417 | 1394.9502 | 2878.2752 | 4988.0577 | 7820.9364 | 12907.9569 | 18207.8664 | 24038.1166 | 30931.0466 | 40341.723 | 43500.6806 | 55777.597 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848 | 67939.5848
Option 6 Winter POE50 W E @ R (MWh) N 2 | 120.9405 | 21.1248 | 73.939 | 293.4665 | 870.2399 | 1715.2123 | 3416.91 | 5855.5972 | 8986.2722 | 12741.4907 | 16567.6183 | 21139.6672 | 22876.8371 | 30325.883 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | 39078.0291 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 198.4884 | 46.9704 | 139.3251 | 418.4851 | 863.4826 | 1496.4173 | 2346.2809 | 3872.3871 | 5462.3599 | 7211.435 | 9279.314 | 12102.5169 | 13050.2042 | 16733.2791 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754 | 20381.8754
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.0318 | 17.8108 | 19.5208 | 20.9532 | 22.2226 | 24.2188 | 26.0237 | 28.525 | 31.1327 | 33.2645 | 35.2756 | 38.2573 | 40.427 | 42.6128 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274 | 44.9274
98% | 13.9949 | 11.7473 | 13.2296 | 14.3989 | 15.8135 | 17.2241 | 18.7433 | 20.4501 | 22.4813 | 24.4066 | 26.4455 | 29.9404 | 31.0535 | 33.2753 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 | 34.9318 |  | 39.322 | 34.9246 | 38.3103 | 41.1462 | 43.6594 | 47.6119 | 51.1852 | 56.1377 | 61.3006 | 65.5213 | 69.503 | 75.4066 | 79.7024 | 84.0301 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127 | 88.6127
97% | 13.6816 | 11.4568 | 12.924 | 14.0815 | 15.4817 | 16.878 | 18.3818 | 20.0713 | 22.0818 | 23.9876 | 26.0058 | 29.4652 | 30.567 | 32.7663 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 | 34.4059 |  | 57.8704 | 51.3413 | 56.3683 | 60.579 | 64.3106 | 70.1791 | 75.4847 | 82.838 | 90.5037 | 96.7704 | 102.6824 | 111.4478 | 117.8261 | 124.2519 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559 | 131.0559
95% | 13.2117 | 11.0211 | 12.4657 | 13.6054 | 14.9841 | 16.3588 | 17.8395 | 19.503 | 21.4826 | 23.3591 | 25.3463 | 28.7524 | 29.8373 | 32.0027 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 | 33.6171 |  | 112.4034 | 99.5461 | 109.4453 | 117.7372 | 125.0856 | 136.6419 | 147.0899 | 161.5702 | 176.6659 | 189.0064 | 200.6485 | 217.9096 | 230.47 | 243.1237 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224 | 256.5224
90% | 109.0356 | 90.0393 | 102.5668 | 112.4501 | 124.4057 | 136.3275 | 149.1676 | 163.5936 | 180.7605 | 197.0331 | 214.2655 | 243.8032 | 253.2107 | 271.9894 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 | 285.989 |  | 156.9238 | 138.341 | 152.6485 | 164.6328 | 175.2535 | 191.956 | 207.0567 | 227.9852 | 249.8032 | 267.6392 | 284.4656 | 309.4133 | 327.567 | 345.8556 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208 | 365.2208
85% | 94.9366 | 76.9671 | 88.8175 | 98.1666 | 109.4759 | 120.7533 | 132.8993 | 146.5455 | 162.7845 | 178.1775 | 194.4784 | 222.4195 | 231.3185 | 249.0821 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 | 262.325 |  | 264.8908 | 231.6872 | 257.2517 | 278.6652 | 297.6421 | 327.4859 | 354.4675 | 391.8624 | 430.8464 | 462.7155 | 492.7808 | 537.3569 | 569.7937 | 602.4715 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731 | 637.0731
80% | 89.8196 | 70.9944 | 83.4091 | 93.2034 | 105.0513 | 116.8657 | 129.5901 | 143.8861 | 160.8984 | 177.0244 | 194.1015 | 223.3731 | 232.6959 | 251.3053 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 | 265.1789 |  | 192.187 | 166.4054 | 186.2555 | 202.8824 | 217.6174 | 240.7903 | 261.7407 | 290.7767 | 321.0467 | 345.7921 | 369.1369 | 403.7489 | 428.9352 | 454.3085 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756 | 481.1756
75% | 118.6466 | 90.3518 | 109.0114 | 123.7325 | 141.5402 | 159.2977 | 178.4228 | 199.9101 | 225.4801 | 249.718 | 275.3854 | 319.3815 | 333.3939 | 361.3645 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 | 382.2169 |  | 189.9756 | 162.2966 | 183.6075 | 201.4581 | 217.2775 | 242.1557 | 264.648 | 295.8208 | 328.3185 | 354.885 | 379.9478 | 417.107 | 444.1468 | 471.3875 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318 | 500.2318
70% | 269.0476 | 192.9482 | 243.1337 | 282.7263 | 330.6203 | 378.3794 | 429.8167 | 487.6073 | 556.378 | 621.5662 | 690.5991 | 808.9275 | 846.614 | 921.8414 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 | 977.9242 |  | 240.4634 | 201.6235 | 231.5275 | 256.5759 | 278.7741 | 313.6839 | 345.2456 | 388.9881 | 434.5896 | 471.8684 | 507.0373 | 559.1801 | 597.1229 | 635.3477 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228 | 675.8228
65% | 274.0679 | 175.4923 | 240.5002 | 291.7865 | 353.8262 | 415.691 | 482.3205 | 557.1796 | 646.2619 | 730.7036 | 820.1256 | 973.4025 | 1022.2198 | 1119.6658 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 | 1192.3127 |  | 244.9542 | 199.7527 | 234.5547 | 263.7059 | 289.5399 | 330.1677 | 366.899 | 417.8063 | 470.877 | 514.2618 | 555.191 | 615.8745 | 660.0321 | 704.5179 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225 | 751.6225
60% | 700.666 | 332.7191 | 575.3698 | 766.8032 | 998.3751 | 1229.2939 | 1477.9977 | 1757.4198 | 2089.9318 | 2405.1224 | 2738.9021 | 3311.0297 | 3493.2471 | 3856.9777 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 | 4128.1424 |  | 511.1887 | 398.1849 | 485.1901 | 558.0679 | 622.6531 | 724.2224 | 816.0506 | 943.319 | 1075.9957 | 1184.4577 | 1286.7808 | 1438.4894 | 1548.8835 | 1660.098 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595 | 1777.8595
55% | 628.6172 | 59.7662 | 384.8974 | 757.6207 | 1209.3115 | 1659.7285 | 2144.8359 | 2689.8606 | 3338.4394 | 3953.2321 | 4604.2836 | 5720.2429 | 6075.6657 | 6785.1376 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 | 7314.0561 |  | 347.6306 | 247.5177 | 324.5978 | 389.1622 | 446.3799 | 536.3628 | 617.7158 | 730.4661 | 848.0079 | 944.0972 | 1034.7479 | 1169.1504 | 1266.9514 | 1365.4792 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072 | 1469.8072
50% | 46.0732 |  |  | 118.8314 | 620.0138 | 1405.4663 | 2278.3588 | 3259.0652 | 4426.1051 | 5532.3507 | 6703.8398 | 8711.8747 | 9351.4153 | 10628.025 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 | 11579.7503 |  | 497.1033 | 273.2722 | 445.6069 | 589.959 | 717.8855 | 919.068 | 1100.9559 | 1353.0414 | 1615.8397 | 1830.6748 | 2033.3504 | 2333.8457 | 2552.5078 | 2772.7948 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499 | 3006.0499
45% | [5 empty] | 71.1267 | 518.1392 | 1445.1521 | 2698.9029 | 3887.3423 | 5145.8729 | 7303.1045 | 7990.1629 | 9361.6244 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 | 10384.0628 |  | 379.2924 | 44.9951 | 275.767 | 595.3495 | 898.9477 | 1376.3987 | 1808.0594 | 2406.3147 | 3029.9938 | 3539.8455 | 4020.8399 | 4733.9826 | 5252.9167 | 5775.707 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735 | 6329.2735
40% | [7 empty] | 18.5617 | 655.2534 | 2007.24 | 3871.0085 | 7075.3667 | 8095.9253 | 10133.0983 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 | 11651.8313 |  |  |  |  | 14.7198 | 165.7266 | 703.0627 | 1434.7377 | 2489.2734 | 3588.6232 | 4487.3313 | 5335.173 | 6592.219 | 7506.9364 | 8428.4512 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147 | 9404.2147
35% | [10 empty] | 314.2452 | 2555.789 | 3647.3012 | 5887.2048 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | 7557.0753 | [7 empty] | 36.9963 | 471.9674 | 1380.5454 | 2286.8057 | 3141.7721 | 4409.3816 | 5331.7857 | 6261.0443 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074 | 7245.0074
30% | [12 empty] | 4.3129 | 143.4437 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | 364.0266 | [9 empty] | 0.14637 | 258.2019 | 916.4791 | 2537.8945 | 4077.8931 | 5653.6235 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156 | 7322.1156
25% | [43 empty] | 89.6131 | 590.0898 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357 | 1553.6357
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 2371.7985 | 1123.5036 | 1866.3252 | 2687.4066 | 4038.8993 | 5743.391 | 7976.5131 | 10928.8061 | 15207.2417 | 20011.2637 | 25844.9051 | 37556.873 | 41668.941 | 50068.8043 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | 56447.8461 | E @ R (MWh) | 3254.2374 | 2267.699 | 3000.6519 | 3755.5945 | 4582.9755 | 6184.0055 | 7914.3566 | 10736.6926 | 14134.2364 | 17333.1386 | 20765.8122 | 26500.6652 | 31123.5108 | 36215.1951 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284 | 42040.2284
Option 6 Summer POE50 W E @ R (MWh) N 2 | 1660.2589 | 786.4525 | 1306.4276 | 1881.1846 | 2827.2295 | 4020.3737 | 5583.5592 | 7650.1643 | 10645.0692 | 14007.8846 | 18091.4336 | 26289.8111 | 29168.2587 | 35048.163 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | 39513.4923 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 976.2712 | 680.3097 | 900.1956 | 1126.6783 | 1374.8926 | 1855.2017 | 2374.307 | 3221.0078 | 4240.2709 | 5199.9416 | 6229.7437 | 7950.1996 | 9337.0532 | 10864.5585 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685 | 12612.0685
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 11.8122 | 9.2886 | 11.5965 | 14.5464 | 17.4025 | 19.9446 | 23.4359 | 27.2523 | 31.1608 | 35.034 | 38.4761 | 42.2278 | 43.6601 | 48.5097 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 |  | 14.7101 | 12.198 | 14.637 | 17.6231 | 20.407 | 23.3712 | 26.4886 | 30.9353 | 34.8123 | 38.469 | 42.2695 | 46.8247 | 48.3497 | 53.2619 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405
98% | 5.7007 | 4.4516 | 5.5939 | 7.054 | 8.4677 | 9.726 | 11.4541 | 13.3432 | 15.2778 | 17.1949 | 18.8987 | 20.7557 | 21.4646 | 23.865 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 |  | 7.1351 | 5.8917 | 7.0989 | 8.5769 | 9.9549 | 11.4221 | 12.9651 | 15.1661 | 17.0852 | 18.8951 | 20.7763 | 23.031 | 23.7858 | 26.2173 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835
97% | 10.9905 | 8.5177 | 10.7792 | 13.6697 | 16.4684 | 18.9594 | 22.3806 | 26.1203 | 29.9502 | 33.7455 | 37.1185 | 40.7948 | 42.1983 | 46.9504 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 |  | 13.8302 | 11.3686 | 13.7586 | 16.6846 | 19.4125 | 22.3172 | 25.3719 | 29.7293 | 33.5283 | 37.1115 | 40.8356 | 45.2992 | 46.7936 | 51.6071 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936
95% | 15.5614 | 11.9092 | 15.2493 | 19.5184 | 23.6518 | 27.3309 | 32.3837 | 37.9069 | 43.5634 | 49.1688 | 54.1504 | 59.58 | 61.6529 | 68.6713 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 |  | 19.7554 | 16.1198 | 19.6496 | 23.9712 | 28.0001 | 32.29 | 36.8016 | 43.2371 | 48.848 | 54.1401 | 59.6403 | 66.2327 | 68.4398 | 75.549 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752
90% | 13.4045 | 9.8855 | 13.1038 | 17.2173 | 21.2 | 24.7449 | 29.6135 | 34.9353 | 40.3856 | 45.7866 | 50.5866 | 55.8183 | 57.8156 | 64.5781 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 |  | 17.4456 | 13.9426 | 17.3436 | 21.5077 | 25.3897 | 29.5233 | 33.8704 | 40.0712 | 45.4776 | 50.5767 | 55.8764 | 62.2284 | 64.3551 | 71.205 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897
85% | 123.8793 | 83.9329 | 120.4651 | 167.1587 | 212.3681 | 252.6072 | 307.8727 | 368.2828 | 430.1509 | 491.4597 | 545.9461 | 605.3325 | 628.0045 | 704.7685 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 |  | 169.7502 | 129.9866 | 168.5932 | 215.8608 | 259.9267 | 306.8483 | 356.1939 | 426.5814 | 487.9512 | 545.8339 | 605.9923 | 678.0964 | 702.2364 | 779.9929 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673
80% | 222.088 | 125.8361 | 213.8613 | 326.3707 | 435.3039 | 532.261 | 665.4245 | 810.9841 | 960.0568 | 1107.7818 | 1239.0681 | 1382.161 | 1436.7897 | 1621.7545 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 |  | 332.6151 | 236.8036 | 329.8273 | 443.7197 | 549.8975 | 662.9563 | 781.8556 | 951.456 | 1099.328 | 1238.7977 | 1383.7507 | 1557.4874 | 1615.6532 | 1803.0095 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382
75% | 396.6559 | 116.4694 | 372.6315 | 701.1915 | 1019.3082 | 1302.451 | 1691.327 | 2116.4032 | 2551.7386 | 2983.1384 | 3366.5325 | 3784.4054 | 3943.9368 | 4484.0876 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 |  | 719.4271 | 439.6298 | 711.2859 | 1043.8848 | 1353.9548 | 1684.119 | 2031.3394 | 2526.6219 | 2958.451 | 3365.7428 | 3789.0478 | 4296.4091 | 4466.2702 | 5013.4048 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713
70% | 246.929 |  | 204.178 | 901.6933 | 1593.649 | 2209.5309 | 3055.3998 | 3980.0102 | 4926.9358 | 5865.3009 | 6699.2458 | 7608.1877 | 7955.1946 | 9130.111 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 |  | 941.3587 | 332.8577 | 923.6502 | 1647.1071 | 2321.5601 | 3039.7213 | 3794.9824 | 4872.3028 | 5811.6018 | 6697.5281 | 7618.2856 | 8721.8795 | 9091.3551 | 10281.4623 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723
65% |  |  |  | 226.1234 | 932.7463 | 1587.2067 | 2486.0603 | 3468.5876 | 4474.828 | 5471.9717 | 6358.1545 | 7324.0318 | 7692.7751 | 8941.2875 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 |  | 258.5342 |  | 243.8113 | 989.553 | 1706.2533 | 2469.3997 | 3271.9699 | 4416.7729 | 5414.9089 | 6356.3291 | 7334.7623 | 8507.4846 | 8900.1039 | 10164.7587 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028
60% |  |  |  |  | 149.8988 | 723.0581 | 1645.246 | 2653.2798 | 3685.6423 | 4708.672 | 5617.8601 | 6608.8117 | 6987.1276 | 8268.0514 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 |  |  |  |  | 184.3862 | 845.1952 | 1628.1529 | 2451.5579 | 3626.0801 | 4650.1278 | 5615.9873 | 6619.8207 | 7822.987 | 8225.7988 | 9523.2841 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284
55% | [5 empty] | 25.7795 | 679.408 | 1854.709 | 3058.5836 | 4251.5748 | 5311.8114 | 6467.3953 | 6908.5629 | 8402.2937 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | [5 empty] | 63.0524 | 659.9292 | 1619.4738 | 2989.126 | 4183.3044 | 5309.6275 | 6480.2334 | 7883.2883 | 8353.0214 | 9866.0651 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246
50% | [7 empty] | 479.7725 | 1727.5166 | 3029.3066 | 4186.235 | 5447.2062 | 5928.6075 | 7558.5641 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | [7 empty] | 307.8144 | 1651.7246 | 2954.8101 | 4183.852 | 5461.2151 | 6992.2262 | 7504.7982 | 9155.829 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017
45% | [8 empty] | 203.3275 | 1315.0503 | 2721.7171 | 4255.7243 | 4841.3627 | 6824.2511 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | [8 empty] | 167.3292 | 1227.8012 | 2718.8181 | 4272.7665 | 6135.285 | 6758.8434 | 8767.3691 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515
40% | [10 empty] | 474.4529 | 2069.885 | 2934.9379 | 5977.8403 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | [10 empty] | 472.4498 | 2093.2934 | 4920.5663 | 5877.4669 | 8959.7119 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735
35% | [12 empty] | 3.8716 | 560.4187 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | [12 empty] | 265.2858 | 528.0265 | 1908.4996 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332
30% | [45 empty] | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1047.0217 | 370.2909 | 967.4586 | 2394.5434 | 4430.4648 | 6733.6002 | 10650.0061 | 15871.5872 | 22179.118 | 29405.186 | 36720.2539 | 45772.3176 | 49487.9623 | 62726.003 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | E @ R (MWh) | 2494.5618 | 1198.7985 | 2449.6557 | 4612.8752 | 7203.004 | 10570.0505 | 14750.6849 | 21787.1338 | 28968.0357 | 36704.1588 | 45878.566 | 58024.6116 | 62275.2981 | 76501.2272 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131
Option 7 Winter POE50 W E @ R (MWh) N 2 | 732.9152 | 259.2037 | 677.221 | 1676.1804 | 3101.3253 | 4713.5201 | 7455.0043 | 11110.111 | 15525.3826 | 20583.6302 | 25704.1777 | 32040.6223 | 34641.5736 | 43908.2021 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 748.3685 | 359.6395 | 734.8967 | 1383.8626 | 2160.9012 | 3171.0152 | 4425.2055 | 6536.1402 | 8690.4107 | 11011.2476 | 13763.5698 | 17407.3835 | 18682.5894 | 22950.3682 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.6224 | 20.765 | 22.5879 | 24.1137 | 25.4654 | 27.5949 | 29.5198 | 32.1902 | 34.9744 | 37.2495 | 39.3954 | 42.5804 | 44.8961 | 47.2293 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006
98% | 16.5594 | 14.6718 | 16.2658 | 17.5277 | 19.0237 | 20.5662 | 22.2043 | 24.0785 | 26.2844 | 28.3516 | 30.524 | 34.2201 | 35.4777 | 37.8454 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 |  | 44.451 | 40.7735 | 44.3828 | 47.4037 | 50.0798 | 54.2961 | 58.1073 | 63.3944 | 68.9067 | 73.4112 | 77.6599 | 83.9659 | 88.5508 | 93.1703 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631
97% | 16.2201 | 14.3516 | 15.9295 | 17.1785 | 18.6593 | 20.1862 | 21.8077 | 23.6628 | 25.8463 | 27.8925 | 30.0429 | 33.7014 | 34.9463 | 37.29 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 |  | 65.4859 | 60.0257 | 65.3846 | 69.87 | 73.8434 | 80.1037 | 85.7624 | 93.6125 | 101.7971 | 108.4851 | 114.7936 | 124.1565 | 130.964 | 137.823 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876
95% | 15.7111 | 13.8713 | 15.4249 | 16.6548 | 18.1128 | 19.6161 | 21.2127 | 23.0393 | 25.1892 | 27.2039 | 29.3212 | 32.9235 | 34.1492 | 36.4568 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 |  | 127.4 | 116.6476 | 127.2006 | 136.0333 | 143.8578 | 156.1858 | 167.3291 | 182.7878 | 198.9051 | 212.0754 | 224.4981 | 242.9359 | 256.3414 | 269.8484 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541
90% | 130.7104 | 114.7563 | 128.2287 | 138.8937 | 151.5375 | 164.5746 | 178.4195 | 194.2596 | 212.9031 | 230.3749 | 248.7356 | 279.974 | 290.603 | 310.6149 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 |  | 178.5986 | 163.058 | 178.3104 | 191.0765 | 202.3853 | 220.203 | 236.3086 | 258.6513 | 281.9458 | 300.981 | 318.9357 | 345.5841 | 364.9593 | 384.4811 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573
85% | 115.4398 | 100.3481 | 113.0923 | 123.1808 | 135.1411 | 147.4735 | 160.5701 | 175.554 | 193.1897 | 209.7171 | 227.0853 | 256.6352 | 266.6896 | 285.6197 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 |  | 303.619 | 275.8513 | 303.104 | 325.9143 | 346.1208 | 377.9573 | 406.7345 | 446.6561 | 488.2784 | 522.2902 | 554.3716 | 601.9865 | 636.6058 | 671.4871 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311
80% | 111.2991 | 95.4888 | 108.8398 | 119.4088 | 131.9386 | 144.8582 | 158.5785 | 174.2759 | 192.7514 | 210.0658 | 228.2611 | 259.2181 | 269.7513 | 289.5829 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 |  | 222.2583 | 200.6975 | 221.8584 | 239.57 | 255.2597 | 279.9798 | 302.3245 | 333.3224 | 365.6409 | 392.0501 | 416.9603 | 453.9319 | 480.8128 | 507.8971 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583
75% | 150.9309 | 127.1676 | 147.2345 | 163.12 | 181.9528 | 201.3713 | 221.9933 | 245.5869 | 273.3561 | 299.3802 | 326.7283 | 373.2576 | 389.0894 | 418.8968 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 |  | 222.2599 | 199.1124 | 221.8307 | 240.8456 | 257.6901 | 284.2293 | 308.2184 | 341.4976 | 376.1945 | 404.5472 | 431.2907 | 470.9831 | 499.8423 | 528.9197 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167
70% | 355.8769 | 291.9649 | 345.9354 | 388.6595 | 439.3106 | 491.5371 | 547.0002 | 610.4557 | 685.1415 | 755.1337 | 828.6866 | 953.828 | 996.4079 | 1076.5754 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 |  | 285.7656 | 253.2844 | 285.1632 | 311.8455 | 335.482 | 372.7226 | 406.3848 | 453.083 | 501.7706 | 541.5558 | 579.0829 | 634.7803 | 675.2763 | 716.0785 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937
65% | 386.5423 | 303.7538 | 373.6646 | 429.0075 | 494.6183 | 562.2701 | 634.1144 | 716.3116 | 813.056 | 903.7206 | 998.9975 | 1161.0998 | 1216.2557 | 1320.1009 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 |  | 297.6766 | 259.8752 | 296.9755 | 328.0282 | 355.5363 | 398.8766 | 438.0523 | 492.3994 | 549.0617 | 595.3635 | 639.0373 | 703.8576 | 750.9864 | 798.4718 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653
60% | 1120.4925 | 811.4729 | 1072.4245 | 1278.9995 | 1523.9013 | 1776.4207 | 2044.5895 | 2351.402 | 2712.5139 | 3050.9321 | 3406.5666 | 4011.6358 | 4217.5128 | 4605.1294 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 |  | 642.9947 | 548.4913 | 641.2421 | 718.8737 | 787.6439 | 895.9948 | 993.9341 | 1129.8017 | 1271.4575 | 1387.2119 | 1496.3964 | 1658.4471 | 1776.2693 | 1894.9828 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165
55% | 1447.5067 | 844.7507 | 1353.748 | 1756.6813 | 2234.3727 | 2726.9226 | 3249.9973 | 3848.4481 | 4552.8123 | 5212.9114 | 5906.5916 | 7086.8049 | 7488.3769 | 8244.4394 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 |  | 464.401 | 380.678 | 462.8484 | 531.6242 | 592.5495 | 688.5403 | 775.3074 | 895.676 | 1021.1726 | 1123.7224 | 1220.4518 | 1364.0167 | 1468.3984 | 1573.5698 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605
50% | 1023.5986 | 186.306 | 855.6256 | 1579.9211 | 2439.4694 | 3325.7539 | 4266.9641 | 5343.8046 | 6611.2235 | 7798.9926 | 9047.1869 | 11170.839 | 11893.4197 | 13253.8635 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 |  | 758.1769 | 570.9902 | 754.7055 | 908.4736 | 1044.6895 | 1259.3045 | 1453.2969 | 1722.4155 | 2002.9989 | 2232.2783 | 2448.5445 | 2769.5249 | 3002.9001 | 3238.0408 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867
45% | 3.8607 |  |  | 128.7608 | 642.1854 | 1516.7957 | 2527.9377 | 3684.7872 | 5046.3752 | 6322.3953 | 7663.3303 | 9944.7695 | 10721.0378 | 12182.5623 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 |  | 994.5681 | 550.3323 | 986.3297 | 1351.2559 | 1674.5265 | 2183.8559 | 2644.2434 | 3282.9219 | 3948.8091 | 4492.9405 | 5006.1885 | 5767.9468 | 6321.7982 | 6879.8398 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814
40% | [5 empty] | 30.864 | 518.0035 | 1729.8767 | 3723.2143 | 5618.6184 | 7610.4472 | 10999.3037 | 12152.3749 | 14323.3278 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 |  | 245.2232 | 6.1061 | 237.7967 | 666.3272 | 1199.3612 | 2097.1486 | 2908.6668 | 4034.4559 | 5208.2054 | 6167.3376 | 7072.0323 | 8414.7724 | 9391.038 | 10374.6896 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51
35% | [8 empty] | 260.8444 | 1291.6349 | 3113.9117 | 6839.6111 | 8107.4308 | 10494.4273 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | [5 empty] | 6.0897 | 256.3183 | 767.9228 | 1830.1246 | 3013.7375 | 3980.9297 | 4893.2269 | 6247.2505 | 7231.72 | 8223.6376 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128
30% | [11 empty] | 257.78 | 456.7488 | 964.1965 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | [8 empty] | 68.044 | 794.1592 | 1909.9605 | 3334.2353 | 5630.2335 | 7299.5843 | 8981.5646 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098
25% | FY39: 17.9814; FY40: 17.9814; FY41: 17.9814; FY42: 17.9814; FY43: 17.9814; FY44: 17.9814; FY45: 17.9814; FY46: 17.9814; FY47: 17.9814; FY48: 17.9814; FY49: 17.9814; FY50: 17.9814; FY51: 17.9814; FY52: 17.9814; FY53: 17.9814; FY54: 17.9814 | [11 empty] | 5.1692 | 579.6374 | 1537.8682 | 2907.3948 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 4894.7486 | 2918.9038 | 4546.4136 | 6157.9939 | 8430.2235 | 11149.2101 | 14573.3927 | 19145.5429 | 25354.7011 | 31987.3251 | 39696.4168 | 53695.6017 | 58570.2717 | 67880.9291 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | E @ R (MWh) | 4875.5009 | 3646.6886 | 4849.7207 | 6091.2554 | 7350.5809 | 9633.3116 | 11982.1132 | 15661.0344 | 20228.0154 | 24482.3898 | 28872.2704 | 36136.5914 | 41958.8115 | 48229.1261 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882
Option 7 Summer POE50 W E @ R (MWh) N 2 | 3426.324 | 2043.2327 | 3182.4895 | 4310.5957 | 5901.1564 | 7804.447 | 10201.3749 | 13401.88 | 17748.2908 | 22391.1276 | 27787.4917 | 37586.9212 | 40999.1902 | 47516.6503 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 1462.6503 | 1094.0066 | 1454.9162 | 1827.3766 | 2205.1743 | 2889.9935 | 3594.634 | 4698.3103 | 6068.4046 | 7344.7169 | 8661.6811 | 10840.9774 | 12587.6434 | 14468.7378 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 11.8122 | 9.2886 | 11.5965 | 14.5464 | 17.4025 | 19.9446 | 23.4359 | 27.2523 | 31.1608 | 35.034 | 38.4761 | 42.2278 | 43.6601 | 48.5097 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 | 53.5259 |  | 14.7101 | 12.198 | 14.637 | 17.6231 | 20.407 | 23.3712 | 26.4886 | 30.9353 | 34.8123 | 38.469 | 42.2695 | 46.8247 | 48.3497 | 53.2619 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405 | 57.8405
98% | 5.7007 | 4.4516 | 5.5939 | 7.054 | 8.4677 | 9.726 | 11.4541 | 13.3432 | 15.2778 | 17.1949 | 18.8987 | 20.7557 | 21.4646 | 23.865 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 | 26.3479 |  | 7.1351 | 5.8917 | 7.0989 | 8.5769 | 9.9549 | 11.4221 | 12.9651 | 15.1661 | 17.0852 | 18.8951 | 20.7763 | 23.031 | 23.7858 | 26.2173 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835 | 28.4835
97% | 10.9905 | 8.5177 | 10.7792 | 13.6697 | 16.4684 | 18.9594 | 22.3806 | 26.1203 | 29.9502 | 33.7455 | 37.1185 | 40.7948 | 42.1983 | 46.9504 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 | 51.8657 |  | 13.8302 | 11.3686 | 13.7586 | 16.6846 | 19.4125 | 22.3172 | 25.3719 | 29.7293 | 33.5283 | 37.1115 | 40.8356 | 45.2992 | 46.7936 | 51.6071 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936 | 56.0936
95% | 15.5614 | 11.9092 | 15.2493 | 19.5184 | 23.6518 | 27.3309 | 32.3837 | 37.9069 | 43.5634 | 49.1688 | 54.1504 | 59.58 | 61.6529 | 68.6713 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 | 75.9309 |  | 19.7554 | 16.1198 | 19.6496 | 23.9712 | 28.0001 | 32.29 | 36.8016 | 43.2371 | 48.848 | 54.1401 | 59.6403 | 66.2327 | 68.4398 | 75.549 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752 | 82.1752
90% | 13.4045 | 9.8855 | 13.1038 | 17.2173 | 21.2 | 24.7449 | 29.6135 | 34.9353 | 40.3856 | 45.7866 | 50.5866 | 55.8183 | 57.8156 | 64.5781 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 | 71.5731 |  | 17.4456 | 13.9426 | 17.3436 | 21.5077 | 25.3897 | 29.5233 | 33.8704 | 40.0712 | 45.4776 | 50.5767 | 55.8764 | 62.2284 | 64.3551 | 71.205 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897 | 77.5897
85% | 123.8793 | 83.9329 | 120.4651 | 167.1587 | 212.3681 | 252.6072 | 307.8727 | 368.2828 | 430.1509 | 491.4597 | 545.9461 | 605.3325 | 628.0045 | 704.7685 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 | 784.1707 |  | 169.7502 | 129.9866 | 168.5932 | 215.8608 | 259.9267 | 306.8483 | 356.1939 | 426.5814 | 487.9512 | 545.8339 | 605.9923 | 678.0964 | 702.2364 | 779.9929 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673 | 852.4673
80% | 222.088 | 125.8361 | 213.8613 | 326.3707 | 435.3039 | 532.261 | 665.4245 | 810.9841 | 960.0568 | 1107.7818 | 1239.0681 | 1382.161 | 1436.7897 | 1621.7545 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 | 1813.076 |  | 332.6151 | 236.8036 | 329.8273 | 443.7197 | 549.8975 | 662.9563 | 781.8556 | 951.456 | 1099.328 | 1238.7977 | 1383.7507 | 1557.4874 | 1615.6532 | 1803.0095 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382 | 1977.6382
75% | 396.6559 | 116.4694 | 372.6315 | 701.1915 | 1019.3082 | 1302.451 | 1691.327 | 2116.4032 | 2551.7386 | 2983.1384 | 3366.5325 | 3784.4054 | 3943.9368 | 4484.0876 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 | 5042.8019 |  | 719.4271 | 439.6298 | 711.2859 | 1043.8848 | 1353.9548 | 1684.119 | 2031.3394 | 2526.6219 | 2958.451 | 3365.7428 | 3789.0478 | 4296.4091 | 4466.2702 | 5013.4048 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713 | 5523.3713
70% | 246.929 |  | 204.178 | 901.6933 | 1593.649 | 2209.5309 | 3055.3998 | 3980.0102 | 4926.9358 | 5865.3009 | 6699.2458 | 7608.1877 | 7955.1946 | 9130.111 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 | 10345.406 |  | 941.3587 | 332.8577 | 923.6502 | 1647.1071 | 2321.5601 | 3039.7213 | 3794.9824 | 4872.3028 | 5811.6018 | 6697.5281 | 7618.2856 | 8721.8795 | 9091.3551 | 10281.4623 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723 | 11390.723
65% |  |  |  | 226.1234 | 932.7463 | 1587.2067 | 2486.0603 | 3468.5876 | 4474.828 | 5471.9717 | 6358.1545 | 7324.0318 | 7692.7751 | 8941.2875 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 | 10232.7077 |  | 258.5342 |  | 243.8113 | 989.553 | 1706.2533 | 2469.3997 | 3271.9699 | 4416.7729 | 5414.9089 | 6356.3291 | 7334.7623 | 8507.4846 | 8900.1039 | 10164.7587 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028 | 11343.5028
60% |  |  |  |  | 149.8988 | 723.0581 | 1645.246 | 2653.2798 | 3685.6423 | 4708.672 | 5617.8601 | 6608.8117 | 6987.1276 | 8268.0514 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 | 9592.9971 |  |  |  |  | 184.3862 | 845.1952 | 1628.1529 | 2451.5579 | 3626.0801 | 4650.1278 | 5615.9873 | 6619.8207 | 7822.987 | 8225.7988 | 9523.2841 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284 | 10732.6284
55% | [5 empty] | 25.7795 | 679.408 | 1854.709 | 3058.5836 | 4251.5748 | 5311.8114 | 6467.3953 | 6908.5629 | 8402.2937 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | 9947.36 | [5 empty] | 63.0524 | 659.9292 | 1619.4738 | 2989.126 | 4183.3044 | 5309.6275 | 6480.2334 | 7883.2883 | 8353.0214 | 9866.0651 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246 | 11276.3246
50% | [7 empty] | 479.7725 | 1727.5166 | 3029.3066 | 4186.235 | 5447.2062 | 5928.6075 | 7558.5641 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | 9244.5377 | [7 empty] | 307.8144 | 1651.7246 | 2954.8101 | 4183.852 | 5461.2151 | 6992.2262 | 7504.7982 | 9155.829 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017 | 10694.7017
45% | [8 empty] | 203.3275 | 1315.0503 | 2721.7171 | 4255.7243 | 4841.3627 | 6824.2511 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | 8875.2859 | [8 empty] | 167.3292 | 1227.8012 | 2718.8181 | 4272.7665 | 6135.285 | 6758.8434 | 8767.3691 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515 | 10639.4515
40% | [10 empty] | 474.4529 | 2069.885 | 2934.9379 | 5977.8403 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | 9125.3188 | [10 empty] | 472.4498 | 2093.2934 | 4920.5663 | 5877.4669 | 8959.7119 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735 | 11832.5735
35% | [12 empty] | 3.8716 | 560.4187 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | 2003.8769 | [12 empty] | 265.2858 | 528.0265 | 1908.4996 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332 | 3584.4332
30% | [45 empty] | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151 | 90.9151
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1047.0217 | 370.2909 | 967.4586 | 2394.5434 | 4430.4648 | 6733.6002 | 10650.0061 | 15871.5872 | 22179.118 | 29405.186 | 36720.2539 | 45772.3176 | 49487.9623 | 62726.003 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | 77286.7823 | E @ R (MWh) | 2494.5618 | 1198.7985 | 2449.6557 | 4612.8752 | 7203.004 | 10570.0505 | 14750.6849 | 21787.1338 | 28968.0357 | 36704.1588 | 45878.566 | 58024.6116 | 62275.2981 | 76501.2272 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131 | 90240.9131
Option 8 Winter POE50 W E @ R (MWh) N 2 | 732.9152 | 259.2037 | 677.221 | 1676.1804 | 3101.3253 | 4713.5201 | 7455.0043 | 11110.111 | 15525.3826 | 20583.6302 | 25704.1777 | 32040.6223 | 34641.5736 | 43908.2021 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | 54100.7476 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 748.3685 | 359.6395 | 734.8967 | 1383.8626 | 2160.9012 | 3171.0152 | 4425.2055 | 6536.1402 | 8690.4107 | 11011.2476 | 13763.5698 | 17407.3835 | 18682.5894 | 22950.3682 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739 | 27072.2739
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22.6224 | 20.765 | 22.5879 | 24.1137 | 25.4654 | 27.5949 | 29.5198 | 32.1902 | 34.9744 | 37.2495 | 39.3954 | 42.5804 | 44.8961 | 47.2293 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006 | 49.7006
98% | 16.5594 | 14.6718 | 16.2658 | 17.5277 | 19.0237 | 20.5662 | 22.2043 | 24.0785 | 26.2844 | 28.3516 | 30.524 | 34.2201 | 35.4777 | 37.8454 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 | 39.657 |  | 44.451 | 40.7735 | 44.3828 | 47.4037 | 50.0798 | 54.2961 | 58.1073 | 63.3944 | 68.9067 | 73.4112 | 77.6599 | 83.9659 | 88.5508 | 93.1703 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631 | 98.0631
97% | 16.2201 | 14.3516 | 15.9295 | 17.1785 | 18.6593 | 20.1862 | 21.8077 | 23.6628 | 25.8463 | 27.8925 | 30.0429 | 33.7014 | 34.9463 | 37.29 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 | 39.0831 |  | 65.4859 | 60.0257 | 65.3846 | 69.87 | 73.8434 | 80.1037 | 85.7624 | 93.6125 | 101.7971 | 108.4851 | 114.7936 | 124.1565 | 130.964 | 137.823 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876 | 145.0876
95% | 15.7111 | 13.8713 | 15.4249 | 16.6548 | 18.1128 | 19.6161 | 21.2127 | 23.0393 | 25.1892 | 27.2039 | 29.3212 | 32.9235 | 34.1492 | 36.4568 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 | 38.2224 |  | 127.4 | 116.6476 | 127.2006 | 136.0333 | 143.8578 | 156.1858 | 167.3291 | 182.7878 | 198.9051 | 212.0754 | 224.4981 | 242.9359 | 256.3414 | 269.8484 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541 | 284.1541
90% | 130.7104 | 114.7563 | 128.2287 | 138.8937 | 151.5375 | 164.5746 | 178.4195 | 194.2596 | 212.9031 | 230.3749 | 248.7356 | 279.974 | 290.603 | 310.6149 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 | 325.9255 |  | 178.5986 | 163.058 | 178.3104 | 191.0765 | 202.3853 | 220.203 | 236.3086 | 258.6513 | 281.9458 | 300.981 | 318.9357 | 345.5841 | 364.9593 | 384.4811 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573 | 405.1573
85% | 115.4398 | 100.3481 | 113.0923 | 123.1808 | 135.1411 | 147.4735 | 160.5701 | 175.554 | 193.1897 | 209.7171 | 227.0853 | 256.6352 | 266.6896 | 285.6197 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 | 300.1028 |  | 303.619 | 275.8513 | 303.104 | 325.9143 | 346.1208 | 377.9573 | 406.7345 | 446.6561 | 488.2784 | 522.2902 | 554.3716 | 601.9865 | 636.6058 | 671.4871 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311 | 708.4311
80% | 111.2991 | 95.4888 | 108.8398 | 119.4088 | 131.9386 | 144.8582 | 158.5785 | 174.2759 | 192.7514 | 210.0658 | 228.2611 | 259.2181 | 269.7513 | 289.5829 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 | 304.7556 |  | 222.2583 | 200.6975 | 221.8584 | 239.57 | 255.2597 | 279.9798 | 302.3245 | 333.3224 | 365.6409 | 392.0501 | 416.9603 | 453.9319 | 480.8128 | 507.8971 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583 | 536.583
75% | 150.9309 | 127.1676 | 147.2345 | 163.12 | 181.9528 | 201.3713 | 221.9933 | 245.5869 | 273.3561 | 299.3802 | 326.7283 | 373.2576 | 389.0894 | 418.8968 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 | 441.7019 |  | 222.2599 | 199.1124 | 221.8307 | 240.8456 | 257.6901 | 284.2293 | 308.2184 | 341.4976 | 376.1945 | 404.5472 | 431.2907 | 470.9831 | 499.8423 | 528.9197 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167 | 559.7167
70% | 355.8769 | 291.9649 | 345.9354 | 388.6595 | 439.3106 | 491.5371 | 547.0002 | 610.4557 | 685.1415 | 755.1337 | 828.6866 | 953.828 | 996.4079 | 1076.5754 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 | 1137.91 |  | 285.7656 | 253.2844 | 285.1632 | 311.8455 | 335.482 | 372.7226 | 406.3848 | 453.083 | 501.7706 | 541.5558 | 579.0829 | 634.7803 | 675.2763 | 716.0785 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937 | 759.2937
65% | 386.5423 | 303.7538 | 373.6646 | 429.0075 | 494.6183 | 562.2701 | 634.1144 | 716.3116 | 813.056 | 903.7206 | 998.9975 | 1161.0998 | 1216.2557 | 1320.1009 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 | 1399.5507 |  | 297.6766 | 259.8752 | 296.9755 | 328.0282 | 355.5363 | 398.8766 | 438.0523 | 492.3994 | 549.0617 | 595.3635 | 639.0373 | 703.8576 | 750.9864 | 798.4718 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653 | 848.7653
60% | 1120.4925 | 811.4729 | 1072.4245 | 1278.9995 | 1523.9013 | 1776.4207 | 2044.5895 | 2351.402 | 2712.5139 | 3050.9321 | 3406.5666 | 4011.6358 | 4217.5128 | 4605.1294 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 | 4901.687 |  | 642.9947 | 548.4913 | 641.2421 | 718.8737 | 787.6439 | 895.9948 | 993.9341 | 1129.8017 | 1271.4575 | 1387.2119 | 1496.3964 | 1658.4471 | 1776.2693 | 1894.9828 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165 | 2020.7165
55% | 1447.5067 | 844.7507 | 1353.748 | 1756.6813 | 2234.3727 | 2726.9226 | 3249.9973 | 3848.4481 | 4552.8123 | 5212.9114 | 5906.5916 | 7086.8049 | 7488.3769 | 8244.4394 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 | 8822.8878 |  | 464.401 | 380.678 | 462.8484 | 531.6242 | 592.5495 | 688.5403 | 775.3074 | 895.676 | 1021.1726 | 1123.7224 | 1220.4518 | 1364.0167 | 1468.3984 | 1573.5698 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605 | 1684.9605
50% | 1023.5986 | 186.306 | 855.6256 | 1579.9211 | 2439.4694 | 3325.7539 | 4266.9641 | 5343.8046 | 6611.2235 | 7798.9926 | 9047.1869 | 11170.839 | 11893.4197 | 13253.8635 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 | 14294.7119 |  | 758.1769 | 570.9902 | 754.7055 | 908.4736 | 1044.6895 | 1259.3045 | 1453.2969 | 1722.4155 | 2002.9989 | 2232.2783 | 2448.5445 | 2769.5249 | 3002.9001 | 3238.0408 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867 | 3487.0867
45% | 3.8607 |  |  | 128.7608 | 642.1854 | 1516.7957 | 2527.9377 | 3684.7872 | 5046.3752 | 6322.3953 | 7663.3303 | 9944.7695 | 10721.0378 | 12182.5623 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 | 13300.7456 |  | 994.5681 | 550.3323 | 986.3297 | 1351.2559 | 1674.5265 | 2183.8559 | 2644.2434 | 3282.9219 | 3948.8091 | 4492.9405 | 5006.1885 | 5767.9468 | 6321.7982 | 6879.8398 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814 | 7470.8814
40% | [5 empty] | 30.864 | 518.0035 | 1729.8767 | 3723.2143 | 5618.6184 | 7610.4472 | 10999.3037 | 12152.3749 | 14323.3278 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 | 15984.2806 |  | 245.2232 | 6.1061 | 237.7967 | 666.3272 | 1199.3612 | 2097.1486 | 2908.6668 | 4034.4559 | 5208.2054 | 6167.3376 | 7072.0323 | 8414.7724 | 9391.038 | 10374.6896 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51 | 11416.51
35% | [8 empty] | 260.8444 | 1291.6349 | 3113.9117 | 6839.6111 | 8107.4308 | 10494.4273 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | 12320.6707 | [5 empty] | 6.0897 | 256.3183 | 767.9228 | 1830.1246 | 3013.7375 | 3980.9297 | 4893.2269 | 6247.2505 | 7231.72 | 8223.6376 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128 | 9274.2128
30% | [11 empty] | 257.78 | 456.7488 | 964.1965 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | 1441.1716 | [8 empty] | 68.044 | 794.1592 | 1909.9605 | 3334.2353 | 5630.2335 | 7299.5843 | 8981.5646 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098 | 10763.0098
25% | FY39: 17.9814; FY40: 17.9814; FY41: 17.9814; FY42: 17.9814; FY43: 17.9814; FY44: 17.9814; FY45: 17.9814; FY46: 17.9814; FY47: 17.9814; FY48: 17.9814; FY49: 17.9814; FY50: 17.9814; FY51: 17.9814; FY52: 17.9814; FY53: 17.9814; FY54: 17.9814 | [11 empty] | 5.1692 | 579.6374 | 1537.8682 | 2907.3948 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579 | 4752.8579
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 4894.7486 | 2918.9038 | 4546.4136 | 6157.9939 | 8430.2235 | 11149.2101 | 14573.3927 | 19145.5429 | 25354.7011 | 31987.3251 | 39696.4168 | 53695.6017 | 58570.2717 | 67880.9291 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | 75111.0455 | E @ R (MWh) | 4875.5009 | 3646.6886 | 4849.7207 | 6091.2554 | 7350.5809 | 9633.3116 | 11982.1132 | 15661.0344 | 20228.0154 | 24482.3898 | 28872.2704 | 36136.5914 | 41958.8115 | 48229.1261 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882 | 55265.1882
Option 8 Summer POE50 W E @ R (MWh) N 2 | 3426.324 | 2043.2327 | 3182.4895 | 4310.5957 | 5901.1564 | 7804.447 | 10201.3749 | 13401.88 | 17748.2908 | 22391.1276 | 27787.4917 | 37586.9212 | 40999.1902 | 47516.6503 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | 52577.7318 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 1462.6503 | 1094.0066 | 1454.9162 | 1827.3766 | 2205.1743 | 2889.9935 | 3594.634 | 4698.3103 | 6068.4046 | 7344.7169 | 8661.6811 | 10840.9774 | 12587.6434 | 14468.7378 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564 | 16579.5564

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-CLN-TRNFMR-9000006730 | 0.2863% | 0.2863% | 0.3164% | 0.3483% | 0.3821% | 0.4177% | 0.4553% | 0.4947% | 0.5362% | 0.5797% | 0.6252% | 0.6728% | 0.7225% | 0.7743% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283%
Tx 2 Pof | DS-CLN-TRNFMR-9000001306 | 0.2863% | 0.2863% | 0.3164% | 0.3483% | 0.3821% | 0.4177% | 0.4553% | 0.4947% | 0.5362% | 0.5797% | 0.6252% | 0.6728% | 0.7225% | 0.7743% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283%
Tx 3 Pof | DS-CLN-TRNFMR-XXXXXXXXXXXX | 0.02036% | 0.02687% | 0.0345% | 0.0433% | 0.05332% | 0.06462% | 0.07725% | 0.09126% | 0.1067% | 0.1236% | 0.142% | 0.1619% | 0.1835% | 0.2066% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315% | 0.2315%
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.593% | 0.5996% | 0.6674% | 0.7399% | 0.8175% | 0.9% | 0.9878% | 1.081% | 1.179% | 1.283% | 1.392% | 1.508% | 1.629% | 1.755% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888% | 1.888%
N-1 Risk |  | 0.2288% | 0.2313% | 0.2575% | 0.2855% | 0.3154% | 0.3472% | 0.3811% | 0.417% | 0.4549% | 0.495% | 0.5372% | 0.5816% | 0.6283% | 0.6772% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284% | 0.7284%
N-2 Risk |  | 0.0002195% | 0.0002283% | 0.0002859% | 0.0003551% | 0.0004377% | 0.0005355% | 0.0006507% | 0.0007854% | 0.0009422% | 0.001124% | 0.001332% | 0.001572% | 0.001845% | 0.002156% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507% | 0.002507%
N Risk |  | 99.77% | 99.77% | 99.74% | 99.71% | 99.68% | 99.65% | 99.62% | 99.58% | 99.54% | 99.5% | 99.46% | 99.42% | 99.37% | 99.32% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27% | 99.27%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0566 | 18.6596 | 37.7703 | 83.6462 | 128.5545 | 196.4131 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.092444 | 0.043841 | 0.10279 | 0.18377 | 0.29815 | 0.53709 | 0.86964 | 1.4573 | 2.3728 | 3.6266 | 5.6712 | 10.7172 | 14.6761 | 27.1123 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.017949 | 0.011121 | 0.022194 | 0.041268 | 0.073214 | 0.12388 | 0.20674 | 0.34568 | 0.55625 | 0.84548 | 1.2402 | 1.8907 | 2.4268 | 3.4057 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058
Total EUE (MWh) - Option 1 | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379
Cost of EUE ($) - Option 1 | 4864.6794 | 2421.9949 | 5507.6886 | 9916.5036 | 16364.7539 | 29126.8 | 47432.9909 | 79451.582 | 351900.6346 | 1019340.7263 | 1968986.7348 | 4241628.1423 | 6418678.4351 | 10000158.5215 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442
Hours at Risk pA. (Hrs) (N) | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 5.1324 | 8.5358 | 14.9646 | 20.2589 | 26.3096 | 26.3096 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687 | 37.1687
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4386 | 17.7416 | 38.2239 | 68.5017 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264 | 111.7264
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.092444 | 0.043841 | 0.10279 | 0.012794 | 0.040593 | 0.11785 | 0.23867 | 0.49414 | 0.94265 | 1.537 | 2.377 | 4.3202 | 6.0443 | 9.7958 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469 | 16.5469
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.017949 | 0.011121 | 0.022194 | 0.0085424 | 0.016867 | 0.03487 | 0.071214 | 0.14398 | 0.2659 | 0.4452 | 0.70277 | 1.1687 | 1.5461 | 2.3011 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603 | 3.2603
Total EUE (MWh) - Option 2 | 0.11039 | 0.054962 | 0.12498 | 0.021336 | 0.057459 | 0.15272 | 0.30988 | 0.63812 | 1.2085 | 1.9822 | 4.5184 | 23.2306 | 45.8142 | 80.5986 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336 | 131.5336
Cost of EUE ($) - Option 2 | 4864.6794 | 2421.9949 | 5507.6886 | 940.2213 | 2532.0626 | 6730.1167 | 13655.5504 | 28120.0743 | 53256.9679 | 87350.6992 | 199110.7338 | 1023699.7325 | 2018891.0649 | 3551733.1481 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183 | 5796281.0183
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0566 | 18.6596 | 37.7703 | 83.6462 | 128.5545 | 196.4131 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.092444 | 0.043841 | 0.10279 | 0.18377 | 0.29815 | 0.53709 | 0.86964 | 1.4573 | 2.3728 | 3.6266 | 5.6712 | 10.7172 | 14.6761 | 27.1123 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.017949 | 0.011121 | 0.022194 | 0.041268 | 0.073214 | 0.12388 | 0.20674 | 0.34568 | 0.55625 | 0.84548 | 1.2402 | 1.8907 | 2.4268 | 3.4057 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058
Total EUE (MWh) - Option 3 | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379
Cost of EUE ($) - Option 3 | 4864.6794 | 2421.9949 | 5507.6886 | 9916.5036 | 16364.7539 | 29126.8 | 47432.9909 | 79451.582 | 351900.6346 | 1019340.7263 | 1968986.7348 | 4241628.1423 | 6418678.4351 | 10000158.5215 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6466 | 21.4172 | 44.081 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006 | 78.4006
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.092444 | 0.043841 | 0.10279 | 3.4067e-05 | 0.0075092 | 0.052892 | 0.13456 | 0.3236 | 0.64895 | 1.1071 | 1.7715 | 3.2605 | 4.5837 | 7.2649 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668 | 11.8668
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.017949 | 0.011121 | 0.022194 | 0.0050909 | 0.009631 | 0.020058 | 0.043186 | 0.096859 | 0.19383 | 0.34075 | 0.55798 | 0.96318 | 1.2903 | 1.9647 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379 | 2.8379
Total EUE (MWh) - Option 4 | 0.11039 | 0.054962 | 0.12498 | 0.005125 | 0.01714 | 0.07295 | 0.17775 | 0.42046 | 0.84278 | 1.4479 | 2.3295 | 10.8702 | 27.2912 | 53.3106 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053 | 93.1053
Cost of EUE ($) - Option 4 | 4864.6794 | 2421.9949 | 5507.6886 | 225.8437 | 755.3156 | 3214.669 | 7832.7725 | 18528.4452 | 37138.6418 | 63803.9001 | 102653.392 | 479015.8831 | 1202639.6973 | 2349234.4826 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865 | 4102864.3865
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0566 | 18.6596 | 37.7703 | 83.6462 | 128.5545 | 196.4131 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.092444 | 0.043841 | 0.10279 | 0.18377 | 0.29815 | 0.53709 | 0.86964 | 1.4573 | 2.3728 | 3.6266 | 5.6712 | 10.7172 | 14.6761 | 27.1123 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.017949 | 0.011121 | 0.022194 | 0.041268 | 0.073214 | 0.12388 | 0.20674 | 0.34568 | 0.55625 | 0.84548 | 1.2402 | 1.8907 | 2.4268 | 3.4057 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058
Total EUE (MWh) - Option 5 | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379
Cost of EUE ($) - Option 5 | 4864.6794 | 2421.9949 | 5507.6886 | 9916.5036 | 16364.7539 | 29126.8 | 47432.9909 | 79451.582 | 351900.6346 | 1019340.7263 | 1968986.7348 | 4241628.1423 | 6418678.4351 | 10000158.5215 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3432 | 6.4982 | 26.5947 | 49.9167 | 82.0843 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628 | 126.3628
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.029827 | 0.0026794 | 0.024405 | 0.059086 | 0.11043 | 0.22784 | 0.39604 | 0.73217 | 1.2743 | 1.9605 | 2.9203 | 5.17 | 7.0379 | 11.3263 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288 | 18.9288
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0084901 | 0.0046286 | 0.0090787 | 0.017062 | 0.033036 | 0.061283 | 0.11124 | 0.1999 | 0.34035 | 0.54035 | 0.82018 | 1.3063 | 1.694 | 2.4626 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227 | 3.4227
Total EUE (MWh) - Option 6 | 0.038317 | 0.007308 | 0.033484 | 0.076149 | 0.14347 | 0.28912 | 0.50728 | 0.93206 | 1.6147 | 2.8441 | 10.2387 | 33.0711 | 58.6485 | 95.8732 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143 | 148.7143
Cost of EUE ($) - Option 6 | 1688.5106 | 322.043 | 1475.5367 | 3355.6313 | 6322.3159 | 12740.8198 | 22354.4887 | 41073.2092 | 71154.7363 | 125330.3226 | 451188.7248 | 1457340.2167 | 2584460.1154 | 4224837.0696 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937 | 6553383.9937
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0566 | 18.6596 | 37.7703 | 83.6462 | 128.5545 | 196.4131 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.092444 | 0.043841 | 0.10279 | 0.18377 | 0.29815 | 0.53709 | 0.86964 | 1.4573 | 2.3728 | 3.6266 | 5.6712 | 10.7172 | 14.6761 | 27.1123 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.017949 | 0.011121 | 0.022194 | 0.041268 | 0.073214 | 0.12388 | 0.20674 | 0.34568 | 0.55625 | 0.84548 | 1.2402 | 1.8907 | 2.4268 | 3.4057 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058
Total EUE (MWh) - Option 7 | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379
Cost of EUE ($) - Option 7 | 4864.6794 | 2421.9949 | 5507.6886 | 9916.5036 | 16364.7539 | 29126.8 | 47432.9909 | 79451.582 | 351900.6346 | 1019340.7263 | 1968986.7348 | 4241628.1423 | 6418678.4351 | 10000158.5215 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0566 | 18.6596 | 37.7703 | 83.6462 | 128.5545 | 196.4131 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641 | 279.5641
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.092444 | 0.043841 | 0.10279 | 0.18377 | 0.29815 | 0.53709 | 0.86964 | 1.4573 | 2.3728 | 3.6266 | 5.6712 | 10.7172 | 14.6761 | 27.1123 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268 | 49.268
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.017949 | 0.011121 | 0.022194 | 0.041268 | 0.073214 | 0.12388 | 0.20674 | 0.34568 | 0.55625 | 0.84548 | 1.2402 | 1.8907 | 2.4268 | 3.4057 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058 | 4.6058
Total EUE (MWh) - Option 8 | 0.11039 | 0.054962 | 0.12498 | 0.22503 | 0.37136 | 0.66097 | 1.0764 | 1.803 | 7.9856 | 23.1316 | 44.6817 | 96.2542 | 145.6575 | 226.9311 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379 | 333.4379
Cost of EUE ($) - Option 8 | 4864.6794 | 2421.9949 | 5507.6886 | 9916.5036 | 16364.7539 | 29126.8 | 47432.9909 | 79451.582 | 351900.6346 | 1019340.7263 | 1968986.7348 | 4241628.1423 | 6418678.4351 | 10000158.5215 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442 | 14693586.6442