## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 162349945.5089 | 67.2% | 33.0819
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 70185987.1383 | 29.05% | 9.9906
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 3438927.3871 | 1.423% | 0.4767
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 5622421.9462 | 2.327% | 0.5178
[5 empty] | 241597281.9805 |  | 44.0669
Customer No. and Vol per Feeder | [6 empty] | 44066.9381 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 70185987.1383 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 0.20739 | E@R MWh | 0.20739
RESIDENTL | 162349945.5089 | [14 empty] | cost of EUE ($) | 9139.1494 | cost of EUE ($M) | 0.0091391
FARM | 5622421.9462
INDUSTRIAL | 3438927.3871
Forecast (FCT)
Forecast | 2031
Summer POE50 | 110.9215
Summer POE10 | 127.4706
Winter POE50 | 96.4157
Winter POE10 | 101.0611
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 16.69 |  | Summer POE50 | 92.5648 |  |  | 100% | 0 | 92.5648 | 100% |  | 0% |  | 0%
|  |  | Summer POE10 | 109.1139 |  |  | 99% | 0 | 91.6392 | 99% |  | 0% | 0 | 0% | 0
Embedded Generation |  |  | Winter POE50 | 78.0591 |  |  | 98% | 0.37816 | 90.7135 | 98% |  | 0% | 0.74738 | 0% | 17.6135
|  |  | Winter POE10 | 82.7045 |  |  | 97% | 0.75633 | 89.7879 | 97% |  | 0% | 0.39733 | 0% | 17.2635
Year | 2031 | [5 empty] | 95% | 1.1345 | 87.9366 | 95% |  | 0% | 0.035295 | 0% | 16.7384
Capacity | 0 | [5 empty] | 90% | 4.538 | 83.3083 | 90% |  | 0% |  | 0% | 139.619
[7 empty] | 85% | 7.9414 | 78.6801 | 85% |  | 0% |  | 0% | 123.8669
Demand Mangement | [6 empty] | 80% | 11.7231 | 74.0518 | 80% |  | 0% |  | 0% | 120.1275
[7 empty] | 75% | 17.7737 | 69.4236 | 75% |  | 0% |  | 0% | 164.2003
Year | 2031 | [5 empty] | 70% | 35.1693 | 64.7954 | 70% |  | 0% |  | 0% | 391.565
Capacity | 1.6667 | [5 empty] | 65% | 59.3718 | 60.1671 | 65% |  | 0% |  | 0% | 432.771
[7 empty] | 60% | 156.9382 | 55.5389 | 60% |  | 0% |  | 0% | 1293.0474
LDC | [6 empty] | 55% | 363.794 | 50.9106 | 55% |  | 0% |  | 0% | 1784.0823
[7 empty] | 50% | 771.4551 | 46.2824 | 50% |  | 0% |  | 0% | 1629.226
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 1255.5054 | 41.6542 | 45% |  | 0% |  | 0% | 148.0142
100% | 0% | 0 |  |  |  |  | 40% | 2059.1045 | 37.0259 | 40% |  | 0% |  | 0%
99% | 0% | 0 |  |  |  |  | 35% | 3060.4836 | 32.3977 | 35% |  | 0% |  | 0%
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3366.0403 | 27.7694 | 30% |  | 0% |  | 0%
97% | 0.01722% | 0.75633 |  |  |  |  | 25% | 3686.3454 | 23.1412 | 25% |  | 0% |  | 0%
95% | 0.02583% | 1.1345 |  |  |  |  | 20% | 4028.5841 | 18.513 | 20% |  | 0% |  | 0%
90% | 0.1033% | 4.538 |  |  |  |  | 15% | 4345.1076 | 13.8847 | 15% |  | 0% |  | 0%
85% | 0.1808% | 7.9414 |  |  |  |  | 10% | 4381.0332 | 9.2565 | 10% |  | 0% |  | 0%
80% | 0.2669% | 11.7231 |  |  |  |  | 5% | 4391.6218 | 4.6282 | 5% |  | 0% |  | 0%
75% | 0.4047% | 17.7737 |  |  |  |  | 9.992e-14% | 4391.6218 | 9.2491e-14 | 9.992e-14% |  | 0% |  | 0%
70% | 0.8008% | 35.1693 | [7 empty] | Total E@R | 0 | Total E@R | 1.18 | Total E@R | 6278.1349
65% | 1.352% | 59.3718 | [7 empty] | Total WE@R | 0 | Total WE@R | 0.0027909 | Total WE@R | 0.016903
60% | 3.573% | 156.9382 |  |  |  |  | MD Weighted LDC
55% | 8.283% | 363.794
50% | 17.57% | 771.4551 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 28.59% | 1255.5054 |  |  |  |  | 100% | 0 | 109.1139 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 46.88% | 2059.1045 |  |  |  |  | 99% | 0.37816 | 108.0228
35% | 69.68% | 3060.4836 |  |  |  |  | 98% | 1.1345 | 106.9316 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 76.64% | 3366.0403 |  |  |  |  | 97% | 2.269 | 105.8405 | 100% |  | 0% |  | 0%
25% | 83.93% | 3686.3454 |  |  |  |  | 95% | 4.538 | 103.6582 | 99% |  | 0% | 7.3244 | 0% | 24.1905
20% | 91.73% | 4028.5841 |  |  |  |  | 90% | 7.9414 | 98.2025 | 98% |  | 0% | 13.8236 | 0% | 47.5558
15% | 98.93% | 4345.1076 |  |  |  |  | 85% | 14.3702 | 92.7468 | 97% |  | 0% | 19.4975 | 0% | 70.0958
10% | 99.75% | 4381.0332 |  |  |  |  | 80% | 19.6645 | 87.2911 | 95% |  | 0% | 35.2812 | 0% | 136.478
5% | 99.99% | 4391.6218 |  |  |  |  | 75% | 25.7152 | 81.8354 | 90% |  | 0% | 39.924 | 0% | 191.7192
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 34.7911 | 76.3797 | 85% |  | 0% | 40.3385 | 0% | 327.0627
[7 empty] | 65% | 46.136 | 70.924 | 80% |  | 0% | 6.1039 | 0% | 240.4616
[7 empty] | 60% | 76.7673 | 65.4683 | 75% |  | 0% |  | 0% | 241.8029
[7 empty] | 55% | 106.2642 | 60.0126 | 70% |  | 0% |  | 0% | 313.1888
LDC | [6 empty] | 50% | 178.4935 | 54.5569 | 65% |  | 0% |  | 0% | 329.5915
[7 empty] | 45% | 367.9538 | 49.1013 | 60% |  | 0% |  | 0% | 722.782
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 741.202 | 43.6456 | 55% |  | 0% |  | 0% | 535.0867
100% | 0% | 0 |  |  |  |  | 35% | 1167.7713 | 38.1899 | 50% |  | 0% |  | 0% | 916.215
99% | 0.00861% | 0.37816 |  |  |  |  | 30% | 2002.3799 | 32.7342 | 45% |  | 0% |  | 0% | 1369.6278
98% | 0.02583% | 1.1345 |  |  |  |  | 25% | 3173.5547 | 27.2785 | 40% |  | 0% |  | 0% | 693.0821
97% | 0.05166% | 2.269 |  |  |  |  | 20% | 3477.5988 | 21.8228 | 35% |  | 0% |  | 0%
95% | 0.1033% | 4.538 |  |  |  |  | 15% | 3788.4498 | 16.3671 | 30% |  | 0% |  | 0%
90% | 0.1808% | 7.9414 |  |  |  |  | 10% | 4317.5016 | 10.9114 | 25% |  | 0% |  | 0%
85% | 0.3272% | 14.3702 |  |  |  |  | 5% | 4391.6218 | 5.4557 | 20% |  | 0% |  | 0%
80% | 0.4477% | 19.6645 |  |  |  |  | 9.992e-14% | 4391.6218 | 1.0903e-13 | 15% |  | 0% |  | 0%
75% | 0.5855% | 25.7152 | [7 empty] | 10% |  | 0% |  | 0%
70% | 0.7921% | 34.7911 | [7 empty] | 5% |  | 0% |  | 0%
65% | 1.05% | 46.136 | [7 empty] | 9.992e-14% |  | 0% |  | 0%
60% | 1.748% | 76.7673 | [7 empty] | Total E@R | 0 | Total E@R | 162.293 | Total E@R | 6158.9404
55% | 2.419% | 106.2642 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.16451 | Total WE@R | 0.0071066
50% | 4.064% | 178.4935
45% | 8.378% | 367.9538 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 16.88% | 741.202 |  |  |  |  | 100% | 0 | 78.0591
35% | 26.59% | 1167.7713 |  |  |  |  | 99% | 0.5944 | 77.2785 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 45.59% | 2002.3799 |  |  |  |  | 98% | 0.8916 | 76.4979
25% | 72.26% | 3173.5547 |  |  |  |  | 97% | 1.486 | 75.7173 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 79.18% | 3477.5988 |  |  |  |  | 95% | 2.3776 | 74.1561 | 100% |  | 0% |  | 0%
15% | 86.26% | 3788.4498 |  |  |  |  | 90% | 3.2692 | 70.2532 | 99% |  | 0% |  | 0% | 17.1001
10% | 98.3% | 4317.5016 |  |  |  |  | 85% | 13.9683 | 66.3502 | 98% |  | 0% |  | 0% | 8.318
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 41.3106 | 62.4473 | 97% |  | 0% |  | 0% | 16.1721
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 126.3094 | 58.5443 | 95% |  | 0% |  | 0% | 23.2142
[7 empty] | 70% | 323.9464 | 54.6414 | 90% |  | 0% |  | 0% | 20.7783
[7 empty] | 65% | 549.5201 | 50.7384 | 85% |  | 0% |  | 0% | 207.5815
[7 empty] | 60% | 799.4641 | 46.8354 | 80% |  | 0% |  | 0% | 423.7706
LDC | [6 empty] | 55% | 1116.2777 | 42.9325 | 75% |  | 0% |  | 0% | 985.6274
[7 empty] | 50% | 1494.9086 | 39.0295 | 70% |  | 0% |  | 0% | 1520.3879
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 2004.0097 | 35.1266 | 65% |  | 0% |  | 0% | 854.8962
100% | 0% | 0 |  |  |  |  | 40% | 2877.179 | 31.2236 | 60% |  | 0% |  | 0% | 108.2178
99% | 0.01353% | 0.5944 |  |  |  |  | 35% | 3454.933 | 27.3207 | 55% |  | 0% |  | 0%
98% | 0.0203% | 0.8916 |  |  |  |  | 30% | 3663.5664 | 23.4177 | 50% |  | 0% |  | 0%
97% | 0.03383% | 1.486 |  |  |  |  | 25% | 3862.6894 | 19.5148 | 45% |  | 0% |  | 0%
95% | 0.05413% | 2.3776 |  |  |  |  | 20% | 4122.7381 | 15.6118 | 40% |  | 0% |  | 0%
90% | 0.07443% | 3.2692 |  |  |  |  | 15% | 4372.3849 | 11.7089 | 35% |  | 0% |  | 0%
85% | 0.318% | 13.9683 |  |  |  |  | 10% | 4374.4653 | 7.8059 | 30% |  | 0% |  | 0%
80% | 0.9406% | 41.3106 |  |  |  |  | 5% | 4374.7625 | 3.903 | 25% |  | 0% |  | 0%
75% | 2.876% | 126.3094 |  |  |  |  | 9.992e-14% | 4375.9513 | 7.7997e-14 | 20% |  | 0% |  | 0%
70% | 7.376% | 323.9464 | [7 empty] | 15% |  | 0% |  | 0%
65% | 12.51% | 549.5201 | [7 empty] | 10% |  | 0% |  | 0%
60% | 18.2% | 799.4641 | [7 empty] | 5% |  | 0% |  | 0%
55% | 25.42% | 1116.2777 | [7 empty] | 9.992e-14% |  | 0% |  | 0%
50% | 34.04% | 1494.9086 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 0 | Total E@R | 4186.0642
45% | 45.63% | 2004.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 0 | Total WE@R | 0.0095755
40% | 65.51% | 2877.179 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 78.66% | 3454.933 |  |  |  |  | 100% | 0 | 82.7045 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 83.41% | 3663.5664 |  |  |  |  | 99% | 0.5944 | 81.8774
25% | 87.95% | 3862.6894 |  |  |  |  | 98% | 0.8916 | 81.0504 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 93.87% | 4122.7381 |  |  |  |  | 97% | 1.486 | 80.2233 | 100% |  | 100% |  | 100%
15% | 99.55% | 4372.3849 |  |  |  |  | 95% | 2.3776 | 78.5692 | 99% |  | 99% |  | 99% | 19.8475
10% | 99.6% | 4374.4653 |  |  |  |  | 90% | 3.2692 | 74.434 | 98% |  | 98% |  | 98% | 9.6779
5% | 99.61% | 4374.7625 |  |  |  |  | 85% | 13.9683 | 70.2988 | 97% |  | 97% |  | 97% | 18.8643
9.992e-14% | 99.63% | 4375.9513 |  |  |  |  | 80% | 41.3106 | 66.1636 | 95% |  | 95% |  | 95% | 27.1904
[7 empty] | 75% | 126.3094 | 62.0284 | 90% |  | 90% |  | 90% | 24.6095
[7 empty] | 70% | 323.9464 | 57.8931 | 85% |  | 85% |  | 85% | 251.0706
[7 empty] | 65% | 549.5201 | 53.7579 | 80% |  | 80% |  | 80% | 528.5585
LDC | [6 empty] | 60% | 799.4641 | 49.6227 | 75% |  | 75% |  | 75% | 1291.6386
[7 empty] | 55% | 1116.2777 | 45.4875 | 70% |  | 70% |  | 70% | 2186.0122
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 1494.9086 | 41.3522 | 65% |  | 65% |  | 65% | 1562.2148
100% | 0% | 0 |  |  |  |  | 45% | 2004.0097 | 37.217 | 60% |  | 60% |  | 60% | 697.4174
99% | 0.01353% | 0.5944 |  |  |  |  | 40% | 2877.179 | 33.0818 | 55% |  | 55% |  | 55% | 20.0065
98% | 0.0203% | 0.8916 |  |  |  |  | 35% | 3454.933 | 28.9466 | 50% |  | 50% |  | 50%
97% | 0.03383% | 1.486 |  |  |  |  | 30% | 3663.5664 | 24.8113 | 45% |  | 45% |  | 45%
95% | 0.05413% | 2.3776 |  |  |  |  | 25% | 3862.6894 | 20.6761 | 40% |  | 40% |  | 40%
90% | 0.07443% | 3.2692 |  |  |  |  | 20% | 4122.7381 | 16.5409 | 35% |  | 35% |  | 35%
85% | 0.318% | 13.9683 |  |  |  |  | 15% | 4372.3849 | 12.4057 | 30% |  | 30% |  | 30%
80% | 0.9406% | 41.3106 |  |  |  |  | 10% | 4374.4653 | 8.2704 | 25% |  | 25% |  | 25%
75% | 2.876% | 126.3094 |  |  |  |  | 5% | 4374.7625 | 4.1352 | 20% |  | 20% |  | 20%
70% | 7.376% | 323.9464 |  |  |  |  | 9.992e-14% | 4375.9513 | 8.2638e-14 | 15% |  | 15% |  | 15%
65% | 12.51% | 549.5201 | [7 empty] | 10% |  | 10% |  | 10%
60% | 18.2% | 799.4641 | [7 empty] | 5% |  | 5% |  | 5%
55% | 25.42% | 1116.2777 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14%
50% | 34.04% | 1494.9086 | [7 empty] | Total E@R | 0 | Total E@R | 0 | Total E@R | 6637.1083
45% | 45.63% | 2004.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 0 | Total WE@R | 0.0065067
40% | 65.51% | 2877.179
35% | 78.66% | 3454.933
30% | 83.41% | 3663.5664
25% | 87.95% | 3862.6894
20% | 93.87% | 4122.7381
15% | 99.55% | 4372.3849
10% | 99.6% | 4374.4653
5% | 99.61% | 4374.7625
9.992e-14% | 99.63% | 4375.9513
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 130.95 |  |  | Year | 2031
SCR (N-1) | 89.2 |  |  | SCR (N) | 130.95
SCR (N-2) | 44.6 |  |  | SCR (N-1) | 89.2
WCR (N) | 142.95 |  |  | SCR (N-2) | 44.6
WCR (N-1) | 97.8 |  |  | WCR (N) | 142.95
WCR (N-2) | 48.9 |  |  | WCR (N-1) | 97.8
|  |  |  | WCR (N-2) | 48.9
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.00044013 | 6.714e-05 | 0.00024045 | 0.00092528 | 0.0020517 | 0.0048215 | 0.0091391 | 0.017951 | 0.032753 | 0.052215 | 0.089097 | 0.59529 | 1.2957 | 2.3673 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733
Total EUE (MWh) | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Residual Values
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00044013 | 6.714e-05 | 0.00024045 | 8.2414e-05 | 0.00015266 | 0.00084409 | 0.002561 | 0.0070066 | 0.014906 | 0.025984 | 0.042646 | 0.079319 | 0.23898 | 0.77812 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423 | 1.6423
Total EUE (MWh) | 0.0099877 | 0.0015236 | 0.0054564 | 0.0018702 | 0.0034643 | 0.019155 | 0.058117 | 0.159 | 0.33825 | 0.58964 | 0.96775 | 1.8 | 5.4231 | 17.6578 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00044013 | 6.714e-05 | 0.00024045 | 0.00092528 | 0.0020517 | 0.0048215 | 0.0091391 | 0.017951 | 0.032753 | 0.052215 | 0.089097 | 0.59529 | 1.2957 | 2.3673 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733
Total EUE (MWh) | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00044013 | 6.714e-05 | 0.00024045 | 5.2033e-05 | 8.9245e-05 | 0.000177 | 0.0009004 | 0.0036212 | 0.0094098 | 0.017407 | 0.029619 | 0.058541 | 0.084673 | 0.305 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418 | 0.92418
Total EUE (MWh) | 0.0099877 | 0.0015236 | 0.0054564 | 0.0011808 | 0.0020252 | 0.0040166 | 0.020433 | 0.082174 | 0.21353 | 0.39501 | 0.67214 | 1.3284 | 1.9215 | 6.9212 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00044013 | 6.714e-05 | 0.00024045 | 0.00092528 | 0.0020517 | 0.0048215 | 0.0091391 | 0.017951 | 0.032753 | 0.052215 | 0.089097 | 0.59529 | 1.2957 | 2.3673 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733
Total EUE (MWh) | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00044013 | 6.714e-05 | 0.00024045 | 0.00092528 | 0.0020517 | 0.0048215 | 0.0091391 | 0.017951 | 0.032753 | 0.052215 | 0.089097 | 0.59529 | 1.2957 | 2.3673 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733
Total EUE (MWh) | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00044013 | 6.714e-05 | 0.00024045 | 0.00092528 | 0.0020517 | 0.0048215 | 0.0091391 | 0.017951 | 0.032753 | 0.052215 | 0.089097 | 0.59529 | 1.2957 | 2.3673 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733
Total EUE (MWh) | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00044013 | 6.714e-05 | 0.00024045 | 0.00092528 | 0.0020517 | 0.0048215 | 0.0091391 | 0.017951 | 0.032753 | 0.052215 | 0.089097 | 0.59529 | 1.2957 | 2.3673 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733 | 3.9733
Total EUE (MWh) | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646

## Key Model Assumption & Inputs
Select ZSS & Region | CLN | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Low | 90% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1B New PHS ZSS + Three new feeders | 1B New PHS ZSS + Three new feeders
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 |  | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667
Added Transfers (MVA) Option 3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Transfers (MVA) Option 4 |  |  |  | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Transfers (MVA) Option 5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
CLN | N/A | DS-CLN-TRNFMR-XXXXXXXXXXXX | New CLN 3rd TX | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 100 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | CLN
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 89.7351 | 104.3341 | 108.3435 | 111.4611 | 115.2173 | 119.0984 | 123.2461 | 128.0275 | 133.6994 | 139.0092 | 144.6013 | 154.2938 | 157.43 | 163.5566 | 168.1999
Summer POE10 | 10 |  |  | 104.9463 | 119.6766 | 124.2514 | 128.0364 | 131.3686 | 136.7682 | 141.634 | 148.4809 | 155.6302 | 161.4365 | 166.8996 | 175.1342 | 181.0486 | 187.0195 | 193.3671
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 69.1182 | 84.5179 | 88.1502 | 92.8679 | 97.437 | 101.4753 | 107.1286 | 113.3315 | 119.6901 | 125.9989 | 131.579 | 137.6925 | 139.8743 | 147.8441 | 156.1056
Winter POE10 | 10 |  |  | 74.018 | 89.4372 | 93.2911 | 98.0701 | 102.5171 | 107.2692 | 112.2902 | 119.5588 | 125.8642 | 131.807 | 137.993 | 145.465 | 147.8036 | 155.8793 | 163.4009
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | CLN | 0 | 18 | 17.73 | 17.46 | 17.2 | 16.94 | 16.69 | 16.44 | 16.19 | 15.95 | 15.71 | 15.48 | 15.24 | 15.01 | 14.79
|  | PowerFactor | 1

## Load Duration Curves
Station
CLN
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.01353% | 0.5944 | 0.00861% | 0.37816 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.02583% | 1.1345 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.03383% | 1.486 | 0.05166% | 2.269 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.05413% | 2.3776 | 0.1033% | 4.538 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.07443% | 3.2692 | 0.1808% | 7.9414 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 0.318% | 13.9683 | 0.3272% | 14.3702 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 0.9406% | 41.3106 | 0.4477% | 19.6645 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 2.876% | 126.3094 | 0.5855% | 25.7152 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 7.376% | 323.9464 | 0.7921% | 34.7911 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 12.51% | 549.5201 | 1.05% | 46.136 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 18.2% | 799.4641 | 1.748% | 76.7673 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 25.42% | 1116.2777 | 2.419% | 106.2642 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 34.04% | 1494.9086 | 4.064% | 178.4935 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 45.63% | 2004.0097 | 8.378% | 367.9538 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 65.51% | 2877.179 | 16.88% | 741.202 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 78.66% | 3454.933 | 26.59% | 1167.7713 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 83.41% | 3663.5664 | 45.59% | 2002.3799 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 87.95% | 3862.6894 | 72.26% | 3173.5547 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 93.87% | 4122.7381 | 79.18% | 3477.5988 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.55% | 4372.3849 | 86.26% | 3788.4498 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.6% | 4374.4653 | 98.3% | 4317.5016 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.61% | 4374.7625 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.63% | 4375.9513 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.01353% | 0.5944 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.03383% | 1.486 | 0.01722% | 0.75633 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.05413% | 2.3776 | 0.02583% | 1.1345 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.07443% | 3.2692 | 0.1033% | 4.538 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 0.318% | 13.9683 | 0.1808% | 7.9414 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 0.9406% | 41.3106 | 0.2669% | 11.7231 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 2.876% | 126.3094 | 0.4047% | 17.7737 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 7.376% | 323.9464 | 0.8008% | 35.1693 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 12.51% | 549.5201 | 1.352% | 59.3718 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 18.2% | 799.4641 | 3.573% | 156.9382 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 25.42% | 1116.2777 | 8.283% | 363.794 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 34.04% | 1494.9086 | 17.57% | 771.4551 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 45.63% | 2004.0097 | 28.59% | 1255.5054 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 65.51% | 2877.179 | 46.88% | 2059.1045 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 78.66% | 3454.933 | 69.68% | 3060.4836 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 83.41% | 3663.5664 | 76.64% | 3366.0403 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 87.95% | 3862.6894 | 83.93% | 3686.3454 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 93.87% | 4122.7381 | 91.73% | 4028.5841 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.55% | 4372.3849 | 98.93% | 4345.1076 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.6% | 4374.4653 | 99.75% | 4381.0332 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.61% | 4374.7625 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.63% | 4375.9513 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 1 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 2 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 3 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 4 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 5 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 6 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 7 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95 | 142.95
SCR N Rating (MVA) - Option 8 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95 | 130.95
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 1 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 3 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 4 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 5 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 6 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 7 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 97.8
SCR N-1 Rating (MVA) - Option 8 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 89.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 1 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 2 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 3 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 4 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 7 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9 | 48.9
SCR N-2 Rating (MVA) - Option 8 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 62.2064 | 76.0661 | 79.3352 | 83.5811 | 87.6933 | 91.3277 | 96.4157 | 101.9983 | 107.7211 | 113.399 | 118.4211 | 123.9233 | 125.8869 | 133.0597 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495 | 140.495
Maximum Demand (MVA) - P10 | 66.6162 | 80.4935 | 83.962 | 88.2631 | 92.2654 | 96.5423 | 101.0611 | 107.6029 | 113.2777 | 118.6263 | 124.1937 | 130.9185 | 133.0232 | 140.2914 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608 | 147.0608
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 18 | 17.73 | 17.46 | 17.2 | 16.94 | 16.69 | 16.44 | 16.19 | 15.95 | 15.71 | 15.48 | 15.24 | 15.01 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79
Demand management (MVA) | 0 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 80.7616 | 93.9007 | 97.5091 | 100.315 | 103.6955 | 107.1885 | 110.9215 | 115.2248 | 120.3295 | 125.1083 | 130.1411 | 138.8645 | 141.687 | 147.2009 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799 | 151.3799
Maximum Demand (MVA) - P10 | 94.4516 | 107.709 | 111.8263 | 115.2328 | 118.2317 | 123.0914 | 127.4706 | 133.6328 | 140.0671 | 145.2928 | 150.2097 | 157.6208 | 162.9437 | 168.3175 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304 | 174.0304
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 18 | 17.73 | 17.46 | 17.2 | 16.94 | 16.69 | 16.44 | 16.19 | 15.95 | 15.71 | 15.48 | 15.24 | 15.01 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79 | 14.79
Demand management (MVA) | 0 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
Option 2 - 1B New PHS ZSS + Three new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667 | 9.6667
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 62.2064 | 56.3994 | 59.9385 | 54.7877 | 59.16 | 63.0544 | 68.3924 | 74.225 | 80.1977 | 86.1157 | 91.3778 | 97.11 | 99.3135 | 106.7163 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 66.6162 | 60.8268 | 64.5653 | 59.4698 | 63.7321 | 68.2689 | 73.0378 | 79.8296 | 85.7544 | 91.343 | 97.1504 | 104.1052 | 106.4499 | 113.9481 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 80.7616 | 74.234 | 78.1124 | 71.5217 | 75.1622 | 78.9152 | 82.8981 | 87.4514 | 92.8062 | 97.8249 | 103.0978 | 112.0511 | 115.1137 | 120.8576 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 94.4516 | 88.0423 | 92.4296 | 86.4394 | 89.6984 | 94.818 | 99.4472 | 105.8595 | 112.5438 | 118.0095 | 123.1663 | 130.8075 | 136.3704 | 141.9742 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 62.2064 | 56.3994 | 59.9385 | 49.9544 | 54.3267 | 58.2211 | 63.5591 | 69.3917 | 75.3644 | 81.2824 | 86.5445 | 92.2766 | 94.4802 | 101.883 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 66.6162 | 60.8268 | 64.5653 | 54.6364 | 58.8987 | 63.4356 | 68.2045 | 74.9962 | 80.9211 | 86.5097 | 92.317 | 99.2718 | 101.6166 | 109.1147 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 80.7616 | 74.234 | 78.1124 | 66.6883 | 70.3289 | 74.0818 | 78.0648 | 82.6181 | 87.9728 | 92.9916 | 98.2645 | 107.2178 | 110.2804 | 116.0243 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 94.4516 | 88.0423 | 92.4296 | 81.6061 | 84.865 | 89.9847 | 94.6139 | 101.0261 | 107.7105 | 113.1762 | 118.333 | 125.9741 | 131.537 | 137.1409 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 100% | 0 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
99% | 0.5944 | 61.5843 | 55.8354 | 59.3391 | 63.8099 | 68.1384 | 71.9939 | 77.2785 | 83.0527 | 88.9657 | 94.8245 | 100.034 | 105.7089 | 107.8904 | 115.2192 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 99% | 0.5944 | 65.9501 | 60.2186 | 63.9197 | 68.4451 | 72.6648 | 77.1562 | 81.8774 | 88.6013 | 94.4669 | 99.9996 | 105.7489 | 112.6341 | 114.9554 | 122.3786 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981
98% | 0.8916 | 60.9623 | 55.2714 | 58.7397 | 63.1653 | 67.4501 | 71.2667 | 76.4979 | 82.2138 | 88.0671 | 93.8667 | 99.0236 | 104.6411 | 106.8006 | 114.0553 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 98% | 0.8916 | 65.2839 | 59.6103 | 63.274 | 67.7537 | 71.9308 | 76.3769 | 81.0504 | 87.7063 | 93.5127 | 98.9895 | 104.6807 | 111.4964 | 113.7942 | 121.1425 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992
97% | 1.486 | 60.3402 | 54.7074 | 58.1403 | 62.5208 | 66.7619 | 70.5394 | 75.7173 | 81.3749 | 87.1685 | 92.9089 | 98.0131 | 103.5733 | 105.7108 | 112.8915 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 97% | 1.486 | 64.6177 | 59.002 | 62.6284 | 67.0623 | 71.1968 | 75.5975 | 80.2233 | 86.8113 | 92.5584 | 97.9794 | 103.6125 | 110.3587 | 112.6331 | 119.9063 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686
95% | 2.3776 | 59.0961 | 53.5795 | 56.9416 | 61.2317 | 65.3853 | 69.085 | 74.1561 | 79.6971 | 85.3712 | 90.9932 | 95.9922 | 101.4378 | 103.5312 | 110.5638 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 95% | 2.3776 | 63.2854 | 57.7855 | 61.3371 | 65.6796 | 69.7288 | 74.0388 | 78.5692 | 85.0214 | 90.65 | 95.9592 | 101.4762 | 108.0832 | 110.3107 | 117.434 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739
90% | 3.2692 | 55.9857 | 50.7595 | 53.9446 | 58.009 | 61.944 | 65.449 | 70.2532 | 75.5025 | 80.878 | 86.2041 | 90.94 | 96.099 | 98.0822 | 104.7447 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 90% | 3.2692 | 59.9546 | 54.7442 | 58.1088 | 62.2228 | 66.0589 | 70.142 | 74.434 | 80.5466 | 85.879 | 90.9087 | 96.1353 | 102.3947 | 104.5049 | 111.2533 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437
85% | 13.9683 | 52.8754 | 47.9395 | 50.9477 | 54.7863 | 58.5027 | 61.8129 | 66.3502 | 71.3079 | 76.3847 | 81.415 | 85.8878 | 90.7601 | 92.6332 | 98.9255 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 85% | 13.9683 | 56.6238 | 51.7028 | 54.8805 | 58.766 | 62.3889 | 66.2453 | 70.2988 | 76.0718 | 81.1079 | 85.8582 | 90.7945 | 96.7061 | 98.6991 | 105.0725 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135
80% | 41.3106 | 49.7651 | 45.1195 | 47.9508 | 51.5635 | 55.0613 | 58.1769 | 62.4473 | 67.1133 | 71.8915 | 76.6259 | 80.8356 | 85.4213 | 87.1842 | 93.1064 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 80% | 41.3106 | 53.293 | 48.6615 | 51.6523 | 55.3092 | 58.719 | 62.3485 | 66.1636 | 71.597 | 76.3369 | 80.8077 | 85.4536 | 91.0175 | 92.8932 | 98.8918 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833
75% | 126.3094 | 46.6548 | 42.2996 | 44.9539 | 48.3408 | 51.62 | 54.5408 | 58.5443 | 62.9187 | 67.3983 | 71.8368 | 75.7833 | 80.0825 | 81.7352 | 87.2872 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 75% | 126.3094 | 49.9622 | 45.6201 | 48.424 | 51.8523 | 55.0491 | 58.4517 | 62.0284 | 67.1222 | 71.5658 | 75.7573 | 80.1128 | 85.3289 | 87.0874 | 92.7111 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531
70% | 323.9464 | 43.5445 | 39.4796 | 41.9569 | 45.1181 | 48.1787 | 50.9048 | 54.6414 | 58.7242 | 62.9051 | 67.0477 | 70.7311 | 74.7436 | 76.2861 | 81.4681 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 70% | 323.9464 | 46.6314 | 42.5788 | 45.1957 | 48.3955 | 51.3791 | 54.5549 | 57.8931 | 62.6474 | 66.7948 | 70.7068 | 74.7719 | 79.6403 | 81.2816 | 86.5303 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229
65% | 549.5201 | 40.4341 | 36.6596 | 38.96 | 41.8954 | 44.7373 | 47.2687 | 50.7384 | 54.5296 | 58.4119 | 62.2585 | 65.6789 | 69.4048 | 70.8371 | 75.6489 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 65% | 549.5201 | 43.3005 | 39.5374 | 41.9675 | 44.9387 | 47.7092 | 50.6581 | 53.7579 | 58.1726 | 62.0237 | 65.6563 | 69.4311 | 73.9517 | 75.4758 | 80.3496 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927
60% | 799.4641 | 37.3238 | 33.8397 | 35.9631 | 38.6726 | 41.296 | 43.6326 | 46.8354 | 50.335 | 53.9186 | 57.4694 | 60.6267 | 64.066 | 65.3881 | 69.8298 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 60% | 799.4641 | 39.9697 | 36.4961 | 38.7392 | 41.4819 | 44.0392 | 46.7614 | 49.6227 | 53.6977 | 57.2526 | 60.6058 | 64.0902 | 68.2631 | 69.6699 | 74.1688 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625
55% | 1116.2777 | 34.2135 | 31.0197 | 32.9662 | 35.4499 | 37.8547 | 39.9966 | 42.9325 | 46.1404 | 49.4254 | 52.6803 | 55.5745 | 58.7271 | 59.9391 | 64.0106 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 55% | 1116.2777 | 36.6389 | 33.4548 | 35.5109 | 38.025 | 40.3693 | 42.8646 | 45.4875 | 49.2229 | 52.4816 | 55.5553 | 58.7494 | 62.5745 | 63.8641 | 67.9881 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323
50% | 1494.9086 | 31.1032 | 28.1997 | 29.9692 | 32.2272 | 34.4133 | 36.3605 | 39.0295 | 41.9458 | 44.9322 | 47.8912 | 50.5222 | 53.3883 | 54.4901 | 58.1915 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 50% | 1494.9086 | 33.3081 | 30.4134 | 32.2827 | 34.5682 | 36.6994 | 38.9678 | 41.3522 | 44.7481 | 47.7105 | 50.5048 | 53.4085 | 56.8859 | 58.0583 | 61.8074 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021
45% | 2004.0097 | 27.9929 | 25.3797 | 26.9723 | 29.0045 | 30.972 | 32.7245 | 35.1266 | 37.7512 | 40.439 | 43.1021 | 45.47 | 48.0495 | 49.0411 | 52.3723 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 45% | 2004.0097 | 29.9773 | 27.3721 | 29.0544 | 31.1114 | 33.0294 | 35.071 | 37.217 | 40.2733 | 42.9395 | 45.4544 | 48.0677 | 51.1973 | 52.2524 | 55.6266 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719
40% | 2877.179 | 24.8826 | 22.5598 | 23.9754 | 25.7818 | 27.5307 | 29.0884 | 31.2236 | 33.5567 | 35.9458 | 38.3129 | 40.4178 | 42.7106 | 43.5921 | 46.5532 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 40% | 2877.179 | 26.6465 | 24.3307 | 25.8261 | 27.6546 | 29.3595 | 31.1742 | 33.0818 | 35.7985 | 38.1684 | 40.4039 | 42.7268 | 45.5087 | 46.4466 | 49.4459 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417
35% | 3454.933 | 21.7722 | 19.7398 | 20.9785 | 22.559 | 24.0893 | 25.4524 | 27.3207 | 29.3621 | 31.4525 | 33.5238 | 35.3656 | 37.3718 | 38.1431 | 40.734 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 35% | 3454.933 | 23.3157 | 21.2894 | 22.5979 | 24.1978 | 25.6896 | 27.2775 | 28.9466 | 31.3237 | 33.3974 | 35.3534 | 37.386 | 39.8201 | 40.6408 | 43.2652 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114
30% | 3663.5664 | 18.6619 | 16.9198 | 17.9815 | 19.3363 | 20.648 | 21.8163 | 23.4177 | 25.1675 | 26.9593 | 28.7347 | 30.3133 | 32.033 | 32.6941 | 34.9149 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 30% | 3663.5664 | 19.9849 | 18.2481 | 19.3696 | 20.7409 | 22.0196 | 23.3807 | 24.8113 | 26.8489 | 28.6263 | 30.3029 | 32.0451 | 34.1316 | 34.835 | 37.0844 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812
25% | 3862.6894 | 15.5516 | 14.0999 | 14.9846 | 16.1136 | 17.2067 | 18.1803 | 19.5148 | 20.9729 | 22.4661 | 23.9456 | 25.2611 | 26.6942 | 27.2451 | 29.0957 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 25% | 3862.6894 | 16.6541 | 15.2067 | 16.1413 | 17.2841 | 18.3497 | 19.4839 | 20.6761 | 22.3741 | 23.8553 | 25.2524 | 26.7043 | 28.443 | 29.0291 | 30.9037 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651
20% | 4122.7381 | 12.4413 | 11.2799 | 11.9877 | 12.8909 | 13.7653 | 14.5442 | 15.6118 | 16.7783 | 17.9729 | 19.1565 | 20.2089 | 21.3553 | 21.796 | 23.2766 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 20% | 4122.7381 | 13.3232 | 12.1654 | 12.9131 | 13.8273 | 14.6797 | 15.5871 | 16.5409 | 17.8992 | 19.0842 | 20.2019 | 21.3634 | 22.7544 | 23.2233 | 24.7229 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208
15% | 4372.3849 | 9.331 | 8.4599 | 8.9908 | 9.6682 | 10.324 | 10.9082 | 11.7089 | 12.5837 | 13.4797 | 14.3674 | 15.1567 | 16.0165 | 16.347 | 17.4574 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 15% | 4372.3849 | 9.9924 | 9.124 | 9.6848 | 10.3705 | 11.0098 | 11.6903 | 12.4057 | 13.4244 | 14.3132 | 15.1515 | 16.0226 | 17.0658 | 17.4175 | 18.5422 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906
10% | 4374.4653 | 6.2206 | 5.6399 | 5.9938 | 6.4454 | 6.8827 | 7.2721 | 7.8059 | 8.3892 | 8.9864 | 9.5782 | 10.1044 | 10.6777 | 10.898 | 11.6383 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 10% | 4374.4653 | 6.6616 | 6.0827 | 6.4565 | 6.9136 | 7.3399 | 7.7936 | 8.2704 | 8.9496 | 9.5421 | 10.101 | 10.6817 | 11.3772 | 11.6117 | 12.3615 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604
5% | 4374.7625 | 3.1103 | 2.82 | 2.9969 | 3.2227 | 3.4413 | 3.6361 | 3.903 | 4.1946 | 4.4932 | 4.7891 | 5.0522 | 5.3388 | 5.449 | 5.8191 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 5% | 4374.7625 | 3.3308 | 3.0413 | 3.2283 | 3.4568 | 3.6699 | 3.8968 | 4.1352 | 4.4748 | 4.7711 | 5.0505 | 5.3409 | 5.6886 | 5.8058 | 6.1807 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302
9.992e-14% | 4375.9513 | 6.2157e-14 | 5.6354e-14 | 5.9891e-14 | 6.4403e-14 | 6.8772e-14 | 7.2663e-14 | 7.7997e-14 | 8.3825e-14 | 8.9793e-14 | 9.5706e-14 | 1.0096e-13 | 1.0669e-13 | 1.0889e-13 | 1.1629e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 9.992e-14% | 4375.9513 | 6.6563e-14 | 6.0778e-14 | 6.4514e-14 | 6.9081e-14 | 7.334e-14 | 7.7873e-14 | 8.2638e-14 | 8.9425e-14 | 9.5345e-14 | 1.0093e-13 | 1.0673e-13 | 1.1368e-13 | 1.1602e-13 | 1.2352e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 100% | 0 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
99% | 0 | 79.9539 | 73.4917 | 77.3313 | 80.3764 | 83.9806 | 87.696 | 91.6392 | 96.1469 | 101.4481 | 106.4167 | 111.6368 | 120.5006 | 123.5326 | 129.219 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 99% | 0.37816 | 93.5071 | 87.1619 | 91.5053 | 95.145 | 98.3714 | 103.4399 | 108.0228 | 114.3709 | 120.9884 | 126.3994 | 131.5047 | 139.0694 | 144.5767 | 150.1244 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979
98% | 0.37816 | 79.1463 | 72.7493 | 76.5502 | 79.5646 | 83.1323 | 86.8102 | 90.7135 | 95.1757 | 100.4234 | 105.3418 | 110.5092 | 119.2834 | 122.2848 | 127.9138 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 98% | 1.1345 | 92.5626 | 86.2815 | 90.581 | 94.184 | 97.3777 | 102.395 | 106.9316 | 113.2156 | 119.7663 | 125.1227 | 130.1764 | 137.6647 | 143.1163 | 148.608 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222
97% | 0.75633 | 78.3387 | 72.007 | 75.7691 | 78.7527 | 82.284 | 85.9244 | 89.7879 | 94.2046 | 99.3986 | 104.2668 | 109.3815 | 118.0663 | 121.037 | 126.6085 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 97% | 2.269 | 91.6181 | 85.401 | 89.6567 | 93.2229 | 96.3841 | 101.3502 | 105.8405 | 112.0603 | 118.5442 | 123.8459 | 128.848 | 136.2599 | 141.6559 | 147.0916 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465
95% | 1.1345 | 76.7235 | 70.5223 | 74.2068 | 77.1289 | 80.5874 | 84.1528 | 87.9366 | 92.2622 | 97.3492 | 102.117 | 107.1262 | 115.6319 | 118.5414 | 123.9981 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 95% | 4.538 | 89.7291 | 83.6402 | 87.8081 | 91.3008 | 94.3968 | 99.2605 | 103.6582 | 109.7498 | 116.1 | 121.2924 | 126.1914 | 133.4504 | 138.7352 | 144.0588 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695
90% | 4.538 | 72.6854 | 66.8106 | 70.3012 | 73.0695 | 76.346 | 79.7237 | 83.3083 | 87.4063 | 92.2255 | 96.7424 | 101.488 | 109.546 | 112.3023 | 117.4718 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 90% | 7.9414 | 85.0065 | 79.2381 | 83.1866 | 86.4955 | 89.4285 | 94.0362 | 98.2025 | 103.9735 | 109.9894 | 114.9086 | 119.5497 | 126.4267 | 131.4333 | 136.4768 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163
85% | 7.9414 | 68.6473 | 63.0989 | 66.3956 | 69.0101 | 72.1045 | 75.2946 | 78.6801 | 82.5504 | 87.1019 | 91.3679 | 95.8498 | 103.4601 | 106.0633 | 110.9456 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 85% | 14.3702 | 80.2839 | 74.836 | 78.5652 | 81.6902 | 84.4603 | 88.812 | 92.7468 | 98.1972 | 103.8789 | 108.5247 | 112.9081 | 119.403 | 124.1315 | 128.8947 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376
80% | 11.7231 | 64.6092 | 59.3872 | 62.49 | 64.9507 | 67.8631 | 70.8655 | 74.0518 | 77.6945 | 81.9783 | 85.9933 | 90.2116 | 97.3742 | 99.8243 | 104.4194 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 80% | 19.6645 | 75.5613 | 70.4338 | 73.9437 | 76.8849 | 79.492 | 83.5878 | 87.2911 | 92.4209 | 97.7684 | 102.1409 | 106.2664 | 112.3793 | 116.8296 | 121.3127 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589
75% | 17.7737 | 60.5712 | 55.6755 | 58.5843 | 60.8912 | 63.6217 | 66.4364 | 69.4236 | 72.8386 | 76.8546 | 80.6187 | 84.5734 | 91.2883 | 93.5853 | 97.8932 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 75% | 25.7152 | 70.8387 | 66.0317 | 69.3222 | 72.0796 | 74.5238 | 78.3635 | 81.8354 | 86.6446 | 91.6579 | 95.7571 | 99.6248 | 105.3556 | 109.5278 | 113.7306 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803
70% | 35.1693 | 56.5331 | 51.9638 | 54.6787 | 56.8318 | 59.3802 | 62.0073 | 64.7954 | 67.9827 | 71.731 | 75.2441 | 78.9351 | 85.2025 | 87.3463 | 91.367 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 70% | 34.7911 | 66.1162 | 61.6296 | 64.7007 | 67.2743 | 69.5555 | 73.1393 | 76.3797 | 80.8683 | 85.5473 | 89.3733 | 92.9831 | 98.3319 | 102.2259 | 106.1486 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016
65% | 59.3718 | 52.495 | 48.2521 | 50.7731 | 52.7724 | 55.1388 | 57.5782 | 60.1671 | 63.1268 | 66.6073 | 69.8695 | 73.2969 | 79.1166 | 81.1072 | 84.8408 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 65% | 46.136 | 61.3936 | 57.2275 | 60.0792 | 62.469 | 64.5873 | 67.9151 | 70.924 | 75.092 | 79.4368 | 82.9895 | 86.3415 | 91.3082 | 94.9241 | 98.5666 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229
60% | 156.9382 | 48.4569 | 44.5404 | 46.8675 | 48.713 | 50.8973 | 53.1491 | 55.5389 | 58.2709 | 61.4837 | 64.495 | 67.6587 | 73.0307 | 74.8682 | 78.3146 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 60% | 76.7673 | 56.671 | 52.8254 | 55.4578 | 57.6637 | 59.619 | 62.6908 | 65.4683 | 69.3157 | 73.3263 | 76.6057 | 79.6998 | 84.2845 | 87.6222 | 90.9845 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442
55% | 363.794 | 44.4189 | 40.8287 | 42.9618 | 44.6536 | 46.6559 | 48.72 | 50.9106 | 53.415 | 56.3601 | 59.1204 | 62.0205 | 66.9448 | 68.6292 | 71.7884 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 55% | 106.2642 | 51.9484 | 48.4233 | 50.8363 | 52.8584 | 54.6508 | 57.4666 | 60.0126 | 63.5394 | 67.2158 | 70.2219 | 73.0582 | 77.2608 | 80.3204 | 83.4025 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655
50% | 771.4551 | 40.3808 | 37.117 | 39.0562 | 40.5942 | 42.4144 | 44.2909 | 46.2824 | 48.5591 | 51.2364 | 53.7458 | 56.3822 | 60.8589 | 62.3902 | 65.2621 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 50% | 178.4935 | 47.2258 | 44.0212 | 46.2148 | 48.0531 | 49.6825 | 52.2423 | 54.5569 | 57.7631 | 61.1052 | 63.8381 | 66.4165 | 70.2371 | 73.0185 | 75.8204 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868
45% | 1255.5054 | 36.3427 | 33.4053 | 35.1506 | 36.5347 | 38.173 | 39.8618 | 41.6542 | 43.7031 | 46.1128 | 48.3712 | 50.744 | 54.773 | 56.1512 | 58.7359 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 45% | 367.9538 | 42.5032 | 39.619 | 41.5933 | 43.2477 | 44.7143 | 47.0181 | 49.1013 | 51.9868 | 54.9947 | 57.4543 | 59.7749 | 63.2134 | 65.7167 | 68.2384 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
40% | 2059.1045 | 32.3046 | 29.6936 | 31.245 | 32.4753 | 33.9315 | 35.4327 | 37.0259 | 38.8472 | 40.9891 | 42.9966 | 45.1058 | 48.6871 | 49.9121 | 52.2097 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 40% | 741.202 | 37.7807 | 35.2169 | 36.9718 | 38.4424 | 39.746 | 41.7939 | 43.6456 | 46.2105 | 48.8842 | 51.0705 | 53.1332 | 56.1897 | 58.4148 | 60.6563 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295
35% | 3060.4836 | 28.2665 | 25.9819 | 27.3394 | 28.4159 | 29.6901 | 31.0036 | 32.3977 | 33.9913 | 35.8655 | 37.6221 | 39.4676 | 42.6012 | 43.6731 | 45.6835 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 35% | 1167.7713 | 33.0581 | 30.8148 | 32.3504 | 33.6371 | 34.7778 | 36.5696 | 38.1899 | 40.4341 | 42.7737 | 44.6867 | 46.4916 | 49.1659 | 51.113 | 53.0743 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508
30% | 3366.0403 | 24.2285 | 22.2702 | 23.4337 | 24.3565 | 25.4487 | 26.5746 | 27.7694 | 29.1354 | 30.7418 | 32.2475 | 33.8293 | 36.5153 | 37.4341 | 39.1573 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 30% | 2002.3799 | 28.3355 | 26.4127 | 27.7289 | 28.8318 | 29.8095 | 31.3454 | 32.7342 | 34.6578 | 36.6631 | 38.3029 | 39.8499 | 42.1422 | 43.8111 | 45.4923 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721
25% | 3686.3454 | 20.1904 | 18.5585 | 19.5281 | 20.2971 | 21.2072 | 22.1455 | 23.1412 | 24.2795 | 25.6182 | 26.8729 | 28.1911 | 30.4294 | 31.1951 | 32.6311 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 25% | 3173.5547 | 23.6129 | 22.0106 | 23.1074 | 24.0265 | 24.8413 | 26.1212 | 27.2785 | 28.8815 | 30.5526 | 31.919 | 33.2083 | 35.1185 | 36.5093 | 37.9102 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934
20% | 4028.5841 | 16.1523 | 14.8468 | 15.6225 | 16.2377 | 16.9658 | 17.7164 | 18.513 | 19.4236 | 20.4946 | 21.4983 | 22.5529 | 24.3436 | 24.9561 | 26.1049 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 20% | 3477.5988 | 18.8903 | 17.6085 | 18.4859 | 19.2212 | 19.873 | 20.8969 | 21.8228 | 23.1052 | 24.4421 | 25.5352 | 26.5666 | 28.0948 | 29.2074 | 30.3282 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147
15% | 4345.1076 | 12.1142 | 11.1351 | 11.7169 | 12.1782 | 12.7243 | 13.2873 | 13.8847 | 14.5677 | 15.3709 | 16.1237 | 16.9147 | 18.2577 | 18.7171 | 19.5786 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 15% | 3788.4498 | 14.1677 | 13.2063 | 13.8644 | 14.4159 | 14.9048 | 15.6727 | 16.3671 | 17.3289 | 18.3316 | 19.1514 | 19.925 | 21.0711 | 21.9056 | 22.7461 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361
10% | 4381.0332 | 8.0762 | 7.4234 | 7.8112 | 8.1188 | 8.4829 | 8.8582 | 9.2565 | 9.7118 | 10.2473 | 10.7492 | 11.2764 | 12.1718 | 12.478 | 13.0524 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 10% | 4317.5016 | 9.4452 | 8.8042 | 9.243 | 9.6106 | 9.9365 | 10.4485 | 10.9114 | 11.5526 | 12.221 | 12.7676 | 13.2833 | 14.0474 | 14.6037 | 15.1641 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574
5% | 4391.6218 | 4.0381 | 3.7117 | 3.9056 | 4.0594 | 4.2414 | 4.4291 | 4.6282 | 4.8559 | 5.1236 | 5.3746 | 5.6382 | 6.0859 | 6.239 | 6.5262 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 5% | 4391.6218 | 4.7226 | 4.4021 | 4.6215 | 4.8053 | 4.9683 | 5.2242 | 5.4557 | 5.7763 | 6.1105 | 6.3838 | 6.6417 | 7.0237 | 7.3019 | 7.582 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787
9.992e-14% | 4391.6218 | 8.0697e-14 | 7.4175e-14 | 7.805e-14 | 8.1123e-14 | 8.4761e-14 | 8.8511e-14 | 9.2491e-14 | 9.704e-14 | 1.0239e-13 | 1.0741e-13 | 1.1267e-13 | 1.2162e-13 | 1.2468e-13 | 1.3042e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 9.992e-14% | 4391.6218 | 9.4376e-14 | 8.7972e-14 | 9.2356e-14 | 9.6029e-14 | 9.9286e-14 | 1.044e-13 | 1.0903e-13 | 1.1543e-13 | 1.2211e-13 | 1.2757e-13 | 1.3273e-13 | 1.4036e-13 | 1.4592e-13 | 1.5152e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.2064 | 56.3994 | 59.9385 | 54.7877 | 59.16 | 63.0544 | 68.3924 | 74.225 | 80.1977 | 86.1157 | 91.3778 | 97.11 | 99.3135 | 106.7163 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 114.3717 | 100% | 0 | 66.6162 | 60.8268 | 64.5653 | 59.4698 | 63.7321 | 68.2689 | 73.0378 | 79.8296 | 85.7544 | 91.343 | 97.1504 | 104.1052 | 106.4499 | 113.9481 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375 | 120.9375
99% | 0.5944 | 61.5843 | 55.8354 | 59.3391 | 54.2399 | 58.5684 | 62.4239 | 67.7085 | 73.4827 | 79.3957 | 85.2545 | 90.464 | 96.1389 | 98.3204 | 105.6492 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 113.228 | 99% | 0.5944 | 65.9501 | 60.2186 | 63.9197 | 58.8751 | 63.0948 | 67.5862 | 72.3074 | 79.0313 | 84.8969 | 90.4296 | 96.1789 | 103.0641 | 105.3854 | 112.8086 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281 | 119.7281
98% | 0.8916 | 60.9623 | 55.2714 | 58.7397 | 53.692 | 57.9768 | 61.7933 | 67.0246 | 72.7405 | 78.5938 | 84.3934 | 89.5502 | 95.1678 | 97.3273 | 104.582 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 112.0843 | 98% | 0.8916 | 65.2839 | 59.6103 | 63.274 | 58.2804 | 62.4574 | 66.9036 | 71.577 | 78.233 | 84.0393 | 89.5161 | 95.2074 | 102.0231 | 104.3209 | 111.6691 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187 | 118.5187
97% | 1.486 | 60.3402 | 54.7074 | 58.1403 | 53.1441 | 57.3852 | 61.1628 | 66.3406 | 71.9982 | 77.7918 | 83.5322 | 88.6365 | 94.1967 | 96.3341 | 103.5148 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 110.9406 | 97% | 1.486 | 64.6177 | 59.002 | 62.6284 | 57.6857 | 61.8201 | 66.2209 | 70.8467 | 77.4347 | 83.1818 | 88.6027 | 94.2359 | 100.982 | 103.2564 | 110.5296 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093 | 117.3093
95% | 2.3776 | 59.0961 | 53.5795 | 56.9416 | 52.0484 | 56.202 | 59.9017 | 64.9728 | 70.5137 | 76.1878 | 81.8099 | 86.8089 | 92.2545 | 94.3479 | 101.3805 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 108.6531 | 95% | 2.3776 | 63.2854 | 57.7855 | 61.3371 | 56.4963 | 60.5455 | 64.8555 | 69.3859 | 75.8381 | 81.4667 | 86.7759 | 92.2929 | 98.8999 | 101.1274 | 108.2507 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906 | 114.8906
90% | 3.2692 | 55.9857 | 50.7595 | 53.9446 | 49.309 | 53.244 | 56.749 | 61.5532 | 66.8025 | 72.178 | 77.5041 | 82.24 | 87.399 | 89.3822 | 96.0447 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 102.9345 | 90% | 3.2692 | 59.9546 | 54.7442 | 58.1088 | 53.5228 | 57.3589 | 61.442 | 65.734 | 71.8466 | 77.179 | 82.2087 | 87.4353 | 93.6947 | 95.8049 | 102.5533 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437 | 108.8437
85% | 13.9683 | 52.8754 | 47.9395 | 50.9477 | 46.5696 | 50.286 | 53.5963 | 58.1335 | 63.0912 | 68.1681 | 73.1983 | 77.6711 | 82.5435 | 84.4165 | 90.7089 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 97.216 | 85% | 13.9683 | 56.6238 | 51.7028 | 54.8805 | 50.5493 | 54.1723 | 58.0286 | 62.0821 | 67.8551 | 72.8912 | 77.6416 | 82.5778 | 88.4894 | 90.4824 | 96.8559 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968 | 102.7968
80% | 41.3106 | 49.7651 | 45.1195 | 47.9508 | 43.8302 | 47.328 | 50.4435 | 54.7139 | 59.38 | 64.1582 | 68.8926 | 73.1022 | 77.688 | 79.4508 | 85.3731 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 91.4974 | 80% | 41.3106 | 53.293 | 48.6615 | 51.6523 | 47.5758 | 50.9857 | 54.6151 | 58.4302 | 63.8637 | 68.6035 | 73.0744 | 77.7203 | 83.2841 | 85.1599 | 91.1585 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75 | 96.75
75% | 126.3094 | 46.6548 | 42.2996 | 44.9539 | 41.0908 | 44.37 | 47.2908 | 51.2943 | 55.6687 | 60.1483 | 64.5868 | 68.5333 | 72.8325 | 74.4852 | 80.0372 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 85.7788 | 75% | 126.3094 | 49.9622 | 45.6201 | 48.424 | 44.6023 | 47.7991 | 51.2017 | 54.7784 | 59.8722 | 64.3158 | 68.5073 | 72.8628 | 78.0789 | 79.8374 | 85.4611 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031 | 90.7031
70% | 323.9464 | 43.5445 | 39.4796 | 41.9569 | 38.3514 | 41.412 | 44.1381 | 47.8747 | 51.9575 | 56.1384 | 60.281 | 63.9645 | 67.977 | 69.5195 | 74.7014 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 80.0602 | 70% | 323.9464 | 46.6314 | 42.5788 | 45.1957 | 41.6288 | 44.6125 | 47.7883 | 51.1265 | 55.8807 | 60.0281 | 63.9401 | 68.0053 | 72.8736 | 74.5149 | 79.7637 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562 | 84.6562
65% | 549.5201 | 40.4341 | 36.6596 | 38.96 | 35.612 | 38.454 | 40.9854 | 44.4551 | 48.2462 | 52.1285 | 55.9752 | 59.3956 | 63.1215 | 64.5538 | 69.3656 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 74.3416 | 65% | 549.5201 | 43.3005 | 39.5374 | 41.9675 | 38.6554 | 41.4259 | 44.3748 | 47.4746 | 51.8892 | 55.7404 | 59.373 | 63.1477 | 67.6684 | 69.1924 | 74.0663 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094 | 78.6094
60% | 799.4641 | 37.3238 | 33.8397 | 35.9631 | 32.8726 | 35.496 | 37.8326 | 41.0354 | 44.535 | 48.1186 | 51.6694 | 54.8267 | 58.266 | 59.5881 | 64.0298 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 68.623 | 60% | 799.4641 | 39.9697 | 36.4961 | 38.7392 | 35.6819 | 38.2392 | 40.9614 | 43.8227 | 47.8977 | 51.4526 | 54.8058 | 58.2902 | 62.4631 | 63.8699 | 68.3688 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625 | 72.5625
55% | 1116.2777 | 34.2135 | 31.0197 | 32.9662 | 30.1333 | 32.538 | 34.6799 | 37.6158 | 40.8237 | 44.1087 | 47.3636 | 50.2578 | 53.4105 | 54.6224 | 58.694 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 62.9044 | 55% | 1116.2777 | 36.6389 | 33.4548 | 35.5109 | 32.7084 | 35.0526 | 37.5479 | 40.1708 | 43.9063 | 47.1649 | 50.2387 | 53.4327 | 57.2578 | 58.5474 | 62.6714 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156 | 66.5156
50% | 1494.9086 | 31.1032 | 28.1997 | 29.9692 | 27.3939 | 29.58 | 31.5272 | 34.1962 | 37.1125 | 40.0989 | 43.0578 | 45.6889 | 48.555 | 49.6568 | 53.3582 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 57.1859 | 50% | 1494.9086 | 33.3081 | 30.4134 | 32.2827 | 29.7349 | 31.866 | 34.1345 | 36.5189 | 39.9148 | 42.8772 | 45.6715 | 48.5752 | 52.0526 | 53.2249 | 56.974 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687 | 60.4687
45% | 2004.0097 | 27.9929 | 25.3797 | 26.9723 | 24.6545 | 26.622 | 28.3745 | 30.7766 | 33.4012 | 36.089 | 38.7521 | 41.12 | 43.6995 | 44.6911 | 48.0223 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 51.4673 | 45% | 2004.0097 | 29.9773 | 27.3721 | 29.0544 | 26.7614 | 28.6794 | 30.721 | 32.867 | 35.9233 | 38.5895 | 41.1044 | 43.7177 | 46.8473 | 47.9024 | 51.2766 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219 | 54.4219
40% | 2877.179 | 24.8826 | 22.5598 | 23.9754 | 21.9151 | 23.664 | 25.2218 | 27.357 | 29.69 | 32.0791 | 34.4463 | 36.5511 | 38.844 | 39.7254 | 42.6865 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 45.7487 | 40% | 2877.179 | 26.6465 | 24.3307 | 25.8261 | 23.7879 | 25.4928 | 27.3076 | 29.2151 | 31.9318 | 34.3018 | 36.5372 | 38.8602 | 41.6421 | 42.58 | 45.5792 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375 | 48.375
35% | 3454.933 | 21.7722 | 19.7398 | 20.9785 | 19.1757 | 20.706 | 22.069 | 23.9373 | 25.9787 | 28.0692 | 30.1405 | 31.9822 | 33.9885 | 34.7597 | 37.3507 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 40.0301 | 35% | 3454.933 | 23.3157 | 21.2894 | 22.5979 | 20.8144 | 22.3062 | 23.8941 | 25.5632 | 27.9403 | 30.014 | 31.9701 | 34.0026 | 36.4368 | 37.2575 | 39.8818 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281 | 42.3281
30% | 3663.5664 | 18.6619 | 16.9198 | 17.9815 | 16.4363 | 17.748 | 18.9163 | 20.5177 | 22.2675 | 24.0593 | 25.8347 | 27.4133 | 29.133 | 29.7941 | 32.0149 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 34.3115 | 30% | 3663.5664 | 19.9849 | 18.2481 | 19.3696 | 17.8409 | 19.1196 | 20.4807 | 21.9113 | 23.9489 | 25.7263 | 27.4029 | 29.1451 | 31.2316 | 31.935 | 34.1844 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812 | 36.2812
25% | 3862.6894 | 15.5516 | 14.0999 | 14.9846 | 13.6969 | 14.79 | 15.7636 | 17.0981 | 18.5562 | 20.0494 | 21.5289 | 22.8444 | 24.2775 | 24.8284 | 26.6791 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 28.5929 | 25% | 3862.6894 | 16.6541 | 15.2067 | 16.1413 | 14.8674 | 15.933 | 17.0672 | 18.2595 | 19.9574 | 21.4386 | 22.8358 | 24.2876 | 26.0263 | 26.6125 | 28.487 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344 | 30.2344
20% | 4122.7381 | 12.4413 | 11.2799 | 11.9877 | 10.9575 | 11.832 | 12.6109 | 13.6785 | 14.845 | 16.0395 | 17.2231 | 18.2756 | 19.422 | 19.8627 | 21.3433 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 22.8743 | 20% | 4122.7381 | 13.3232 | 12.1654 | 12.9131 | 11.894 | 12.7464 | 13.6538 | 14.6076 | 15.9659 | 17.1509 | 18.2686 | 19.4301 | 20.821 | 21.29 | 22.7896 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875 | 24.1875
15% | 4372.3849 | 9.331 | 8.4599 | 8.9908 | 8.2182 | 8.874 | 9.4582 | 10.2589 | 11.1337 | 12.0297 | 12.9174 | 13.7067 | 14.5665 | 14.897 | 16.0074 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 17.1558 | 15% | 4372.3849 | 9.9924 | 9.124 | 9.6848 | 8.9205 | 9.5598 | 10.2403 | 10.9557 | 11.9744 | 12.8632 | 13.7015 | 14.5726 | 15.6158 | 15.9675 | 17.0922 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406 | 18.1406
10% | 4374.4653 | 6.2206 | 5.6399 | 5.9938 | 5.4788 | 5.916 | 6.3054 | 6.8392 | 7.4225 | 8.0198 | 8.6116 | 9.1378 | 9.711 | 9.9314 | 10.6716 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 11.4372 | 10% | 4374.4653 | 6.6616 | 6.0827 | 6.4565 | 5.947 | 6.3732 | 6.8269 | 7.3038 | 7.983 | 8.5754 | 9.1343 | 9.715 | 10.4105 | 10.645 | 11.3948 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937 | 12.0937
5% | 4374.7625 | 3.1103 | 2.82 | 2.9969 | 2.7394 | 2.958 | 3.1527 | 3.4196 | 3.7112 | 4.0099 | 4.3058 | 4.5689 | 4.8555 | 4.9657 | 5.3358 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5.7186 | 5% | 4374.7625 | 3.3308 | 3.0413 | 3.2283 | 2.9735 | 3.1866 | 3.4134 | 3.6519 | 3.9915 | 4.2877 | 4.5672 | 4.8575 | 5.2053 | 5.3225 | 5.6974 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469 | 6.0469
9.992e-14% | 4375.9513 | 6.2157e-14 | 5.6354e-14 | 5.9891e-14 | 5.4744e-14 | 5.9113e-14 | 6.3004e-14 | 6.8338e-14 | 7.4166e-14 | 8.0134e-14 | 8.6047e-14 | 9.1305e-14 | 9.7032e-14 | 9.9234e-14 | 1.0663e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 1.1428e-13 | 9.992e-14% | 4375.9513 | 6.6563e-14 | 6.0778e-14 | 6.4514e-14 | 5.9422e-14 | 6.3681e-14 | 6.8214e-14 | 7.2979e-14 | 7.9766e-14 | 8.5686e-14 | 9.127e-14 | 9.7073e-14 | 1.0402e-13 | 1.0636e-13 | 1.1386e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13 | 1.2084e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 80.7616 | 74.234 | 78.1124 | 71.5217 | 75.1622 | 78.9152 | 82.8981 | 87.4514 | 92.8062 | 97.8249 | 103.0978 | 112.0511 | 115.1137 | 120.8576 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 125.2566 | 100% | 0 | 94.4516 | 88.0423 | 92.4296 | 86.4394 | 89.6984 | 94.818 | 99.4472 | 105.8595 | 112.5438 | 118.0095 | 123.1663 | 130.8075 | 136.3704 | 141.9742 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907 | 147.907
99% | 0 | 79.9539 | 73.4917 | 77.3313 | 70.8064 | 74.4106 | 78.126 | 82.0692 | 86.5769 | 91.8781 | 96.8467 | 102.0668 | 110.9306 | 113.9626 | 119.649 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 124.004 | 99% | 0.37816 | 93.5071 | 87.1619 | 91.5053 | 85.575 | 88.8014 | 93.8699 | 98.4528 | 104.8009 | 111.4184 | 116.8294 | 121.9347 | 129.4994 | 135.0067 | 140.5544 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279 | 146.4279
98% | 0.37816 | 79.1463 | 72.7493 | 76.5502 | 70.0912 | 73.659 | 77.3369 | 81.2402 | 85.7024 | 90.95 | 95.8684 | 101.0358 | 109.8101 | 112.8114 | 118.4405 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 122.7514 | 98% | 1.1345 | 92.5626 | 86.2815 | 90.581 | 84.7107 | 87.9044 | 92.9217 | 97.4583 | 103.7423 | 110.2929 | 115.6493 | 120.703 | 128.1913 | 133.643 | 139.1347 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489 | 144.9489
97% | 0.75633 | 78.3387 | 72.007 | 75.7691 | 69.376 | 72.9073 | 76.5477 | 80.4112 | 84.8279 | 90.022 | 94.8902 | 100.0049 | 108.6896 | 111.6603 | 117.2319 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 121.4989 | 97% | 2.269 | 91.6181 | 85.401 | 89.6567 | 83.8463 | 87.0074 | 91.9735 | 96.4638 | 102.6837 | 109.1675 | 114.4692 | 119.4714 | 126.8832 | 132.2793 | 137.715 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698 | 143.4698
95% | 1.1345 | 76.7235 | 70.5223 | 74.2068 | 67.9456 | 71.4041 | 74.9694 | 78.7532 | 83.0789 | 88.1658 | 92.9337 | 97.9429 | 106.4486 | 109.358 | 114.8147 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 118.9937 | 95% | 4.538 | 89.7291 | 83.6402 | 87.8081 | 82.1175 | 85.2135 | 90.0771 | 94.4749 | 100.5665 | 106.9166 | 112.109 | 117.008 | 124.2671 | 129.5519 | 134.8755 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117 | 140.5117
90% | 4.538 | 72.6854 | 66.8106 | 70.3012 | 64.3695 | 67.646 | 71.0237 | 74.6083 | 78.7063 | 83.5255 | 88.0424 | 92.788 | 100.846 | 103.6023 | 108.7718 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 112.7309 | 90% | 7.9414 | 85.0065 | 79.2381 | 83.1866 | 77.7955 | 80.7285 | 85.3362 | 89.5025 | 95.2735 | 101.2894 | 106.2086 | 110.8497 | 117.7267 | 122.7333 | 127.7768 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163 | 133.1163
85% | 7.9414 | 68.6473 | 63.0989 | 66.3956 | 60.7934 | 63.8879 | 67.0779 | 70.4634 | 74.3337 | 78.8852 | 83.1512 | 87.6331 | 95.2435 | 97.8466 | 102.729 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 106.4681 | 85% | 14.3702 | 80.2839 | 74.836 | 78.5652 | 73.4735 | 76.2436 | 80.5953 | 84.5301 | 89.9805 | 95.6622 | 100.3081 | 104.6914 | 111.1864 | 115.9148 | 120.6781 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721 | 125.721
80% | 11.7231 | 64.6092 | 59.3872 | 62.49 | 57.2173 | 60.1298 | 63.1321 | 66.3185 | 69.9611 | 74.2449 | 78.2599 | 82.4782 | 89.6409 | 92.091 | 96.6861 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 100.2052 | 80% | 19.6645 | 75.5613 | 70.4338 | 73.9437 | 69.1516 | 71.7587 | 75.8544 | 79.5578 | 84.6876 | 90.035 | 94.4076 | 98.5331 | 104.646 | 109.0963 | 113.5793 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256 | 118.3256
75% | 17.7737 | 60.5712 | 55.6755 | 58.5843 | 53.6412 | 56.3717 | 59.1864 | 62.1736 | 65.5886 | 69.6046 | 73.3687 | 77.3234 | 84.0383 | 86.3353 | 90.6432 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 93.9424 | 75% | 25.7152 | 70.8387 | 66.0317 | 69.3222 | 64.8296 | 67.2738 | 71.1135 | 74.5854 | 79.3946 | 84.4079 | 88.5071 | 92.3748 | 98.1056 | 102.2778 | 106.4806 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303 | 110.9303
70% | 35.1693 | 56.5331 | 51.9638 | 54.6787 | 50.0652 | 52.6135 | 55.2406 | 58.0287 | 61.216 | 64.9643 | 68.4774 | 72.1685 | 78.4358 | 80.5796 | 84.6003 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 87.6796 | 70% | 34.7911 | 66.1162 | 61.6296 | 64.7007 | 60.5076 | 62.7889 | 66.3726 | 69.6131 | 74.1016 | 78.7807 | 82.6067 | 86.2164 | 91.5652 | 95.4593 | 99.3819 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349 | 103.5349
65% | 59.3718 | 52.495 | 48.2521 | 50.7731 | 46.4891 | 48.8554 | 51.2949 | 53.8838 | 56.8434 | 60.324 | 63.5862 | 67.0136 | 72.8332 | 74.8239 | 78.5574 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 81.4168 | 65% | 46.136 | 61.3936 | 57.2275 | 60.0792 | 56.1856 | 58.3039 | 61.6317 | 64.6407 | 68.8087 | 73.1535 | 76.7062 | 80.0581 | 85.0249 | 88.6407 | 92.2832 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396 | 96.1396
60% | 156.9382 | 48.4569 | 44.5404 | 46.8675 | 42.913 | 45.0973 | 47.3491 | 49.7389 | 52.4709 | 55.6837 | 58.695 | 61.8587 | 67.2307 | 69.0682 | 72.5146 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 75.1539 | 60% | 76.7673 | 56.671 | 52.8254 | 55.4578 | 51.8637 | 53.819 | 56.8908 | 59.6683 | 63.5157 | 67.5263 | 70.8057 | 73.8998 | 78.4845 | 81.8222 | 85.1845 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442 | 88.7442
55% | 363.794 | 44.4189 | 40.8287 | 42.9618 | 39.3369 | 41.3392 | 43.4034 | 45.594 | 48.0983 | 51.0434 | 53.8037 | 56.7038 | 61.6281 | 63.3125 | 66.4717 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 68.8911 | 55% | 106.2642 | 51.9484 | 48.4233 | 50.8363 | 47.5417 | 49.3341 | 52.1499 | 54.696 | 58.2227 | 61.8991 | 64.9052 | 67.7415 | 71.9441 | 75.0037 | 78.0858 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489 | 81.3489
50% | 771.4551 | 40.3808 | 37.117 | 39.0562 | 35.7608 | 37.5811 | 39.4576 | 41.4491 | 43.7257 | 46.4031 | 48.9125 | 51.5489 | 56.0256 | 57.5569 | 60.4288 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 62.6283 | 50% | 178.4935 | 47.2258 | 44.0212 | 46.2148 | 43.2197 | 44.8492 | 47.409 | 49.7236 | 52.9297 | 56.2719 | 59.0048 | 61.5832 | 65.4037 | 68.1852 | 70.9871 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535 | 73.9535
45% | 1255.5054 | 36.3427 | 33.4053 | 35.1506 | 32.1847 | 33.823 | 35.5118 | 37.3042 | 39.3531 | 41.7628 | 44.0212 | 46.394 | 50.423 | 51.8012 | 54.3859 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 56.3654 | 45% | 367.9538 | 42.5032 | 39.619 | 41.5933 | 38.8977 | 40.3643 | 42.6681 | 44.7513 | 47.6368 | 50.6447 | 53.1043 | 55.4249 | 58.8634 | 61.3667 | 63.8884 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582 | 66.5582
40% | 2059.1045 | 32.3046 | 29.6936 | 31.245 | 28.6087 | 30.0649 | 31.5661 | 33.1593 | 34.9806 | 37.1225 | 39.13 | 41.2391 | 44.8205 | 46.0455 | 48.343 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 50.1026 | 40% | 741.202 | 37.7807 | 35.2169 | 36.9718 | 34.5758 | 35.8794 | 37.9272 | 39.7789 | 42.3438 | 45.0175 | 47.2038 | 49.2665 | 52.323 | 54.5482 | 56.7897 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628 | 59.1628
35% | 3060.4836 | 28.2665 | 25.9819 | 27.3394 | 25.0326 | 26.3068 | 27.6203 | 29.0143 | 30.608 | 32.4822 | 34.2387 | 36.0842 | 39.2179 | 40.2898 | 42.3002 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 43.8398 | 35% | 1167.7713 | 33.0581 | 30.8148 | 32.3504 | 30.2538 | 31.3944 | 33.1863 | 34.8065 | 37.0508 | 39.3903 | 41.3033 | 43.1082 | 45.7826 | 47.7296 | 49.691 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675 | 51.7675
30% | 3366.0403 | 24.2285 | 22.2702 | 23.4337 | 21.4565 | 22.5487 | 23.6746 | 24.8694 | 26.2354 | 27.8418 | 29.3475 | 30.9293 | 33.6153 | 34.5341 | 36.2573 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 37.577 | 30% | 2002.3799 | 28.3355 | 26.4127 | 27.7289 | 25.9318 | 26.9095 | 28.4454 | 29.8342 | 31.7578 | 33.7631 | 35.4029 | 36.9499 | 39.2422 | 40.9111 | 42.5923 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721 | 44.3721
25% | 3686.3454 | 20.1904 | 18.5585 | 19.5281 | 17.8804 | 18.7906 | 19.7288 | 20.7245 | 21.8629 | 23.2015 | 24.4562 | 25.7745 | 28.0128 | 28.7784 | 30.2144 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 31.3141 | 25% | 3173.5547 | 23.6129 | 22.0106 | 23.1074 | 21.6099 | 22.4246 | 23.7045 | 24.8618 | 26.4649 | 28.136 | 29.5024 | 30.7916 | 32.7019 | 34.0926 | 35.4935 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768 | 36.9768
20% | 4028.5841 | 16.1523 | 14.8468 | 15.6225 | 14.3043 | 15.0324 | 15.783 | 16.5796 | 17.4903 | 18.5612 | 19.565 | 20.6196 | 22.4102 | 23.0227 | 24.1715 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 20% | 3477.5988 | 18.8903 | 17.6085 | 18.4859 | 17.2879 | 17.9397 | 18.9636 | 19.8894 | 21.1719 | 22.5088 | 23.6019 | 24.6333 | 26.1615 | 27.2741 | 28.3948 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814 | 29.5814
15% | 4345.1076 | 12.1142 | 11.1351 | 11.7169 | 10.7282 | 11.2743 | 11.8373 | 12.4347 | 13.1177 | 13.9209 | 14.6737 | 15.4647 | 16.8077 | 17.2671 | 18.1286 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 18.7885 | 15% | 3788.4498 | 14.1677 | 13.2063 | 13.8644 | 12.9659 | 13.4548 | 14.2227 | 14.9171 | 15.8789 | 16.8816 | 17.7014 | 18.475 | 19.6211 | 20.4556 | 21.2961 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861 | 22.1861
10% | 4381.0332 | 8.0762 | 7.4234 | 7.8112 | 7.1522 | 7.5162 | 7.8915 | 8.2898 | 8.7451 | 9.2806 | 9.7825 | 10.3098 | 11.2051 | 11.5114 | 12.0858 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 12.5257 | 10% | 4317.5016 | 9.4452 | 8.8042 | 9.243 | 8.6439 | 8.9698 | 9.4818 | 9.9447 | 10.5859 | 11.2544 | 11.801 | 12.3166 | 13.0807 | 13.637 | 14.1974 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907 | 14.7907
5% | 4391.6218 | 4.0381 | 3.7117 | 3.9056 | 3.5761 | 3.7581 | 3.9458 | 4.1449 | 4.3726 | 4.6403 | 4.8912 | 5.1549 | 5.6026 | 5.7557 | 6.0429 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 6.2628 | 5% | 4391.6218 | 4.7226 | 4.4021 | 4.6215 | 4.322 | 4.4849 | 4.7409 | 4.9724 | 5.293 | 5.6272 | 5.9005 | 6.1583 | 6.5404 | 6.8185 | 7.0987 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954 | 7.3954
9.992e-14% | 4391.6218 | 8.0697e-14 | 7.4175e-14 | 7.805e-14 | 7.1464e-14 | 7.5102e-14 | 7.8852e-14 | 8.2832e-14 | 8.7382e-14 | 9.2732e-14 | 9.7747e-14 | 1.0302e-13 | 1.1196e-13 | 1.1502e-13 | 1.2076e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 1.2516e-13 | 9.992e-14% | 4391.6218 | 9.4376e-14 | 8.7972e-14 | 9.2356e-14 | 8.637e-14 | 8.9627e-14 | 9.4742e-14 | 9.9368e-14 | 1.0577e-13 | 1.1245e-13 | 1.1792e-13 | 1.2307e-13 | 1.307e-13 | 1.3626e-13 | 1.4186e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13 | 1.4779e-13
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 100% | 0 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
99% | 0.5944 | 61.5843 | 55.8354 | 59.3391 | 63.8099 | 68.1384 | 71.9939 | 77.2785 | 83.0527 | 88.9657 | 94.8245 | 100.034 | 105.7089 | 107.8904 | 115.2192 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 99% | 0.5944 | 65.9501 | 60.2186 | 63.9197 | 68.4451 | 72.6648 | 77.1562 | 81.8774 | 88.6013 | 94.4669 | 99.9996 | 105.7489 | 112.6341 | 114.9554 | 122.3786 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981
98% | 0.8916 | 60.9623 | 55.2714 | 58.7397 | 63.1653 | 67.4501 | 71.2667 | 76.4979 | 82.2138 | 88.0671 | 93.8667 | 99.0236 | 104.6411 | 106.8006 | 114.0553 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 98% | 0.8916 | 65.2839 | 59.6103 | 63.274 | 67.7537 | 71.9308 | 76.3769 | 81.0504 | 87.7063 | 93.5127 | 98.9895 | 104.6807 | 111.4964 | 113.7942 | 121.1425 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992
97% | 1.486 | 60.3402 | 54.7074 | 58.1403 | 62.5208 | 66.7619 | 70.5394 | 75.7173 | 81.3749 | 87.1685 | 92.9089 | 98.0131 | 103.5733 | 105.7108 | 112.8915 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 97% | 1.486 | 64.6177 | 59.002 | 62.6284 | 67.0623 | 71.1968 | 75.5975 | 80.2233 | 86.8113 | 92.5584 | 97.9794 | 103.6125 | 110.3587 | 112.6331 | 119.9063 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686
95% | 2.3776 | 59.0961 | 53.5795 | 56.9416 | 61.2317 | 65.3853 | 69.085 | 74.1561 | 79.6971 | 85.3712 | 90.9932 | 95.9922 | 101.4378 | 103.5312 | 110.5638 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 95% | 2.3776 | 63.2854 | 57.7855 | 61.3371 | 65.6796 | 69.7288 | 74.0388 | 78.5692 | 85.0214 | 90.65 | 95.9592 | 101.4762 | 108.0832 | 110.3107 | 117.434 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739
90% | 3.2692 | 55.9857 | 50.7595 | 53.9446 | 58.009 | 61.944 | 65.449 | 70.2532 | 75.5025 | 80.878 | 86.2041 | 90.94 | 96.099 | 98.0822 | 104.7447 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 90% | 3.2692 | 59.9546 | 54.7442 | 58.1088 | 62.2228 | 66.0589 | 70.142 | 74.434 | 80.5466 | 85.879 | 90.9087 | 96.1353 | 102.3947 | 104.5049 | 111.2533 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437
85% | 13.9683 | 52.8754 | 47.9395 | 50.9477 | 54.7863 | 58.5027 | 61.8129 | 66.3502 | 71.3079 | 76.3847 | 81.415 | 85.8878 | 90.7601 | 92.6332 | 98.9255 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 85% | 13.9683 | 56.6238 | 51.7028 | 54.8805 | 58.766 | 62.3889 | 66.2453 | 70.2988 | 76.0718 | 81.1079 | 85.8582 | 90.7945 | 96.7061 | 98.6991 | 105.0725 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135
80% | 41.3106 | 49.7651 | 45.1195 | 47.9508 | 51.5635 | 55.0613 | 58.1769 | 62.4473 | 67.1133 | 71.8915 | 76.6259 | 80.8356 | 85.4213 | 87.1842 | 93.1064 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 80% | 41.3106 | 53.293 | 48.6615 | 51.6523 | 55.3092 | 58.719 | 62.3485 | 66.1636 | 71.597 | 76.3369 | 80.8077 | 85.4536 | 91.0175 | 92.8932 | 98.8918 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833
75% | 126.3094 | 46.6548 | 42.2996 | 44.9539 | 48.3408 | 51.62 | 54.5408 | 58.5443 | 62.9187 | 67.3983 | 71.8368 | 75.7833 | 80.0825 | 81.7352 | 87.2872 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 75% | 126.3094 | 49.9622 | 45.6201 | 48.424 | 51.8523 | 55.0491 | 58.4517 | 62.0284 | 67.1222 | 71.5658 | 75.7573 | 80.1128 | 85.3289 | 87.0874 | 92.7111 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531
70% | 323.9464 | 43.5445 | 39.4796 | 41.9569 | 45.1181 | 48.1787 | 50.9048 | 54.6414 | 58.7242 | 62.9051 | 67.0477 | 70.7311 | 74.7436 | 76.2861 | 81.4681 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 70% | 323.9464 | 46.6314 | 42.5788 | 45.1957 | 48.3955 | 51.3791 | 54.5549 | 57.8931 | 62.6474 | 66.7948 | 70.7068 | 74.7719 | 79.6403 | 81.2816 | 86.5303 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229
65% | 549.5201 | 40.4341 | 36.6596 | 38.96 | 41.8954 | 44.7373 | 47.2687 | 50.7384 | 54.5296 | 58.4119 | 62.2585 | 65.6789 | 69.4048 | 70.8371 | 75.6489 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 65% | 549.5201 | 43.3005 | 39.5374 | 41.9675 | 44.9387 | 47.7092 | 50.6581 | 53.7579 | 58.1726 | 62.0237 | 65.6563 | 69.4311 | 73.9517 | 75.4758 | 80.3496 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927
60% | 799.4641 | 37.3238 | 33.8397 | 35.9631 | 38.6726 | 41.296 | 43.6326 | 46.8354 | 50.335 | 53.9186 | 57.4694 | 60.6267 | 64.066 | 65.3881 | 69.8298 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 60% | 799.4641 | 39.9697 | 36.4961 | 38.7392 | 41.4819 | 44.0392 | 46.7614 | 49.6227 | 53.6977 | 57.2526 | 60.6058 | 64.0902 | 68.2631 | 69.6699 | 74.1688 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625
55% | 1116.2777 | 34.2135 | 31.0197 | 32.9662 | 35.4499 | 37.8547 | 39.9966 | 42.9325 | 46.1404 | 49.4254 | 52.6803 | 55.5745 | 58.7271 | 59.9391 | 64.0106 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 55% | 1116.2777 | 36.6389 | 33.4548 | 35.5109 | 38.025 | 40.3693 | 42.8646 | 45.4875 | 49.2229 | 52.4816 | 55.5553 | 58.7494 | 62.5745 | 63.8641 | 67.9881 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323
50% | 1494.9086 | 31.1032 | 28.1997 | 29.9692 | 32.2272 | 34.4133 | 36.3605 | 39.0295 | 41.9458 | 44.9322 | 47.8912 | 50.5222 | 53.3883 | 54.4901 | 58.1915 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 50% | 1494.9086 | 33.3081 | 30.4134 | 32.2827 | 34.5682 | 36.6994 | 38.9678 | 41.3522 | 44.7481 | 47.7105 | 50.5048 | 53.4085 | 56.8859 | 58.0583 | 61.8074 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021
45% | 2004.0097 | 27.9929 | 25.3797 | 26.9723 | 29.0045 | 30.972 | 32.7245 | 35.1266 | 37.7512 | 40.439 | 43.1021 | 45.47 | 48.0495 | 49.0411 | 52.3723 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 45% | 2004.0097 | 29.9773 | 27.3721 | 29.0544 | 31.1114 | 33.0294 | 35.071 | 37.217 | 40.2733 | 42.9395 | 45.4544 | 48.0677 | 51.1973 | 52.2524 | 55.6266 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719
40% | 2877.179 | 24.8826 | 22.5598 | 23.9754 | 25.7818 | 27.5307 | 29.0884 | 31.2236 | 33.5567 | 35.9458 | 38.3129 | 40.4178 | 42.7106 | 43.5921 | 46.5532 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 40% | 2877.179 | 26.6465 | 24.3307 | 25.8261 | 27.6546 | 29.3595 | 31.1742 | 33.0818 | 35.7985 | 38.1684 | 40.4039 | 42.7268 | 45.5087 | 46.4466 | 49.4459 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417
35% | 3454.933 | 21.7722 | 19.7398 | 20.9785 | 22.559 | 24.0893 | 25.4524 | 27.3207 | 29.3621 | 31.4525 | 33.5238 | 35.3656 | 37.3718 | 38.1431 | 40.734 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 35% | 3454.933 | 23.3157 | 21.2894 | 22.5979 | 24.1978 | 25.6896 | 27.2775 | 28.9466 | 31.3237 | 33.3974 | 35.3534 | 37.386 | 39.8201 | 40.6408 | 43.2652 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114
30% | 3663.5664 | 18.6619 | 16.9198 | 17.9815 | 19.3363 | 20.648 | 21.8163 | 23.4177 | 25.1675 | 26.9593 | 28.7347 | 30.3133 | 32.033 | 32.6941 | 34.9149 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 30% | 3663.5664 | 19.9849 | 18.2481 | 19.3696 | 20.7409 | 22.0196 | 23.3807 | 24.8113 | 26.8489 | 28.6263 | 30.3029 | 32.0451 | 34.1316 | 34.835 | 37.0844 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812
25% | 3862.6894 | 15.5516 | 14.0999 | 14.9846 | 16.1136 | 17.2067 | 18.1803 | 19.5148 | 20.9729 | 22.4661 | 23.9456 | 25.2611 | 26.6942 | 27.2451 | 29.0957 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 25% | 3862.6894 | 16.6541 | 15.2067 | 16.1413 | 17.2841 | 18.3497 | 19.4839 | 20.6761 | 22.3741 | 23.8553 | 25.2524 | 26.7043 | 28.443 | 29.0291 | 30.9037 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651
20% | 4122.7381 | 12.4413 | 11.2799 | 11.9877 | 12.8909 | 13.7653 | 14.5442 | 15.6118 | 16.7783 | 17.9729 | 19.1565 | 20.2089 | 21.3553 | 21.796 | 23.2766 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 20% | 4122.7381 | 13.3232 | 12.1654 | 12.9131 | 13.8273 | 14.6797 | 15.5871 | 16.5409 | 17.8992 | 19.0842 | 20.2019 | 21.3634 | 22.7544 | 23.2233 | 24.7229 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208
15% | 4372.3849 | 9.331 | 8.4599 | 8.9908 | 9.6682 | 10.324 | 10.9082 | 11.7089 | 12.5837 | 13.4797 | 14.3674 | 15.1567 | 16.0165 | 16.347 | 17.4574 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 15% | 4372.3849 | 9.9924 | 9.124 | 9.6848 | 10.3705 | 11.0098 | 11.6903 | 12.4057 | 13.4244 | 14.3132 | 15.1515 | 16.0226 | 17.0658 | 17.4175 | 18.5422 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906
10% | 4374.4653 | 6.2206 | 5.6399 | 5.9938 | 6.4454 | 6.8827 | 7.2721 | 7.8059 | 8.3892 | 8.9864 | 9.5782 | 10.1044 | 10.6777 | 10.898 | 11.6383 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 10% | 4374.4653 | 6.6616 | 6.0827 | 6.4565 | 6.9136 | 7.3399 | 7.7936 | 8.2704 | 8.9496 | 9.5421 | 10.101 | 10.6817 | 11.3772 | 11.6117 | 12.3615 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604
5% | 4374.7625 | 3.1103 | 2.82 | 2.9969 | 3.2227 | 3.4413 | 3.6361 | 3.903 | 4.1946 | 4.4932 | 4.7891 | 5.0522 | 5.3388 | 5.449 | 5.8191 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 5% | 4374.7625 | 3.3308 | 3.0413 | 3.2283 | 3.4568 | 3.6699 | 3.8968 | 4.1352 | 4.4748 | 4.7711 | 5.0505 | 5.3409 | 5.6886 | 5.8058 | 6.1807 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302
9.992e-14% | 4375.9513 | 6.2157e-14 | 5.6354e-14 | 5.9891e-14 | 6.4403e-14 | 6.8772e-14 | 7.2663e-14 | 7.7997e-14 | 8.3825e-14 | 8.9793e-14 | 9.5706e-14 | 1.0096e-13 | 1.0669e-13 | 1.0889e-13 | 1.1629e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 9.992e-14% | 4375.9513 | 6.6563e-14 | 6.0778e-14 | 6.4514e-14 | 6.9081e-14 | 7.334e-14 | 7.7873e-14 | 8.2638e-14 | 8.9425e-14 | 9.5345e-14 | 1.0093e-13 | 1.0673e-13 | 1.1368e-13 | 1.1602e-13 | 1.2352e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 100% | 0 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
99% | 0 | 79.9539 | 73.4917 | 77.3313 | 80.3764 | 83.9806 | 87.696 | 91.6392 | 96.1469 | 101.4481 | 106.4167 | 111.6368 | 120.5006 | 123.5326 | 129.219 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 99% | 0.37816 | 93.5071 | 87.1619 | 91.5053 | 95.145 | 98.3714 | 103.4399 | 108.0228 | 114.3709 | 120.9884 | 126.3994 | 131.5047 | 139.0694 | 144.5767 | 150.1244 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979
98% | 0.37816 | 79.1463 | 72.7493 | 76.5502 | 79.5646 | 83.1323 | 86.8102 | 90.7135 | 95.1757 | 100.4234 | 105.3418 | 110.5092 | 119.2834 | 122.2848 | 127.9138 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 98% | 1.1345 | 92.5626 | 86.2815 | 90.581 | 94.184 | 97.3777 | 102.395 | 106.9316 | 113.2156 | 119.7663 | 125.1227 | 130.1764 | 137.6647 | 143.1163 | 148.608 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222
97% | 0.75633 | 78.3387 | 72.007 | 75.7691 | 78.7527 | 82.284 | 85.9244 | 89.7879 | 94.2046 | 99.3986 | 104.2668 | 109.3815 | 118.0663 | 121.037 | 126.6085 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 97% | 2.269 | 91.6181 | 85.401 | 89.6567 | 93.2229 | 96.3841 | 101.3502 | 105.8405 | 112.0603 | 118.5442 | 123.8459 | 128.848 | 136.2599 | 141.6559 | 147.0916 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465
95% | 1.1345 | 76.7235 | 70.5223 | 74.2068 | 77.1289 | 80.5874 | 84.1528 | 87.9366 | 92.2622 | 97.3492 | 102.117 | 107.1262 | 115.6319 | 118.5414 | 123.9981 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 95% | 4.538 | 89.7291 | 83.6402 | 87.8081 | 91.3008 | 94.3968 | 99.2605 | 103.6582 | 109.7498 | 116.1 | 121.2924 | 126.1914 | 133.4504 | 138.7352 | 144.0588 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695
90% | 4.538 | 72.6854 | 66.8106 | 70.3012 | 73.0695 | 76.346 | 79.7237 | 83.3083 | 87.4063 | 92.2255 | 96.7424 | 101.488 | 109.546 | 112.3023 | 117.4718 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 90% | 7.9414 | 85.0065 | 79.2381 | 83.1866 | 86.4955 | 89.4285 | 94.0362 | 98.2025 | 103.9735 | 109.9894 | 114.9086 | 119.5497 | 126.4267 | 131.4333 | 136.4768 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163
85% | 7.9414 | 68.6473 | 63.0989 | 66.3956 | 69.0101 | 72.1045 | 75.2946 | 78.6801 | 82.5504 | 87.1019 | 91.3679 | 95.8498 | 103.4601 | 106.0633 | 110.9456 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 85% | 14.3702 | 80.2839 | 74.836 | 78.5652 | 81.6902 | 84.4603 | 88.812 | 92.7468 | 98.1972 | 103.8789 | 108.5247 | 112.9081 | 119.403 | 124.1315 | 128.8947 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376
80% | 11.7231 | 64.6092 | 59.3872 | 62.49 | 64.9507 | 67.8631 | 70.8655 | 74.0518 | 77.6945 | 81.9783 | 85.9933 | 90.2116 | 97.3742 | 99.8243 | 104.4194 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 80% | 19.6645 | 75.5613 | 70.4338 | 73.9437 | 76.8849 | 79.492 | 83.5878 | 87.2911 | 92.4209 | 97.7684 | 102.1409 | 106.2664 | 112.3793 | 116.8296 | 121.3127 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589
75% | 17.7737 | 60.5712 | 55.6755 | 58.5843 | 60.8912 | 63.6217 | 66.4364 | 69.4236 | 72.8386 | 76.8546 | 80.6187 | 84.5734 | 91.2883 | 93.5853 | 97.8932 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 75% | 25.7152 | 70.8387 | 66.0317 | 69.3222 | 72.0796 | 74.5238 | 78.3635 | 81.8354 | 86.6446 | 91.6579 | 95.7571 | 99.6248 | 105.3556 | 109.5278 | 113.7306 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803
70% | 35.1693 | 56.5331 | 51.9638 | 54.6787 | 56.8318 | 59.3802 | 62.0073 | 64.7954 | 67.9827 | 71.731 | 75.2441 | 78.9351 | 85.2025 | 87.3463 | 91.367 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 70% | 34.7911 | 66.1162 | 61.6296 | 64.7007 | 67.2743 | 69.5555 | 73.1393 | 76.3797 | 80.8683 | 85.5473 | 89.3733 | 92.9831 | 98.3319 | 102.2259 | 106.1486 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016
65% | 59.3718 | 52.495 | 48.2521 | 50.7731 | 52.7724 | 55.1388 | 57.5782 | 60.1671 | 63.1268 | 66.6073 | 69.8695 | 73.2969 | 79.1166 | 81.1072 | 84.8408 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 65% | 46.136 | 61.3936 | 57.2275 | 60.0792 | 62.469 | 64.5873 | 67.9151 | 70.924 | 75.092 | 79.4368 | 82.9895 | 86.3415 | 91.3082 | 94.9241 | 98.5666 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229
60% | 156.9382 | 48.4569 | 44.5404 | 46.8675 | 48.713 | 50.8973 | 53.1491 | 55.5389 | 58.2709 | 61.4837 | 64.495 | 67.6587 | 73.0307 | 74.8682 | 78.3146 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 60% | 76.7673 | 56.671 | 52.8254 | 55.4578 | 57.6637 | 59.619 | 62.6908 | 65.4683 | 69.3157 | 73.3263 | 76.6057 | 79.6998 | 84.2845 | 87.6222 | 90.9845 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442
55% | 363.794 | 44.4189 | 40.8287 | 42.9618 | 44.6536 | 46.6559 | 48.72 | 50.9106 | 53.415 | 56.3601 | 59.1204 | 62.0205 | 66.9448 | 68.6292 | 71.7884 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 55% | 106.2642 | 51.9484 | 48.4233 | 50.8363 | 52.8584 | 54.6508 | 57.4666 | 60.0126 | 63.5394 | 67.2158 | 70.2219 | 73.0582 | 77.2608 | 80.3204 | 83.4025 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655
50% | 771.4551 | 40.3808 | 37.117 | 39.0562 | 40.5942 | 42.4144 | 44.2909 | 46.2824 | 48.5591 | 51.2364 | 53.7458 | 56.3822 | 60.8589 | 62.3902 | 65.2621 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 50% | 178.4935 | 47.2258 | 44.0212 | 46.2148 | 48.0531 | 49.6825 | 52.2423 | 54.5569 | 57.7631 | 61.1052 | 63.8381 | 66.4165 | 70.2371 | 73.0185 | 75.8204 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868
45% | 1255.5054 | 36.3427 | 33.4053 | 35.1506 | 36.5347 | 38.173 | 39.8618 | 41.6542 | 43.7031 | 46.1128 | 48.3712 | 50.744 | 54.773 | 56.1512 | 58.7359 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 45% | 367.9538 | 42.5032 | 39.619 | 41.5933 | 43.2477 | 44.7143 | 47.0181 | 49.1013 | 51.9868 | 54.9947 | 57.4543 | 59.7749 | 63.2134 | 65.7167 | 68.2384 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
40% | 2059.1045 | 32.3046 | 29.6936 | 31.245 | 32.4753 | 33.9315 | 35.4327 | 37.0259 | 38.8472 | 40.9891 | 42.9966 | 45.1058 | 48.6871 | 49.9121 | 52.2097 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 40% | 741.202 | 37.7807 | 35.2169 | 36.9718 | 38.4424 | 39.746 | 41.7939 | 43.6456 | 46.2105 | 48.8842 | 51.0705 | 53.1332 | 56.1897 | 58.4148 | 60.6563 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295
35% | 3060.4836 | 28.2665 | 25.9819 | 27.3394 | 28.4159 | 29.6901 | 31.0036 | 32.3977 | 33.9913 | 35.8655 | 37.6221 | 39.4676 | 42.6012 | 43.6731 | 45.6835 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 35% | 1167.7713 | 33.0581 | 30.8148 | 32.3504 | 33.6371 | 34.7778 | 36.5696 | 38.1899 | 40.4341 | 42.7737 | 44.6867 | 46.4916 | 49.1659 | 51.113 | 53.0743 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508
30% | 3366.0403 | 24.2285 | 22.2702 | 23.4337 | 24.3565 | 25.4487 | 26.5746 | 27.7694 | 29.1354 | 30.7418 | 32.2475 | 33.8293 | 36.5153 | 37.4341 | 39.1573 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 30% | 2002.3799 | 28.3355 | 26.4127 | 27.7289 | 28.8318 | 29.8095 | 31.3454 | 32.7342 | 34.6578 | 36.6631 | 38.3029 | 39.8499 | 42.1422 | 43.8111 | 45.4923 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721
25% | 3686.3454 | 20.1904 | 18.5585 | 19.5281 | 20.2971 | 21.2072 | 22.1455 | 23.1412 | 24.2795 | 25.6182 | 26.8729 | 28.1911 | 30.4294 | 31.1951 | 32.6311 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 25% | 3173.5547 | 23.6129 | 22.0106 | 23.1074 | 24.0265 | 24.8413 | 26.1212 | 27.2785 | 28.8815 | 30.5526 | 31.919 | 33.2083 | 35.1185 | 36.5093 | 37.9102 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934
20% | 4028.5841 | 16.1523 | 14.8468 | 15.6225 | 16.2377 | 16.9658 | 17.7164 | 18.513 | 19.4236 | 20.4946 | 21.4983 | 22.5529 | 24.3436 | 24.9561 | 26.1049 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 20% | 3477.5988 | 18.8903 | 17.6085 | 18.4859 | 19.2212 | 19.873 | 20.8969 | 21.8228 | 23.1052 | 24.4421 | 25.5352 | 26.5666 | 28.0948 | 29.2074 | 30.3282 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147
15% | 4345.1076 | 12.1142 | 11.1351 | 11.7169 | 12.1782 | 12.7243 | 13.2873 | 13.8847 | 14.5677 | 15.3709 | 16.1237 | 16.9147 | 18.2577 | 18.7171 | 19.5786 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 15% | 3788.4498 | 14.1677 | 13.2063 | 13.8644 | 14.4159 | 14.9048 | 15.6727 | 16.3671 | 17.3289 | 18.3316 | 19.1514 | 19.925 | 21.0711 | 21.9056 | 22.7461 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361
10% | 4381.0332 | 8.0762 | 7.4234 | 7.8112 | 8.1188 | 8.4829 | 8.8582 | 9.2565 | 9.7118 | 10.2473 | 10.7492 | 11.2764 | 12.1718 | 12.478 | 13.0524 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 10% | 4317.5016 | 9.4452 | 8.8042 | 9.243 | 9.6106 | 9.9365 | 10.4485 | 10.9114 | 11.5526 | 12.221 | 12.7676 | 13.2833 | 14.0474 | 14.6037 | 15.1641 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574
5% | 4391.6218 | 4.0381 | 3.7117 | 3.9056 | 4.0594 | 4.2414 | 4.4291 | 4.6282 | 4.8559 | 5.1236 | 5.3746 | 5.6382 | 6.0859 | 6.239 | 6.5262 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 5% | 4391.6218 | 4.7226 | 4.4021 | 4.6215 | 4.8053 | 4.9683 | 5.2242 | 5.4557 | 5.7763 | 6.1105 | 6.3838 | 6.6417 | 7.0237 | 7.3019 | 7.582 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787
9.992e-14% | 4391.6218 | 8.0697e-14 | 7.4175e-14 | 7.805e-14 | 8.1123e-14 | 8.4761e-14 | 8.8511e-14 | 9.2491e-14 | 9.704e-14 | 1.0239e-13 | 1.0741e-13 | 1.1267e-13 | 1.2162e-13 | 1.2468e-13 | 1.3042e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 9.992e-14% | 4391.6218 | 9.4376e-14 | 8.7972e-14 | 9.2356e-14 | 9.6029e-14 | 9.9286e-14 | 1.044e-13 | 1.0903e-13 | 1.1543e-13 | 1.2211e-13 | 1.2757e-13 | 1.3273e-13 | 1.4036e-13 | 1.4592e-13 | 1.5152e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.2064 | 56.3994 | 59.9385 | 49.9544 | 54.3267 | 58.2211 | 63.5591 | 69.3917 | 75.3644 | 81.2824 | 86.5445 | 92.2766 | 94.4802 | 101.883 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 109.5384 | 100% | 0 | 66.6162 | 60.8268 | 64.5653 | 54.6364 | 58.8987 | 63.4356 | 68.2045 | 74.9962 | 80.9211 | 86.5097 | 92.317 | 99.2718 | 101.6166 | 109.1147 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041 | 116.1041
99% | 0.5944 | 61.5843 | 55.8354 | 59.3391 | 49.4549 | 53.7834 | 57.6389 | 62.9235 | 68.6977 | 74.6107 | 80.4695 | 85.679 | 91.3539 | 93.5354 | 100.8642 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 108.443 | 99% | 0.5944 | 65.9501 | 60.2186 | 63.9197 | 54.0901 | 58.3098 | 62.8012 | 67.5224 | 74.2463 | 80.1119 | 85.6446 | 91.3939 | 98.2791 | 100.6004 | 108.0236 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431 | 114.9431
98% | 0.8916 | 60.9623 | 55.2714 | 58.7397 | 48.9553 | 53.2401 | 57.0567 | 62.2879 | 68.0038 | 73.8571 | 79.6567 | 84.8136 | 90.4311 | 92.5906 | 99.8453 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 107.3476 | 98% | 0.8916 | 65.2839 | 59.6103 | 63.274 | 53.5437 | 57.7208 | 62.1669 | 66.8404 | 73.4963 | 79.3027 | 84.7795 | 90.4707 | 97.2864 | 99.5842 | 106.9325 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782 | 113.782
97% | 1.486 | 60.3402 | 54.7074 | 58.1403 | 48.4558 | 52.6969 | 56.4744 | 61.6523 | 67.3099 | 73.1035 | 78.8439 | 83.9481 | 89.5083 | 91.6458 | 98.8265 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 106.2522 | 97% | 1.486 | 64.6177 | 59.002 | 62.6284 | 52.9973 | 57.1318 | 61.5325 | 66.1583 | 72.7463 | 78.4934 | 83.9144 | 89.5475 | 96.2937 | 98.5681 | 105.8413 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621 | 112.621
95% | 2.3776 | 59.0961 | 53.5795 | 56.9416 | 47.4567 | 51.6103 | 55.31 | 60.3811 | 65.9221 | 71.5962 | 77.2182 | 82.2172 | 87.6628 | 89.7562 | 96.7888 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 104.0615 | 95% | 2.3776 | 63.2854 | 57.7855 | 61.3371 | 51.9046 | 55.9538 | 60.2638 | 64.7942 | 71.2464 | 76.875 | 82.1842 | 87.7012 | 94.3082 | 96.5357 | 103.659 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989 | 110.2989
90% | 3.2692 | 55.9857 | 50.7595 | 53.9446 | 44.959 | 48.894 | 52.399 | 57.2032 | 62.4525 | 67.828 | 73.1541 | 77.89 | 83.049 | 85.0322 | 91.6947 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 98.5845 | 90% | 3.2692 | 59.9546 | 54.7442 | 58.1088 | 49.1728 | 53.0089 | 57.092 | 61.384 | 67.4966 | 72.829 | 77.8587 | 83.0853 | 89.3447 | 91.4549 | 98.2033 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937 | 104.4937
85% | 13.9683 | 52.8754 | 47.9395 | 50.9477 | 42.4613 | 46.1777 | 49.4879 | 54.0252 | 58.9829 | 64.0597 | 69.09 | 73.5628 | 78.4351 | 80.3082 | 86.6005 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 93.1076 | 85% | 13.9683 | 56.6238 | 51.7028 | 54.8805 | 46.441 | 50.0639 | 53.9203 | 57.9738 | 63.7468 | 68.7829 | 73.5332 | 78.4695 | 84.3811 | 86.3741 | 92.7475 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885 | 98.6885
80% | 41.3106 | 49.7651 | 45.1195 | 47.9508 | 39.9635 | 43.4613 | 46.5769 | 50.8473 | 55.5133 | 60.2915 | 65.0259 | 69.2356 | 73.8213 | 75.5842 | 81.5064 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 87.6307 | 80% | 41.3106 | 53.293 | 48.6615 | 51.6523 | 43.7092 | 47.119 | 50.7485 | 54.5636 | 59.997 | 64.7369 | 69.2077 | 73.8536 | 79.4175 | 81.2932 | 87.2918 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833 | 92.8833
75% | 126.3094 | 46.6548 | 42.2996 | 44.9539 | 37.4658 | 40.745 | 43.6658 | 47.6693 | 52.0437 | 56.5233 | 60.9618 | 64.9083 | 69.2075 | 70.8602 | 76.4122 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 82.1538 | 75% | 126.3094 | 49.9622 | 45.6201 | 48.424 | 40.9773 | 44.1741 | 47.5767 | 51.1534 | 56.2472 | 60.6908 | 64.8823 | 69.2378 | 74.4539 | 76.2124 | 81.8361 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781 | 87.0781
70% | 323.9464 | 43.5445 | 39.4796 | 41.9569 | 34.9681 | 38.0287 | 40.7548 | 44.4914 | 48.5742 | 52.7551 | 56.8977 | 60.5811 | 64.5936 | 66.1361 | 71.3181 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 76.6769 | 70% | 323.9464 | 46.6314 | 42.5788 | 45.1957 | 38.2455 | 41.2291 | 44.4049 | 47.7431 | 52.4974 | 56.6448 | 60.5568 | 64.6219 | 69.4903 | 71.1316 | 76.3803 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729 | 81.2729
65% | 549.5201 | 40.4341 | 36.6596 | 38.96 | 32.4704 | 35.3123 | 37.8437 | 41.3134 | 45.1046 | 48.9869 | 52.8335 | 56.2539 | 59.9798 | 61.4121 | 66.2239 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 71.1999 | 65% | 549.5201 | 43.3005 | 39.5374 | 41.9675 | 35.5137 | 38.2842 | 41.2331 | 44.3329 | 48.7476 | 52.5987 | 56.2313 | 60.0061 | 64.5267 | 66.0508 | 70.9246 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677 | 75.4677
60% | 799.4641 | 37.3238 | 33.8397 | 35.9631 | 29.9726 | 32.596 | 34.9326 | 38.1354 | 41.635 | 45.2186 | 48.7694 | 51.9267 | 55.366 | 56.6881 | 61.1298 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 65.723 | 60% | 799.4641 | 39.9697 | 36.4961 | 38.7392 | 32.7819 | 35.3392 | 38.0614 | 40.9227 | 44.9977 | 48.5526 | 51.9058 | 55.3902 | 59.5631 | 60.9699 | 65.4688 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625 | 69.6625
55% | 1116.2777 | 34.2135 | 31.0197 | 32.9662 | 27.4749 | 29.8797 | 32.0216 | 34.9575 | 38.1654 | 41.4504 | 44.7053 | 47.5995 | 50.7521 | 51.9641 | 56.0356 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 60.2461 | 55% | 1116.2777 | 36.6389 | 33.4548 | 35.5109 | 30.05 | 32.3943 | 34.8896 | 37.5125 | 41.2479 | 44.5066 | 47.5803 | 50.7744 | 54.5995 | 55.8891 | 60.0131 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573 | 63.8573
50% | 1494.9086 | 31.1032 | 28.1997 | 29.9692 | 24.9772 | 27.1633 | 29.1105 | 31.7795 | 34.6958 | 37.6822 | 40.6412 | 43.2722 | 46.1383 | 47.2401 | 50.9415 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 54.7692 | 50% | 1494.9086 | 33.3081 | 30.4134 | 32.2827 | 27.3182 | 29.4494 | 31.7178 | 34.1022 | 37.4981 | 40.4605 | 43.2548 | 46.1585 | 49.6359 | 50.8083 | 54.5574 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521 | 58.0521
45% | 2004.0097 | 27.9929 | 25.3797 | 26.9723 | 22.4795 | 24.447 | 26.1995 | 28.6016 | 31.2262 | 33.914 | 36.5771 | 38.945 | 41.5245 | 42.5161 | 45.8473 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 49.2923 | 45% | 2004.0097 | 29.9773 | 27.3721 | 29.0544 | 24.5864 | 26.5044 | 28.546 | 30.692 | 33.7483 | 36.4145 | 38.9294 | 41.5427 | 44.6723 | 45.7274 | 49.1016 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469 | 52.2469
40% | 2877.179 | 24.8826 | 22.5598 | 23.9754 | 19.9818 | 21.7307 | 23.2884 | 25.4236 | 27.7567 | 30.1458 | 32.5129 | 34.6178 | 36.9106 | 37.7921 | 40.7532 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 43.8154 | 40% | 2877.179 | 26.6465 | 24.3307 | 25.8261 | 21.8546 | 23.5595 | 25.3742 | 27.2818 | 29.9985 | 32.3684 | 34.6039 | 36.9268 | 39.7087 | 40.6466 | 43.6459 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417 | 46.4417
35% | 3454.933 | 21.7722 | 19.7398 | 20.9785 | 17.484 | 19.0143 | 20.3774 | 22.2457 | 24.2871 | 26.3775 | 28.4488 | 30.2906 | 32.2968 | 33.0681 | 35.659 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 38.3384 | 35% | 3454.933 | 23.3157 | 21.2894 | 22.5979 | 19.1228 | 20.6146 | 22.2025 | 23.8716 | 26.2487 | 28.3224 | 30.2784 | 32.311 | 34.7451 | 35.5658 | 38.1902 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364 | 40.6364
30% | 3663.5664 | 18.6619 | 16.9198 | 17.9815 | 14.9863 | 16.298 | 17.4663 | 19.0677 | 20.8175 | 22.6093 | 24.3847 | 25.9633 | 27.683 | 28.3441 | 30.5649 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 32.8615 | 30% | 3663.5664 | 19.9849 | 18.2481 | 19.3696 | 16.3909 | 17.6696 | 19.0307 | 20.4613 | 22.4989 | 24.2763 | 25.9529 | 27.6951 | 29.7816 | 30.485 | 32.7344 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312 | 34.8312
25% | 3862.6894 | 15.5516 | 14.0999 | 14.9846 | 12.4886 | 13.5817 | 14.5553 | 15.8898 | 17.3479 | 18.8411 | 20.3206 | 21.6361 | 23.0692 | 23.6201 | 25.4707 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 27.3846 | 25% | 3862.6894 | 16.6541 | 15.2067 | 16.1413 | 13.6591 | 14.7247 | 15.8589 | 17.0511 | 18.7491 | 20.2303 | 21.6274 | 23.0793 | 24.818 | 25.4041 | 27.2787 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026 | 29.026
20% | 4122.7381 | 12.4413 | 11.2799 | 11.9877 | 9.9909 | 10.8653 | 11.6442 | 12.7118 | 13.8783 | 15.0729 | 16.2565 | 17.3089 | 18.4553 | 18.896 | 20.3766 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 21.9077 | 20% | 4122.7381 | 13.3232 | 12.1654 | 12.9131 | 10.9273 | 11.7797 | 12.6871 | 13.6409 | 14.9992 | 16.1842 | 17.3019 | 18.4634 | 19.8544 | 20.3233 | 21.8229 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208 | 23.2208
15% | 4372.3849 | 9.331 | 8.4599 | 8.9908 | 7.4932 | 8.149 | 8.7332 | 9.5339 | 10.4087 | 11.3047 | 12.1924 | 12.9817 | 13.8415 | 14.172 | 15.2824 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 16.4308 | 15% | 4372.3849 | 9.9924 | 9.124 | 9.6848 | 8.1955 | 8.8348 | 9.5153 | 10.2307 | 11.2494 | 12.1382 | 12.9765 | 13.8476 | 14.8908 | 15.2425 | 16.3672 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156 | 17.4156
10% | 4374.4653 | 6.2206 | 5.6399 | 5.9938 | 4.9954 | 5.4327 | 5.8221 | 6.3559 | 6.9392 | 7.5364 | 8.1282 | 8.6544 | 9.2277 | 9.448 | 10.1883 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10.9538 | 10% | 4374.4653 | 6.6616 | 6.0827 | 6.4565 | 5.4636 | 5.8899 | 6.3436 | 6.8204 | 7.4996 | 8.0921 | 8.651 | 9.2317 | 9.9272 | 10.1617 | 10.9115 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104 | 11.6104
5% | 4374.7625 | 3.1103 | 2.82 | 2.9969 | 2.4977 | 2.7163 | 2.9111 | 3.178 | 3.4696 | 3.7682 | 4.0641 | 4.3272 | 4.6138 | 4.724 | 5.0941 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5.4769 | 5% | 4374.7625 | 3.3308 | 3.0413 | 3.2283 | 2.7318 | 2.9449 | 3.1718 | 3.4102 | 3.7498 | 4.0461 | 4.3255 | 4.6159 | 4.9636 | 5.0808 | 5.4557 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052 | 5.8052
9.992e-14% | 4375.9513 | 6.2157e-14 | 5.6354e-14 | 5.9891e-14 | 4.9914e-14 | 5.4283e-14 | 5.8175e-14 | 6.3508e-14 | 6.9336e-14 | 7.5304e-14 | 8.1217e-14 | 8.6475e-14 | 9.2203e-14 | 9.4405e-14 | 1.018e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 1.0945e-13 | 9.992e-14% | 4375.9513 | 6.6563e-14 | 6.0778e-14 | 6.4514e-14 | 5.4593e-14 | 5.8852e-14 | 6.3385e-14 | 6.815e-14 | 7.4936e-14 | 8.0856e-14 | 8.6441e-14 | 9.2243e-14 | 9.9192e-14 | 1.0154e-13 | 1.0903e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13 | 1.1601e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 80.7616 | 74.234 | 78.1124 | 66.6883 | 70.3289 | 74.0818 | 78.0648 | 82.6181 | 87.9728 | 92.9916 | 98.2645 | 107.2178 | 110.2804 | 116.0243 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 120.4232 | 100% | 0 | 94.4516 | 88.0423 | 92.4296 | 81.6061 | 84.865 | 89.9847 | 94.6139 | 101.0261 | 107.7105 | 113.1762 | 118.333 | 125.9741 | 131.537 | 137.1409 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737 | 143.0737
99% | 0 | 79.9539 | 73.4917 | 77.3313 | 66.0214 | 69.6256 | 73.341 | 77.2842 | 81.7919 | 87.0931 | 92.0617 | 97.2818 | 106.1456 | 109.1776 | 114.864 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 119.219 | 99% | 0.37816 | 93.5071 | 87.1619 | 91.5053 | 80.79 | 84.0164 | 89.0849 | 93.6678 | 100.0159 | 106.6334 | 112.0444 | 117.1497 | 124.7144 | 130.2217 | 135.7694 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429 | 141.6429
98% | 0.37816 | 79.1463 | 72.7493 | 76.5502 | 65.3546 | 68.9223 | 72.6002 | 76.5035 | 80.9657 | 86.2134 | 91.1318 | 96.2992 | 105.0734 | 108.0748 | 113.7038 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 118.0148 | 98% | 1.1345 | 92.5626 | 86.2815 | 90.581 | 79.974 | 83.1677 | 88.185 | 92.7216 | 99.0056 | 105.5563 | 110.9127 | 115.9664 | 123.4547 | 128.9063 | 134.398 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122 | 140.2122
97% | 0.75633 | 78.3387 | 72.007 | 75.7691 | 64.6877 | 68.219 | 71.8594 | 75.7229 | 80.1396 | 85.3336 | 90.2018 | 95.3165 | 104.0013 | 106.972 | 112.5435 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 116.8105 | 97% | 2.269 | 91.6181 | 85.401 | 89.6567 | 79.1579 | 82.3191 | 87.2852 | 91.7755 | 97.9953 | 104.4792 | 109.7809 | 114.783 | 122.1949 | 127.5909 | 133.0266 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815 | 138.7815
95% | 1.1345 | 76.7235 | 70.5223 | 74.2068 | 63.3539 | 66.8124 | 70.3778 | 74.1616 | 78.4872 | 83.5742 | 88.342 | 93.3512 | 101.8569 | 104.7664 | 110.2231 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 114.4021 | 95% | 4.538 | 89.7291 | 83.6402 | 87.8081 | 77.5258 | 80.6218 | 85.4855 | 89.8832 | 95.9748 | 102.325 | 107.5174 | 112.4164 | 119.6754 | 124.9602 | 130.2838 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92 | 135.92
90% | 4.538 | 72.6854 | 66.8106 | 70.3012 | 60.0195 | 63.296 | 66.6737 | 70.2583 | 74.3563 | 79.1755 | 83.6924 | 88.438 | 96.496 | 99.2523 | 104.4218 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 108.3809 | 90% | 7.9414 | 85.0065 | 79.2381 | 83.1866 | 73.4455 | 76.3785 | 80.9862 | 85.1525 | 90.9235 | 96.9394 | 101.8586 | 106.4997 | 113.3767 | 118.3833 | 123.4268 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663 | 128.7663
85% | 7.9414 | 68.6473 | 63.0989 | 66.3956 | 56.6851 | 59.7795 | 62.9696 | 66.3551 | 70.2254 | 74.7769 | 79.0429 | 83.5248 | 91.1351 | 93.7383 | 98.6206 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 102.3597 | 85% | 14.3702 | 80.2839 | 74.836 | 78.5652 | 69.3652 | 72.1353 | 76.487 | 80.4218 | 85.8722 | 91.5539 | 96.1997 | 100.5831 | 107.078 | 111.8065 | 116.5697 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126 | 121.6126
80% | 11.7231 | 64.6092 | 59.3872 | 62.49 | 53.3507 | 56.2631 | 59.2655 | 62.4518 | 66.0945 | 70.3783 | 74.3933 | 78.6116 | 85.7742 | 88.2243 | 92.8194 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 96.3386 | 80% | 19.6645 | 75.5613 | 70.4338 | 73.9437 | 65.2849 | 67.892 | 71.9878 | 75.6911 | 80.8209 | 86.1684 | 90.5409 | 94.6664 | 100.7793 | 105.2296 | 109.7127 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589 | 114.4589
75% | 17.7737 | 60.5712 | 55.6755 | 58.5843 | 50.0162 | 52.7467 | 55.5614 | 58.5486 | 61.9636 | 65.9796 | 69.7437 | 73.6984 | 80.4133 | 82.7103 | 87.0182 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 90.3174 | 75% | 25.7152 | 70.8387 | 66.0317 | 69.3222 | 61.2046 | 63.6488 | 67.4885 | 70.9604 | 75.7696 | 80.7829 | 84.8821 | 88.7498 | 94.4806 | 98.6528 | 102.8556 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053 | 107.3053
70% | 35.1693 | 56.5331 | 51.9638 | 54.6787 | 46.6818 | 49.2302 | 51.8573 | 54.6454 | 57.8327 | 61.581 | 65.0941 | 68.7851 | 75.0525 | 77.1963 | 81.217 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 84.2963 | 70% | 34.7911 | 66.1162 | 61.6296 | 64.7007 | 57.1243 | 59.4055 | 62.9893 | 66.2297 | 70.7183 | 75.3973 | 79.2233 | 82.8331 | 88.1819 | 92.0759 | 95.9986 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516 | 100.1516
65% | 59.3718 | 52.495 | 48.2521 | 50.7731 | 43.3474 | 45.7138 | 48.1532 | 50.7421 | 53.7018 | 57.1823 | 60.4445 | 63.8719 | 69.6916 | 71.6822 | 75.4158 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 78.2751 | 65% | 46.136 | 61.3936 | 57.2275 | 60.0792 | 53.044 | 55.1623 | 58.4901 | 61.499 | 65.667 | 70.0118 | 73.5645 | 76.9165 | 81.8832 | 85.4991 | 89.1416 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979 | 92.9979
60% | 156.9382 | 48.4569 | 44.5404 | 46.8675 | 40.013 | 42.1973 | 44.4491 | 46.8389 | 49.5709 | 52.7837 | 55.795 | 58.9587 | 64.3307 | 66.1682 | 69.6146 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 72.2539 | 60% | 76.7673 | 56.671 | 52.8254 | 55.4578 | 48.9637 | 50.919 | 53.9908 | 56.7683 | 60.6157 | 64.6263 | 67.9057 | 70.9998 | 75.5845 | 78.9222 | 82.2845 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442 | 85.8442
55% | 363.794 | 44.4189 | 40.8287 | 42.9618 | 36.6786 | 38.6809 | 40.745 | 42.9356 | 45.44 | 48.3851 | 51.1454 | 54.0455 | 58.9698 | 60.6542 | 63.8134 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 66.2328 | 55% | 106.2642 | 51.9484 | 48.4233 | 50.8363 | 44.8834 | 46.6758 | 49.4916 | 52.0376 | 55.5644 | 59.2408 | 62.2469 | 65.0832 | 69.2858 | 72.3454 | 75.4275 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905 | 78.6905
50% | 771.4551 | 40.3808 | 37.117 | 39.0562 | 33.3442 | 35.1644 | 37.0409 | 39.0324 | 41.3091 | 43.9864 | 46.4958 | 49.1322 | 53.6089 | 55.1402 | 58.0121 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 60.2116 | 50% | 178.4935 | 47.2258 | 44.0212 | 46.2148 | 40.8031 | 42.4325 | 44.9923 | 47.3069 | 50.5131 | 53.8552 | 56.5881 | 59.1665 | 62.9871 | 65.7685 | 68.5704 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368 | 71.5368
45% | 1255.5054 | 36.3427 | 33.4053 | 35.1506 | 30.0097 | 31.648 | 33.3368 | 35.1292 | 37.1781 | 39.5878 | 41.8462 | 44.219 | 48.248 | 49.6262 | 52.2109 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 54.1904 | 45% | 367.9538 | 42.5032 | 39.619 | 41.5933 | 36.7227 | 38.1893 | 40.4931 | 42.5763 | 45.4618 | 48.4697 | 50.9293 | 53.2499 | 56.6884 | 59.1917 | 61.7134 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832 | 64.3832
40% | 2059.1045 | 32.3046 | 29.6936 | 31.245 | 26.6753 | 28.1315 | 29.6327 | 31.2259 | 33.0472 | 35.1891 | 37.1966 | 39.3058 | 42.8871 | 44.1121 | 46.4097 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 48.1693 | 40% | 741.202 | 37.7807 | 35.2169 | 36.9718 | 32.6424 | 33.946 | 35.9939 | 37.8456 | 40.4105 | 43.0842 | 45.2705 | 47.3332 | 50.3897 | 52.6148 | 54.8563 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295 | 57.2295
35% | 3060.4836 | 28.2665 | 25.9819 | 27.3394 | 23.3409 | 24.6151 | 25.9286 | 27.3227 | 28.9163 | 30.7905 | 32.5471 | 34.3926 | 37.5262 | 38.5981 | 40.6085 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 42.1481 | 35% | 1167.7713 | 33.0581 | 30.8148 | 32.3504 | 28.5621 | 29.7028 | 31.4946 | 33.1149 | 35.3591 | 37.6987 | 39.6117 | 41.4166 | 44.0909 | 46.038 | 47.9993 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758 | 50.0758
30% | 3366.0403 | 24.2285 | 22.2702 | 23.4337 | 20.0065 | 21.0987 | 22.2246 | 23.4194 | 24.7854 | 26.3918 | 27.8975 | 29.4793 | 32.1653 | 33.0841 | 34.8073 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 36.127 | 30% | 2002.3799 | 28.3355 | 26.4127 | 27.7289 | 24.4818 | 25.4595 | 26.9954 | 28.3842 | 30.3078 | 32.3131 | 33.9529 | 35.4999 | 37.7922 | 39.4611 | 41.1423 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221 | 42.9221
25% | 3686.3454 | 20.1904 | 18.5585 | 19.5281 | 16.6721 | 17.5822 | 18.5205 | 19.5162 | 20.6545 | 21.9932 | 23.2479 | 24.5661 | 26.8044 | 27.5701 | 29.0061 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 30.1058 | 25% | 3173.5547 | 23.6129 | 22.0106 | 23.1074 | 20.4015 | 21.2163 | 22.4962 | 23.6535 | 25.2565 | 26.9276 | 28.294 | 29.5833 | 31.4935 | 32.8843 | 34.2852 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684 | 35.7684
20% | 4028.5841 | 16.1523 | 14.8468 | 15.6225 | 13.3377 | 14.0658 | 14.8164 | 15.613 | 16.5236 | 17.5946 | 18.5983 | 19.6529 | 21.4436 | 22.0561 | 23.2049 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 24.0846 | 20% | 3477.5988 | 18.8903 | 17.6085 | 18.4859 | 16.3212 | 16.973 | 17.9969 | 18.9228 | 20.2052 | 21.5421 | 22.6352 | 23.6666 | 25.1948 | 26.3074 | 27.4282 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147 | 28.6147
15% | 4345.1076 | 12.1142 | 11.1351 | 11.7169 | 10.0032 | 10.5493 | 11.1123 | 11.7097 | 12.3927 | 13.1959 | 13.9487 | 14.7397 | 16.0827 | 16.5421 | 17.4036 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 18.0635 | 15% | 3788.4498 | 14.1677 | 13.2063 | 13.8644 | 12.2409 | 12.7298 | 13.4977 | 14.1921 | 15.1539 | 16.1566 | 16.9764 | 17.75 | 18.8961 | 19.7306 | 20.5711 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611 | 21.4611
10% | 4381.0332 | 8.0762 | 7.4234 | 7.8112 | 6.6688 | 7.0329 | 7.4082 | 7.8065 | 8.2618 | 8.7973 | 9.2992 | 9.8264 | 10.7218 | 11.028 | 11.6024 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 12.0423 | 10% | 4317.5016 | 9.4452 | 8.8042 | 9.243 | 8.1606 | 8.4865 | 8.9985 | 9.4614 | 10.1026 | 10.771 | 11.3176 | 11.8333 | 12.5974 | 13.1537 | 13.7141 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074 | 14.3074
5% | 4391.6218 | 4.0381 | 3.7117 | 3.9056 | 3.3344 | 3.5164 | 3.7041 | 3.9032 | 4.1309 | 4.3986 | 4.6496 | 4.9132 | 5.3609 | 5.514 | 5.8012 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 6.0212 | 5% | 4391.6218 | 4.7226 | 4.4021 | 4.6215 | 4.0803 | 4.2433 | 4.4992 | 4.7307 | 5.0513 | 5.3855 | 5.6588 | 5.9167 | 6.2987 | 6.5769 | 6.857 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537 | 7.1537
9.992e-14% | 4391.6218 | 8.0697e-14 | 7.4175e-14 | 7.805e-14 | 6.6635e-14 | 7.0273e-14 | 7.4023e-14 | 7.8002e-14 | 8.2552e-14 | 8.7903e-14 | 9.2917e-14 | 9.8186e-14 | 1.0713e-13 | 1.1019e-13 | 1.1593e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 1.2033e-13 | 9.992e-14% | 4391.6218 | 9.4376e-14 | 8.7972e-14 | 9.2356e-14 | 8.1541e-14 | 8.4797e-14 | 8.9913e-14 | 9.4538e-14 | 1.0095e-13 | 1.0762e-13 | 1.1309e-13 | 1.1824e-13 | 1.2587e-13 | 1.3143e-13 | 1.3703e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13 | 1.4296e-13
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 100% | 0 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
99% | 0.5944 | 61.5843 | 55.8354 | 59.3391 | 63.8099 | 68.1384 | 71.9939 | 77.2785 | 83.0527 | 88.9657 | 94.8245 | 100.034 | 105.7089 | 107.8904 | 115.2192 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 99% | 0.5944 | 65.9501 | 60.2186 | 63.9197 | 68.4451 | 72.6648 | 77.1562 | 81.8774 | 88.6013 | 94.4669 | 99.9996 | 105.7489 | 112.6341 | 114.9554 | 122.3786 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981
98% | 0.8916 | 60.9623 | 55.2714 | 58.7397 | 63.1653 | 67.4501 | 71.2667 | 76.4979 | 82.2138 | 88.0671 | 93.8667 | 99.0236 | 104.6411 | 106.8006 | 114.0553 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 98% | 0.8916 | 65.2839 | 59.6103 | 63.274 | 67.7537 | 71.9308 | 76.3769 | 81.0504 | 87.7063 | 93.5127 | 98.9895 | 104.6807 | 111.4964 | 113.7942 | 121.1425 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992
97% | 1.486 | 60.3402 | 54.7074 | 58.1403 | 62.5208 | 66.7619 | 70.5394 | 75.7173 | 81.3749 | 87.1685 | 92.9089 | 98.0131 | 103.5733 | 105.7108 | 112.8915 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 97% | 1.486 | 64.6177 | 59.002 | 62.6284 | 67.0623 | 71.1968 | 75.5975 | 80.2233 | 86.8113 | 92.5584 | 97.9794 | 103.6125 | 110.3587 | 112.6331 | 119.9063 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686
95% | 2.3776 | 59.0961 | 53.5795 | 56.9416 | 61.2317 | 65.3853 | 69.085 | 74.1561 | 79.6971 | 85.3712 | 90.9932 | 95.9922 | 101.4378 | 103.5312 | 110.5638 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 95% | 2.3776 | 63.2854 | 57.7855 | 61.3371 | 65.6796 | 69.7288 | 74.0388 | 78.5692 | 85.0214 | 90.65 | 95.9592 | 101.4762 | 108.0832 | 110.3107 | 117.434 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739
90% | 3.2692 | 55.9857 | 50.7595 | 53.9446 | 58.009 | 61.944 | 65.449 | 70.2532 | 75.5025 | 80.878 | 86.2041 | 90.94 | 96.099 | 98.0822 | 104.7447 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 90% | 3.2692 | 59.9546 | 54.7442 | 58.1088 | 62.2228 | 66.0589 | 70.142 | 74.434 | 80.5466 | 85.879 | 90.9087 | 96.1353 | 102.3947 | 104.5049 | 111.2533 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437
85% | 13.9683 | 52.8754 | 47.9395 | 50.9477 | 54.7863 | 58.5027 | 61.8129 | 66.3502 | 71.3079 | 76.3847 | 81.415 | 85.8878 | 90.7601 | 92.6332 | 98.9255 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 85% | 13.9683 | 56.6238 | 51.7028 | 54.8805 | 58.766 | 62.3889 | 66.2453 | 70.2988 | 76.0718 | 81.1079 | 85.8582 | 90.7945 | 96.7061 | 98.6991 | 105.0725 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135
80% | 41.3106 | 49.7651 | 45.1195 | 47.9508 | 51.5635 | 55.0613 | 58.1769 | 62.4473 | 67.1133 | 71.8915 | 76.6259 | 80.8356 | 85.4213 | 87.1842 | 93.1064 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 80% | 41.3106 | 53.293 | 48.6615 | 51.6523 | 55.3092 | 58.719 | 62.3485 | 66.1636 | 71.597 | 76.3369 | 80.8077 | 85.4536 | 91.0175 | 92.8932 | 98.8918 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833
75% | 126.3094 | 46.6548 | 42.2996 | 44.9539 | 48.3408 | 51.62 | 54.5408 | 58.5443 | 62.9187 | 67.3983 | 71.8368 | 75.7833 | 80.0825 | 81.7352 | 87.2872 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 75% | 126.3094 | 49.9622 | 45.6201 | 48.424 | 51.8523 | 55.0491 | 58.4517 | 62.0284 | 67.1222 | 71.5658 | 75.7573 | 80.1128 | 85.3289 | 87.0874 | 92.7111 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531
70% | 323.9464 | 43.5445 | 39.4796 | 41.9569 | 45.1181 | 48.1787 | 50.9048 | 54.6414 | 58.7242 | 62.9051 | 67.0477 | 70.7311 | 74.7436 | 76.2861 | 81.4681 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 70% | 323.9464 | 46.6314 | 42.5788 | 45.1957 | 48.3955 | 51.3791 | 54.5549 | 57.8931 | 62.6474 | 66.7948 | 70.7068 | 74.7719 | 79.6403 | 81.2816 | 86.5303 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229
65% | 549.5201 | 40.4341 | 36.6596 | 38.96 | 41.8954 | 44.7373 | 47.2687 | 50.7384 | 54.5296 | 58.4119 | 62.2585 | 65.6789 | 69.4048 | 70.8371 | 75.6489 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 65% | 549.5201 | 43.3005 | 39.5374 | 41.9675 | 44.9387 | 47.7092 | 50.6581 | 53.7579 | 58.1726 | 62.0237 | 65.6563 | 69.4311 | 73.9517 | 75.4758 | 80.3496 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927
60% | 799.4641 | 37.3238 | 33.8397 | 35.9631 | 38.6726 | 41.296 | 43.6326 | 46.8354 | 50.335 | 53.9186 | 57.4694 | 60.6267 | 64.066 | 65.3881 | 69.8298 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 60% | 799.4641 | 39.9697 | 36.4961 | 38.7392 | 41.4819 | 44.0392 | 46.7614 | 49.6227 | 53.6977 | 57.2526 | 60.6058 | 64.0902 | 68.2631 | 69.6699 | 74.1688 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625
55% | 1116.2777 | 34.2135 | 31.0197 | 32.9662 | 35.4499 | 37.8547 | 39.9966 | 42.9325 | 46.1404 | 49.4254 | 52.6803 | 55.5745 | 58.7271 | 59.9391 | 64.0106 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 55% | 1116.2777 | 36.6389 | 33.4548 | 35.5109 | 38.025 | 40.3693 | 42.8646 | 45.4875 | 49.2229 | 52.4816 | 55.5553 | 58.7494 | 62.5745 | 63.8641 | 67.9881 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323
50% | 1494.9086 | 31.1032 | 28.1997 | 29.9692 | 32.2272 | 34.4133 | 36.3605 | 39.0295 | 41.9458 | 44.9322 | 47.8912 | 50.5222 | 53.3883 | 54.4901 | 58.1915 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 50% | 1494.9086 | 33.3081 | 30.4134 | 32.2827 | 34.5682 | 36.6994 | 38.9678 | 41.3522 | 44.7481 | 47.7105 | 50.5048 | 53.4085 | 56.8859 | 58.0583 | 61.8074 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021
45% | 2004.0097 | 27.9929 | 25.3797 | 26.9723 | 29.0045 | 30.972 | 32.7245 | 35.1266 | 37.7512 | 40.439 | 43.1021 | 45.47 | 48.0495 | 49.0411 | 52.3723 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 45% | 2004.0097 | 29.9773 | 27.3721 | 29.0544 | 31.1114 | 33.0294 | 35.071 | 37.217 | 40.2733 | 42.9395 | 45.4544 | 48.0677 | 51.1973 | 52.2524 | 55.6266 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719
40% | 2877.179 | 24.8826 | 22.5598 | 23.9754 | 25.7818 | 27.5307 | 29.0884 | 31.2236 | 33.5567 | 35.9458 | 38.3129 | 40.4178 | 42.7106 | 43.5921 | 46.5532 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 40% | 2877.179 | 26.6465 | 24.3307 | 25.8261 | 27.6546 | 29.3595 | 31.1742 | 33.0818 | 35.7985 | 38.1684 | 40.4039 | 42.7268 | 45.5087 | 46.4466 | 49.4459 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417
35% | 3454.933 | 21.7722 | 19.7398 | 20.9785 | 22.559 | 24.0893 | 25.4524 | 27.3207 | 29.3621 | 31.4525 | 33.5238 | 35.3656 | 37.3718 | 38.1431 | 40.734 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 35% | 3454.933 | 23.3157 | 21.2894 | 22.5979 | 24.1978 | 25.6896 | 27.2775 | 28.9466 | 31.3237 | 33.3974 | 35.3534 | 37.386 | 39.8201 | 40.6408 | 43.2652 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114
30% | 3663.5664 | 18.6619 | 16.9198 | 17.9815 | 19.3363 | 20.648 | 21.8163 | 23.4177 | 25.1675 | 26.9593 | 28.7347 | 30.3133 | 32.033 | 32.6941 | 34.9149 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 30% | 3663.5664 | 19.9849 | 18.2481 | 19.3696 | 20.7409 | 22.0196 | 23.3807 | 24.8113 | 26.8489 | 28.6263 | 30.3029 | 32.0451 | 34.1316 | 34.835 | 37.0844 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812
25% | 3862.6894 | 15.5516 | 14.0999 | 14.9846 | 16.1136 | 17.2067 | 18.1803 | 19.5148 | 20.9729 | 22.4661 | 23.9456 | 25.2611 | 26.6942 | 27.2451 | 29.0957 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 25% | 3862.6894 | 16.6541 | 15.2067 | 16.1413 | 17.2841 | 18.3497 | 19.4839 | 20.6761 | 22.3741 | 23.8553 | 25.2524 | 26.7043 | 28.443 | 29.0291 | 30.9037 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651
20% | 4122.7381 | 12.4413 | 11.2799 | 11.9877 | 12.8909 | 13.7653 | 14.5442 | 15.6118 | 16.7783 | 17.9729 | 19.1565 | 20.2089 | 21.3553 | 21.796 | 23.2766 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 20% | 4122.7381 | 13.3232 | 12.1654 | 12.9131 | 13.8273 | 14.6797 | 15.5871 | 16.5409 | 17.8992 | 19.0842 | 20.2019 | 21.3634 | 22.7544 | 23.2233 | 24.7229 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208
15% | 4372.3849 | 9.331 | 8.4599 | 8.9908 | 9.6682 | 10.324 | 10.9082 | 11.7089 | 12.5837 | 13.4797 | 14.3674 | 15.1567 | 16.0165 | 16.347 | 17.4574 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 15% | 4372.3849 | 9.9924 | 9.124 | 9.6848 | 10.3705 | 11.0098 | 11.6903 | 12.4057 | 13.4244 | 14.3132 | 15.1515 | 16.0226 | 17.0658 | 17.4175 | 18.5422 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906
10% | 4374.4653 | 6.2206 | 5.6399 | 5.9938 | 6.4454 | 6.8827 | 7.2721 | 7.8059 | 8.3892 | 8.9864 | 9.5782 | 10.1044 | 10.6777 | 10.898 | 11.6383 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 10% | 4374.4653 | 6.6616 | 6.0827 | 6.4565 | 6.9136 | 7.3399 | 7.7936 | 8.2704 | 8.9496 | 9.5421 | 10.101 | 10.6817 | 11.3772 | 11.6117 | 12.3615 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604
5% | 4374.7625 | 3.1103 | 2.82 | 2.9969 | 3.2227 | 3.4413 | 3.6361 | 3.903 | 4.1946 | 4.4932 | 4.7891 | 5.0522 | 5.3388 | 5.449 | 5.8191 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 5% | 4374.7625 | 3.3308 | 3.0413 | 3.2283 | 3.4568 | 3.6699 | 3.8968 | 4.1352 | 4.4748 | 4.7711 | 5.0505 | 5.3409 | 5.6886 | 5.8058 | 6.1807 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302
9.992e-14% | 4375.9513 | 6.2157e-14 | 5.6354e-14 | 5.9891e-14 | 6.4403e-14 | 6.8772e-14 | 7.2663e-14 | 7.7997e-14 | 8.3825e-14 | 8.9793e-14 | 9.5706e-14 | 1.0096e-13 | 1.0669e-13 | 1.0889e-13 | 1.1629e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 9.992e-14% | 4375.9513 | 6.6563e-14 | 6.0778e-14 | 6.4514e-14 | 6.9081e-14 | 7.334e-14 | 7.7873e-14 | 8.2638e-14 | 8.9425e-14 | 9.5345e-14 | 1.0093e-13 | 1.0673e-13 | 1.1368e-13 | 1.1602e-13 | 1.2352e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 100% | 0 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
99% | 0 | 79.9539 | 73.4917 | 77.3313 | 80.3764 | 83.9806 | 87.696 | 91.6392 | 96.1469 | 101.4481 | 106.4167 | 111.6368 | 120.5006 | 123.5326 | 129.219 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 99% | 0.37816 | 93.5071 | 87.1619 | 91.5053 | 95.145 | 98.3714 | 103.4399 | 108.0228 | 114.3709 | 120.9884 | 126.3994 | 131.5047 | 139.0694 | 144.5767 | 150.1244 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979
98% | 0.37816 | 79.1463 | 72.7493 | 76.5502 | 79.5646 | 83.1323 | 86.8102 | 90.7135 | 95.1757 | 100.4234 | 105.3418 | 110.5092 | 119.2834 | 122.2848 | 127.9138 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 98% | 1.1345 | 92.5626 | 86.2815 | 90.581 | 94.184 | 97.3777 | 102.395 | 106.9316 | 113.2156 | 119.7663 | 125.1227 | 130.1764 | 137.6647 | 143.1163 | 148.608 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222
97% | 0.75633 | 78.3387 | 72.007 | 75.7691 | 78.7527 | 82.284 | 85.9244 | 89.7879 | 94.2046 | 99.3986 | 104.2668 | 109.3815 | 118.0663 | 121.037 | 126.6085 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 97% | 2.269 | 91.6181 | 85.401 | 89.6567 | 93.2229 | 96.3841 | 101.3502 | 105.8405 | 112.0603 | 118.5442 | 123.8459 | 128.848 | 136.2599 | 141.6559 | 147.0916 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465
95% | 1.1345 | 76.7235 | 70.5223 | 74.2068 | 77.1289 | 80.5874 | 84.1528 | 87.9366 | 92.2622 | 97.3492 | 102.117 | 107.1262 | 115.6319 | 118.5414 | 123.9981 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 95% | 4.538 | 89.7291 | 83.6402 | 87.8081 | 91.3008 | 94.3968 | 99.2605 | 103.6582 | 109.7498 | 116.1 | 121.2924 | 126.1914 | 133.4504 | 138.7352 | 144.0588 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695
90% | 4.538 | 72.6854 | 66.8106 | 70.3012 | 73.0695 | 76.346 | 79.7237 | 83.3083 | 87.4063 | 92.2255 | 96.7424 | 101.488 | 109.546 | 112.3023 | 117.4718 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 90% | 7.9414 | 85.0065 | 79.2381 | 83.1866 | 86.4955 | 89.4285 | 94.0362 | 98.2025 | 103.9735 | 109.9894 | 114.9086 | 119.5497 | 126.4267 | 131.4333 | 136.4768 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163
85% | 7.9414 | 68.6473 | 63.0989 | 66.3956 | 69.0101 | 72.1045 | 75.2946 | 78.6801 | 82.5504 | 87.1019 | 91.3679 | 95.8498 | 103.4601 | 106.0633 | 110.9456 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 85% | 14.3702 | 80.2839 | 74.836 | 78.5652 | 81.6902 | 84.4603 | 88.812 | 92.7468 | 98.1972 | 103.8789 | 108.5247 | 112.9081 | 119.403 | 124.1315 | 128.8947 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376
80% | 11.7231 | 64.6092 | 59.3872 | 62.49 | 64.9507 | 67.8631 | 70.8655 | 74.0518 | 77.6945 | 81.9783 | 85.9933 | 90.2116 | 97.3742 | 99.8243 | 104.4194 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 80% | 19.6645 | 75.5613 | 70.4338 | 73.9437 | 76.8849 | 79.492 | 83.5878 | 87.2911 | 92.4209 | 97.7684 | 102.1409 | 106.2664 | 112.3793 | 116.8296 | 121.3127 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589
75% | 17.7737 | 60.5712 | 55.6755 | 58.5843 | 60.8912 | 63.6217 | 66.4364 | 69.4236 | 72.8386 | 76.8546 | 80.6187 | 84.5734 | 91.2883 | 93.5853 | 97.8932 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 75% | 25.7152 | 70.8387 | 66.0317 | 69.3222 | 72.0796 | 74.5238 | 78.3635 | 81.8354 | 86.6446 | 91.6579 | 95.7571 | 99.6248 | 105.3556 | 109.5278 | 113.7306 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803
70% | 35.1693 | 56.5331 | 51.9638 | 54.6787 | 56.8318 | 59.3802 | 62.0073 | 64.7954 | 67.9827 | 71.731 | 75.2441 | 78.9351 | 85.2025 | 87.3463 | 91.367 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 70% | 34.7911 | 66.1162 | 61.6296 | 64.7007 | 67.2743 | 69.5555 | 73.1393 | 76.3797 | 80.8683 | 85.5473 | 89.3733 | 92.9831 | 98.3319 | 102.2259 | 106.1486 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016
65% | 59.3718 | 52.495 | 48.2521 | 50.7731 | 52.7724 | 55.1388 | 57.5782 | 60.1671 | 63.1268 | 66.6073 | 69.8695 | 73.2969 | 79.1166 | 81.1072 | 84.8408 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 65% | 46.136 | 61.3936 | 57.2275 | 60.0792 | 62.469 | 64.5873 | 67.9151 | 70.924 | 75.092 | 79.4368 | 82.9895 | 86.3415 | 91.3082 | 94.9241 | 98.5666 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229
60% | 156.9382 | 48.4569 | 44.5404 | 46.8675 | 48.713 | 50.8973 | 53.1491 | 55.5389 | 58.2709 | 61.4837 | 64.495 | 67.6587 | 73.0307 | 74.8682 | 78.3146 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 60% | 76.7673 | 56.671 | 52.8254 | 55.4578 | 57.6637 | 59.619 | 62.6908 | 65.4683 | 69.3157 | 73.3263 | 76.6057 | 79.6998 | 84.2845 | 87.6222 | 90.9845 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442
55% | 363.794 | 44.4189 | 40.8287 | 42.9618 | 44.6536 | 46.6559 | 48.72 | 50.9106 | 53.415 | 56.3601 | 59.1204 | 62.0205 | 66.9448 | 68.6292 | 71.7884 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 55% | 106.2642 | 51.9484 | 48.4233 | 50.8363 | 52.8584 | 54.6508 | 57.4666 | 60.0126 | 63.5394 | 67.2158 | 70.2219 | 73.0582 | 77.2608 | 80.3204 | 83.4025 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655
50% | 771.4551 | 40.3808 | 37.117 | 39.0562 | 40.5942 | 42.4144 | 44.2909 | 46.2824 | 48.5591 | 51.2364 | 53.7458 | 56.3822 | 60.8589 | 62.3902 | 65.2621 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 50% | 178.4935 | 47.2258 | 44.0212 | 46.2148 | 48.0531 | 49.6825 | 52.2423 | 54.5569 | 57.7631 | 61.1052 | 63.8381 | 66.4165 | 70.2371 | 73.0185 | 75.8204 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868
45% | 1255.5054 | 36.3427 | 33.4053 | 35.1506 | 36.5347 | 38.173 | 39.8618 | 41.6542 | 43.7031 | 46.1128 | 48.3712 | 50.744 | 54.773 | 56.1512 | 58.7359 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 45% | 367.9538 | 42.5032 | 39.619 | 41.5933 | 43.2477 | 44.7143 | 47.0181 | 49.1013 | 51.9868 | 54.9947 | 57.4543 | 59.7749 | 63.2134 | 65.7167 | 68.2384 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
40% | 2059.1045 | 32.3046 | 29.6936 | 31.245 | 32.4753 | 33.9315 | 35.4327 | 37.0259 | 38.8472 | 40.9891 | 42.9966 | 45.1058 | 48.6871 | 49.9121 | 52.2097 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 40% | 741.202 | 37.7807 | 35.2169 | 36.9718 | 38.4424 | 39.746 | 41.7939 | 43.6456 | 46.2105 | 48.8842 | 51.0705 | 53.1332 | 56.1897 | 58.4148 | 60.6563 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295
35% | 3060.4836 | 28.2665 | 25.9819 | 27.3394 | 28.4159 | 29.6901 | 31.0036 | 32.3977 | 33.9913 | 35.8655 | 37.6221 | 39.4676 | 42.6012 | 43.6731 | 45.6835 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 35% | 1167.7713 | 33.0581 | 30.8148 | 32.3504 | 33.6371 | 34.7778 | 36.5696 | 38.1899 | 40.4341 | 42.7737 | 44.6867 | 46.4916 | 49.1659 | 51.113 | 53.0743 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508
30% | 3366.0403 | 24.2285 | 22.2702 | 23.4337 | 24.3565 | 25.4487 | 26.5746 | 27.7694 | 29.1354 | 30.7418 | 32.2475 | 33.8293 | 36.5153 | 37.4341 | 39.1573 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 30% | 2002.3799 | 28.3355 | 26.4127 | 27.7289 | 28.8318 | 29.8095 | 31.3454 | 32.7342 | 34.6578 | 36.6631 | 38.3029 | 39.8499 | 42.1422 | 43.8111 | 45.4923 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721
25% | 3686.3454 | 20.1904 | 18.5585 | 19.5281 | 20.2971 | 21.2072 | 22.1455 | 23.1412 | 24.2795 | 25.6182 | 26.8729 | 28.1911 | 30.4294 | 31.1951 | 32.6311 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 25% | 3173.5547 | 23.6129 | 22.0106 | 23.1074 | 24.0265 | 24.8413 | 26.1212 | 27.2785 | 28.8815 | 30.5526 | 31.919 | 33.2083 | 35.1185 | 36.5093 | 37.9102 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934
20% | 4028.5841 | 16.1523 | 14.8468 | 15.6225 | 16.2377 | 16.9658 | 17.7164 | 18.513 | 19.4236 | 20.4946 | 21.4983 | 22.5529 | 24.3436 | 24.9561 | 26.1049 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 20% | 3477.5988 | 18.8903 | 17.6085 | 18.4859 | 19.2212 | 19.873 | 20.8969 | 21.8228 | 23.1052 | 24.4421 | 25.5352 | 26.5666 | 28.0948 | 29.2074 | 30.3282 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147
15% | 4345.1076 | 12.1142 | 11.1351 | 11.7169 | 12.1782 | 12.7243 | 13.2873 | 13.8847 | 14.5677 | 15.3709 | 16.1237 | 16.9147 | 18.2577 | 18.7171 | 19.5786 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 15% | 3788.4498 | 14.1677 | 13.2063 | 13.8644 | 14.4159 | 14.9048 | 15.6727 | 16.3671 | 17.3289 | 18.3316 | 19.1514 | 19.925 | 21.0711 | 21.9056 | 22.7461 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361
10% | 4381.0332 | 8.0762 | 7.4234 | 7.8112 | 8.1188 | 8.4829 | 8.8582 | 9.2565 | 9.7118 | 10.2473 | 10.7492 | 11.2764 | 12.1718 | 12.478 | 13.0524 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 10% | 4317.5016 | 9.4452 | 8.8042 | 9.243 | 9.6106 | 9.9365 | 10.4485 | 10.9114 | 11.5526 | 12.221 | 12.7676 | 13.2833 | 14.0474 | 14.6037 | 15.1641 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574
5% | 4391.6218 | 4.0381 | 3.7117 | 3.9056 | 4.0594 | 4.2414 | 4.4291 | 4.6282 | 4.8559 | 5.1236 | 5.3746 | 5.6382 | 6.0859 | 6.239 | 6.5262 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 5% | 4391.6218 | 4.7226 | 4.4021 | 4.6215 | 4.8053 | 4.9683 | 5.2242 | 5.4557 | 5.7763 | 6.1105 | 6.3838 | 6.6417 | 7.0237 | 7.3019 | 7.582 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787
9.992e-14% | 4391.6218 | 8.0697e-14 | 7.4175e-14 | 7.805e-14 | 8.1123e-14 | 8.4761e-14 | 8.8511e-14 | 9.2491e-14 | 9.704e-14 | 1.0239e-13 | 1.0741e-13 | 1.1267e-13 | 1.2162e-13 | 1.2468e-13 | 1.3042e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 9.992e-14% | 4391.6218 | 9.4376e-14 | 8.7972e-14 | 9.2356e-14 | 9.6029e-14 | 9.9286e-14 | 1.044e-13 | 1.0903e-13 | 1.1543e-13 | 1.2211e-13 | 1.2757e-13 | 1.3273e-13 | 1.4036e-13 | 1.4592e-13 | 1.5152e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 100% | 0 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
99% | 0.5944 | 61.5843 | 55.8354 | 59.3391 | 63.8099 | 68.1384 | 71.9939 | 77.2785 | 83.0527 | 88.9657 | 94.8245 | 100.034 | 105.7089 | 107.8904 | 115.2192 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 99% | 0.5944 | 65.9501 | 60.2186 | 63.9197 | 68.4451 | 72.6648 | 77.1562 | 81.8774 | 88.6013 | 94.4669 | 99.9996 | 105.7489 | 112.6341 | 114.9554 | 122.3786 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981
98% | 0.8916 | 60.9623 | 55.2714 | 58.7397 | 63.1653 | 67.4501 | 71.2667 | 76.4979 | 82.2138 | 88.0671 | 93.8667 | 99.0236 | 104.6411 | 106.8006 | 114.0553 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 98% | 0.8916 | 65.2839 | 59.6103 | 63.274 | 67.7537 | 71.9308 | 76.3769 | 81.0504 | 87.7063 | 93.5127 | 98.9895 | 104.6807 | 111.4964 | 113.7942 | 121.1425 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992
97% | 1.486 | 60.3402 | 54.7074 | 58.1403 | 62.5208 | 66.7619 | 70.5394 | 75.7173 | 81.3749 | 87.1685 | 92.9089 | 98.0131 | 103.5733 | 105.7108 | 112.8915 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 97% | 1.486 | 64.6177 | 59.002 | 62.6284 | 67.0623 | 71.1968 | 75.5975 | 80.2233 | 86.8113 | 92.5584 | 97.9794 | 103.6125 | 110.3587 | 112.6331 | 119.9063 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686
95% | 2.3776 | 59.0961 | 53.5795 | 56.9416 | 61.2317 | 65.3853 | 69.085 | 74.1561 | 79.6971 | 85.3712 | 90.9932 | 95.9922 | 101.4378 | 103.5312 | 110.5638 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 95% | 2.3776 | 63.2854 | 57.7855 | 61.3371 | 65.6796 | 69.7288 | 74.0388 | 78.5692 | 85.0214 | 90.65 | 95.9592 | 101.4762 | 108.0832 | 110.3107 | 117.434 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739
90% | 3.2692 | 55.9857 | 50.7595 | 53.9446 | 58.009 | 61.944 | 65.449 | 70.2532 | 75.5025 | 80.878 | 86.2041 | 90.94 | 96.099 | 98.0822 | 104.7447 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 90% | 3.2692 | 59.9546 | 54.7442 | 58.1088 | 62.2228 | 66.0589 | 70.142 | 74.434 | 80.5466 | 85.879 | 90.9087 | 96.1353 | 102.3947 | 104.5049 | 111.2533 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437
85% | 13.9683 | 52.8754 | 47.9395 | 50.9477 | 54.7863 | 58.5027 | 61.8129 | 66.3502 | 71.3079 | 76.3847 | 81.415 | 85.8878 | 90.7601 | 92.6332 | 98.9255 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 85% | 13.9683 | 56.6238 | 51.7028 | 54.8805 | 58.766 | 62.3889 | 66.2453 | 70.2988 | 76.0718 | 81.1079 | 85.8582 | 90.7945 | 96.7061 | 98.6991 | 105.0725 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135
80% | 41.3106 | 49.7651 | 45.1195 | 47.9508 | 51.5635 | 55.0613 | 58.1769 | 62.4473 | 67.1133 | 71.8915 | 76.6259 | 80.8356 | 85.4213 | 87.1842 | 93.1064 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 80% | 41.3106 | 53.293 | 48.6615 | 51.6523 | 55.3092 | 58.719 | 62.3485 | 66.1636 | 71.597 | 76.3369 | 80.8077 | 85.4536 | 91.0175 | 92.8932 | 98.8918 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833
75% | 126.3094 | 46.6548 | 42.2996 | 44.9539 | 48.3408 | 51.62 | 54.5408 | 58.5443 | 62.9187 | 67.3983 | 71.8368 | 75.7833 | 80.0825 | 81.7352 | 87.2872 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 75% | 126.3094 | 49.9622 | 45.6201 | 48.424 | 51.8523 | 55.0491 | 58.4517 | 62.0284 | 67.1222 | 71.5658 | 75.7573 | 80.1128 | 85.3289 | 87.0874 | 92.7111 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531
70% | 323.9464 | 43.5445 | 39.4796 | 41.9569 | 45.1181 | 48.1787 | 50.9048 | 54.6414 | 58.7242 | 62.9051 | 67.0477 | 70.7311 | 74.7436 | 76.2861 | 81.4681 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 70% | 323.9464 | 46.6314 | 42.5788 | 45.1957 | 48.3955 | 51.3791 | 54.5549 | 57.8931 | 62.6474 | 66.7948 | 70.7068 | 74.7719 | 79.6403 | 81.2816 | 86.5303 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229
65% | 549.5201 | 40.4341 | 36.6596 | 38.96 | 41.8954 | 44.7373 | 47.2687 | 50.7384 | 54.5296 | 58.4119 | 62.2585 | 65.6789 | 69.4048 | 70.8371 | 75.6489 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 65% | 549.5201 | 43.3005 | 39.5374 | 41.9675 | 44.9387 | 47.7092 | 50.6581 | 53.7579 | 58.1726 | 62.0237 | 65.6563 | 69.4311 | 73.9517 | 75.4758 | 80.3496 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927
60% | 799.4641 | 37.3238 | 33.8397 | 35.9631 | 38.6726 | 41.296 | 43.6326 | 46.8354 | 50.335 | 53.9186 | 57.4694 | 60.6267 | 64.066 | 65.3881 | 69.8298 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 60% | 799.4641 | 39.9697 | 36.4961 | 38.7392 | 41.4819 | 44.0392 | 46.7614 | 49.6227 | 53.6977 | 57.2526 | 60.6058 | 64.0902 | 68.2631 | 69.6699 | 74.1688 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625
55% | 1116.2777 | 34.2135 | 31.0197 | 32.9662 | 35.4499 | 37.8547 | 39.9966 | 42.9325 | 46.1404 | 49.4254 | 52.6803 | 55.5745 | 58.7271 | 59.9391 | 64.0106 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 55% | 1116.2777 | 36.6389 | 33.4548 | 35.5109 | 38.025 | 40.3693 | 42.8646 | 45.4875 | 49.2229 | 52.4816 | 55.5553 | 58.7494 | 62.5745 | 63.8641 | 67.9881 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323
50% | 1494.9086 | 31.1032 | 28.1997 | 29.9692 | 32.2272 | 34.4133 | 36.3605 | 39.0295 | 41.9458 | 44.9322 | 47.8912 | 50.5222 | 53.3883 | 54.4901 | 58.1915 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 50% | 1494.9086 | 33.3081 | 30.4134 | 32.2827 | 34.5682 | 36.6994 | 38.9678 | 41.3522 | 44.7481 | 47.7105 | 50.5048 | 53.4085 | 56.8859 | 58.0583 | 61.8074 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021
45% | 2004.0097 | 27.9929 | 25.3797 | 26.9723 | 29.0045 | 30.972 | 32.7245 | 35.1266 | 37.7512 | 40.439 | 43.1021 | 45.47 | 48.0495 | 49.0411 | 52.3723 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 45% | 2004.0097 | 29.9773 | 27.3721 | 29.0544 | 31.1114 | 33.0294 | 35.071 | 37.217 | 40.2733 | 42.9395 | 45.4544 | 48.0677 | 51.1973 | 52.2524 | 55.6266 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719
40% | 2877.179 | 24.8826 | 22.5598 | 23.9754 | 25.7818 | 27.5307 | 29.0884 | 31.2236 | 33.5567 | 35.9458 | 38.3129 | 40.4178 | 42.7106 | 43.5921 | 46.5532 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 40% | 2877.179 | 26.6465 | 24.3307 | 25.8261 | 27.6546 | 29.3595 | 31.1742 | 33.0818 | 35.7985 | 38.1684 | 40.4039 | 42.7268 | 45.5087 | 46.4466 | 49.4459 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417
35% | 3454.933 | 21.7722 | 19.7398 | 20.9785 | 22.559 | 24.0893 | 25.4524 | 27.3207 | 29.3621 | 31.4525 | 33.5238 | 35.3656 | 37.3718 | 38.1431 | 40.734 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 35% | 3454.933 | 23.3157 | 21.2894 | 22.5979 | 24.1978 | 25.6896 | 27.2775 | 28.9466 | 31.3237 | 33.3974 | 35.3534 | 37.386 | 39.8201 | 40.6408 | 43.2652 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114
30% | 3663.5664 | 18.6619 | 16.9198 | 17.9815 | 19.3363 | 20.648 | 21.8163 | 23.4177 | 25.1675 | 26.9593 | 28.7347 | 30.3133 | 32.033 | 32.6941 | 34.9149 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 30% | 3663.5664 | 19.9849 | 18.2481 | 19.3696 | 20.7409 | 22.0196 | 23.3807 | 24.8113 | 26.8489 | 28.6263 | 30.3029 | 32.0451 | 34.1316 | 34.835 | 37.0844 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812
25% | 3862.6894 | 15.5516 | 14.0999 | 14.9846 | 16.1136 | 17.2067 | 18.1803 | 19.5148 | 20.9729 | 22.4661 | 23.9456 | 25.2611 | 26.6942 | 27.2451 | 29.0957 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 25% | 3862.6894 | 16.6541 | 15.2067 | 16.1413 | 17.2841 | 18.3497 | 19.4839 | 20.6761 | 22.3741 | 23.8553 | 25.2524 | 26.7043 | 28.443 | 29.0291 | 30.9037 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651
20% | 4122.7381 | 12.4413 | 11.2799 | 11.9877 | 12.8909 | 13.7653 | 14.5442 | 15.6118 | 16.7783 | 17.9729 | 19.1565 | 20.2089 | 21.3553 | 21.796 | 23.2766 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 20% | 4122.7381 | 13.3232 | 12.1654 | 12.9131 | 13.8273 | 14.6797 | 15.5871 | 16.5409 | 17.8992 | 19.0842 | 20.2019 | 21.3634 | 22.7544 | 23.2233 | 24.7229 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208
15% | 4372.3849 | 9.331 | 8.4599 | 8.9908 | 9.6682 | 10.324 | 10.9082 | 11.7089 | 12.5837 | 13.4797 | 14.3674 | 15.1567 | 16.0165 | 16.347 | 17.4574 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 15% | 4372.3849 | 9.9924 | 9.124 | 9.6848 | 10.3705 | 11.0098 | 11.6903 | 12.4057 | 13.4244 | 14.3132 | 15.1515 | 16.0226 | 17.0658 | 17.4175 | 18.5422 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906
10% | 4374.4653 | 6.2206 | 5.6399 | 5.9938 | 6.4454 | 6.8827 | 7.2721 | 7.8059 | 8.3892 | 8.9864 | 9.5782 | 10.1044 | 10.6777 | 10.898 | 11.6383 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 10% | 4374.4653 | 6.6616 | 6.0827 | 6.4565 | 6.9136 | 7.3399 | 7.7936 | 8.2704 | 8.9496 | 9.5421 | 10.101 | 10.6817 | 11.3772 | 11.6117 | 12.3615 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604
5% | 4374.7625 | 3.1103 | 2.82 | 2.9969 | 3.2227 | 3.4413 | 3.6361 | 3.903 | 4.1946 | 4.4932 | 4.7891 | 5.0522 | 5.3388 | 5.449 | 5.8191 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 5% | 4374.7625 | 3.3308 | 3.0413 | 3.2283 | 3.4568 | 3.6699 | 3.8968 | 4.1352 | 4.4748 | 4.7711 | 5.0505 | 5.3409 | 5.6886 | 5.8058 | 6.1807 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302
9.992e-14% | 4375.9513 | 6.2157e-14 | 5.6354e-14 | 5.9891e-14 | 6.4403e-14 | 6.8772e-14 | 7.2663e-14 | 7.7997e-14 | 8.3825e-14 | 8.9793e-14 | 9.5706e-14 | 1.0096e-13 | 1.0669e-13 | 1.0889e-13 | 1.1629e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 9.992e-14% | 4375.9513 | 6.6563e-14 | 6.0778e-14 | 6.4514e-14 | 6.9081e-14 | 7.334e-14 | 7.7873e-14 | 8.2638e-14 | 8.9425e-14 | 9.5345e-14 | 1.0093e-13 | 1.0673e-13 | 1.1368e-13 | 1.1602e-13 | 1.2352e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 100% | 0 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
99% | 0 | 79.9539 | 73.4917 | 77.3313 | 80.3764 | 83.9806 | 87.696 | 91.6392 | 96.1469 | 101.4481 | 106.4167 | 111.6368 | 120.5006 | 123.5326 | 129.219 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 99% | 0.37816 | 93.5071 | 87.1619 | 91.5053 | 95.145 | 98.3714 | 103.4399 | 108.0228 | 114.3709 | 120.9884 | 126.3994 | 131.5047 | 139.0694 | 144.5767 | 150.1244 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979
98% | 0.37816 | 79.1463 | 72.7493 | 76.5502 | 79.5646 | 83.1323 | 86.8102 | 90.7135 | 95.1757 | 100.4234 | 105.3418 | 110.5092 | 119.2834 | 122.2848 | 127.9138 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 98% | 1.1345 | 92.5626 | 86.2815 | 90.581 | 94.184 | 97.3777 | 102.395 | 106.9316 | 113.2156 | 119.7663 | 125.1227 | 130.1764 | 137.6647 | 143.1163 | 148.608 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222
97% | 0.75633 | 78.3387 | 72.007 | 75.7691 | 78.7527 | 82.284 | 85.9244 | 89.7879 | 94.2046 | 99.3986 | 104.2668 | 109.3815 | 118.0663 | 121.037 | 126.6085 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 97% | 2.269 | 91.6181 | 85.401 | 89.6567 | 93.2229 | 96.3841 | 101.3502 | 105.8405 | 112.0603 | 118.5442 | 123.8459 | 128.848 | 136.2599 | 141.6559 | 147.0916 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465
95% | 1.1345 | 76.7235 | 70.5223 | 74.2068 | 77.1289 | 80.5874 | 84.1528 | 87.9366 | 92.2622 | 97.3492 | 102.117 | 107.1262 | 115.6319 | 118.5414 | 123.9981 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 95% | 4.538 | 89.7291 | 83.6402 | 87.8081 | 91.3008 | 94.3968 | 99.2605 | 103.6582 | 109.7498 | 116.1 | 121.2924 | 126.1914 | 133.4504 | 138.7352 | 144.0588 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695
90% | 4.538 | 72.6854 | 66.8106 | 70.3012 | 73.0695 | 76.346 | 79.7237 | 83.3083 | 87.4063 | 92.2255 | 96.7424 | 101.488 | 109.546 | 112.3023 | 117.4718 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 90% | 7.9414 | 85.0065 | 79.2381 | 83.1866 | 86.4955 | 89.4285 | 94.0362 | 98.2025 | 103.9735 | 109.9894 | 114.9086 | 119.5497 | 126.4267 | 131.4333 | 136.4768 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163
85% | 7.9414 | 68.6473 | 63.0989 | 66.3956 | 69.0101 | 72.1045 | 75.2946 | 78.6801 | 82.5504 | 87.1019 | 91.3679 | 95.8498 | 103.4601 | 106.0633 | 110.9456 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 85% | 14.3702 | 80.2839 | 74.836 | 78.5652 | 81.6902 | 84.4603 | 88.812 | 92.7468 | 98.1972 | 103.8789 | 108.5247 | 112.9081 | 119.403 | 124.1315 | 128.8947 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376
80% | 11.7231 | 64.6092 | 59.3872 | 62.49 | 64.9507 | 67.8631 | 70.8655 | 74.0518 | 77.6945 | 81.9783 | 85.9933 | 90.2116 | 97.3742 | 99.8243 | 104.4194 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 80% | 19.6645 | 75.5613 | 70.4338 | 73.9437 | 76.8849 | 79.492 | 83.5878 | 87.2911 | 92.4209 | 97.7684 | 102.1409 | 106.2664 | 112.3793 | 116.8296 | 121.3127 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589
75% | 17.7737 | 60.5712 | 55.6755 | 58.5843 | 60.8912 | 63.6217 | 66.4364 | 69.4236 | 72.8386 | 76.8546 | 80.6187 | 84.5734 | 91.2883 | 93.5853 | 97.8932 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 75% | 25.7152 | 70.8387 | 66.0317 | 69.3222 | 72.0796 | 74.5238 | 78.3635 | 81.8354 | 86.6446 | 91.6579 | 95.7571 | 99.6248 | 105.3556 | 109.5278 | 113.7306 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803
70% | 35.1693 | 56.5331 | 51.9638 | 54.6787 | 56.8318 | 59.3802 | 62.0073 | 64.7954 | 67.9827 | 71.731 | 75.2441 | 78.9351 | 85.2025 | 87.3463 | 91.367 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 70% | 34.7911 | 66.1162 | 61.6296 | 64.7007 | 67.2743 | 69.5555 | 73.1393 | 76.3797 | 80.8683 | 85.5473 | 89.3733 | 92.9831 | 98.3319 | 102.2259 | 106.1486 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016
65% | 59.3718 | 52.495 | 48.2521 | 50.7731 | 52.7724 | 55.1388 | 57.5782 | 60.1671 | 63.1268 | 66.6073 | 69.8695 | 73.2969 | 79.1166 | 81.1072 | 84.8408 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 65% | 46.136 | 61.3936 | 57.2275 | 60.0792 | 62.469 | 64.5873 | 67.9151 | 70.924 | 75.092 | 79.4368 | 82.9895 | 86.3415 | 91.3082 | 94.9241 | 98.5666 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229
60% | 156.9382 | 48.4569 | 44.5404 | 46.8675 | 48.713 | 50.8973 | 53.1491 | 55.5389 | 58.2709 | 61.4837 | 64.495 | 67.6587 | 73.0307 | 74.8682 | 78.3146 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 60% | 76.7673 | 56.671 | 52.8254 | 55.4578 | 57.6637 | 59.619 | 62.6908 | 65.4683 | 69.3157 | 73.3263 | 76.6057 | 79.6998 | 84.2845 | 87.6222 | 90.9845 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442
55% | 363.794 | 44.4189 | 40.8287 | 42.9618 | 44.6536 | 46.6559 | 48.72 | 50.9106 | 53.415 | 56.3601 | 59.1204 | 62.0205 | 66.9448 | 68.6292 | 71.7884 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 55% | 106.2642 | 51.9484 | 48.4233 | 50.8363 | 52.8584 | 54.6508 | 57.4666 | 60.0126 | 63.5394 | 67.2158 | 70.2219 | 73.0582 | 77.2608 | 80.3204 | 83.4025 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655
50% | 771.4551 | 40.3808 | 37.117 | 39.0562 | 40.5942 | 42.4144 | 44.2909 | 46.2824 | 48.5591 | 51.2364 | 53.7458 | 56.3822 | 60.8589 | 62.3902 | 65.2621 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 50% | 178.4935 | 47.2258 | 44.0212 | 46.2148 | 48.0531 | 49.6825 | 52.2423 | 54.5569 | 57.7631 | 61.1052 | 63.8381 | 66.4165 | 70.2371 | 73.0185 | 75.8204 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868
45% | 1255.5054 | 36.3427 | 33.4053 | 35.1506 | 36.5347 | 38.173 | 39.8618 | 41.6542 | 43.7031 | 46.1128 | 48.3712 | 50.744 | 54.773 | 56.1512 | 58.7359 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 45% | 367.9538 | 42.5032 | 39.619 | 41.5933 | 43.2477 | 44.7143 | 47.0181 | 49.1013 | 51.9868 | 54.9947 | 57.4543 | 59.7749 | 63.2134 | 65.7167 | 68.2384 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
40% | 2059.1045 | 32.3046 | 29.6936 | 31.245 | 32.4753 | 33.9315 | 35.4327 | 37.0259 | 38.8472 | 40.9891 | 42.9966 | 45.1058 | 48.6871 | 49.9121 | 52.2097 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 40% | 741.202 | 37.7807 | 35.2169 | 36.9718 | 38.4424 | 39.746 | 41.7939 | 43.6456 | 46.2105 | 48.8842 | 51.0705 | 53.1332 | 56.1897 | 58.4148 | 60.6563 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295
35% | 3060.4836 | 28.2665 | 25.9819 | 27.3394 | 28.4159 | 29.6901 | 31.0036 | 32.3977 | 33.9913 | 35.8655 | 37.6221 | 39.4676 | 42.6012 | 43.6731 | 45.6835 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 35% | 1167.7713 | 33.0581 | 30.8148 | 32.3504 | 33.6371 | 34.7778 | 36.5696 | 38.1899 | 40.4341 | 42.7737 | 44.6867 | 46.4916 | 49.1659 | 51.113 | 53.0743 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508
30% | 3366.0403 | 24.2285 | 22.2702 | 23.4337 | 24.3565 | 25.4487 | 26.5746 | 27.7694 | 29.1354 | 30.7418 | 32.2475 | 33.8293 | 36.5153 | 37.4341 | 39.1573 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 30% | 2002.3799 | 28.3355 | 26.4127 | 27.7289 | 28.8318 | 29.8095 | 31.3454 | 32.7342 | 34.6578 | 36.6631 | 38.3029 | 39.8499 | 42.1422 | 43.8111 | 45.4923 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721
25% | 3686.3454 | 20.1904 | 18.5585 | 19.5281 | 20.2971 | 21.2072 | 22.1455 | 23.1412 | 24.2795 | 25.6182 | 26.8729 | 28.1911 | 30.4294 | 31.1951 | 32.6311 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 25% | 3173.5547 | 23.6129 | 22.0106 | 23.1074 | 24.0265 | 24.8413 | 26.1212 | 27.2785 | 28.8815 | 30.5526 | 31.919 | 33.2083 | 35.1185 | 36.5093 | 37.9102 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934
20% | 4028.5841 | 16.1523 | 14.8468 | 15.6225 | 16.2377 | 16.9658 | 17.7164 | 18.513 | 19.4236 | 20.4946 | 21.4983 | 22.5529 | 24.3436 | 24.9561 | 26.1049 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 20% | 3477.5988 | 18.8903 | 17.6085 | 18.4859 | 19.2212 | 19.873 | 20.8969 | 21.8228 | 23.1052 | 24.4421 | 25.5352 | 26.5666 | 28.0948 | 29.2074 | 30.3282 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147
15% | 4345.1076 | 12.1142 | 11.1351 | 11.7169 | 12.1782 | 12.7243 | 13.2873 | 13.8847 | 14.5677 | 15.3709 | 16.1237 | 16.9147 | 18.2577 | 18.7171 | 19.5786 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 15% | 3788.4498 | 14.1677 | 13.2063 | 13.8644 | 14.4159 | 14.9048 | 15.6727 | 16.3671 | 17.3289 | 18.3316 | 19.1514 | 19.925 | 21.0711 | 21.9056 | 22.7461 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361
10% | 4381.0332 | 8.0762 | 7.4234 | 7.8112 | 8.1188 | 8.4829 | 8.8582 | 9.2565 | 9.7118 | 10.2473 | 10.7492 | 11.2764 | 12.1718 | 12.478 | 13.0524 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 10% | 4317.5016 | 9.4452 | 8.8042 | 9.243 | 9.6106 | 9.9365 | 10.4485 | 10.9114 | 11.5526 | 12.221 | 12.7676 | 13.2833 | 14.0474 | 14.6037 | 15.1641 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574
5% | 4391.6218 | 4.0381 | 3.7117 | 3.9056 | 4.0594 | 4.2414 | 4.4291 | 4.6282 | 4.8559 | 5.1236 | 5.3746 | 5.6382 | 6.0859 | 6.239 | 6.5262 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 5% | 4391.6218 | 4.7226 | 4.4021 | 4.6215 | 4.8053 | 4.9683 | 5.2242 | 5.4557 | 5.7763 | 6.1105 | 6.3838 | 6.6417 | 7.0237 | 7.3019 | 7.582 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787
9.992e-14% | 4391.6218 | 8.0697e-14 | 7.4175e-14 | 7.805e-14 | 8.1123e-14 | 8.4761e-14 | 8.8511e-14 | 9.2491e-14 | 9.704e-14 | 1.0239e-13 | 1.0741e-13 | 1.1267e-13 | 1.2162e-13 | 1.2468e-13 | 1.3042e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 9.992e-14% | 4391.6218 | 9.4376e-14 | 8.7972e-14 | 9.2356e-14 | 9.6029e-14 | 9.9286e-14 | 1.044e-13 | 1.0903e-13 | 1.1543e-13 | 1.2211e-13 | 1.2757e-13 | 1.3273e-13 | 1.4036e-13 | 1.4592e-13 | 1.5152e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 100% | 0 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
99% | 0.5944 | 61.5843 | 55.8354 | 59.3391 | 63.8099 | 68.1384 | 71.9939 | 77.2785 | 83.0527 | 88.9657 | 94.8245 | 100.034 | 105.7089 | 107.8904 | 115.2192 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 99% | 0.5944 | 65.9501 | 60.2186 | 63.9197 | 68.4451 | 72.6648 | 77.1562 | 81.8774 | 88.6013 | 94.4669 | 99.9996 | 105.7489 | 112.6341 | 114.9554 | 122.3786 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981
98% | 0.8916 | 60.9623 | 55.2714 | 58.7397 | 63.1653 | 67.4501 | 71.2667 | 76.4979 | 82.2138 | 88.0671 | 93.8667 | 99.0236 | 104.6411 | 106.8006 | 114.0553 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 98% | 0.8916 | 65.2839 | 59.6103 | 63.274 | 67.7537 | 71.9308 | 76.3769 | 81.0504 | 87.7063 | 93.5127 | 98.9895 | 104.6807 | 111.4964 | 113.7942 | 121.1425 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992
97% | 1.486 | 60.3402 | 54.7074 | 58.1403 | 62.5208 | 66.7619 | 70.5394 | 75.7173 | 81.3749 | 87.1685 | 92.9089 | 98.0131 | 103.5733 | 105.7108 | 112.8915 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 97% | 1.486 | 64.6177 | 59.002 | 62.6284 | 67.0623 | 71.1968 | 75.5975 | 80.2233 | 86.8113 | 92.5584 | 97.9794 | 103.6125 | 110.3587 | 112.6331 | 119.9063 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686
95% | 2.3776 | 59.0961 | 53.5795 | 56.9416 | 61.2317 | 65.3853 | 69.085 | 74.1561 | 79.6971 | 85.3712 | 90.9932 | 95.9922 | 101.4378 | 103.5312 | 110.5638 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 95% | 2.3776 | 63.2854 | 57.7855 | 61.3371 | 65.6796 | 69.7288 | 74.0388 | 78.5692 | 85.0214 | 90.65 | 95.9592 | 101.4762 | 108.0832 | 110.3107 | 117.434 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739
90% | 3.2692 | 55.9857 | 50.7595 | 53.9446 | 58.009 | 61.944 | 65.449 | 70.2532 | 75.5025 | 80.878 | 86.2041 | 90.94 | 96.099 | 98.0822 | 104.7447 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 90% | 3.2692 | 59.9546 | 54.7442 | 58.1088 | 62.2228 | 66.0589 | 70.142 | 74.434 | 80.5466 | 85.879 | 90.9087 | 96.1353 | 102.3947 | 104.5049 | 111.2533 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437
85% | 13.9683 | 52.8754 | 47.9395 | 50.9477 | 54.7863 | 58.5027 | 61.8129 | 66.3502 | 71.3079 | 76.3847 | 81.415 | 85.8878 | 90.7601 | 92.6332 | 98.9255 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 85% | 13.9683 | 56.6238 | 51.7028 | 54.8805 | 58.766 | 62.3889 | 66.2453 | 70.2988 | 76.0718 | 81.1079 | 85.8582 | 90.7945 | 96.7061 | 98.6991 | 105.0725 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135
80% | 41.3106 | 49.7651 | 45.1195 | 47.9508 | 51.5635 | 55.0613 | 58.1769 | 62.4473 | 67.1133 | 71.8915 | 76.6259 | 80.8356 | 85.4213 | 87.1842 | 93.1064 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 80% | 41.3106 | 53.293 | 48.6615 | 51.6523 | 55.3092 | 58.719 | 62.3485 | 66.1636 | 71.597 | 76.3369 | 80.8077 | 85.4536 | 91.0175 | 92.8932 | 98.8918 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833
75% | 126.3094 | 46.6548 | 42.2996 | 44.9539 | 48.3408 | 51.62 | 54.5408 | 58.5443 | 62.9187 | 67.3983 | 71.8368 | 75.7833 | 80.0825 | 81.7352 | 87.2872 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 75% | 126.3094 | 49.9622 | 45.6201 | 48.424 | 51.8523 | 55.0491 | 58.4517 | 62.0284 | 67.1222 | 71.5658 | 75.7573 | 80.1128 | 85.3289 | 87.0874 | 92.7111 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531
70% | 323.9464 | 43.5445 | 39.4796 | 41.9569 | 45.1181 | 48.1787 | 50.9048 | 54.6414 | 58.7242 | 62.9051 | 67.0477 | 70.7311 | 74.7436 | 76.2861 | 81.4681 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 70% | 323.9464 | 46.6314 | 42.5788 | 45.1957 | 48.3955 | 51.3791 | 54.5549 | 57.8931 | 62.6474 | 66.7948 | 70.7068 | 74.7719 | 79.6403 | 81.2816 | 86.5303 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229
65% | 549.5201 | 40.4341 | 36.6596 | 38.96 | 41.8954 | 44.7373 | 47.2687 | 50.7384 | 54.5296 | 58.4119 | 62.2585 | 65.6789 | 69.4048 | 70.8371 | 75.6489 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 65% | 549.5201 | 43.3005 | 39.5374 | 41.9675 | 44.9387 | 47.7092 | 50.6581 | 53.7579 | 58.1726 | 62.0237 | 65.6563 | 69.4311 | 73.9517 | 75.4758 | 80.3496 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927
60% | 799.4641 | 37.3238 | 33.8397 | 35.9631 | 38.6726 | 41.296 | 43.6326 | 46.8354 | 50.335 | 53.9186 | 57.4694 | 60.6267 | 64.066 | 65.3881 | 69.8298 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 60% | 799.4641 | 39.9697 | 36.4961 | 38.7392 | 41.4819 | 44.0392 | 46.7614 | 49.6227 | 53.6977 | 57.2526 | 60.6058 | 64.0902 | 68.2631 | 69.6699 | 74.1688 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625
55% | 1116.2777 | 34.2135 | 31.0197 | 32.9662 | 35.4499 | 37.8547 | 39.9966 | 42.9325 | 46.1404 | 49.4254 | 52.6803 | 55.5745 | 58.7271 | 59.9391 | 64.0106 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 55% | 1116.2777 | 36.6389 | 33.4548 | 35.5109 | 38.025 | 40.3693 | 42.8646 | 45.4875 | 49.2229 | 52.4816 | 55.5553 | 58.7494 | 62.5745 | 63.8641 | 67.9881 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323
50% | 1494.9086 | 31.1032 | 28.1997 | 29.9692 | 32.2272 | 34.4133 | 36.3605 | 39.0295 | 41.9458 | 44.9322 | 47.8912 | 50.5222 | 53.3883 | 54.4901 | 58.1915 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 50% | 1494.9086 | 33.3081 | 30.4134 | 32.2827 | 34.5682 | 36.6994 | 38.9678 | 41.3522 | 44.7481 | 47.7105 | 50.5048 | 53.4085 | 56.8859 | 58.0583 | 61.8074 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021
45% | 2004.0097 | 27.9929 | 25.3797 | 26.9723 | 29.0045 | 30.972 | 32.7245 | 35.1266 | 37.7512 | 40.439 | 43.1021 | 45.47 | 48.0495 | 49.0411 | 52.3723 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 45% | 2004.0097 | 29.9773 | 27.3721 | 29.0544 | 31.1114 | 33.0294 | 35.071 | 37.217 | 40.2733 | 42.9395 | 45.4544 | 48.0677 | 51.1973 | 52.2524 | 55.6266 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719
40% | 2877.179 | 24.8826 | 22.5598 | 23.9754 | 25.7818 | 27.5307 | 29.0884 | 31.2236 | 33.5567 | 35.9458 | 38.3129 | 40.4178 | 42.7106 | 43.5921 | 46.5532 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 40% | 2877.179 | 26.6465 | 24.3307 | 25.8261 | 27.6546 | 29.3595 | 31.1742 | 33.0818 | 35.7985 | 38.1684 | 40.4039 | 42.7268 | 45.5087 | 46.4466 | 49.4459 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417
35% | 3454.933 | 21.7722 | 19.7398 | 20.9785 | 22.559 | 24.0893 | 25.4524 | 27.3207 | 29.3621 | 31.4525 | 33.5238 | 35.3656 | 37.3718 | 38.1431 | 40.734 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 35% | 3454.933 | 23.3157 | 21.2894 | 22.5979 | 24.1978 | 25.6896 | 27.2775 | 28.9466 | 31.3237 | 33.3974 | 35.3534 | 37.386 | 39.8201 | 40.6408 | 43.2652 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114
30% | 3663.5664 | 18.6619 | 16.9198 | 17.9815 | 19.3363 | 20.648 | 21.8163 | 23.4177 | 25.1675 | 26.9593 | 28.7347 | 30.3133 | 32.033 | 32.6941 | 34.9149 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 30% | 3663.5664 | 19.9849 | 18.2481 | 19.3696 | 20.7409 | 22.0196 | 23.3807 | 24.8113 | 26.8489 | 28.6263 | 30.3029 | 32.0451 | 34.1316 | 34.835 | 37.0844 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812
25% | 3862.6894 | 15.5516 | 14.0999 | 14.9846 | 16.1136 | 17.2067 | 18.1803 | 19.5148 | 20.9729 | 22.4661 | 23.9456 | 25.2611 | 26.6942 | 27.2451 | 29.0957 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 25% | 3862.6894 | 16.6541 | 15.2067 | 16.1413 | 17.2841 | 18.3497 | 19.4839 | 20.6761 | 22.3741 | 23.8553 | 25.2524 | 26.7043 | 28.443 | 29.0291 | 30.9037 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651
20% | 4122.7381 | 12.4413 | 11.2799 | 11.9877 | 12.8909 | 13.7653 | 14.5442 | 15.6118 | 16.7783 | 17.9729 | 19.1565 | 20.2089 | 21.3553 | 21.796 | 23.2766 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 20% | 4122.7381 | 13.3232 | 12.1654 | 12.9131 | 13.8273 | 14.6797 | 15.5871 | 16.5409 | 17.8992 | 19.0842 | 20.2019 | 21.3634 | 22.7544 | 23.2233 | 24.7229 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208
15% | 4372.3849 | 9.331 | 8.4599 | 8.9908 | 9.6682 | 10.324 | 10.9082 | 11.7089 | 12.5837 | 13.4797 | 14.3674 | 15.1567 | 16.0165 | 16.347 | 17.4574 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 15% | 4372.3849 | 9.9924 | 9.124 | 9.6848 | 10.3705 | 11.0098 | 11.6903 | 12.4057 | 13.4244 | 14.3132 | 15.1515 | 16.0226 | 17.0658 | 17.4175 | 18.5422 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906
10% | 4374.4653 | 6.2206 | 5.6399 | 5.9938 | 6.4454 | 6.8827 | 7.2721 | 7.8059 | 8.3892 | 8.9864 | 9.5782 | 10.1044 | 10.6777 | 10.898 | 11.6383 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 10% | 4374.4653 | 6.6616 | 6.0827 | 6.4565 | 6.9136 | 7.3399 | 7.7936 | 8.2704 | 8.9496 | 9.5421 | 10.101 | 10.6817 | 11.3772 | 11.6117 | 12.3615 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604
5% | 4374.7625 | 3.1103 | 2.82 | 2.9969 | 3.2227 | 3.4413 | 3.6361 | 3.903 | 4.1946 | 4.4932 | 4.7891 | 5.0522 | 5.3388 | 5.449 | 5.8191 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 5% | 4374.7625 | 3.3308 | 3.0413 | 3.2283 | 3.4568 | 3.6699 | 3.8968 | 4.1352 | 4.4748 | 4.7711 | 5.0505 | 5.3409 | 5.6886 | 5.8058 | 6.1807 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302
9.992e-14% | 4375.9513 | 6.2157e-14 | 5.6354e-14 | 5.9891e-14 | 6.4403e-14 | 6.8772e-14 | 7.2663e-14 | 7.7997e-14 | 8.3825e-14 | 8.9793e-14 | 9.5706e-14 | 1.0096e-13 | 1.0669e-13 | 1.0889e-13 | 1.1629e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 9.992e-14% | 4375.9513 | 6.6563e-14 | 6.0778e-14 | 6.4514e-14 | 6.9081e-14 | 7.334e-14 | 7.7873e-14 | 8.2638e-14 | 8.9425e-14 | 9.5345e-14 | 1.0093e-13 | 1.0673e-13 | 1.1368e-13 | 1.1602e-13 | 1.2352e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 100% | 0 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
99% | 0 | 79.9539 | 73.4917 | 77.3313 | 80.3764 | 83.9806 | 87.696 | 91.6392 | 96.1469 | 101.4481 | 106.4167 | 111.6368 | 120.5006 | 123.5326 | 129.219 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 99% | 0.37816 | 93.5071 | 87.1619 | 91.5053 | 95.145 | 98.3714 | 103.4399 | 108.0228 | 114.3709 | 120.9884 | 126.3994 | 131.5047 | 139.0694 | 144.5767 | 150.1244 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979
98% | 0.37816 | 79.1463 | 72.7493 | 76.5502 | 79.5646 | 83.1323 | 86.8102 | 90.7135 | 95.1757 | 100.4234 | 105.3418 | 110.5092 | 119.2834 | 122.2848 | 127.9138 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 98% | 1.1345 | 92.5626 | 86.2815 | 90.581 | 94.184 | 97.3777 | 102.395 | 106.9316 | 113.2156 | 119.7663 | 125.1227 | 130.1764 | 137.6647 | 143.1163 | 148.608 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222
97% | 0.75633 | 78.3387 | 72.007 | 75.7691 | 78.7527 | 82.284 | 85.9244 | 89.7879 | 94.2046 | 99.3986 | 104.2668 | 109.3815 | 118.0663 | 121.037 | 126.6085 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 97% | 2.269 | 91.6181 | 85.401 | 89.6567 | 93.2229 | 96.3841 | 101.3502 | 105.8405 | 112.0603 | 118.5442 | 123.8459 | 128.848 | 136.2599 | 141.6559 | 147.0916 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465
95% | 1.1345 | 76.7235 | 70.5223 | 74.2068 | 77.1289 | 80.5874 | 84.1528 | 87.9366 | 92.2622 | 97.3492 | 102.117 | 107.1262 | 115.6319 | 118.5414 | 123.9981 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 95% | 4.538 | 89.7291 | 83.6402 | 87.8081 | 91.3008 | 94.3968 | 99.2605 | 103.6582 | 109.7498 | 116.1 | 121.2924 | 126.1914 | 133.4504 | 138.7352 | 144.0588 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695
90% | 4.538 | 72.6854 | 66.8106 | 70.3012 | 73.0695 | 76.346 | 79.7237 | 83.3083 | 87.4063 | 92.2255 | 96.7424 | 101.488 | 109.546 | 112.3023 | 117.4718 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 90% | 7.9414 | 85.0065 | 79.2381 | 83.1866 | 86.4955 | 89.4285 | 94.0362 | 98.2025 | 103.9735 | 109.9894 | 114.9086 | 119.5497 | 126.4267 | 131.4333 | 136.4768 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163
85% | 7.9414 | 68.6473 | 63.0989 | 66.3956 | 69.0101 | 72.1045 | 75.2946 | 78.6801 | 82.5504 | 87.1019 | 91.3679 | 95.8498 | 103.4601 | 106.0633 | 110.9456 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 85% | 14.3702 | 80.2839 | 74.836 | 78.5652 | 81.6902 | 84.4603 | 88.812 | 92.7468 | 98.1972 | 103.8789 | 108.5247 | 112.9081 | 119.403 | 124.1315 | 128.8947 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376
80% | 11.7231 | 64.6092 | 59.3872 | 62.49 | 64.9507 | 67.8631 | 70.8655 | 74.0518 | 77.6945 | 81.9783 | 85.9933 | 90.2116 | 97.3742 | 99.8243 | 104.4194 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 80% | 19.6645 | 75.5613 | 70.4338 | 73.9437 | 76.8849 | 79.492 | 83.5878 | 87.2911 | 92.4209 | 97.7684 | 102.1409 | 106.2664 | 112.3793 | 116.8296 | 121.3127 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589
75% | 17.7737 | 60.5712 | 55.6755 | 58.5843 | 60.8912 | 63.6217 | 66.4364 | 69.4236 | 72.8386 | 76.8546 | 80.6187 | 84.5734 | 91.2883 | 93.5853 | 97.8932 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 75% | 25.7152 | 70.8387 | 66.0317 | 69.3222 | 72.0796 | 74.5238 | 78.3635 | 81.8354 | 86.6446 | 91.6579 | 95.7571 | 99.6248 | 105.3556 | 109.5278 | 113.7306 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803
70% | 35.1693 | 56.5331 | 51.9638 | 54.6787 | 56.8318 | 59.3802 | 62.0073 | 64.7954 | 67.9827 | 71.731 | 75.2441 | 78.9351 | 85.2025 | 87.3463 | 91.367 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 70% | 34.7911 | 66.1162 | 61.6296 | 64.7007 | 67.2743 | 69.5555 | 73.1393 | 76.3797 | 80.8683 | 85.5473 | 89.3733 | 92.9831 | 98.3319 | 102.2259 | 106.1486 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016
65% | 59.3718 | 52.495 | 48.2521 | 50.7731 | 52.7724 | 55.1388 | 57.5782 | 60.1671 | 63.1268 | 66.6073 | 69.8695 | 73.2969 | 79.1166 | 81.1072 | 84.8408 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 65% | 46.136 | 61.3936 | 57.2275 | 60.0792 | 62.469 | 64.5873 | 67.9151 | 70.924 | 75.092 | 79.4368 | 82.9895 | 86.3415 | 91.3082 | 94.9241 | 98.5666 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229
60% | 156.9382 | 48.4569 | 44.5404 | 46.8675 | 48.713 | 50.8973 | 53.1491 | 55.5389 | 58.2709 | 61.4837 | 64.495 | 67.6587 | 73.0307 | 74.8682 | 78.3146 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 60% | 76.7673 | 56.671 | 52.8254 | 55.4578 | 57.6637 | 59.619 | 62.6908 | 65.4683 | 69.3157 | 73.3263 | 76.6057 | 79.6998 | 84.2845 | 87.6222 | 90.9845 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442
55% | 363.794 | 44.4189 | 40.8287 | 42.9618 | 44.6536 | 46.6559 | 48.72 | 50.9106 | 53.415 | 56.3601 | 59.1204 | 62.0205 | 66.9448 | 68.6292 | 71.7884 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 55% | 106.2642 | 51.9484 | 48.4233 | 50.8363 | 52.8584 | 54.6508 | 57.4666 | 60.0126 | 63.5394 | 67.2158 | 70.2219 | 73.0582 | 77.2608 | 80.3204 | 83.4025 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655
50% | 771.4551 | 40.3808 | 37.117 | 39.0562 | 40.5942 | 42.4144 | 44.2909 | 46.2824 | 48.5591 | 51.2364 | 53.7458 | 56.3822 | 60.8589 | 62.3902 | 65.2621 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 50% | 178.4935 | 47.2258 | 44.0212 | 46.2148 | 48.0531 | 49.6825 | 52.2423 | 54.5569 | 57.7631 | 61.1052 | 63.8381 | 66.4165 | 70.2371 | 73.0185 | 75.8204 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868
45% | 1255.5054 | 36.3427 | 33.4053 | 35.1506 | 36.5347 | 38.173 | 39.8618 | 41.6542 | 43.7031 | 46.1128 | 48.3712 | 50.744 | 54.773 | 56.1512 | 58.7359 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 45% | 367.9538 | 42.5032 | 39.619 | 41.5933 | 43.2477 | 44.7143 | 47.0181 | 49.1013 | 51.9868 | 54.9947 | 57.4543 | 59.7749 | 63.2134 | 65.7167 | 68.2384 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
40% | 2059.1045 | 32.3046 | 29.6936 | 31.245 | 32.4753 | 33.9315 | 35.4327 | 37.0259 | 38.8472 | 40.9891 | 42.9966 | 45.1058 | 48.6871 | 49.9121 | 52.2097 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 40% | 741.202 | 37.7807 | 35.2169 | 36.9718 | 38.4424 | 39.746 | 41.7939 | 43.6456 | 46.2105 | 48.8842 | 51.0705 | 53.1332 | 56.1897 | 58.4148 | 60.6563 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295
35% | 3060.4836 | 28.2665 | 25.9819 | 27.3394 | 28.4159 | 29.6901 | 31.0036 | 32.3977 | 33.9913 | 35.8655 | 37.6221 | 39.4676 | 42.6012 | 43.6731 | 45.6835 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 35% | 1167.7713 | 33.0581 | 30.8148 | 32.3504 | 33.6371 | 34.7778 | 36.5696 | 38.1899 | 40.4341 | 42.7737 | 44.6867 | 46.4916 | 49.1659 | 51.113 | 53.0743 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508
30% | 3366.0403 | 24.2285 | 22.2702 | 23.4337 | 24.3565 | 25.4487 | 26.5746 | 27.7694 | 29.1354 | 30.7418 | 32.2475 | 33.8293 | 36.5153 | 37.4341 | 39.1573 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 30% | 2002.3799 | 28.3355 | 26.4127 | 27.7289 | 28.8318 | 29.8095 | 31.3454 | 32.7342 | 34.6578 | 36.6631 | 38.3029 | 39.8499 | 42.1422 | 43.8111 | 45.4923 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721
25% | 3686.3454 | 20.1904 | 18.5585 | 19.5281 | 20.2971 | 21.2072 | 22.1455 | 23.1412 | 24.2795 | 25.6182 | 26.8729 | 28.1911 | 30.4294 | 31.1951 | 32.6311 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 25% | 3173.5547 | 23.6129 | 22.0106 | 23.1074 | 24.0265 | 24.8413 | 26.1212 | 27.2785 | 28.8815 | 30.5526 | 31.919 | 33.2083 | 35.1185 | 36.5093 | 37.9102 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934
20% | 4028.5841 | 16.1523 | 14.8468 | 15.6225 | 16.2377 | 16.9658 | 17.7164 | 18.513 | 19.4236 | 20.4946 | 21.4983 | 22.5529 | 24.3436 | 24.9561 | 26.1049 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 20% | 3477.5988 | 18.8903 | 17.6085 | 18.4859 | 19.2212 | 19.873 | 20.8969 | 21.8228 | 23.1052 | 24.4421 | 25.5352 | 26.5666 | 28.0948 | 29.2074 | 30.3282 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147
15% | 4345.1076 | 12.1142 | 11.1351 | 11.7169 | 12.1782 | 12.7243 | 13.2873 | 13.8847 | 14.5677 | 15.3709 | 16.1237 | 16.9147 | 18.2577 | 18.7171 | 19.5786 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 15% | 3788.4498 | 14.1677 | 13.2063 | 13.8644 | 14.4159 | 14.9048 | 15.6727 | 16.3671 | 17.3289 | 18.3316 | 19.1514 | 19.925 | 21.0711 | 21.9056 | 22.7461 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361
10% | 4381.0332 | 8.0762 | 7.4234 | 7.8112 | 8.1188 | 8.4829 | 8.8582 | 9.2565 | 9.7118 | 10.2473 | 10.7492 | 11.2764 | 12.1718 | 12.478 | 13.0524 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 10% | 4317.5016 | 9.4452 | 8.8042 | 9.243 | 9.6106 | 9.9365 | 10.4485 | 10.9114 | 11.5526 | 12.221 | 12.7676 | 13.2833 | 14.0474 | 14.6037 | 15.1641 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574
5% | 4391.6218 | 4.0381 | 3.7117 | 3.9056 | 4.0594 | 4.2414 | 4.4291 | 4.6282 | 4.8559 | 5.1236 | 5.3746 | 5.6382 | 6.0859 | 6.239 | 6.5262 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 5% | 4391.6218 | 4.7226 | 4.4021 | 4.6215 | 4.8053 | 4.9683 | 5.2242 | 5.4557 | 5.7763 | 6.1105 | 6.3838 | 6.6417 | 7.0237 | 7.3019 | 7.582 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787
9.992e-14% | 4391.6218 | 8.0697e-14 | 7.4175e-14 | 7.805e-14 | 8.1123e-14 | 8.4761e-14 | 8.8511e-14 | 9.2491e-14 | 9.704e-14 | 1.0239e-13 | 1.0741e-13 | 1.1267e-13 | 1.2162e-13 | 1.2468e-13 | 1.3042e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 9.992e-14% | 4391.6218 | 9.4376e-14 | 8.7972e-14 | 9.2356e-14 | 9.6029e-14 | 9.9286e-14 | 1.044e-13 | 1.0903e-13 | 1.1543e-13 | 1.2211e-13 | 1.2757e-13 | 1.3273e-13 | 1.4036e-13 | 1.4592e-13 | 1.5152e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.2064 | 56.3994 | 59.9385 | 64.4544 | 68.8267 | 72.7211 | 78.0591 | 83.8917 | 89.8644 | 95.7824 | 101.0445 | 106.7766 | 108.9802 | 116.383 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 124.0384 | 100% | 0 | 66.6162 | 60.8268 | 64.5653 | 69.1364 | 73.3987 | 77.9356 | 82.7045 | 89.4962 | 95.4211 | 101.0097 | 106.817 | 113.7718 | 116.1166 | 123.6147 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041 | 130.6041
99% | 0.5944 | 61.5843 | 55.8354 | 59.3391 | 63.8099 | 68.1384 | 71.9939 | 77.2785 | 83.0527 | 88.9657 | 94.8245 | 100.034 | 105.7089 | 107.8904 | 115.2192 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 122.798 | 99% | 0.5944 | 65.9501 | 60.2186 | 63.9197 | 68.4451 | 72.6648 | 77.1562 | 81.8774 | 88.6013 | 94.4669 | 99.9996 | 105.7489 | 112.6341 | 114.9554 | 122.3786 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981 | 129.2981
98% | 0.8916 | 60.9623 | 55.2714 | 58.7397 | 63.1653 | 67.4501 | 71.2667 | 76.4979 | 82.2138 | 88.0671 | 93.8667 | 99.0236 | 104.6411 | 106.8006 | 114.0553 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 121.5576 | 98% | 0.8916 | 65.2839 | 59.6103 | 63.274 | 67.7537 | 71.9308 | 76.3769 | 81.0504 | 87.7063 | 93.5127 | 98.9895 | 104.6807 | 111.4964 | 113.7942 | 121.1425 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992 | 127.992
97% | 1.486 | 60.3402 | 54.7074 | 58.1403 | 62.5208 | 66.7619 | 70.5394 | 75.7173 | 81.3749 | 87.1685 | 92.9089 | 98.0131 | 103.5733 | 105.7108 | 112.8915 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 120.3172 | 97% | 1.486 | 64.6177 | 59.002 | 62.6284 | 67.0623 | 71.1968 | 75.5975 | 80.2233 | 86.8113 | 92.5584 | 97.9794 | 103.6125 | 110.3587 | 112.6331 | 119.9063 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686 | 126.686
95% | 2.3776 | 59.0961 | 53.5795 | 56.9416 | 61.2317 | 65.3853 | 69.085 | 74.1561 | 79.6971 | 85.3712 | 90.9932 | 95.9922 | 101.4378 | 103.5312 | 110.5638 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 117.8365 | 95% | 2.3776 | 63.2854 | 57.7855 | 61.3371 | 65.6796 | 69.7288 | 74.0388 | 78.5692 | 85.0214 | 90.65 | 95.9592 | 101.4762 | 108.0832 | 110.3107 | 117.434 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739 | 124.0739
90% | 3.2692 | 55.9857 | 50.7595 | 53.9446 | 58.009 | 61.944 | 65.449 | 70.2532 | 75.5025 | 80.878 | 86.2041 | 90.94 | 96.099 | 98.0822 | 104.7447 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 111.6345 | 90% | 3.2692 | 59.9546 | 54.7442 | 58.1088 | 62.2228 | 66.0589 | 70.142 | 74.434 | 80.5466 | 85.879 | 90.9087 | 96.1353 | 102.3947 | 104.5049 | 111.2533 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437 | 117.5437
85% | 13.9683 | 52.8754 | 47.9395 | 50.9477 | 54.7863 | 58.5027 | 61.8129 | 66.3502 | 71.3079 | 76.3847 | 81.415 | 85.8878 | 90.7601 | 92.6332 | 98.9255 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 105.4326 | 85% | 13.9683 | 56.6238 | 51.7028 | 54.8805 | 58.766 | 62.3889 | 66.2453 | 70.2988 | 76.0718 | 81.1079 | 85.8582 | 90.7945 | 96.7061 | 98.6991 | 105.0725 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135 | 111.0135
80% | 41.3106 | 49.7651 | 45.1195 | 47.9508 | 51.5635 | 55.0613 | 58.1769 | 62.4473 | 67.1133 | 71.8915 | 76.6259 | 80.8356 | 85.4213 | 87.1842 | 93.1064 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 99.2307 | 80% | 41.3106 | 53.293 | 48.6615 | 51.6523 | 55.3092 | 58.719 | 62.3485 | 66.1636 | 71.597 | 76.3369 | 80.8077 | 85.4536 | 91.0175 | 92.8932 | 98.8918 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833 | 104.4833
75% | 126.3094 | 46.6548 | 42.2996 | 44.9539 | 48.3408 | 51.62 | 54.5408 | 58.5443 | 62.9187 | 67.3983 | 71.8368 | 75.7833 | 80.0825 | 81.7352 | 87.2872 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 93.0288 | 75% | 126.3094 | 49.9622 | 45.6201 | 48.424 | 51.8523 | 55.0491 | 58.4517 | 62.0284 | 67.1222 | 71.5658 | 75.7573 | 80.1128 | 85.3289 | 87.0874 | 92.7111 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531 | 97.9531
70% | 323.9464 | 43.5445 | 39.4796 | 41.9569 | 45.1181 | 48.1787 | 50.9048 | 54.6414 | 58.7242 | 62.9051 | 67.0477 | 70.7311 | 74.7436 | 76.2861 | 81.4681 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 86.8269 | 70% | 323.9464 | 46.6314 | 42.5788 | 45.1957 | 48.3955 | 51.3791 | 54.5549 | 57.8931 | 62.6474 | 66.7948 | 70.7068 | 74.7719 | 79.6403 | 81.2816 | 86.5303 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229 | 91.4229
65% | 549.5201 | 40.4341 | 36.6596 | 38.96 | 41.8954 | 44.7373 | 47.2687 | 50.7384 | 54.5296 | 58.4119 | 62.2585 | 65.6789 | 69.4048 | 70.8371 | 75.6489 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 80.6249 | 65% | 549.5201 | 43.3005 | 39.5374 | 41.9675 | 44.9387 | 47.7092 | 50.6581 | 53.7579 | 58.1726 | 62.0237 | 65.6563 | 69.4311 | 73.9517 | 75.4758 | 80.3496 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927 | 84.8927
60% | 799.4641 | 37.3238 | 33.8397 | 35.9631 | 38.6726 | 41.296 | 43.6326 | 46.8354 | 50.335 | 53.9186 | 57.4694 | 60.6267 | 64.066 | 65.3881 | 69.8298 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 74.423 | 60% | 799.4641 | 39.9697 | 36.4961 | 38.7392 | 41.4819 | 44.0392 | 46.7614 | 49.6227 | 53.6977 | 57.2526 | 60.6058 | 64.0902 | 68.2631 | 69.6699 | 74.1688 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625 | 78.3625
55% | 1116.2777 | 34.2135 | 31.0197 | 32.9662 | 35.4499 | 37.8547 | 39.9966 | 42.9325 | 46.1404 | 49.4254 | 52.6803 | 55.5745 | 58.7271 | 59.9391 | 64.0106 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 68.2211 | 55% | 1116.2777 | 36.6389 | 33.4548 | 35.5109 | 38.025 | 40.3693 | 42.8646 | 45.4875 | 49.2229 | 52.4816 | 55.5553 | 58.7494 | 62.5745 | 63.8641 | 67.9881 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323 | 71.8323
50% | 1494.9086 | 31.1032 | 28.1997 | 29.9692 | 32.2272 | 34.4133 | 36.3605 | 39.0295 | 41.9458 | 44.9322 | 47.8912 | 50.5222 | 53.3883 | 54.4901 | 58.1915 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 62.0192 | 50% | 1494.9086 | 33.3081 | 30.4134 | 32.2827 | 34.5682 | 36.6994 | 38.9678 | 41.3522 | 44.7481 | 47.7105 | 50.5048 | 53.4085 | 56.8859 | 58.0583 | 61.8074 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021 | 65.3021
45% | 2004.0097 | 27.9929 | 25.3797 | 26.9723 | 29.0045 | 30.972 | 32.7245 | 35.1266 | 37.7512 | 40.439 | 43.1021 | 45.47 | 48.0495 | 49.0411 | 52.3723 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 55.8173 | 45% | 2004.0097 | 29.9773 | 27.3721 | 29.0544 | 31.1114 | 33.0294 | 35.071 | 37.217 | 40.2733 | 42.9395 | 45.4544 | 48.0677 | 51.1973 | 52.2524 | 55.6266 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719 | 58.7719
40% | 2877.179 | 24.8826 | 22.5598 | 23.9754 | 25.7818 | 27.5307 | 29.0884 | 31.2236 | 33.5567 | 35.9458 | 38.3129 | 40.4178 | 42.7106 | 43.5921 | 46.5532 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 49.6154 | 40% | 2877.179 | 26.6465 | 24.3307 | 25.8261 | 27.6546 | 29.3595 | 31.1742 | 33.0818 | 35.7985 | 38.1684 | 40.4039 | 42.7268 | 45.5087 | 46.4466 | 49.4459 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417 | 52.2417
35% | 3454.933 | 21.7722 | 19.7398 | 20.9785 | 22.559 | 24.0893 | 25.4524 | 27.3207 | 29.3621 | 31.4525 | 33.5238 | 35.3656 | 37.3718 | 38.1431 | 40.734 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 43.4134 | 35% | 3454.933 | 23.3157 | 21.2894 | 22.5979 | 24.1978 | 25.6896 | 27.2775 | 28.9466 | 31.3237 | 33.3974 | 35.3534 | 37.386 | 39.8201 | 40.6408 | 43.2652 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114 | 45.7114
30% | 3663.5664 | 18.6619 | 16.9198 | 17.9815 | 19.3363 | 20.648 | 21.8163 | 23.4177 | 25.1675 | 26.9593 | 28.7347 | 30.3133 | 32.033 | 32.6941 | 34.9149 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 37.2115 | 30% | 3663.5664 | 19.9849 | 18.2481 | 19.3696 | 20.7409 | 22.0196 | 23.3807 | 24.8113 | 26.8489 | 28.6263 | 30.3029 | 32.0451 | 34.1316 | 34.835 | 37.0844 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812 | 39.1812
25% | 3862.6894 | 15.5516 | 14.0999 | 14.9846 | 16.1136 | 17.2067 | 18.1803 | 19.5148 | 20.9729 | 22.4661 | 23.9456 | 25.2611 | 26.6942 | 27.2451 | 29.0957 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 31.0096 | 25% | 3862.6894 | 16.6541 | 15.2067 | 16.1413 | 17.2841 | 18.3497 | 19.4839 | 20.6761 | 22.3741 | 23.8553 | 25.2524 | 26.7043 | 28.443 | 29.0291 | 30.9037 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651 | 32.651
20% | 4122.7381 | 12.4413 | 11.2799 | 11.9877 | 12.8909 | 13.7653 | 14.5442 | 15.6118 | 16.7783 | 17.9729 | 19.1565 | 20.2089 | 21.3553 | 21.796 | 23.2766 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 24.8077 | 20% | 4122.7381 | 13.3232 | 12.1654 | 12.9131 | 13.8273 | 14.6797 | 15.5871 | 16.5409 | 17.8992 | 19.0842 | 20.2019 | 21.3634 | 22.7544 | 23.2233 | 24.7229 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208 | 26.1208
15% | 4372.3849 | 9.331 | 8.4599 | 8.9908 | 9.6682 | 10.324 | 10.9082 | 11.7089 | 12.5837 | 13.4797 | 14.3674 | 15.1567 | 16.0165 | 16.347 | 17.4574 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 18.6058 | 15% | 4372.3849 | 9.9924 | 9.124 | 9.6848 | 10.3705 | 11.0098 | 11.6903 | 12.4057 | 13.4244 | 14.3132 | 15.1515 | 16.0226 | 17.0658 | 17.4175 | 18.5422 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906 | 19.5906
10% | 4374.4653 | 6.2206 | 5.6399 | 5.9938 | 6.4454 | 6.8827 | 7.2721 | 7.8059 | 8.3892 | 8.9864 | 9.5782 | 10.1044 | 10.6777 | 10.898 | 11.6383 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 12.4038 | 10% | 4374.4653 | 6.6616 | 6.0827 | 6.4565 | 6.9136 | 7.3399 | 7.7936 | 8.2704 | 8.9496 | 9.5421 | 10.101 | 10.6817 | 11.3772 | 11.6117 | 12.3615 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604 | 13.0604
5% | 4374.7625 | 3.1103 | 2.82 | 2.9969 | 3.2227 | 3.4413 | 3.6361 | 3.903 | 4.1946 | 4.4932 | 4.7891 | 5.0522 | 5.3388 | 5.449 | 5.8191 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 6.2019 | 5% | 4374.7625 | 3.3308 | 3.0413 | 3.2283 | 3.4568 | 3.6699 | 3.8968 | 4.1352 | 4.4748 | 4.7711 | 5.0505 | 5.3409 | 5.6886 | 5.8058 | 6.1807 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302 | 6.5302
9.992e-14% | 4375.9513 | 6.2157e-14 | 5.6354e-14 | 5.9891e-14 | 6.4403e-14 | 6.8772e-14 | 7.2663e-14 | 7.7997e-14 | 8.3825e-14 | 8.9793e-14 | 9.5706e-14 | 1.0096e-13 | 1.0669e-13 | 1.0889e-13 | 1.1629e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 1.2394e-13 | 9.992e-14% | 4375.9513 | 6.6563e-14 | 6.0778e-14 | 6.4514e-14 | 6.9081e-14 | 7.334e-14 | 7.7873e-14 | 8.2638e-14 | 8.9425e-14 | 9.5345e-14 | 1.0093e-13 | 1.0673e-13 | 1.1368e-13 | 1.1602e-13 | 1.2352e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13 | 1.305e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 80.7616 | 74.234 | 78.1124 | 81.1883 | 84.8289 | 88.5818 | 92.5648 | 97.1181 | 102.4728 | 107.4916 | 112.7645 | 121.7178 | 124.7804 | 130.5243 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 134.9232 | 100% | 0 | 94.4516 | 88.0423 | 92.4296 | 96.1061 | 99.365 | 104.4847 | 109.1139 | 115.5261 | 122.2105 | 127.6762 | 132.833 | 140.4741 | 146.037 | 151.6409 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737 | 157.5737
99% | 0 | 79.9539 | 73.4917 | 77.3313 | 80.3764 | 83.9806 | 87.696 | 91.6392 | 96.1469 | 101.4481 | 106.4167 | 111.6368 | 120.5006 | 123.5326 | 129.219 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 133.574 | 99% | 0.37816 | 93.5071 | 87.1619 | 91.5053 | 95.145 | 98.3714 | 103.4399 | 108.0228 | 114.3709 | 120.9884 | 126.3994 | 131.5047 | 139.0694 | 144.5767 | 150.1244 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979 | 155.9979
98% | 0.37816 | 79.1463 | 72.7493 | 76.5502 | 79.5646 | 83.1323 | 86.8102 | 90.7135 | 95.1757 | 100.4234 | 105.3418 | 110.5092 | 119.2834 | 122.2848 | 127.9138 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 132.2248 | 98% | 1.1345 | 92.5626 | 86.2815 | 90.581 | 94.184 | 97.3777 | 102.395 | 106.9316 | 113.2156 | 119.7663 | 125.1227 | 130.1764 | 137.6647 | 143.1163 | 148.608 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222 | 154.4222
97% | 0.75633 | 78.3387 | 72.007 | 75.7691 | 78.7527 | 82.284 | 85.9244 | 89.7879 | 94.2046 | 99.3986 | 104.2668 | 109.3815 | 118.0663 | 121.037 | 126.6085 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 130.8755 | 97% | 2.269 | 91.6181 | 85.401 | 89.6567 | 93.2229 | 96.3841 | 101.3502 | 105.8405 | 112.0603 | 118.5442 | 123.8459 | 128.848 | 136.2599 | 141.6559 | 147.0916 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465 | 152.8465
95% | 1.1345 | 76.7235 | 70.5223 | 74.2068 | 77.1289 | 80.5874 | 84.1528 | 87.9366 | 92.2622 | 97.3492 | 102.117 | 107.1262 | 115.6319 | 118.5414 | 123.9981 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 128.1771 | 95% | 4.538 | 89.7291 | 83.6402 | 87.8081 | 91.3008 | 94.3968 | 99.2605 | 103.6582 | 109.7498 | 116.1 | 121.2924 | 126.1914 | 133.4504 | 138.7352 | 144.0588 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695 | 149.695
90% | 4.538 | 72.6854 | 66.8106 | 70.3012 | 73.0695 | 76.346 | 79.7237 | 83.3083 | 87.4063 | 92.2255 | 96.7424 | 101.488 | 109.546 | 112.3023 | 117.4718 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 121.4309 | 90% | 7.9414 | 85.0065 | 79.2381 | 83.1866 | 86.4955 | 89.4285 | 94.0362 | 98.2025 | 103.9735 | 109.9894 | 114.9086 | 119.5497 | 126.4267 | 131.4333 | 136.4768 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163 | 141.8163
85% | 7.9414 | 68.6473 | 63.0989 | 66.3956 | 69.0101 | 72.1045 | 75.2946 | 78.6801 | 82.5504 | 87.1019 | 91.3679 | 95.8498 | 103.4601 | 106.0633 | 110.9456 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 114.6847 | 85% | 14.3702 | 80.2839 | 74.836 | 78.5652 | 81.6902 | 84.4603 | 88.812 | 92.7468 | 98.1972 | 103.8789 | 108.5247 | 112.9081 | 119.403 | 124.1315 | 128.8947 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376 | 133.9376
80% | 11.7231 | 64.6092 | 59.3872 | 62.49 | 64.9507 | 67.8631 | 70.8655 | 74.0518 | 77.6945 | 81.9783 | 85.9933 | 90.2116 | 97.3742 | 99.8243 | 104.4194 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 107.9386 | 80% | 19.6645 | 75.5613 | 70.4338 | 73.9437 | 76.8849 | 79.492 | 83.5878 | 87.2911 | 92.4209 | 97.7684 | 102.1409 | 106.2664 | 112.3793 | 116.8296 | 121.3127 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589 | 126.0589
75% | 17.7737 | 60.5712 | 55.6755 | 58.5843 | 60.8912 | 63.6217 | 66.4364 | 69.4236 | 72.8386 | 76.8546 | 80.6187 | 84.5734 | 91.2883 | 93.5853 | 97.8932 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 101.1924 | 75% | 25.7152 | 70.8387 | 66.0317 | 69.3222 | 72.0796 | 74.5238 | 78.3635 | 81.8354 | 86.6446 | 91.6579 | 95.7571 | 99.6248 | 105.3556 | 109.5278 | 113.7306 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803 | 118.1803
70% | 35.1693 | 56.5331 | 51.9638 | 54.6787 | 56.8318 | 59.3802 | 62.0073 | 64.7954 | 67.9827 | 71.731 | 75.2441 | 78.9351 | 85.2025 | 87.3463 | 91.367 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 94.4463 | 70% | 34.7911 | 66.1162 | 61.6296 | 64.7007 | 67.2743 | 69.5555 | 73.1393 | 76.3797 | 80.8683 | 85.5473 | 89.3733 | 92.9831 | 98.3319 | 102.2259 | 106.1486 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016 | 110.3016
65% | 59.3718 | 52.495 | 48.2521 | 50.7731 | 52.7724 | 55.1388 | 57.5782 | 60.1671 | 63.1268 | 66.6073 | 69.8695 | 73.2969 | 79.1166 | 81.1072 | 84.8408 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 87.7001 | 65% | 46.136 | 61.3936 | 57.2275 | 60.0792 | 62.469 | 64.5873 | 67.9151 | 70.924 | 75.092 | 79.4368 | 82.9895 | 86.3415 | 91.3082 | 94.9241 | 98.5666 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229 | 102.4229
60% | 156.9382 | 48.4569 | 44.5404 | 46.8675 | 48.713 | 50.8973 | 53.1491 | 55.5389 | 58.2709 | 61.4837 | 64.495 | 67.6587 | 73.0307 | 74.8682 | 78.3146 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 80.9539 | 60% | 76.7673 | 56.671 | 52.8254 | 55.4578 | 57.6637 | 59.619 | 62.6908 | 65.4683 | 69.3157 | 73.3263 | 76.6057 | 79.6998 | 84.2845 | 87.6222 | 90.9845 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442 | 94.5442
55% | 363.794 | 44.4189 | 40.8287 | 42.9618 | 44.6536 | 46.6559 | 48.72 | 50.9106 | 53.415 | 56.3601 | 59.1204 | 62.0205 | 66.9448 | 68.6292 | 71.7884 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 74.2078 | 55% | 106.2642 | 51.9484 | 48.4233 | 50.8363 | 52.8584 | 54.6508 | 57.4666 | 60.0126 | 63.5394 | 67.2158 | 70.2219 | 73.0582 | 77.2608 | 80.3204 | 83.4025 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655 | 86.6655
50% | 771.4551 | 40.3808 | 37.117 | 39.0562 | 40.5942 | 42.4144 | 44.2909 | 46.2824 | 48.5591 | 51.2364 | 53.7458 | 56.3822 | 60.8589 | 62.3902 | 65.2621 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 67.4616 | 50% | 178.4935 | 47.2258 | 44.0212 | 46.2148 | 48.0531 | 49.6825 | 52.2423 | 54.5569 | 57.7631 | 61.1052 | 63.8381 | 66.4165 | 70.2371 | 73.0185 | 75.8204 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868 | 78.7868
45% | 1255.5054 | 36.3427 | 33.4053 | 35.1506 | 36.5347 | 38.173 | 39.8618 | 41.6542 | 43.7031 | 46.1128 | 48.3712 | 50.744 | 54.773 | 56.1512 | 58.7359 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 60.7154 | 45% | 367.9538 | 42.5032 | 39.619 | 41.5933 | 43.2477 | 44.7143 | 47.0181 | 49.1013 | 51.9868 | 54.9947 | 57.4543 | 59.7749 | 63.2134 | 65.7167 | 68.2384 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082 | 70.9082
40% | 2059.1045 | 32.3046 | 29.6936 | 31.245 | 32.4753 | 33.9315 | 35.4327 | 37.0259 | 38.8472 | 40.9891 | 42.9966 | 45.1058 | 48.6871 | 49.9121 | 52.2097 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 53.9693 | 40% | 741.202 | 37.7807 | 35.2169 | 36.9718 | 38.4424 | 39.746 | 41.7939 | 43.6456 | 46.2105 | 48.8842 | 51.0705 | 53.1332 | 56.1897 | 58.4148 | 60.6563 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295 | 63.0295
35% | 3060.4836 | 28.2665 | 25.9819 | 27.3394 | 28.4159 | 29.6901 | 31.0036 | 32.3977 | 33.9913 | 35.8655 | 37.6221 | 39.4676 | 42.6012 | 43.6731 | 45.6835 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 47.2231 | 35% | 1167.7713 | 33.0581 | 30.8148 | 32.3504 | 33.6371 | 34.7778 | 36.5696 | 38.1899 | 40.4341 | 42.7737 | 44.6867 | 46.4916 | 49.1659 | 51.113 | 53.0743 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508 | 55.1508
30% | 3366.0403 | 24.2285 | 22.2702 | 23.4337 | 24.3565 | 25.4487 | 26.5746 | 27.7694 | 29.1354 | 30.7418 | 32.2475 | 33.8293 | 36.5153 | 37.4341 | 39.1573 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 40.477 | 30% | 2002.3799 | 28.3355 | 26.4127 | 27.7289 | 28.8318 | 29.8095 | 31.3454 | 32.7342 | 34.6578 | 36.6631 | 38.3029 | 39.8499 | 42.1422 | 43.8111 | 45.4923 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721 | 47.2721
25% | 3686.3454 | 20.1904 | 18.5585 | 19.5281 | 20.2971 | 21.2072 | 22.1455 | 23.1412 | 24.2795 | 25.6182 | 26.8729 | 28.1911 | 30.4294 | 31.1951 | 32.6311 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 33.7308 | 25% | 3173.5547 | 23.6129 | 22.0106 | 23.1074 | 24.0265 | 24.8413 | 26.1212 | 27.2785 | 28.8815 | 30.5526 | 31.919 | 33.2083 | 35.1185 | 36.5093 | 37.9102 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934 | 39.3934
20% | 4028.5841 | 16.1523 | 14.8468 | 15.6225 | 16.2377 | 16.9658 | 17.7164 | 18.513 | 19.4236 | 20.4946 | 21.4983 | 22.5529 | 24.3436 | 24.9561 | 26.1049 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 26.9846 | 20% | 3477.5988 | 18.8903 | 17.6085 | 18.4859 | 19.2212 | 19.873 | 20.8969 | 21.8228 | 23.1052 | 24.4421 | 25.5352 | 26.5666 | 28.0948 | 29.2074 | 30.3282 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147 | 31.5147
15% | 4345.1076 | 12.1142 | 11.1351 | 11.7169 | 12.1782 | 12.7243 | 13.2873 | 13.8847 | 14.5677 | 15.3709 | 16.1237 | 16.9147 | 18.2577 | 18.7171 | 19.5786 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 20.2385 | 15% | 3788.4498 | 14.1677 | 13.2063 | 13.8644 | 14.4159 | 14.9048 | 15.6727 | 16.3671 | 17.3289 | 18.3316 | 19.1514 | 19.925 | 21.0711 | 21.9056 | 22.7461 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361 | 23.6361
10% | 4381.0332 | 8.0762 | 7.4234 | 7.8112 | 8.1188 | 8.4829 | 8.8582 | 9.2565 | 9.7118 | 10.2473 | 10.7492 | 11.2764 | 12.1718 | 12.478 | 13.0524 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 13.4923 | 10% | 4317.5016 | 9.4452 | 8.8042 | 9.243 | 9.6106 | 9.9365 | 10.4485 | 10.9114 | 11.5526 | 12.221 | 12.7676 | 13.2833 | 14.0474 | 14.6037 | 15.1641 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574 | 15.7574
5% | 4391.6218 | 4.0381 | 3.7117 | 3.9056 | 4.0594 | 4.2414 | 4.4291 | 4.6282 | 4.8559 | 5.1236 | 5.3746 | 5.6382 | 6.0859 | 6.239 | 6.5262 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 6.7462 | 5% | 4391.6218 | 4.7226 | 4.4021 | 4.6215 | 4.8053 | 4.9683 | 5.2242 | 5.4557 | 5.7763 | 6.1105 | 6.3838 | 6.6417 | 7.0237 | 7.3019 | 7.582 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787 | 7.8787
9.992e-14% | 4391.6218 | 8.0697e-14 | 7.4175e-14 | 7.805e-14 | 8.1123e-14 | 8.4761e-14 | 8.8511e-14 | 9.2491e-14 | 9.704e-14 | 1.0239e-13 | 1.0741e-13 | 1.1267e-13 | 1.2162e-13 | 1.2468e-13 | 1.3042e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 1.3482e-13 | 9.992e-14% | 4391.6218 | 9.4376e-14 | 8.7972e-14 | 9.2356e-14 | 9.6029e-14 | 9.9286e-14 | 1.044e-13 | 1.0903e-13 | 1.1543e-13 | 1.2211e-13 | 1.2757e-13 | 1.3273e-13 | 1.4036e-13 | 1.4592e-13 | 1.5152e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13 | 1.5745e-13

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 162349945.5089 | 67.2% | 33.0819
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 70185987.1383 | 29.05% | 9.9906
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 3438927.3871 | 1.423% | 0.4767
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 5622421.9462 | 2.327% | 0.5178
|  | 241597281.9805 |  | 44.0669 | KW/h
|  |  |  | 44066.9381 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0.46093 | 3.3361 | 5.4293 | 7.5378 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702
98% | FY39: 0.73718; FY40: 0.73718; FY41: 0.73718; FY42: 0.73718; FY43: 0.73718; FY44: 0.73718; FY45: 0.73718; FY46: 0.73718; FY47: 0.73718; FY48: 0.73718; FY49: 0.73718; FY50: 0.73718; FY51: 0.73718; FY52: 0.73718; FY53: 0.73718; FY54: 0.73718 | [11 empty] | 0.087593 | 5.6097 | 9.754 | 13.9287 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486
97% | FY39: 0.22773; FY40: 0.22773; FY41: 0.22773; FY42: 0.22773; FY43: 0.22773; FY44: 0.22773; FY45: 0.22773; FY46: 0.22773; FY47: 0.22773; FY48: 0.22773; FY49: 0.22773; FY50: 0.22773; FY51: 0.22773; FY52: 0.22773; FY53: 0.22773; FY54: 0.22773 | [12 empty] | 6.8209 | 12.9742 | 19.1727 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352
95% | [42 empty] | 8.8608 | 20.978 | 33.1844 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075
90% | [42 empty] | 1.5148 | 14.0709 | 31.7129 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907
85% | [43 empty] | 0.10284 | 12.9496 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321
80% | [45 empty] | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54852 | 26.1423 | 63.3092 | 118.4862 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16456 | 7.8427 | 18.9928 | 35.5458 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [43 empty] | 1.7919 | 3.9005 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329 | 6.1329
98% | [43 empty] | 2.5525 | 6.7272 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471 | 11.1471
97% | [43 empty] | 2.2816 | 8.4801 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426 | 15.0426
95% | [43 empty] | 0.73498 | 12.1282 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513 | 25.0513
90% | [44 empty] | 3.694 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958 | 19.958
85% | [45 empty] | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398 | 2.0398
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.361 | 34.9301 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716 | 79.3716
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2083 | 10.479 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115 | 23.8115
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0.46093 | 3.3361 | 5.4293 | 7.5378 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702
98% | FY39: 0.73718; FY40: 0.73718; FY41: 0.73718; FY42: 0.73718; FY43: 0.73718; FY44: 0.73718; FY45: 0.73718; FY46: 0.73718; FY47: 0.73718; FY48: 0.73718; FY49: 0.73718; FY50: 0.73718; FY51: 0.73718; FY52: 0.73718; FY53: 0.73718; FY54: 0.73718 | [11 empty] | 0.087593 | 5.6097 | 9.754 | 13.9287 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486
97% | FY39: 0.22773; FY40: 0.22773; FY41: 0.22773; FY42: 0.22773; FY43: 0.22773; FY44: 0.22773; FY45: 0.22773; FY46: 0.22773; FY47: 0.22773; FY48: 0.22773; FY49: 0.22773; FY50: 0.22773; FY51: 0.22773; FY52: 0.22773; FY53: 0.22773; FY54: 0.22773 | [12 empty] | 6.8209 | 12.9742 | 19.1727 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352
95% | [42 empty] | 8.8608 | 20.978 | 33.1844 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075
90% | [42 empty] | 1.5148 | 14.0709 | 31.7129 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907
85% | [43 empty] | 0.10284 | 12.9496 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321
80% | [45 empty] | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54852 | 26.1423 | 63.3092 | 118.4862 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16456 | 7.8427 | 18.9928 | 35.5458 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [43 empty] | 0.049538 | 2.0819 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142 | 4.3142
98% | [44 empty] | 3.1265 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463 | 7.5463
97% | [44 empty] | 3.1338 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963 | 9.6963
95% | [44 empty] | 1.7837 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232 | 14.5232
90% | [45 empty] | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759 | 5.8759
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049538 | 10.1259 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956 | 41.956
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014861 | 3.0378 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868 | 12.5868
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0.46093 | 3.3361 | 5.4293 | 7.5378 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702
98% | FY39: 0.73718; FY40: 0.73718; FY41: 0.73718; FY42: 0.73718; FY43: 0.73718; FY44: 0.73718; FY45: 0.73718; FY46: 0.73718; FY47: 0.73718; FY48: 0.73718; FY49: 0.73718; FY50: 0.73718; FY51: 0.73718; FY52: 0.73718; FY53: 0.73718; FY54: 0.73718 | [11 empty] | 0.087593 | 5.6097 | 9.754 | 13.9287 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486
97% | FY39: 0.22773; FY40: 0.22773; FY41: 0.22773; FY42: 0.22773; FY43: 0.22773; FY44: 0.22773; FY45: 0.22773; FY46: 0.22773; FY47: 0.22773; FY48: 0.22773; FY49: 0.22773; FY50: 0.22773; FY51: 0.22773; FY52: 0.22773; FY53: 0.22773; FY54: 0.22773 | [12 empty] | 6.8209 | 12.9742 | 19.1727 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352
95% | [42 empty] | 8.8608 | 20.978 | 33.1844 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075
90% | [42 empty] | 1.5148 | 14.0709 | 31.7129 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907
85% | [43 empty] | 0.10284 | 12.9496 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321
80% | [45 empty] | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54852 | 26.1423 | 63.3092 | 118.4862 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16456 | 7.8427 | 18.9928 | 35.5458 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0.46093 | 3.3361 | 5.4293 | 7.5378 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702
98% | FY39: 0.73718; FY40: 0.73718; FY41: 0.73718; FY42: 0.73718; FY43: 0.73718; FY44: 0.73718; FY45: 0.73718; FY46: 0.73718; FY47: 0.73718; FY48: 0.73718; FY49: 0.73718; FY50: 0.73718; FY51: 0.73718; FY52: 0.73718; FY53: 0.73718; FY54: 0.73718 | [11 empty] | 0.087593 | 5.6097 | 9.754 | 13.9287 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486
97% | FY39: 0.22773; FY40: 0.22773; FY41: 0.22773; FY42: 0.22773; FY43: 0.22773; FY44: 0.22773; FY45: 0.22773; FY46: 0.22773; FY47: 0.22773; FY48: 0.22773; FY49: 0.22773; FY50: 0.22773; FY51: 0.22773; FY52: 0.22773; FY53: 0.22773; FY54: 0.22773 | [12 empty] | 6.8209 | 12.9742 | 19.1727 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352
95% | [42 empty] | 8.8608 | 20.978 | 33.1844 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075
90% | [42 empty] | 1.5148 | 14.0709 | 31.7129 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907
85% | [43 empty] | 0.10284 | 12.9496 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321
80% | [45 empty] | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54852 | 26.1423 | 63.3092 | 118.4862 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16456 | 7.8427 | 18.9928 | 35.5458 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0.46093 | 3.3361 | 5.4293 | 7.5378 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702
98% | FY39: 0.73718; FY40: 0.73718; FY41: 0.73718; FY42: 0.73718; FY43: 0.73718; FY44: 0.73718; FY45: 0.73718; FY46: 0.73718; FY47: 0.73718; FY48: 0.73718; FY49: 0.73718; FY50: 0.73718; FY51: 0.73718; FY52: 0.73718; FY53: 0.73718; FY54: 0.73718 | [11 empty] | 0.087593 | 5.6097 | 9.754 | 13.9287 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486
97% | FY39: 0.22773; FY40: 0.22773; FY41: 0.22773; FY42: 0.22773; FY43: 0.22773; FY44: 0.22773; FY45: 0.22773; FY46: 0.22773; FY47: 0.22773; FY48: 0.22773; FY49: 0.22773; FY50: 0.22773; FY51: 0.22773; FY52: 0.22773; FY53: 0.22773; FY54: 0.22773 | [12 empty] | 6.8209 | 12.9742 | 19.1727 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352
95% | [42 empty] | 8.8608 | 20.978 | 33.1844 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075
90% | [42 empty] | 1.5148 | 14.0709 | 31.7129 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907
85% | [43 empty] | 0.10284 | 12.9496 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321
80% | [45 empty] | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54852 | 26.1423 | 63.3092 | 118.4862 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16456 | 7.8427 | 18.9928 | 35.5458 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY39: 0; FY40: 0; FY41: 0; FY42: 0; FY43: 0; FY44: 0; FY45: 0; FY46: 0; FY47: 0; FY48: 0; FY49: 0; FY50: 0; FY51: 0; FY52: 0; FY53: 0; FY54: 0 | [11 empty] | 0.46093 | 3.3361 | 5.4293 | 7.5378 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702 | 9.7702
98% | FY39: 0.73718; FY40: 0.73718; FY41: 0.73718; FY42: 0.73718; FY43: 0.73718; FY44: 0.73718; FY45: 0.73718; FY46: 0.73718; FY47: 0.73718; FY48: 0.73718; FY49: 0.73718; FY50: 0.73718; FY51: 0.73718; FY52: 0.73718; FY53: 0.73718; FY54: 0.73718 | [11 empty] | 0.087593 | 5.6097 | 9.754 | 13.9287 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486 | 18.3486
97% | FY39: 0.22773; FY40: 0.22773; FY41: 0.22773; FY42: 0.22773; FY43: 0.22773; FY44: 0.22773; FY45: 0.22773; FY46: 0.22773; FY47: 0.22773; FY48: 0.22773; FY49: 0.22773; FY50: 0.22773; FY51: 0.22773; FY52: 0.22773; FY53: 0.22773; FY54: 0.22773 | [12 empty] | 6.8209 | 12.9742 | 19.1727 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352 | 25.7352
95% | [42 empty] | 8.8608 | 20.978 | 33.1844 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075 | 46.1075
90% | [42 empty] | 1.5148 | 14.0709 | 31.7129 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907 | 50.3907
85% | [43 empty] | 0.10284 | 12.9496 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321 | 44.5321
80% | [45 empty] | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999 | 2.999
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | 0.96491 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54852 | 26.1423 | 63.3092 | 118.4862 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833 | 197.8833
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | 0.67544 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16456 | 7.8427 | 18.9928 | 35.5458 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365 | 59.365

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [10 empty] | 1.6282 | 5.0183 | 6.3216 | 10.6998 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | [10 empty] | 1.6076 | 5.0422 | 9.1555 | 10.5422 | 14.9768 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105
98% | [10 empty] | 0.5138 | 2.1918 | 2.8369 | 5.004 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | [10 empty] | 0.50361 | 2.2037 | 4.2396 | 4.926 | 7.121 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671
97% | [10 empty] | 0.42698 | 3.749 | 5.026 | 9.3162 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | [10 empty] | 0.40682 | 3.7724 | 7.803 | 9.1618 | 13.5073 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579
95% | [10 empty] | 0.01002 | 4.1955 | 6.0816 | 12.4178 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | [10 empty] | 0.0071007 | 4.2301 | 10.1829 | 12.1898 | 18.6077 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902
90% | [11 empty] | 1.105 | 2.6808 | 8.786 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | [11 empty] | 1.128 | 6.6325 | 8.5663 | 14.7502 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146
85% | [12 empty] | 0.078177 | 43.1723 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | [12 empty] | 19.8527 | 40.678 | 110.8742 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071
80% | FY38: 2.9762; FY39: 123.906; FY40: 123.906; FY41: 123.906; FY42: 123.906; FY43: 123.906; FY44: 123.906; FY45: 123.906; FY46: 123.906; FY47: 123.906; FY48: 123.906; FY49: 123.906; FY50: 123.906; FY51: 123.906; FY52: 123.906; FY53: 123.906; FY54: 123.906 | [13 empty] | 1.9034 | 114.3499 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012
75% | FY39: 14.0268; FY40: 14.0268; FY41: 14.0268; FY42: 14.0268; FY43: 14.0268; FY44: 14.0268; FY45: 14.0268; FY46: 14.0268; FY47: 14.0268; FY48: 14.0268; FY49: 14.0268; FY50: 14.0268; FY51: 14.0268; FY52: 14.0268; FY53: 14.0268; FY54: 14.0268 | [14 empty] | 8.1965 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543
70% | [45 empty] | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.579 | 16.2596 | 23.0251 | 92.3724 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5252 | 16.3764 | 57.8662 | 87.9675 | 302.3837 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8053 | 11.3817 | 16.1175 | 64.6606 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75755 | 4.9129 | 17.3599 | 26.3903 | 90.7151 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8074 |  | 1.0465 | 2.4299 | 3.6562 | 5.5826 | 7.3244 | 9.7372 | 12.2523 | 14.3089 | 16.2493 | 19.1244 | 21.2176 | 23.3262 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585
98% | [6 empty] | 0.74738 | 2.4434 | 4.438 | 6.3075 | 8.2716 | 11.6066 | 12.7474 | 14.887 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 |  | 2.9004 |  | 1.394 | 4.133 | 6.5608 | 10.3749 | 13.8236 | 18.6006 | 23.5803 | 27.6522 | 31.4939 | 37.1864 | 41.3307 | 45.5054 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253
97% | [6 empty] | 0.39733 | 2.0762 | 4.0505 | 5.901 | 7.8452 | 11.1463 | 12.2755 | 14.3934 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 |  | 3.2791 |  | 1.0424 | 5.1091 | 8.7139 | 14.377 | 19.4975 | 26.5902 | 33.984 | 40.0298 | 45.7339 | 54.186 | 60.3393 | 66.5378 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003
95% | [6 empty] | 0.035295 | 1.5253 | 3.4692 | 5.2912 | 7.2055 | 10.4559 | 11.5677 | 13.653 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 |  | 3.3435 |  | 0.12801 | 6.9473 | 14.046 | 25.1978 | 35.2812 | 49.2485 | 63.8085 | 75.7141 | 86.9468 | 103.5909 | 115.7082 | 127.9146 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376
90% | [7 empty] | 3.2862 | 19.0165 | 34.8166 | 51.4168 | 79.6038 | 89.2455 | 107.3285 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 |  | 0.10086 |  |  | 1.5629 | 9.2325 | 25.3503 | 39.924 | 60.1111 | 81.1549 | 98.3621 | 114.597 | 138.6529 | 156.1661 | 173.8081 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486
85% | [8 empty] | 3.0403 | 16.5244 | 32.2272 | 58.8906 | 68.0111 | 85.1167 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | [5 empty] | 0.033792 | 14.391 | 40.3385 | 76.4086 | 114.0093 | 144.7549 | 173.7631 | 216.7459 | 248.0383 | 279.5608 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342
80% | [9 empty] | 1.6534 | 14.4863 | 42.4194 | 51.9742 | 69.8943 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | [7 empty] | 6.1039 | 32.3432 | 61.5391 | 85.4121 | 107.9362 | 141.311 | 165.6087 | 190.085 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984
75% | [10 empty] | 0.54907 | 31.0475 | 45.4087 | 72.3432 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | [8 empty] | 5.4335 | 33.3578 | 58.9878 | 83.1694 | 119.0005 | 145.0863 | 171.3638 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843
70% | [11 empty] | 6.2329 | 26.8094 | 94.4596 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | [9 empty] | 4.4864 | 30.5426 | 64.4749 | 114.7539 | 151.3582 | 188.2316 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27
65% | FY38: 8.7073; FY39: 49.3711; FY40: 49.3711; FY41: 49.3711; FY42: 49.3711; FY43: 49.3711; FY44: 49.3711; FY45: 49.3711; FY46: 49.3711; FY47: 49.3711; FY48: 49.3711; FY49: 49.3711; FY50: 49.3711; FY51: 49.3711; FY52: 49.3711; FY53: 49.3711; FY54: 49.3711 | [10 empty] | 0.026693 | 12.2235 | 63.759 | 106.3587 | 149.2717 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044
60% | [42 empty] | 9.6914 | 68.7248 | 170.7858 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674
55% | [44 empty] | 6.1944 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 9.3311 | 34.0146 | 70.4941 | 122.0016 | 251.4031 | 318.0395 | 480.783 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | E @ R (MWh) | 11.4313 | 0 | 3.611 | 20.1823 | 42.2433 | 95.2734 | 162.293 | 278.4728 | 428.1726 | 575.7911 | 736.588 | 1018.0024 | 1279.9369 | 1592.5853 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83
Option 1 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.826 | 6.5317 | 23.8102 | 49.3459 | 85.4011 | 175.9822 | 222.6276 | 336.5481 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 3.4294 | 0 | 1.0833 | 6.0547 | 12.673 | 28.582 | 48.6879 | 83.5419 | 128.4518 | 172.7373 | 220.9764 | 305.4007 | 383.9811 | 477.7756 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [12 empty] | 0.60449 | 4.9827 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | 9.5103 | [12 empty] | 3.4384 | 4.8251 | 9.2597 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934 | 13.3934
98% | [12 empty] | 0.040522 | 2.1742 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | 4.4152 | [12 empty] | 1.4098 | 2.0962 | 4.2912 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373 | 6.3373
97% | FY38: 3.714; FY39: 8.1506; FY40: 8.1506; FY41: 8.1506; FY42: 8.1506; FY43: 8.1506; FY44: 8.1506; FY45: 8.1506; FY46: 8.1506; FY47: 8.1506; FY48: 8.1506; FY49: 8.1506; FY50: 8.1506; FY51: 8.1506; FY52: 8.1506; FY53: 8.1506; FY54: 8.1506 | [12 empty] | 2.2008 | 3.5596 | 7.9051 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557 | 11.9557
95% | FY38: 4.1438; FY39: 10.6963; FY40: 10.6963; FY41: 10.6963; FY42: 10.6963; FY43: 10.6963; FY44: 10.6963; FY45: 10.6963; FY46: 10.6963; FY47: 10.6963; FY48: 10.6963; FY49: 10.6963; FY50: 10.6963; FY51: 10.6963; FY52: 10.6963; FY53: 10.6963; FY54: 10.6963 | [12 empty] | 1.9089 | 3.9158 | 10.3337 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162 | 16.3162
90% | FY38: 1.0711; FY39: 7.1273; FY40: 7.1273; FY41: 7.1273; FY42: 7.1273; FY43: 7.1273; FY44: 7.1273; FY45: 7.1273; FY46: 7.1273; FY47: 7.1273; FY48: 7.1273; FY49: 7.1273; FY50: 7.1273; FY51: 7.1273; FY52: 7.1273; FY53: 7.1273; FY54: 7.1273 | [12 empty] | 0.10361 | 0.92732 | 6.7779 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422 | 12.5422
85% | FY39: 24.6623; FY40: 24.6623; FY41: 24.6623; FY42: 24.6623; FY43: 24.6623; FY44: 24.6623; FY45: 24.6623; FY46: 24.6623; FY47: 24.6623; FY48: 24.6623; FY49: 24.6623; FY50: 24.6623; FY51: 24.6623; FY52: 24.6623; FY53: 24.6623; FY54: 24.6623 | [14 empty] | 21.2142 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102 | 85.8102
80% | [45 empty] | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502 | 56.4502
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64501 | 16.0858 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | 64.5621 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0614 | 15.324 | 59.7819 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052 | 202.8052
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45151 | 11.2601 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | 45.1934 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7184 | 4.5972 | 17.9346 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415 | 60.8415
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8074 |  | 1.0465 |  | 0.052358 | 1.9453 | 3.6871 | 6.0999 | 8.615 | 10.6716 | 12.612 | 15.4871 | 17.5803 | 19.6889 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212 | 21.9212
98% | [8 empty] | 0.83728 | 2.7067 | 4.6708 | 8.0059 | 9.1467 | 11.2862 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 | 12.9248 |  | 2.9004 |  | 1.394 |  |  | 3.1734 | 6.6221 | 11.3991 | 16.3788 | 20.4506 | 24.2924 | 29.9849 | 34.1292 | 38.3039 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238 | 42.7238
97% | [8 empty] | 0.48632 | 2.3368 | 4.281 | 7.5821 | 8.7113 | 10.8292 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 | 12.4511 |  | 3.2791 |  | 1.0424 |  |  | 3.6844 | 8.8049 | 15.8976 | 23.2914 | 29.3372 | 35.0413 | 43.4934 | 49.6467 | 55.8452 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077 | 62.4077
95% | [8 empty] | 0.068826 | 1.7819 | 3.6961 | 6.9465 | 8.0584 | 10.1436 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 | 11.7406 |  | 3.3435 |  | 0.12801 |  |  | 4.1416 | 14.225 | 28.1923 | 42.7524 | 54.6579 | 65.8907 | 82.5347 | 94.652 | 106.8584 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814 | 119.7814
90% | [9 empty] | 4.8501 | 20.984 | 49.1711 | 58.8127 | 76.8958 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 | 90.7446 |  | 0.10086 |  |  |  |  | 0.27616 | 9.4912 | 29.6784 | 50.7221 | 67.9293 | 84.1642 | 108.2201 | 125.7333 | 143.3754 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532 | 162.0532
85% | [10 empty] | 4.2499 | 30.1029 | 39.2234 | 56.329 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | 69.4292 | [7 empty] | 0.059158 | 22.0317 | 59.6324 | 90.378 | 119.3863 | 162.369 | 193.6615 | 225.184 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573 | 258.5573
80% | [11 empty] | 12.2608 | 21.8156 | 39.7357 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | 53.4598 | [8 empty] | 0.3047 | 19.317 | 43.1901 | 65.7141 | 99.089 | 123.3866 | 147.8629 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763 | 173.7763
75% | [11 empty] | 0.10497 | 4.393 | 27.0139 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | 47.6416 | [9 empty] | 0.37489 | 13.9046 | 37.8402 | 73.6712 | 99.757 | 126.0346 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855 | 153.855
70% | FY38: 2.9979; FY39: 31.2347; FY40: 31.2347; FY41: 31.2347; FY42: 31.2347; FY43: 31.2347; FY44: 31.2347; FY45: 31.2347; FY46: 31.2347; FY47: 31.2347; FY48: 31.2347; FY49: 31.2347; FY50: 31.2347; FY51: 31.2347; FY52: 31.2347; FY53: 31.2347; FY54: 31.2347 | [11 empty] | 7.4271 | 51.1467 | 87.751 | 124.6244 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627 | 163.6627
65% | [42 empty] | 4.8519 | 32.5933 | 75.2461 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787 | 120.6787
60% | [44 empty] | 20.51 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335 | 99.7335
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3924 | 11.6755 | 37.8819 | 114.1742 | 150.161 | 235.2313 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | 329.6264 | E @ R (MWh) | 11.4313 | 0 | 3.611 | 0 | 0.052358 | 13.2207 | 42.8895 | 113.6036 | 221.0839 | 330.5193 | 452.3682 | 670.8481 | 858.8908 | 1083.5336 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151 | 1379.151
Option 2 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9747 | 8.1728 | 26.5173 | 79.9219 | 105.1127 | 164.6619 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | 230.7385 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 3.4294 | 0 | 1.0833 | 0 | 0.015707 | 3.9662 | 12.8668 | 34.0811 | 66.3252 | 99.1558 | 135.7105 | 201.2544 | 257.6672 | 325.0601 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453 | 413.7453
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [10 empty] | 1.6282 | 5.0183 | 6.3216 | 10.6998 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | [10 empty] | 1.6076 | 5.0422 | 9.1555 | 10.5422 | 14.9768 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105
98% | [10 empty] | 0.5138 | 2.1918 | 2.8369 | 5.004 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | [10 empty] | 0.50361 | 2.2037 | 4.2396 | 4.926 | 7.121 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671
97% | [10 empty] | 0.42698 | 3.749 | 5.026 | 9.3162 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | [10 empty] | 0.40682 | 3.7724 | 7.803 | 9.1618 | 13.5073 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579
95% | [10 empty] | 0.01002 | 4.1955 | 6.0816 | 12.4178 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | [10 empty] | 0.0071007 | 4.2301 | 10.1829 | 12.1898 | 18.6077 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902
90% | [11 empty] | 1.105 | 2.6808 | 8.786 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | [11 empty] | 1.128 | 6.6325 | 8.5663 | 14.7502 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146
85% | [12 empty] | 0.078177 | 43.1723 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | [12 empty] | 19.8527 | 40.678 | 110.8742 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071
80% | FY38: 2.9762; FY39: 123.906; FY40: 123.906; FY41: 123.906; FY42: 123.906; FY43: 123.906; FY44: 123.906; FY45: 123.906; FY46: 123.906; FY47: 123.906; FY48: 123.906; FY49: 123.906; FY50: 123.906; FY51: 123.906; FY52: 123.906; FY53: 123.906; FY54: 123.906 | [13 empty] | 1.9034 | 114.3499 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012
75% | FY39: 14.0268; FY40: 14.0268; FY41: 14.0268; FY42: 14.0268; FY43: 14.0268; FY44: 14.0268; FY45: 14.0268; FY46: 14.0268; FY47: 14.0268; FY48: 14.0268; FY49: 14.0268; FY50: 14.0268; FY51: 14.0268; FY52: 14.0268; FY53: 14.0268; FY54: 14.0268 | [14 empty] | 8.1965 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543
70% | [45 empty] | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.579 | 16.2596 | 23.0251 | 92.3724 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5252 | 16.3764 | 57.8662 | 87.9675 | 302.3837 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8053 | 11.3817 | 16.1175 | 64.6606 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75755 | 4.9129 | 17.3599 | 26.3903 | 90.7151 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8074 |  | 1.0465 | 2.4299 | 3.6562 | 5.5826 | 7.3244 | 9.7372 | 12.2523 | 14.3089 | 16.2493 | 19.1244 | 21.2176 | 23.3262 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585
98% | [6 empty] | 0.74738 | 2.4434 | 4.438 | 6.3075 | 8.2716 | 11.6066 | 12.7474 | 14.887 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 |  | 2.9004 |  | 1.394 | 4.133 | 6.5608 | 10.3749 | 13.8236 | 18.6006 | 23.5803 | 27.6522 | 31.4939 | 37.1864 | 41.3307 | 45.5054 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253
97% | [6 empty] | 0.39733 | 2.0762 | 4.0505 | 5.901 | 7.8452 | 11.1463 | 12.2755 | 14.3934 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 |  | 3.2791 |  | 1.0424 | 5.1091 | 8.7139 | 14.377 | 19.4975 | 26.5902 | 33.984 | 40.0298 | 45.7339 | 54.186 | 60.3393 | 66.5378 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003
95% | [6 empty] | 0.035295 | 1.5253 | 3.4692 | 5.2912 | 7.2055 | 10.4559 | 11.5677 | 13.653 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 |  | 3.3435 |  | 0.12801 | 6.9473 | 14.046 | 25.1978 | 35.2812 | 49.2485 | 63.8085 | 75.7141 | 86.9468 | 103.5909 | 115.7082 | 127.9146 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376
90% | [7 empty] | 3.2862 | 19.0165 | 34.8166 | 51.4168 | 79.6038 | 89.2455 | 107.3285 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 |  | 0.10086 |  |  | 1.5629 | 9.2325 | 25.3503 | 39.924 | 60.1111 | 81.1549 | 98.3621 | 114.597 | 138.6529 | 156.1661 | 173.8081 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486
85% | [8 empty] | 3.0403 | 16.5244 | 32.2272 | 58.8906 | 68.0111 | 85.1167 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | [5 empty] | 0.033792 | 14.391 | 40.3385 | 76.4086 | 114.0093 | 144.7549 | 173.7631 | 216.7459 | 248.0383 | 279.5608 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342
80% | [9 empty] | 1.6534 | 14.4863 | 42.4194 | 51.9742 | 69.8943 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | [7 empty] | 6.1039 | 32.3432 | 61.5391 | 85.4121 | 107.9362 | 141.311 | 165.6087 | 190.085 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984
75% | [10 empty] | 0.54907 | 31.0475 | 45.4087 | 72.3432 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | [8 empty] | 5.4335 | 33.3578 | 58.9878 | 83.1694 | 119.0005 | 145.0863 | 171.3638 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843
70% | [11 empty] | 6.2329 | 26.8094 | 94.4596 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | [9 empty] | 4.4864 | 30.5426 | 64.4749 | 114.7539 | 151.3582 | 188.2316 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27
65% | FY38: 8.7073; FY39: 49.3711; FY40: 49.3711; FY41: 49.3711; FY42: 49.3711; FY43: 49.3711; FY44: 49.3711; FY45: 49.3711; FY46: 49.3711; FY47: 49.3711; FY48: 49.3711; FY49: 49.3711; FY50: 49.3711; FY51: 49.3711; FY52: 49.3711; FY53: 49.3711; FY54: 49.3711 | [10 empty] | 0.026693 | 12.2235 | 63.759 | 106.3587 | 149.2717 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044
60% | [42 empty] | 9.6914 | 68.7248 | 170.7858 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674
55% | [44 empty] | 6.1944 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 9.3311 | 34.0146 | 70.4941 | 122.0016 | 251.4031 | 318.0395 | 480.783 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | E @ R (MWh) | 11.4313 | 0 | 3.611 | 20.1823 | 42.2433 | 95.2734 | 162.293 | 278.4728 | 428.1726 | 575.7911 | 736.588 | 1018.0024 | 1279.9369 | 1592.5853 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83
Option 3 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.826 | 6.5317 | 23.8102 | 49.3459 | 85.4011 | 175.9822 | 222.6276 | 336.5481 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 3.4294 | 0 | 1.0833 | 6.0547 | 12.673 | 28.582 | 48.6879 | 83.5419 | 128.4518 | 172.7373 | 220.9764 | 305.4007 | 383.9811 | 477.7756 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 2.1241; FY39: 6.6517; FY40: 6.6517; FY41: 6.6517; FY42: 6.6517; FY43: 6.6517; FY44: 6.6517; FY45: 6.6517; FY46: 6.6517; FY47: 6.6517; FY48: 6.6517; FY49: 6.6517; FY50: 6.6517; FY51: 6.6517; FY52: 6.6517; FY53: 6.6517; FY54: 6.6517 | [12 empty] | 0.57982 | 1.9665 | 6.4012 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349 | 10.5349
98% | FY38: 0.75927; FY39: 3.0003; FY40: 3.0003; FY41: 3.0003; FY42: 3.0003; FY43: 3.0003; FY44: 3.0003; FY45: 3.0003; FY46: 3.0003; FY47: 3.0003; FY48: 3.0003; FY49: 3.0003; FY50: 3.0003; FY51: 3.0003; FY52: 3.0003; FY53: 3.0003; FY54: 3.0003 | [12 empty] | 0.034362 | 0.68127 | 2.8763 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224 | 4.9224
97% | FY38: 0.91294; FY39: 5.3495; FY40: 5.3495; FY41: 5.3495; FY42: 5.3495; FY43: 5.3495; FY44: 5.3495; FY45: 5.3495; FY46: 5.3495; FY47: 5.3495; FY48: 5.3495; FY49: 5.3495; FY50: 5.3495; FY51: 5.3495; FY52: 5.3495; FY53: 5.3495; FY54: 5.3495 | [13 empty] | 0.75853 | 5.104 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546 | 9.1546
95% | FY38: 0.23053; FY39: 6.5593; FY40: 6.5593; FY41: 6.5593; FY42: 6.5593; FY43: 6.5593; FY44: 6.5593; FY45: 6.5593; FY46: 6.5593; FY47: 6.5593; FY48: 6.5593; FY49: 6.5593; FY50: 6.5593; FY51: 6.5593; FY52: 6.5593; FY53: 6.5593; FY54: 6.5593 | [13 empty] | 0.1294 | 6.1967 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792 | 12.1792
90% | FY39: 3.1411; FY40: 3.1411; FY41: 3.1411; FY42: 3.1411; FY43: 3.1411; FY44: 3.1411; FY45: 3.1411; FY46: 3.1411; FY47: 3.1411; FY48: 3.1411; FY49: 3.1411; FY50: 3.1411; FY51: 3.1411; FY52: 3.1411; FY53: 3.1411; FY54: 3.1411 | [14 empty] | 2.7917 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556 | 8.556
85% | FY39: 0.6012; FY40: 0.6012; FY41: 0.6012; FY42: 0.6012; FY43: 0.6012; FY44: 0.6012; FY45: 0.6012; FY46: 0.6012; FY47: 0.6012; FY48: 0.6012; FY49: 0.6012; FY50: 0.6012; FY51: 0.6012; FY52: 0.6012; FY53: 0.6012; FY54: 0.6012 | [14 empty] | 0.15946 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617 | 40.5617
80% | [45 empty] | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591 | 1.8591
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0269 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | 25.3032 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61418 | 3.5358 | 23.5294 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679 | 87.7679
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8188 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | 17.7122 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18426 | 1.0607 | 7.0588 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304 | 26.3304
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8074 |  | 1.0465 |  |  | 0.12939 | 1.8684 | 4.2812 | 6.7963 | 8.8529 | 10.7933 | 13.6685 | 15.7616 | 17.8702 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026 | 20.1026
98% | [9 empty] | 0.90635 | 2.8705 | 6.2055 | 7.3463 | 9.4858 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 | 11.1244 |  | 2.9004 |  | 1.394 |  |  |  | 3.0213 | 7.7983 | 12.778 | 16.8499 | 20.6917 | 26.3842 | 30.5284 | 34.7032 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123 | 39.123
97% | [9 empty] | 0.55469 | 2.4989 | 5.8 | 6.9292 | 9.0471 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 | 10.669 |  | 3.2791 |  | 1.0424 |  |  |  | 3.4586 | 10.5513 | 17.9451 | 23.9909 | 29.695 | 38.1471 | 44.3004 | 50.4989 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614 | 57.0614
95% | [9 empty] | 0.10204 | 1.9415 | 5.1918 | 6.3037 | 8.3889 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 | 9.9859 |  | 3.3435 |  | 0.12801 |  |  |  | 3.697 | 17.6643 | 32.2243 | 44.1298 | 55.3626 | 72.0067 | 84.1239 | 96.3303 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533 | 109.2533
90% | [10 empty] | 5.9687 | 33.9547 | 43.5963 | 61.6794 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 | 75.5282 |  | 0.10086 | [5 empty] | 0.16791 | 14.462 | 35.5057 | 52.7129 | 68.9478 | 93.0037 | 110.517 | 128.159 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368 | 146.8368
85% | [11 empty] | 15.709 | 24.8295 | 41.9351 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | 55.0353 | [8 empty] | 1.8903 | 32.444 | 63.1896 | 92.1978 | 135.1806 | 166.473 | 197.9955 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689 | 231.3689
80% | [11 empty] | 1.3208 | 7.0627 | 24.6564 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | 38.3805 | [9 empty] | 2.7235 | 22.079 | 44.6031 | 77.978 | 102.2756 | 126.7519 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653 | 152.6653
75% | FY38: 6.8317; FY39: 24.977; FY40: 24.977; FY41: 24.977; FY42: 24.977; FY43: 24.977; FY44: 24.977; FY45: 24.977; FY46: 24.977; FY47: 24.977; FY48: 24.977; FY49: 24.977; FY50: 24.977; FY51: 24.977; FY52: 24.977; FY53: 24.977; FY54: 24.977 | [10 empty] | 0.96131 | 15.2792 | 51.0065 | 77.0923 | 103.3699 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904 | 131.1904
70% | FY39: 1.8037; FY40: 1.8037; FY41: 1.8037; FY42: 1.8037; FY43: 1.8037; FY44: 1.8037; FY45: 1.8037; FY46: 1.8037; FY47: 1.8037; FY48: 1.8037; FY49: 1.8037; FY50: 1.8037; FY51: 1.8037; FY52: 1.8037; FY53: 1.8037; FY54: 1.8037 | [12 empty] | 20.0899 | 55.9473 | 92.8207 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591 | 131.8591
65% | [43 empty] | 7.1336 | 38.2361 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659 | 83.6659
60% | [45 empty] | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881 | 30.881
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5631 | 13.2795 | 68.1818 | 96.0677 | 162.0244 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | 227.504 | E @ R (MWh) | 11.4313 | 0 | 3.611 | 0 | 0 | 0.12939 | 12.2132 | 56.6474 | 140.4169 | 232.7664 | 337.5704 | 527.4651 | 694.1532 | 886.7357 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078 | 1134.0078
Option 4 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0942 | 9.2957 | 47.7273 | 67.2474 | 113.4171 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | 159.2528 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 3.4294 | 0 | 1.0833 | 0 | 0 | 0.038816 | 3.6639 | 16.9942 | 42.1251 | 69.8299 | 101.2711 | 158.2395 | 208.246 | 266.0207 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023 | 340.2023
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [10 empty] | 1.6282 | 5.0183 | 6.3216 | 10.6998 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | [10 empty] | 1.6076 | 5.0422 | 9.1555 | 10.5422 | 14.9768 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105
98% | [10 empty] | 0.5138 | 2.1918 | 2.8369 | 5.004 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | [10 empty] | 0.50361 | 2.2037 | 4.2396 | 4.926 | 7.121 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671
97% | [10 empty] | 0.42698 | 3.749 | 5.026 | 9.3162 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | [10 empty] | 0.40682 | 3.7724 | 7.803 | 9.1618 | 13.5073 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579
95% | [10 empty] | 0.01002 | 4.1955 | 6.0816 | 12.4178 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | [10 empty] | 0.0071007 | 4.2301 | 10.1829 | 12.1898 | 18.6077 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902
90% | [11 empty] | 1.105 | 2.6808 | 8.786 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | [11 empty] | 1.128 | 6.6325 | 8.5663 | 14.7502 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146
85% | [12 empty] | 0.078177 | 43.1723 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | [12 empty] | 19.8527 | 40.678 | 110.8742 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071
80% | FY38: 2.9762; FY39: 123.906; FY40: 123.906; FY41: 123.906; FY42: 123.906; FY43: 123.906; FY44: 123.906; FY45: 123.906; FY46: 123.906; FY47: 123.906; FY48: 123.906; FY49: 123.906; FY50: 123.906; FY51: 123.906; FY52: 123.906; FY53: 123.906; FY54: 123.906 | [13 empty] | 1.9034 | 114.3499 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012
75% | FY39: 14.0268; FY40: 14.0268; FY41: 14.0268; FY42: 14.0268; FY43: 14.0268; FY44: 14.0268; FY45: 14.0268; FY46: 14.0268; FY47: 14.0268; FY48: 14.0268; FY49: 14.0268; FY50: 14.0268; FY51: 14.0268; FY52: 14.0268; FY53: 14.0268; FY54: 14.0268 | [14 empty] | 8.1965 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543
70% | [45 empty] | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.579 | 16.2596 | 23.0251 | 92.3724 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5252 | 16.3764 | 57.8662 | 87.9675 | 302.3837 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8053 | 11.3817 | 16.1175 | 64.6606 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75755 | 4.9129 | 17.3599 | 26.3903 | 90.7151 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8074 |  | 1.0465 | 2.4299 | 3.6562 | 5.5826 | 7.3244 | 9.7372 | 12.2523 | 14.3089 | 16.2493 | 19.1244 | 21.2176 | 23.3262 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585
98% | [6 empty] | 0.74738 | 2.4434 | 4.438 | 6.3075 | 8.2716 | 11.6066 | 12.7474 | 14.887 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 |  | 2.9004 |  | 1.394 | 4.133 | 6.5608 | 10.3749 | 13.8236 | 18.6006 | 23.5803 | 27.6522 | 31.4939 | 37.1864 | 41.3307 | 45.5054 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253
97% | [6 empty] | 0.39733 | 2.0762 | 4.0505 | 5.901 | 7.8452 | 11.1463 | 12.2755 | 14.3934 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 |  | 3.2791 |  | 1.0424 | 5.1091 | 8.7139 | 14.377 | 19.4975 | 26.5902 | 33.984 | 40.0298 | 45.7339 | 54.186 | 60.3393 | 66.5378 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003
95% | [6 empty] | 0.035295 | 1.5253 | 3.4692 | 5.2912 | 7.2055 | 10.4559 | 11.5677 | 13.653 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 |  | 3.3435 |  | 0.12801 | 6.9473 | 14.046 | 25.1978 | 35.2812 | 49.2485 | 63.8085 | 75.7141 | 86.9468 | 103.5909 | 115.7082 | 127.9146 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376
90% | [7 empty] | 3.2862 | 19.0165 | 34.8166 | 51.4168 | 79.6038 | 89.2455 | 107.3285 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 |  | 0.10086 |  |  | 1.5629 | 9.2325 | 25.3503 | 39.924 | 60.1111 | 81.1549 | 98.3621 | 114.597 | 138.6529 | 156.1661 | 173.8081 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486
85% | [8 empty] | 3.0403 | 16.5244 | 32.2272 | 58.8906 | 68.0111 | 85.1167 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | [5 empty] | 0.033792 | 14.391 | 40.3385 | 76.4086 | 114.0093 | 144.7549 | 173.7631 | 216.7459 | 248.0383 | 279.5608 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342
80% | [9 empty] | 1.6534 | 14.4863 | 42.4194 | 51.9742 | 69.8943 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | [7 empty] | 6.1039 | 32.3432 | 61.5391 | 85.4121 | 107.9362 | 141.311 | 165.6087 | 190.085 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984
75% | [10 empty] | 0.54907 | 31.0475 | 45.4087 | 72.3432 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | [8 empty] | 5.4335 | 33.3578 | 58.9878 | 83.1694 | 119.0005 | 145.0863 | 171.3638 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843
70% | [11 empty] | 6.2329 | 26.8094 | 94.4596 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | [9 empty] | 4.4864 | 30.5426 | 64.4749 | 114.7539 | 151.3582 | 188.2316 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27
65% | FY38: 8.7073; FY39: 49.3711; FY40: 49.3711; FY41: 49.3711; FY42: 49.3711; FY43: 49.3711; FY44: 49.3711; FY45: 49.3711; FY46: 49.3711; FY47: 49.3711; FY48: 49.3711; FY49: 49.3711; FY50: 49.3711; FY51: 49.3711; FY52: 49.3711; FY53: 49.3711; FY54: 49.3711 | [10 empty] | 0.026693 | 12.2235 | 63.759 | 106.3587 | 149.2717 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044
60% | [42 empty] | 9.6914 | 68.7248 | 170.7858 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674
55% | [44 empty] | 6.1944 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 9.3311 | 34.0146 | 70.4941 | 122.0016 | 251.4031 | 318.0395 | 480.783 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | E @ R (MWh) | 11.4313 | 0 | 3.611 | 20.1823 | 42.2433 | 95.2734 | 162.293 | 278.4728 | 428.1726 | 575.7911 | 736.588 | 1018.0024 | 1279.9369 | 1592.5853 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83
Option 5 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.826 | 6.5317 | 23.8102 | 49.3459 | 85.4011 | 175.9822 | 222.6276 | 336.5481 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 3.4294 | 0 | 1.0833 | 6.0547 | 12.673 | 28.582 | 48.6879 | 83.5419 | 128.4518 | 172.7373 | 220.9764 | 305.4007 | 383.9811 | 477.7756 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [10 empty] | 1.6282 | 5.0183 | 6.3216 | 10.6998 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | [10 empty] | 1.6076 | 5.0422 | 9.1555 | 10.5422 | 14.9768 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105
98% | [10 empty] | 0.5138 | 2.1918 | 2.8369 | 5.004 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | [10 empty] | 0.50361 | 2.2037 | 4.2396 | 4.926 | 7.121 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671
97% | [10 empty] | 0.42698 | 3.749 | 5.026 | 9.3162 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | [10 empty] | 0.40682 | 3.7724 | 7.803 | 9.1618 | 13.5073 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579
95% | [10 empty] | 0.01002 | 4.1955 | 6.0816 | 12.4178 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | [10 empty] | 0.0071007 | 4.2301 | 10.1829 | 12.1898 | 18.6077 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902
90% | [11 empty] | 1.105 | 2.6808 | 8.786 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | [11 empty] | 1.128 | 6.6325 | 8.5663 | 14.7502 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146
85% | [12 empty] | 0.078177 | 43.1723 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | [12 empty] | 19.8527 | 40.678 | 110.8742 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071
80% | FY38: 2.9762; FY39: 123.906; FY40: 123.906; FY41: 123.906; FY42: 123.906; FY43: 123.906; FY44: 123.906; FY45: 123.906; FY46: 123.906; FY47: 123.906; FY48: 123.906; FY49: 123.906; FY50: 123.906; FY51: 123.906; FY52: 123.906; FY53: 123.906; FY54: 123.906 | [13 empty] | 1.9034 | 114.3499 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012
75% | FY39: 14.0268; FY40: 14.0268; FY41: 14.0268; FY42: 14.0268; FY43: 14.0268; FY44: 14.0268; FY45: 14.0268; FY46: 14.0268; FY47: 14.0268; FY48: 14.0268; FY49: 14.0268; FY50: 14.0268; FY51: 14.0268; FY52: 14.0268; FY53: 14.0268; FY54: 14.0268 | [14 empty] | 8.1965 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543
70% | [45 empty] | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.579 | 16.2596 | 23.0251 | 92.3724 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5252 | 16.3764 | 57.8662 | 87.9675 | 302.3837 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8053 | 11.3817 | 16.1175 | 64.6606 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75755 | 4.9129 | 17.3599 | 26.3903 | 90.7151 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8074 |  | 1.0465 | 2.4299 | 3.6562 | 5.5826 | 7.3244 | 9.7372 | 12.2523 | 14.3089 | 16.2493 | 19.1244 | 21.2176 | 23.3262 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585
98% | [6 empty] | 0.74738 | 2.4434 | 4.438 | 6.3075 | 8.2716 | 11.6066 | 12.7474 | 14.887 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 |  | 2.9004 |  | 1.394 | 4.133 | 6.5608 | 10.3749 | 13.8236 | 18.6006 | 23.5803 | 27.6522 | 31.4939 | 37.1864 | 41.3307 | 45.5054 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253
97% | [6 empty] | 0.39733 | 2.0762 | 4.0505 | 5.901 | 7.8452 | 11.1463 | 12.2755 | 14.3934 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 |  | 3.2791 |  | 1.0424 | 5.1091 | 8.7139 | 14.377 | 19.4975 | 26.5902 | 33.984 | 40.0298 | 45.7339 | 54.186 | 60.3393 | 66.5378 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003
95% | [6 empty] | 0.035295 | 1.5253 | 3.4692 | 5.2912 | 7.2055 | 10.4559 | 11.5677 | 13.653 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 |  | 3.3435 |  | 0.12801 | 6.9473 | 14.046 | 25.1978 | 35.2812 | 49.2485 | 63.8085 | 75.7141 | 86.9468 | 103.5909 | 115.7082 | 127.9146 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376
90% | [7 empty] | 3.2862 | 19.0165 | 34.8166 | 51.4168 | 79.6038 | 89.2455 | 107.3285 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 |  | 0.10086 |  |  | 1.5629 | 9.2325 | 25.3503 | 39.924 | 60.1111 | 81.1549 | 98.3621 | 114.597 | 138.6529 | 156.1661 | 173.8081 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486
85% | [8 empty] | 3.0403 | 16.5244 | 32.2272 | 58.8906 | 68.0111 | 85.1167 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | [5 empty] | 0.033792 | 14.391 | 40.3385 | 76.4086 | 114.0093 | 144.7549 | 173.7631 | 216.7459 | 248.0383 | 279.5608 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342
80% | [9 empty] | 1.6534 | 14.4863 | 42.4194 | 51.9742 | 69.8943 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | [7 empty] | 6.1039 | 32.3432 | 61.5391 | 85.4121 | 107.9362 | 141.311 | 165.6087 | 190.085 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984
75% | [10 empty] | 0.54907 | 31.0475 | 45.4087 | 72.3432 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | [8 empty] | 5.4335 | 33.3578 | 58.9878 | 83.1694 | 119.0005 | 145.0863 | 171.3638 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843
70% | [11 empty] | 6.2329 | 26.8094 | 94.4596 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | [9 empty] | 4.4864 | 30.5426 | 64.4749 | 114.7539 | 151.3582 | 188.2316 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27
65% | FY38: 8.7073; FY39: 49.3711; FY40: 49.3711; FY41: 49.3711; FY42: 49.3711; FY43: 49.3711; FY44: 49.3711; FY45: 49.3711; FY46: 49.3711; FY47: 49.3711; FY48: 49.3711; FY49: 49.3711; FY50: 49.3711; FY51: 49.3711; FY52: 49.3711; FY53: 49.3711; FY54: 49.3711 | [10 empty] | 0.026693 | 12.2235 | 63.759 | 106.3587 | 149.2717 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044
60% | [42 empty] | 9.6914 | 68.7248 | 170.7858 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674
55% | [44 empty] | 6.1944 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 9.3311 | 34.0146 | 70.4941 | 122.0016 | 251.4031 | 318.0395 | 480.783 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | E @ R (MWh) | 11.4313 | 0 | 3.611 | 20.1823 | 42.2433 | 95.2734 | 162.293 | 278.4728 | 428.1726 | 575.7911 | 736.588 | 1018.0024 | 1279.9369 | 1592.5853 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83
Option 6 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.826 | 6.5317 | 23.8102 | 49.3459 | 85.4011 | 175.9822 | 222.6276 | 336.5481 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 3.4294 | 0 | 1.0833 | 6.0547 | 12.673 | 28.582 | 48.6879 | 83.5419 | 128.4518 | 172.7373 | 220.9764 | 305.4007 | 383.9811 | 477.7756 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [10 empty] | 1.6282 | 5.0183 | 6.3216 | 10.6998 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | [10 empty] | 1.6076 | 5.0422 | 9.1555 | 10.5422 | 14.9768 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105
98% | [10 empty] | 0.5138 | 2.1918 | 2.8369 | 5.004 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | [10 empty] | 0.50361 | 2.2037 | 4.2396 | 4.926 | 7.121 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671
97% | [10 empty] | 0.42698 | 3.749 | 5.026 | 9.3162 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | [10 empty] | 0.40682 | 3.7724 | 7.803 | 9.1618 | 13.5073 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579
95% | [10 empty] | 0.01002 | 4.1955 | 6.0816 | 12.4178 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | [10 empty] | 0.0071007 | 4.2301 | 10.1829 | 12.1898 | 18.6077 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902
90% | [11 empty] | 1.105 | 2.6808 | 8.786 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | [11 empty] | 1.128 | 6.6325 | 8.5663 | 14.7502 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146
85% | [12 empty] | 0.078177 | 43.1723 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | [12 empty] | 19.8527 | 40.678 | 110.8742 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071
80% | FY38: 2.9762; FY39: 123.906; FY40: 123.906; FY41: 123.906; FY42: 123.906; FY43: 123.906; FY44: 123.906; FY45: 123.906; FY46: 123.906; FY47: 123.906; FY48: 123.906; FY49: 123.906; FY50: 123.906; FY51: 123.906; FY52: 123.906; FY53: 123.906; FY54: 123.906 | [13 empty] | 1.9034 | 114.3499 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012
75% | FY39: 14.0268; FY40: 14.0268; FY41: 14.0268; FY42: 14.0268; FY43: 14.0268; FY44: 14.0268; FY45: 14.0268; FY46: 14.0268; FY47: 14.0268; FY48: 14.0268; FY49: 14.0268; FY50: 14.0268; FY51: 14.0268; FY52: 14.0268; FY53: 14.0268; FY54: 14.0268 | [14 empty] | 8.1965 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543
70% | [45 empty] | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.579 | 16.2596 | 23.0251 | 92.3724 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5252 | 16.3764 | 57.8662 | 87.9675 | 302.3837 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8053 | 11.3817 | 16.1175 | 64.6606 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75755 | 4.9129 | 17.3599 | 26.3903 | 90.7151 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8074 |  | 1.0465 | 2.4299 | 3.6562 | 5.5826 | 7.3244 | 9.7372 | 12.2523 | 14.3089 | 16.2493 | 19.1244 | 21.2176 | 23.3262 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585
98% | [6 empty] | 0.74738 | 2.4434 | 4.438 | 6.3075 | 8.2716 | 11.6066 | 12.7474 | 14.887 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 |  | 2.9004 |  | 1.394 | 4.133 | 6.5608 | 10.3749 | 13.8236 | 18.6006 | 23.5803 | 27.6522 | 31.4939 | 37.1864 | 41.3307 | 45.5054 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253
97% | [6 empty] | 0.39733 | 2.0762 | 4.0505 | 5.901 | 7.8452 | 11.1463 | 12.2755 | 14.3934 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 |  | 3.2791 |  | 1.0424 | 5.1091 | 8.7139 | 14.377 | 19.4975 | 26.5902 | 33.984 | 40.0298 | 45.7339 | 54.186 | 60.3393 | 66.5378 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003
95% | [6 empty] | 0.035295 | 1.5253 | 3.4692 | 5.2912 | 7.2055 | 10.4559 | 11.5677 | 13.653 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 |  | 3.3435 |  | 0.12801 | 6.9473 | 14.046 | 25.1978 | 35.2812 | 49.2485 | 63.8085 | 75.7141 | 86.9468 | 103.5909 | 115.7082 | 127.9146 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376
90% | [7 empty] | 3.2862 | 19.0165 | 34.8166 | 51.4168 | 79.6038 | 89.2455 | 107.3285 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 |  | 0.10086 |  |  | 1.5629 | 9.2325 | 25.3503 | 39.924 | 60.1111 | 81.1549 | 98.3621 | 114.597 | 138.6529 | 156.1661 | 173.8081 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486
85% | [8 empty] | 3.0403 | 16.5244 | 32.2272 | 58.8906 | 68.0111 | 85.1167 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | [5 empty] | 0.033792 | 14.391 | 40.3385 | 76.4086 | 114.0093 | 144.7549 | 173.7631 | 216.7459 | 248.0383 | 279.5608 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342
80% | [9 empty] | 1.6534 | 14.4863 | 42.4194 | 51.9742 | 69.8943 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | [7 empty] | 6.1039 | 32.3432 | 61.5391 | 85.4121 | 107.9362 | 141.311 | 165.6087 | 190.085 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984
75% | [10 empty] | 0.54907 | 31.0475 | 45.4087 | 72.3432 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | [8 empty] | 5.4335 | 33.3578 | 58.9878 | 83.1694 | 119.0005 | 145.0863 | 171.3638 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843
70% | [11 empty] | 6.2329 | 26.8094 | 94.4596 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | [9 empty] | 4.4864 | 30.5426 | 64.4749 | 114.7539 | 151.3582 | 188.2316 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27
65% | FY38: 8.7073; FY39: 49.3711; FY40: 49.3711; FY41: 49.3711; FY42: 49.3711; FY43: 49.3711; FY44: 49.3711; FY45: 49.3711; FY46: 49.3711; FY47: 49.3711; FY48: 49.3711; FY49: 49.3711; FY50: 49.3711; FY51: 49.3711; FY52: 49.3711; FY53: 49.3711; FY54: 49.3711 | [10 empty] | 0.026693 | 12.2235 | 63.759 | 106.3587 | 149.2717 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044
60% | [42 empty] | 9.6914 | 68.7248 | 170.7858 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674
55% | [44 empty] | 6.1944 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 9.3311 | 34.0146 | 70.4941 | 122.0016 | 251.4031 | 318.0395 | 480.783 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | E @ R (MWh) | 11.4313 | 0 | 3.611 | 20.1823 | 42.2433 | 95.2734 | 162.293 | 278.4728 | 428.1726 | 575.7911 | 736.588 | 1018.0024 | 1279.9369 | 1592.5853 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83
Option 7 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.826 | 6.5317 | 23.8102 | 49.3459 | 85.4011 | 175.9822 | 222.6276 | 336.5481 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 3.4294 | 0 | 1.0833 | 6.0547 | 12.673 | 28.582 | 48.6879 | 83.5419 | 128.4518 | 172.7373 | 220.9764 | 305.4007 | 383.9811 | 477.7756 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | [10 empty] | 1.6282 | 5.0183 | 6.3216 | 10.6998 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | 15.2274 | [10 empty] | 1.6076 | 5.0422 | 9.1555 | 10.5422 | 14.9768 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105 | 19.1105
98% | [10 empty] | 0.5138 | 2.1918 | 2.8369 | 5.004 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | 7.245 | [10 empty] | 0.50361 | 2.2037 | 4.2396 | 4.926 | 7.121 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671 | 9.1671
97% | [10 empty] | 0.42698 | 3.749 | 5.026 | 9.3162 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | 13.7528 | [10 empty] | 0.40682 | 3.7724 | 7.803 | 9.1618 | 13.5073 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579 | 17.5579
95% | [10 empty] | 0.01002 | 4.1955 | 6.0816 | 12.4178 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | 18.9703 | [10 empty] | 0.0071007 | 4.2301 | 10.1829 | 12.1898 | 18.6077 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902 | 24.5902
90% | [11 empty] | 1.105 | 2.6808 | 8.786 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | 15.0996 | [11 empty] | 1.128 | 6.6325 | 8.5663 | 14.7502 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146 | 20.5146
85% | [12 empty] | 0.078177 | 43.1723 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | 114.8402 | [12 empty] | 19.8527 | 40.678 | 110.8742 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071 | 176.3071
80% | FY38: 2.9762; FY39: 123.906; FY40: 123.906; FY41: 123.906; FY42: 123.906; FY43: 123.906; FY44: 123.906; FY45: 123.906; FY46: 123.906; FY47: 123.906; FY48: 123.906; FY49: 123.906; FY50: 123.906; FY51: 123.906; FY52: 123.906; FY53: 123.906; FY54: 123.906 | [13 empty] | 1.9034 | 114.3499 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012 | 272.012
75% | FY39: 14.0268; FY40: 14.0268; FY41: 14.0268; FY42: 14.0268; FY43: 14.0268; FY44: 14.0268; FY45: 14.0268; FY46: 14.0268; FY47: 14.0268; FY48: 14.0268; FY49: 14.0268; FY50: 14.0268; FY51: 14.0268; FY52: 14.0268; FY53: 14.0268; FY54: 14.0268 | [14 empty] | 8.1965 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543 | 290.543
70% | [45 empty] | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469 | 0.35469
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.579 | 16.2596 | 23.0251 | 92.3724 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | 323.0682 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5252 | 16.3764 | 57.8662 | 87.9675 | 302.3837 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571 | 830.1571
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8053 | 11.3817 | 16.1175 | 64.6606 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | 226.1477 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75755 | 4.9129 | 17.3599 | 26.3903 | 90.7151 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471 | 249.0471
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8074 |  | 1.0465 | 2.4299 | 3.6562 | 5.5826 | 7.3244 | 9.7372 | 12.2523 | 14.3089 | 16.2493 | 19.1244 | 21.2176 | 23.3262 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585 | 25.5585
98% | [6 empty] | 0.74738 | 2.4434 | 4.438 | 6.3075 | 8.2716 | 11.6066 | 12.7474 | 14.887 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 | 16.5255 |  | 2.9004 |  | 1.394 | 4.133 | 6.5608 | 10.3749 | 13.8236 | 18.6006 | 23.5803 | 27.6522 | 31.4939 | 37.1864 | 41.3307 | 45.5054 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253 | 49.9253
97% | [6 empty] | 0.39733 | 2.0762 | 4.0505 | 5.901 | 7.8452 | 11.1463 | 12.2755 | 14.3934 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 | 16.0153 |  | 3.2791 |  | 1.0424 | 5.1091 | 8.7139 | 14.377 | 19.4975 | 26.5902 | 33.984 | 40.0298 | 45.7339 | 54.186 | 60.3393 | 66.5378 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003 | 73.1003
95% | [6 empty] | 0.035295 | 1.5253 | 3.4692 | 5.2912 | 7.2055 | 10.4559 | 11.5677 | 13.653 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 | 15.25 |  | 3.3435 |  | 0.12801 | 6.9473 | 14.046 | 25.1978 | 35.2812 | 49.2485 | 63.8085 | 75.7141 | 86.9468 | 103.5909 | 115.7082 | 127.9146 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376 | 140.8376
90% | [7 empty] | 3.2862 | 19.0165 | 34.8166 | 51.4168 | 79.6038 | 89.2455 | 107.3285 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 | 121.1774 |  | 0.10086 |  |  | 1.5629 | 9.2325 | 25.3503 | 39.924 | 60.1111 | 81.1549 | 98.3621 | 114.597 | 138.6529 | 156.1661 | 173.8081 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486 | 192.486
85% | [8 empty] | 3.0403 | 16.5244 | 32.2272 | 58.8906 | 68.0111 | 85.1167 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | 98.217 | [5 empty] | 0.033792 | 14.391 | 40.3385 | 76.4086 | 114.0093 | 144.7549 | 173.7631 | 216.7459 | 248.0383 | 279.5608 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342 | 312.9342
80% | [9 empty] | 1.6534 | 14.4863 | 42.4194 | 51.9742 | 69.8943 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | 83.6184 | [7 empty] | 6.1039 | 32.3432 | 61.5391 | 85.4121 | 107.9362 | 141.311 | 165.6087 | 190.085 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984 | 215.9984
75% | [10 empty] | 0.54907 | 31.0475 | 45.4087 | 72.3432 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | 92.9709 | [8 empty] | 5.4335 | 33.3578 | 58.9878 | 83.1694 | 119.0005 | 145.0863 | 171.3638 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843 | 199.1843
70% | [11 empty] | 6.2329 | 26.8094 | 94.4596 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | 149.9382 | [9 empty] | 4.4864 | 30.5426 | 64.4749 | 114.7539 | 151.3582 | 188.2316 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27 | 227.27
65% | FY38: 8.7073; FY39: 49.3711; FY40: 49.3711; FY41: 49.3711; FY42: 49.3711; FY43: 49.3711; FY44: 49.3711; FY45: 49.3711; FY46: 49.3711; FY47: 49.3711; FY48: 49.3711; FY49: 49.3711; FY50: 49.3711; FY51: 49.3711; FY52: 49.3711; FY53: 49.3711; FY54: 49.3711 | [10 empty] | 0.026693 | 12.2235 | 63.759 | 106.3587 | 149.2717 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044 | 194.7044
60% | [42 empty] | 9.6914 | 68.7248 | 170.7858 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674 | 284.3674
55% | [44 empty] | 6.1944 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637 | 53.4637
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 9.3311 | 34.0146 | 70.4941 | 122.0016 | 251.4031 | 318.0395 | 480.783 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | 643.0837 | E @ R (MWh) | 11.4313 | 0 | 3.611 | 20.1823 | 42.2433 | 95.2734 | 162.293 | 278.4728 | 428.1726 | 575.7911 | 736.588 | 1018.0024 | 1279.9369 | 1592.5853 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83 | 1969.83
Option 8 Summer POE50 W E @ R (MWh) N 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.826 | 6.5317 | 23.8102 | 49.3459 | 85.4011 | 175.9822 | 222.6276 | 336.5481 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | 450.1586 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 3.4294 | 0 | 1.0833 | 6.0547 | 12.673 | 28.582 | 48.6879 | 83.5419 | 128.4518 | 172.7373 | 220.9764 | 305.4007 | 383.9811 | 477.7756 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949 | 590.949

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.7244 | 4.29 | 6.3831 | 9.0539 | 11.6398 | 13.9431 | 17.1001 | 20.5496 | 24.082 | 27.5821 | 30.6942 | 34.0844 | 35.3876 | 39.7658 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 |  | 10.3325 | 6.9085 | 9.1195 | 11.823 | 14.3438 | 17.0271 | 19.8475 | 23.8643 | 27.3684 | 30.6736 | 34.1083 | 38.2215 | 39.6082 | 44.0428 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765
98% | 3.6773 | 1.9774 | 3.0134 | 4.3354 | 5.6153 | 6.7554 | 8.318 | 10.0255 | 11.7739 | 13.5064 | 15.0468 | 16.7248 | 17.3699 | 19.537 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 |  | 4.9683 | 3.2735 | 4.3679 | 5.706 | 6.9538 | 8.2819 | 9.6779 | 11.6662 | 13.4006 | 15.0366 | 16.7367 | 18.7726 | 19.459 | 21.654 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001
97% | 6.9849 | 3.6195 | 5.6706 | 8.2877 | 10.8216 | 13.0786 | 16.1721 | 19.5523 | 23.0137 | 26.4434 | 29.493 | 32.815 | 34.0921 | 38.3822 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 |  | 9.5406 | 6.1854 | 8.352 | 11.0011 | 13.4713 | 16.1006 | 18.8643 | 22.8004 | 26.234 | 29.4728 | 32.8384 | 36.869 | 38.2278 | 42.5733 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239
95% | 9.6454 | 4.675 | 7.7042 | 11.5696 | 15.3119 | 18.6453 | 23.2142 | 28.2065 | 33.3188 | 38.3841 | 42.8881 | 47.7945 | 49.6806 | 56.0169 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 |  | 13.4199 | 8.4646 | 11.6645 | 15.577 | 19.2253 | 23.1085 | 27.1904 | 33.0036 | 38.0749 | 42.8584 | 47.8291 | 53.7819 | 55.7888 | 62.2068 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892
90% | 7.7042 | 2.915 | 5.8338 | 9.5582 | 13.1641 | 16.3759 | 20.7783 | 25.5886 | 30.5145 | 35.3952 | 39.735 | 44.4624 | 46.2798 | 52.385 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 |  | 11.3411 | 6.5665 | 9.6497 | 13.4196 | 16.9348 | 20.6765 | 24.6095 | 30.2108 | 35.0972 | 39.7063 | 44.4958 | 50.2316 | 52.1653 | 58.3493 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136
85% | 59.1725 | 6.5594 | 37.941 | 80.2181 | 121.15 | 157.6086 | 207.5815 | 262.1847 | 318.1 | 373.5026 | 422.7651 | 476.4282 | 497.0576 | 566.3606 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 |  | 100.4564 | 46.2576 | 81.2564 | 124.05 | 163.9527 | 206.4256 | 251.0706 | 314.6534 | 370.1203 | 422.4394 | 476.8066 | 541.9157 | 563.8663 | 634.0625 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954
80% | 66.1755 |  | 19.1279 | 116.8852 | 215.5116 | 303.3595 | 423.7706 | 555.3382 | 690.0675 | 823.5613 | 942.2604 | 1071.5629 | 1121.27 | 1288.2572 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 |  | 165.6499 | 35.3125 | 119.3871 | 222.4994 | 318.6459 | 420.9852 | 528.5585 | 681.7629 | 815.4116 | 941.4757 | 1072.4748 | 1229.3566 | 1282.2472 | 1451.3867 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488
75% | 10.2262 |  |  | 93.5568 | 377.4509 | 633.9922 | 985.6274 | 1369.8429 | 1763.2916 | 2153.1324 | 2499.7681 | 2877.3687 | 3022.528 | 3510.1789 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 |  | 231.8404 |  | 99.7224 | 397.8571 | 678.6328 | 977.4934 | 1291.6386 | 1739.0397 | 2129.3327 | 2497.4763 | 2880.0318 | 3338.1721 | 3492.628 | 3986.5643 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834
70% |  |  |  |  | 212.4458 | 755.5237 | 1520.3879 | 2356.1194 | 3211.9346 | 4059.9021 | 4813.8914 | 5635.2347 | 5950.9798 | 7011.7001 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 |  | 33.4714 |  |  | 249.167 | 852.6245 | 1502.6951 | 2186.0122 | 3159.1828 | 4008.134 | 4808.9065 | 5641.0272 | 6637.5573 | 6973.5242 | 8047.9163 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033
65% | [5 empty] | 124.667 | 854.8962 | 1742.9773 | 2652.4003 | 3553.4839 | 4354.7027 | 5227.4943 | 5563.0175 | 6690.1807 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | [5 empty] | 188.8845 | 836.0951 | 1562.2148 | 2596.3441 | 3498.4731 | 4349.4055 | 5233.6497 | 6292.6018 | 6649.6135 | 7791.3048 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242
60% | [6 empty] | 108.2178 | 882.8726 | 1815.9042 | 2740.38 | 3562.3985 | 4457.8479 | 4802.0813 | 5958.5057 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | [6 empty] | 99.1317 | 697.4174 | 1758.3928 | 2683.9411 | 3556.9639 | 4464.1631 | 5550.6057 | 5916.8854 | 7088.2151 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618
55% | [7 empty] | 77.7648 | 878.2155 | 1956.2796 | 2914.8646 | 3959.0799 | 4360.5028 | 5709.0504 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | [7 empty] | 20.0065 | 811.1494 | 1890.4642 | 2908.5271 | 3966.4443 | 5233.3836 | 5660.5155 | 7026.4447 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859
50% | [8 empty] | 11.6315 | 564.915 | 1570.6907 | 2710.1367 | 3148.1687 | 4619.7015 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | [8 empty] | 4.4119 | 509.0069 | 1563.7752 | 2718.1727 | 4100.6547 | 4566.7403 | 6057.2399 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986
45% | [10 empty] | 132.5918 | 960.492 | 1458.8799 | 3249.0414 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | [10 empty] | 129.8083 | 968.7958 | 2617.6063 | 3184.6126 | 4997.8477 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419
40% | [12 empty] | 1.595 | 904.5952 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | [12 empty] | 405.0509 | 845.1405 | 3175.0768 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163
35% | FY39: 23.8357; FY40: 23.8357; FY41: 23.8357; FY42: 23.8357; FY43: 23.8357; FY44: 23.8357; FY45: 23.8357; FY46: 23.8357; FY47: 23.8357; FY48: 23.8357; FY49: 23.8357; FY50: 23.8357; FY51: 23.8357; FY52: 23.8357; FY53: 23.8357; FY54: 23.8357 | [14 empty] | 13.9282 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 171.3105 | 24.0364 | 85.674 | 333.4649 | 983.111 | 2043.9492 | 4186.0642 | 7351.0223 | 11464.2481 | 16366.4681 | 21371.7903 | 27551.5264 | 30108.8907 | 39713.6588 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | E @ R (MWh) | 581.0205 | 112.9686 | 343.5196 | 1051.1003 | 2273.6695 | 4128.0206 | 6637.1083 | 11186.4823 | 16045.0591 | 21336.5256 | 27597.5743 | 36144.7813 | 39341.0228 | 50498.8132 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421
Option 1 Winter POE50 W E @ R (MWh) N 2 | 119.9174 | 16.8255 | 59.9718 | 233.4254 | 688.1777 | 1430.7644 | 2930.2449 | 5145.7156 | 8024.9736 | 11456.5276 | 14960.2532 | 19286.0685 | 21076.2235 | 27799.5611 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 174.3061 | 33.8906 | 103.0559 | 315.3301 | 682.1008 | 1238.4062 | 1991.1325 | 3355.9447 | 4813.5177 | 6400.9577 | 8279.2723 | 10843.4344 | 11802.3068 | 15149.644 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.6735 | 16.2619 | 17.9127 | 19.2961 | 20.5223 | 22.4487 | 24.1905 | 26.6033 | 29.1184 | 31.175 | 33.1154 | 35.9906 | 38.0837 | 40.1923 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247
98% | 13.2169 | 10.7854 | 12.2301 | 13.3759 | 14.7319 | 16.1299 | 17.6135 | 19.3096 | 21.3042 | 23.1736 | 25.1377 | 28.4728 | 29.6135 | 31.7531 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 |  | 36.6327 | 31.8578 | 35.1263 | 37.8652 | 40.2931 | 44.1071 | 47.5558 | 52.3328 | 57.3126 | 61.3844 | 65.2262 | 70.9187 | 75.063 | 79.2377 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576
97% | 12.9115 | 10.5047 | 11.9347 | 13.0688 | 14.4111 | 15.7949 | 17.2635 | 18.9423 | 20.9166 | 22.7671 | 24.7113 | 28.0125 | 29.1417 | 31.2595 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 |  | 53.8775 | 46.7879 | 51.6408 | 55.7075 | 59.3123 | 64.9753 | 70.0958 | 77.1886 | 84.5824 | 90.6281 | 96.3323 | 104.7844 | 110.9376 | 117.1362 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987
95% | 12.4534 | 10.0836 | 11.4916 | 12.6083 | 13.93 | 15.2924 | 16.7384 | 18.3914 | 20.3354 | 22.1574 | 24.0716 | 27.322 | 28.4339 | 30.5191 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 |  | 104.5403 | 90.5793 | 100.1358 | 108.1441 | 115.2428 | 126.3946 | 136.478 | 150.4453 | 165.0053 | 176.9108 | 188.1436 | 204.7877 | 216.905 | 229.1113 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344
90% | 102.4598 | 81.9097 | 94.1198 | 103.8034 | 115.2646 | 127.0798 | 139.619 | 153.9538 | 170.8116 | 186.6118 | 203.2119 | 231.399 | 241.0406 | 259.1237 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 |  | 145.5592 | 125.3812 | 139.1933 | 150.7678 | 161.0276 | 177.1454 | 191.7192 | 211.9063 | 232.95 | 250.1572 | 266.3921 | 290.448 | 307.9613 | 325.6033 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811
85% | 88.7163 | 69.277 | 80.8271 | 89.9872 | 100.8289 | 112.0055 | 123.8669 | 137.4268 | 153.3734 | 168.3195 | 184.0224 | 210.6858 | 219.8063 | 236.9119 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 |  | 244.5846 | 208.5309 | 233.2102 | 253.8913 | 272.2235 | 301.0225 | 327.0627 | 363.1327 | 400.7334 | 431.4791 | 460.4873 | 503.4701 | 534.7625 | 566.285 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584
80% | 83.3031 | 62.9381 | 75.0382 | 84.6345 | 95.9925 | 107.7013 | 120.1275 | 134.3332 | 151.0391 | 166.697 | 183.1476 | 211.0806 | 220.6354 | 238.5556 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 |  | 176.4199 | 148.4252 | 167.588 | 183.6462 | 197.8806 | 220.2422 | 240.4616 | 268.469 | 297.6648 | 321.5379 | 344.0619 | 377.4368 | 401.7344 | 426.2108 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242
75% | 108.852 | 78.2428 | 96.4297 | 110.8532 | 127.9246 | 145.5233 | 164.2003 | 185.5518 | 210.6613 | 234.1955 | 258.9213 | 300.9056 | 315.2667 | 342.2012 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 |  | 173.0481 | 142.9932 | 163.5662 | 180.8063 | 196.0882 | 220.0955 | 241.8029 | 271.8714 | 303.2159 | 328.8458 | 353.0275 | 388.8585 | 414.9443 | 441.2219 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423
70% | 242.705 | 160.3811 | 209.295 | 248.0873 | 294.0011 | 341.3328 | 391.565 | 448.9902 | 516.5227 | 579.8184 | 646.3187 | 759.2361 | 797.8606 | 870.3014 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 |  | 216.7103 | 174.5365 | 203.4051 | 227.5968 | 249.0408 | 282.7284 | 313.1888 | 355.3817 | 399.365 | 435.3296 | 469.262 | 519.541 | 556.1452 | 593.0186 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057
65% | 239.9449 | 133.3064 | 196.6672 | 246.9168 | 306.3914 | 367.7027 | 432.771 | 507.1569 | 594.6353 | 676.6255 | 762.7668 | 909.0346 | 959.067 | 1052.9034 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 |  | 217.3105 | 168.2289 | 201.826 | 229.9801 | 254.9365 | 294.1419 | 329.5915 | 378.6953 | 429.8828 | 471.7382 | 511.2284 | 569.7428 | 612.3426 | 655.2556 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882
60% | 573.2972 | 175.3008 | 411.757 | 599.321 | 821.318 | 1050.171 | 1293.0474 | 1570.7031 | 1897.2283 | 2203.2682 | 2524.8027 | 3070.7675 | 3257.5203 | 3607.7777 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 |  | 442.0796 | 319.3756 | 403.3682 | 473.7535 | 536.1444 | 634.158 | 722.782 | 845.5415 | 973.5103 | 1078.1488 | 1176.8743 | 1323.1602 | 1429.6596 | 1536.9421 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237
55% | 381.0194 |  | 136.1535 | 430.9394 | 863.9541 | 1310.3415 | 1784.0823 | 2325.6616 | 2962.563 | 3559.5068 | 4186.6736 | 5251.6012 | 5615.8706 | 6299.0625 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 |  | 286.4051 | 177.6985 | 252.1097 | 314.4659 | 369.7396 | 456.5724 | 535.0867 | 643.8425 | 757.2134 | 849.9153 | 937.3788 | 1066.9773 | 1161.3279 | 1256.3723 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971
50% |  |  |  | 0.14412 | 203.1188 | 781.1825 | 1629.226 | 2603.733 | 3749.7605 | 4823.8893 | 5952.4007 | 7868.6101 | 8524.0692 | 9753.3911 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 |  | 360.2162 | 119.9202 | 283.539 | 422.9541 | 546.5343 | 740.6737 | 916.215 | 1159.3697 | 1412.8427 | 1620.1043 | 1815.654 | 2105.4085 | 2316.3562 | 2528.8551 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307
45% | [6 empty] | 148.0142 | 781.2185 | 1972.306 | 3126.2423 | 4338.6019 | 6397.1855 | 7101.3451 | 8422.0054 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 |  | 138.3055 |  | 53.4493 | 235.0575 | 492.2929 | 953.0292 | 1369.6278 | 1946.6883 | 2548.2366 | 3040.1146 | 3504.1977 | 4191.8501 | 4692.4761 | 5196.7834 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008
40% | [8 empty] | 179.4633 | 1063.2321 | 2671.8859 | 5729.7119 | 6775.6727 | 8737.3855 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | [5 empty] | 0.49049 | 208.8808 | 693.0821 | 1679.0967 | 2739.4369 | 3606.4631 | 4424.4955 | 5636.61 | 6519.0562 | 7407.9911 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194
35% | [10 empty] | 22.7176 | 1374.291 | 2264.6059 | 4352.5967 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | [8 empty] | 95.7648 | 640.6468 | 1398.5353 | 2223.4418 | 3445.7422 | 4335.6039 | 5232.0089 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458
30% | FY38: 27.4824; FY39: 155.8275; FY40: 155.8275; FY41: 155.8275; FY42: 155.8275; FY43: 155.8275; FY44: 155.8275; FY45: 155.8275; FY46: 155.8275; FY47: 155.8275; FY48: 155.8275; FY49: 155.8275; FY50: 155.8275; FY51: 155.8275; FY52: 155.8275; FY53: 155.8275; FY54: 155.8275 | [10 empty] | 0.49093 | 224.8097 | 1238.6494 | 2424.2493 | 3908.703 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712
25% | [44 empty] | 61.4871 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1858.8794 | 792.7296 | 1335.9441 | 1953.7399 | 2971.8672 | 4390.2575 | 6278.1349 | 8905.3721 | 12620.9206 | 16856.5044 | 22009.3916 | 32398.316 | 36379.9495 | 44293.2304 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | E @ R (MWh) | 2614.363 | 1770.577 | 2306.0705 | 2893.9325 | 3511.7693 | 4746.6157 | 6158.9404 | 8526.3297 | 11471.7175 | 14192.9586 | 17094.1285 | 22074.3763 | 26147.6089 | 30602.4157 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504
Option 1 Summer POE50 W E @ R (MWh) N 2 | 1301.2156 | 554.9107 | 935.1608 | 1367.6179 | 2080.307 | 3073.1803 | 4394.6944 | 6233.7605 | 8834.6444 | 11799.5531 | 15406.5742 | 22678.8212 | 25465.9646 | 31005.2613 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 784.3089 | 531.1731 | 691.8211 | 868.1798 | 1053.5308 | 1423.9847 | 1847.6821 | 2557.8989 | 3441.5153 | 4257.8876 | 5128.2385 | 6622.3129 | 7844.2827 | 9180.7247 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.7244 | 4.29 | 6.3831 | 3.3368 | 5.9227 | 8.2259 | 11.383 | 14.8325 | 18.3649 | 21.865 | 24.9771 | 28.3672 | 29.6705 | 34.0487 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 | 38.5763 |  | 10.3325 | 6.9085 | 9.1195 | 6.1059 | 8.6267 | 11.3099 | 14.1304 | 18.1472 | 21.6513 | 24.9565 | 28.3912 | 32.5044 | 33.8911 | 38.3257 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594 | 42.4594
98% | 3.6773 | 1.9774 | 3.0134 | 1.5056 | 2.7855 | 3.9256 | 5.4882 | 7.1957 | 8.9441 | 10.6765 | 12.217 | 13.895 | 14.5401 | 16.7072 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 | 18.9482 |  | 4.9683 | 3.2735 | 4.3679 | 2.8762 | 4.124 | 5.4521 | 6.8481 | 8.8363 | 10.5708 | 12.2068 | 13.9068 | 15.9428 | 16.6292 | 18.8242 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703 | 20.8703
97% | 6.9849 | 3.6195 | 5.6706 | 2.6855 | 5.2194 | 7.4764 | 10.5699 | 13.9501 | 17.4115 | 20.8412 | 23.8908 | 27.2128 | 28.4899 | 32.7801 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 | 37.2166 |  | 9.5406 | 6.1854 | 8.352 | 5.3989 | 7.8691 | 10.4984 | 13.2621 | 17.1982 | 20.6318 | 23.8706 | 27.2362 | 31.2668 | 32.6256 | 36.9711 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217 | 41.0217
95% | 9.6454 | 4.675 | 7.7042 | 3.2955 | 7.0379 | 10.3713 | 14.9402 | 19.9325 | 25.0448 | 30.1101 | 34.6141 | 39.5205 | 41.4066 | 47.7429 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 | 54.2954 |  | 13.4199 | 8.4646 | 11.6645 | 7.303 | 10.9513 | 14.8345 | 18.9164 | 24.7296 | 29.8009 | 34.5844 | 39.5551 | 45.5079 | 47.5148 | 53.9328 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152 | 59.9152
90% | 7.7042 | 2.915 | 5.8338 | 1.5859 | 5.1918 | 8.4036 | 12.806 | 17.6162 | 22.5421 | 27.4228 | 31.7626 | 36.4901 | 38.3074 | 44.4127 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 | 50.7263 |  | 11.3411 | 6.5665 | 9.6497 | 5.4472 | 8.9625 | 12.7041 | 16.6371 | 22.2385 | 27.1249 | 31.7339 | 36.5234 | 42.2592 | 44.193 | 50.3769 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412 | 56.1412
85% | 59.1725 | 6.5594 | 37.941 | 0.32663 | 30.653 | 67.1116 | 117.0846 | 171.6877 | 227.6031 | 283.0057 | 332.2681 | 385.9312 | 406.5606 | 475.8636 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 | 547.5316 |  | 100.4564 | 46.2576 | 81.2564 | 33.5531 | 73.4558 | 115.9286 | 160.5737 | 224.1565 | 279.6234 | 331.9424 | 386.3097 | 451.4187 | 473.3694 | 543.5656 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985 | 608.9985
80% | 66.1755 |  | 19.1279 |  | 8.8783 | 85.3049 | 205.716 | 337.2836 | 472.0129 | 605.5068 | 724.2059 | 853.5083 | 903.2155 | 1070.2026 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 | 1242.8882 |  | 165.6499 | 35.3125 | 119.3871 | 12.5066 | 100.5913 | 202.9307 | 310.5039 | 463.7083 | 597.357 | 723.4211 | 854.4202 | 1011.302 | 1064.1926 | 1233.3321 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942 | 1390.9942
75% | 10.2262 |  |  |  |  | 32.1165 | 348.8449 | 733.0603 | 1126.509 | 1516.3498 | 1862.9855 | 2240.5862 | 2385.7455 | 2873.3963 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 | 3377.6884 |  | 231.8404 |  | 99.7224 |  | 58.0155 | 340.7109 | 654.8561 | 1102.2571 | 1492.5502 | 1860.6938 | 2243.2492 | 2701.3896 | 2855.8455 | 3349.7817 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009 | 3810.2009
70% | [6 empty] | 165.6608 | 971.0132 | 1826.8284 | 2674.7959 | 3428.7852 | 4250.1285 | 4565.8736 | 5626.594 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 | 6723.5117 |  | 33.4714 |  |  |  |  | 153.3704 | 800.9061 | 1774.0766 | 2623.0278 | 3423.8004 | 4255.921 | 5252.4511 | 5588.4181 | 6662.8101 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971 | 7664.2971
65% | [7 empty] | 284.098 | 1180.5319 | 2081.6156 | 2882.8343 | 3755.626 | 4091.1492 | 5218.3124 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | 6383.9404 | [7 empty] | 153.0989 | 1124.4758 | 2026.6047 | 2877.5372 | 3761.7814 | 4820.7335 | 5177.7452 | 6319.4365 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559 | 7383.6559
60% | [8 empty] | 324.8538 | 1230.3019 | 2052.3203 | 2947.7697 | 3292.0032 | 4448.4276 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | 5644.3154 | [8 empty] | 279.7659 | 1173.863 | 2046.8857 | 2954.0849 | 4040.5275 | 4406.8073 | 5578.137 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836 | 6669.9836
55% | [9 empty] | 282.1621 | 1153.9087 | 2198.1241 | 2599.547 | 3948.0946 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | 5342.6619 | [9 empty] | 240.7288 | 1147.5712 | 2205.4885 | 3472.4278 | 3899.5597 | 5265.4889 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301 | 6538.7301
50% | [10 empty] | 76.3904 | 793.2261 | 1226.6166 | 2698.1495 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | 4219.899 | [10 empty] | 74.2808 | 800.7325 | 2179.1027 | 2645.1883 | 4135.6879 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466 | 5525.0466
45% | [12 empty] | 29.3579 | 948.166 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | 2762.6703 | [12 empty] | 486.033 | 894.5814 | 2660.2251 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194 | 4350.4194
40% | FY39: 503.1804; FY40: 503.1804; FY41: 503.1804; FY42: 503.1804; FY43: 503.1804; FY44: 503.1804; FY45: 503.1804; FY46: 503.1804; FY47: 503.1804; FY48: 503.1804; FY49: 503.1804; FY50: 503.1804; FY51: 503.1804; FY52: 503.1804; FY53: 503.1804; FY54: 503.1804 | [14 empty] | 432.8293 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447 | 2201.447
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 171.3105 | 24.0364 | 85.674 | 12.736 | 65.6886 | 222.9358 | 892.4936 | 2570.6699 | 5250.6467 | 8784.6533 | 12641.1602 | 17570.3857 | 19652.4836 | 27482.898 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | 36948.0501 | E @ R (MWh) | 581.0205 | 112.9686 | 343.5196 | 73.191 | 272.5961 | 867.7396 | 2149.7327 | 5059.59 | 8543.5345 | 12613.4849 | 17607.6002 | 24582.867 | 27180.5611 | 36379.7249 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811 | 46364.1811
Option 2 Winter POE50 W E @ R (MWh) N 2 | 119.9174 | 16.8255 | 59.9718 | 8.9152 | 45.982 | 156.055 | 624.7455 | 1799.4689 | 3675.4527 | 6149.2573 | 8848.8121 | 12299.27 | 13756.7385 | 19238.0286 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | 25863.6351 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 174.3061 | 33.8906 | 103.0559 | 21.9573 | 81.7788 | 260.3219 | 644.9198 | 1517.877 | 2563.0604 | 3784.0455 | 5282.2801 | 7374.8601 | 8154.1683 | 10913.9175 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543 | 13909.2543
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.6735 | 16.2619 | 17.9127 | 15.6587 | 16.885 | 18.8114 | 20.5532 | 22.966 | 25.4811 | 27.5377 | 29.4781 | 32.3533 | 34.4464 | 36.555 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874 | 38.7874
98% | 13.2169 | 10.7854 | 12.2301 | 9.7751 | 11.1312 | 12.5291 | 14.0127 | 15.7088 | 17.7034 | 19.5729 | 21.537 | 24.872 | 26.0128 | 28.1523 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 | 29.7909 |  | 36.6327 | 31.8578 | 35.1263 | 30.6637 | 33.0916 | 36.9056 | 40.3543 | 45.1313 | 50.111 | 54.1829 | 58.0247 | 63.7172 | 67.8614 | 72.0362 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561 | 76.4561
97% | 12.9115 | 10.5047 | 11.9347 | 9.5046 | 10.8469 | 12.2307 | 13.6993 | 15.3781 | 17.3524 | 19.2029 | 21.1471 | 24.4483 | 25.5775 | 27.6953 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 | 29.3172 |  | 53.8775 | 46.7879 | 51.6408 | 45.0149 | 48.6197 | 54.2827 | 59.4032 | 66.496 | 73.8898 | 79.9355 | 85.6397 | 94.0918 | 100.2451 | 106.4436 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061 | 113.0061
95% | 12.4534 | 10.0836 | 11.4916 | 9.0989 | 10.4206 | 11.7831 | 13.229 | 14.882 | 16.826 | 18.648 | 20.5623 | 23.8127 | 24.9245 | 27.0097 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 | 28.6067 |  | 104.5403 | 90.5793 | 100.1358 | 87.0879 | 94.1866 | 105.3384 | 115.4218 | 129.3891 | 143.9491 | 155.8546 | 167.0874 | 183.7315 | 195.8488 | 208.0551 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782 | 220.9782
90% | 102.4598 | 81.9097 | 94.1198 | 73.3706 | 84.8318 | 96.647 | 109.1862 | 123.521 | 140.3788 | 156.179 | 172.7792 | 200.9662 | 210.6079 | 228.6909 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 | 242.5398 |  | 145.5592 | 125.3812 | 139.1933 | 120.335 | 130.5949 | 146.7127 | 161.2864 | 181.4735 | 202.5173 | 219.7245 | 235.9593 | 260.0152 | 277.5285 | 295.1705 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483 | 313.8483
85% | 88.7163 | 69.277 | 80.8271 | 61.1995 | 72.0412 | 83.2177 | 95.0791 | 108.6391 | 124.5856 | 139.5318 | 155.2346 | 181.898 | 191.0185 | 208.1241 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 | 221.2244 |  | 244.5846 | 208.5309 | 233.2102 | 199.5144 | 217.8466 | 246.6456 | 272.6858 | 308.7559 | 346.3566 | 377.1022 | 406.1104 | 449.0932 | 480.3856 | 511.9081 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815 | 545.2815
80% | 83.3031 | 62.9381 | 75.0382 | 54.4759 | 65.8339 | 77.5427 | 89.9689 | 104.1746 | 120.8805 | 136.5384 | 152.989 | 180.922 | 190.4768 | 208.397 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 | 222.1211 |  | 176.4199 | 148.4252 | 167.588 | 141.4242 | 155.6586 | 178.0202 | 198.2396 | 226.2469 | 255.4428 | 279.3158 | 301.8399 | 335.2148 | 359.5124 | 383.9887 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021 | 409.9021
75% | 108.852 | 78.2428 | 96.4297 | 65.524 | 82.5954 | 100.194 | 118.871 | 140.2225 | 165.332 | 188.8662 | 213.592 | 255.5763 | 269.9374 | 296.8719 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 | 317.4997 |  | 173.0481 | 142.9932 | 163.5662 | 135.477 | 150.7589 | 174.7662 | 196.4736 | 226.5421 | 257.8866 | 283.5165 | 307.6982 | 343.5292 | 369.615 | 395.8926 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131 | 423.7131
70% | 242.705 | 160.3811 | 209.295 | 126.1734 | 172.0872 | 219.419 | 269.6511 | 327.0763 | 394.6088 | 457.9045 | 524.4048 | 637.3222 | 675.9467 | 748.3876 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 | 803.8661 |  | 216.7103 | 174.5365 | 203.4051 | 163.9895 | 185.4335 | 219.1211 | 249.5816 | 291.7744 | 335.7578 | 371.7224 | 405.6547 | 455.9338 | 492.538 | 529.4114 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498 | 568.4498
65% | 239.9449 | 133.3064 | 196.6672 | 88.9954 | 148.47 | 209.7813 | 274.8496 | 349.2355 | 436.7139 | 518.7041 | 604.8454 | 751.1132 | 801.1456 | 894.982 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 | 966.8463 |  | 217.3105 | 168.2289 | 201.826 | 155.9545 | 180.9108 | 220.1162 | 255.5659 | 304.6696 | 355.8572 | 397.7125 | 437.2028 | 495.7171 | 538.3169 | 581.2299 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625 | 626.6625
60% | 573.2972 | 175.3008 | 411.757 | 48.6811 | 231.8544 | 460.7074 | 703.5838 | 981.2395 | 1307.7647 | 1613.8046 | 1935.3391 | 2481.3039 | 2668.0568 | 3018.3141 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 | 3286.5576 |  | 442.0796 | 319.3756 | 403.3682 | 288.6894 | 351.0803 | 449.0938 | 537.7179 | 660.4774 | 788.4462 | 893.0846 | 991.8101 | 1138.0961 | 1244.5955 | 1351.878 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595 | 1465.4595
55% | 381.0194 |  | 136.1535 |  | 6.8068 | 198.1031 | 634.3085 | 1175.8878 | 1812.7891 | 2409.7329 | 3036.8997 | 4101.8273 | 4466.0967 | 5149.2887 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 | 5672.5089 |  | 286.4051 | 177.6985 | 252.1097 | 150.5128 | 205.7865 | 292.6192 | 371.1336 | 479.8894 | 593.2603 | 685.9622 | 773.4257 | 903.0242 | 997.3748 | 1092.4191 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044 | 1193.044
50% | [6 empty] | 48.5853 | 570.4845 | 1680.8804 | 2755.0092 | 3883.5206 | 5799.73 | 6455.1891 | 7684.5111 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 | 8625.9831 |  | 360.2162 | 119.9202 | 283.539 | 72.3097 | 179.9702 | 374.1096 | 549.6509 | 792.8056 | 1046.2786 | 1253.5402 | 1449.0899 | 1738.8444 | 1949.7921 | 2162.291 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666 | 2387.2666
45% | [8 empty] | 169.5672 | 920.2204 | 2116.0044 | 4174.5879 | 4878.7475 | 6199.4079 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 | 7210.8312 |  | 138.3055 |  | 53.4493 |  | 1.3116 | 157.6651 | 499.6892 | 1076.7497 | 1678.298 | 2170.1761 | 2634.2592 | 3321.9115 | 3822.5376 | 4326.8448 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622 | 4860.7622
40% | [10 empty] | 250.865 | 2428.2589 | 3474.2197 | 5435.9325 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | 6938.3036 | [7 empty] | 0.85866 | 325.1539 | 1206.0091 | 2073.0353 | 2891.0677 | 4103.1822 | 4985.6284 | 5874.5633 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916 | 6815.6916
35% | [11 empty] | 4.3432 | 181.7593 | 1160.8446 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | 2420.6802 | [9 empty] | 6.6074 | 245.0692 | 754.2017 | 1899.4285 | 2789.2902 | 3685.6951 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732 | 4634.732
30% | [42 empty] | 89.2353 | 599.4448 | 1523.6094 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398 | 2898.8398
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1858.8794 | 792.7296 | 1335.9441 | 546.7986 | 896.9195 | 1482.155 | 2385.0245 | 3926.4497 | 6405.383 | 9353.9149 | 13109.7202 | 21270.9821 | 24539.7169 | 31316.6098 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | 37016.6767 | E @ R (MWh) | 2614.363 | 1770.577 | 2306.0705 | 1606.6319 | 1952.1347 | 2674.208 | 3528.6156 | 5138.5208 | 7366.1489 | 9567.4724 | 11928.5494 | 15907.1192 | 19304.9614 | 23137.992 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807 | 27592.8807
Option 2 Summer POE50 W E @ R (MWh) N 2 | 1301.2156 | 554.9107 | 935.1608 | 382.759 | 627.8436 | 1037.5085 | 1669.5172 | 2748.5148 | 4483.7681 | 6547.7404 | 9176.8041 | 14889.6875 | 17177.8018 | 21921.6268 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | 25911.6737 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 784.3089 | 531.1731 | 691.8211 | 481.9896 | 585.6404 | 802.2624 | 1058.5847 | 1541.5562 | 2209.8447 | 2870.2417 | 3578.5648 | 4772.1358 | 5791.4884 | 6941.3976 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642 | 8277.8642
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.7244 | 4.29 | 6.3831 | 9.0539 | 11.6398 | 13.9431 | 17.1001 | 20.5496 | 24.082 | 27.5821 | 30.6942 | 34.0844 | 35.3876 | 39.7658 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 |  | 10.3325 | 6.9085 | 9.1195 | 11.823 | 14.3438 | 17.0271 | 19.8475 | 23.8643 | 27.3684 | 30.6736 | 34.1083 | 38.2215 | 39.6082 | 44.0428 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765
98% | 3.6773 | 1.9774 | 3.0134 | 4.3354 | 5.6153 | 6.7554 | 8.318 | 10.0255 | 11.7739 | 13.5064 | 15.0468 | 16.7248 | 17.3699 | 19.537 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 |  | 4.9683 | 3.2735 | 4.3679 | 5.706 | 6.9538 | 8.2819 | 9.6779 | 11.6662 | 13.4006 | 15.0366 | 16.7367 | 18.7726 | 19.459 | 21.654 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001
97% | 6.9849 | 3.6195 | 5.6706 | 8.2877 | 10.8216 | 13.0786 | 16.1721 | 19.5523 | 23.0137 | 26.4434 | 29.493 | 32.815 | 34.0921 | 38.3822 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 |  | 9.5406 | 6.1854 | 8.352 | 11.0011 | 13.4713 | 16.1006 | 18.8643 | 22.8004 | 26.234 | 29.4728 | 32.8384 | 36.869 | 38.2278 | 42.5733 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239
95% | 9.6454 | 4.675 | 7.7042 | 11.5696 | 15.3119 | 18.6453 | 23.2142 | 28.2065 | 33.3188 | 38.3841 | 42.8881 | 47.7945 | 49.6806 | 56.0169 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 |  | 13.4199 | 8.4646 | 11.6645 | 15.577 | 19.2253 | 23.1085 | 27.1904 | 33.0036 | 38.0749 | 42.8584 | 47.8291 | 53.7819 | 55.7888 | 62.2068 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892
90% | 7.7042 | 2.915 | 5.8338 | 9.5582 | 13.1641 | 16.3759 | 20.7783 | 25.5886 | 30.5145 | 35.3952 | 39.735 | 44.4624 | 46.2798 | 52.385 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 |  | 11.3411 | 6.5665 | 9.6497 | 13.4196 | 16.9348 | 20.6765 | 24.6095 | 30.2108 | 35.0972 | 39.7063 | 44.4958 | 50.2316 | 52.1653 | 58.3493 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136
85% | 59.1725 | 6.5594 | 37.941 | 80.2181 | 121.15 | 157.6086 | 207.5815 | 262.1847 | 318.1 | 373.5026 | 422.7651 | 476.4282 | 497.0576 | 566.3606 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 |  | 100.4564 | 46.2576 | 81.2564 | 124.05 | 163.9527 | 206.4256 | 251.0706 | 314.6534 | 370.1203 | 422.4394 | 476.8066 | 541.9157 | 563.8663 | 634.0625 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954
80% | 66.1755 |  | 19.1279 | 116.8852 | 215.5116 | 303.3595 | 423.7706 | 555.3382 | 690.0675 | 823.5613 | 942.2604 | 1071.5629 | 1121.27 | 1288.2572 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 |  | 165.6499 | 35.3125 | 119.3871 | 222.4994 | 318.6459 | 420.9852 | 528.5585 | 681.7629 | 815.4116 | 941.4757 | 1072.4748 | 1229.3566 | 1282.2472 | 1451.3867 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488
75% | 10.2262 |  |  | 93.5568 | 377.4509 | 633.9922 | 985.6274 | 1369.8429 | 1763.2916 | 2153.1324 | 2499.7681 | 2877.3687 | 3022.528 | 3510.1789 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 |  | 231.8404 |  | 99.7224 | 397.8571 | 678.6328 | 977.4934 | 1291.6386 | 1739.0397 | 2129.3327 | 2497.4763 | 2880.0318 | 3338.1721 | 3492.628 | 3986.5643 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834
70% |  |  |  |  | 212.4458 | 755.5237 | 1520.3879 | 2356.1194 | 3211.9346 | 4059.9021 | 4813.8914 | 5635.2347 | 5950.9798 | 7011.7001 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 |  | 33.4714 |  |  | 249.167 | 852.6245 | 1502.6951 | 2186.0122 | 3159.1828 | 4008.134 | 4808.9065 | 5641.0272 | 6637.5573 | 6973.5242 | 8047.9163 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033
65% | [5 empty] | 124.667 | 854.8962 | 1742.9773 | 2652.4003 | 3553.4839 | 4354.7027 | 5227.4943 | 5563.0175 | 6690.1807 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | [5 empty] | 188.8845 | 836.0951 | 1562.2148 | 2596.3441 | 3498.4731 | 4349.4055 | 5233.6497 | 6292.6018 | 6649.6135 | 7791.3048 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242
60% | [6 empty] | 108.2178 | 882.8726 | 1815.9042 | 2740.38 | 3562.3985 | 4457.8479 | 4802.0813 | 5958.5057 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | [6 empty] | 99.1317 | 697.4174 | 1758.3928 | 2683.9411 | 3556.9639 | 4464.1631 | 5550.6057 | 5916.8854 | 7088.2151 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618
55% | [7 empty] | 77.7648 | 878.2155 | 1956.2796 | 2914.8646 | 3959.0799 | 4360.5028 | 5709.0504 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | [7 empty] | 20.0065 | 811.1494 | 1890.4642 | 2908.5271 | 3966.4443 | 5233.3836 | 5660.5155 | 7026.4447 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859
50% | [8 empty] | 11.6315 | 564.915 | 1570.6907 | 2710.1367 | 3148.1687 | 4619.7015 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | [8 empty] | 4.4119 | 509.0069 | 1563.7752 | 2718.1727 | 4100.6547 | 4566.7403 | 6057.2399 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986
45% | [10 empty] | 132.5918 | 960.492 | 1458.8799 | 3249.0414 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | [10 empty] | 129.8083 | 968.7958 | 2617.6063 | 3184.6126 | 4997.8477 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419
40% | [12 empty] | 1.595 | 904.5952 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | [12 empty] | 405.0509 | 845.1405 | 3175.0768 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163
35% | FY39: 23.8357; FY40: 23.8357; FY41: 23.8357; FY42: 23.8357; FY43: 23.8357; FY44: 23.8357; FY45: 23.8357; FY46: 23.8357; FY47: 23.8357; FY48: 23.8357; FY49: 23.8357; FY50: 23.8357; FY51: 23.8357; FY52: 23.8357; FY53: 23.8357; FY54: 23.8357 | [14 empty] | 13.9282 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 171.3105 | 24.0364 | 85.674 | 333.4649 | 983.111 | 2043.9492 | 4186.0642 | 7351.0223 | 11464.2481 | 16366.4681 | 21371.7903 | 27551.5264 | 30108.8907 | 39713.6588 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | E @ R (MWh) | 581.0205 | 112.9686 | 343.5196 | 1051.1003 | 2273.6695 | 4128.0206 | 6637.1083 | 11186.4823 | 16045.0591 | 21336.5256 | 27597.5743 | 36144.7813 | 39341.0228 | 50498.8132 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421
Option 3 Winter POE50 W E @ R (MWh) N 2 | 119.9174 | 16.8255 | 59.9718 | 233.4254 | 688.1777 | 1430.7644 | 2930.2449 | 5145.7156 | 8024.9736 | 11456.5276 | 14960.2532 | 19286.0685 | 21076.2235 | 27799.5611 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 174.3061 | 33.8906 | 103.0559 | 315.3301 | 682.1008 | 1238.4062 | 1991.1325 | 3355.9447 | 4813.5177 | 6400.9577 | 8279.2723 | 10843.4344 | 11802.3068 | 15149.644 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.6735 | 16.2619 | 17.9127 | 19.2961 | 20.5223 | 22.4487 | 24.1905 | 26.6033 | 29.1184 | 31.175 | 33.1154 | 35.9906 | 38.0837 | 40.1923 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247
98% | 13.2169 | 10.7854 | 12.2301 | 13.3759 | 14.7319 | 16.1299 | 17.6135 | 19.3096 | 21.3042 | 23.1736 | 25.1377 | 28.4728 | 29.6135 | 31.7531 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 |  | 36.6327 | 31.8578 | 35.1263 | 37.8652 | 40.2931 | 44.1071 | 47.5558 | 52.3328 | 57.3126 | 61.3844 | 65.2262 | 70.9187 | 75.063 | 79.2377 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576
97% | 12.9115 | 10.5047 | 11.9347 | 13.0688 | 14.4111 | 15.7949 | 17.2635 | 18.9423 | 20.9166 | 22.7671 | 24.7113 | 28.0125 | 29.1417 | 31.2595 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 |  | 53.8775 | 46.7879 | 51.6408 | 55.7075 | 59.3123 | 64.9753 | 70.0958 | 77.1886 | 84.5824 | 90.6281 | 96.3323 | 104.7844 | 110.9376 | 117.1362 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987
95% | 12.4534 | 10.0836 | 11.4916 | 12.6083 | 13.93 | 15.2924 | 16.7384 | 18.3914 | 20.3354 | 22.1574 | 24.0716 | 27.322 | 28.4339 | 30.5191 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 |  | 104.5403 | 90.5793 | 100.1358 | 108.1441 | 115.2428 | 126.3946 | 136.478 | 150.4453 | 165.0053 | 176.9108 | 188.1436 | 204.7877 | 216.905 | 229.1113 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344
90% | 102.4598 | 81.9097 | 94.1198 | 103.8034 | 115.2646 | 127.0798 | 139.619 | 153.9538 | 170.8116 | 186.6118 | 203.2119 | 231.399 | 241.0406 | 259.1237 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 |  | 145.5592 | 125.3812 | 139.1933 | 150.7678 | 161.0276 | 177.1454 | 191.7192 | 211.9063 | 232.95 | 250.1572 | 266.3921 | 290.448 | 307.9613 | 325.6033 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811
85% | 88.7163 | 69.277 | 80.8271 | 89.9872 | 100.8289 | 112.0055 | 123.8669 | 137.4268 | 153.3734 | 168.3195 | 184.0224 | 210.6858 | 219.8063 | 236.9119 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 |  | 244.5846 | 208.5309 | 233.2102 | 253.8913 | 272.2235 | 301.0225 | 327.0627 | 363.1327 | 400.7334 | 431.4791 | 460.4873 | 503.4701 | 534.7625 | 566.285 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584
80% | 83.3031 | 62.9381 | 75.0382 | 84.6345 | 95.9925 | 107.7013 | 120.1275 | 134.3332 | 151.0391 | 166.697 | 183.1476 | 211.0806 | 220.6354 | 238.5556 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 |  | 176.4199 | 148.4252 | 167.588 | 183.6462 | 197.8806 | 220.2422 | 240.4616 | 268.469 | 297.6648 | 321.5379 | 344.0619 | 377.4368 | 401.7344 | 426.2108 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242
75% | 108.852 | 78.2428 | 96.4297 | 110.8532 | 127.9246 | 145.5233 | 164.2003 | 185.5518 | 210.6613 | 234.1955 | 258.9213 | 300.9056 | 315.2667 | 342.2012 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 |  | 173.0481 | 142.9932 | 163.5662 | 180.8063 | 196.0882 | 220.0955 | 241.8029 | 271.8714 | 303.2159 | 328.8458 | 353.0275 | 388.8585 | 414.9443 | 441.2219 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423
70% | 242.705 | 160.3811 | 209.295 | 248.0873 | 294.0011 | 341.3328 | 391.565 | 448.9902 | 516.5227 | 579.8184 | 646.3187 | 759.2361 | 797.8606 | 870.3014 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 |  | 216.7103 | 174.5365 | 203.4051 | 227.5968 | 249.0408 | 282.7284 | 313.1888 | 355.3817 | 399.365 | 435.3296 | 469.262 | 519.541 | 556.1452 | 593.0186 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057
65% | 239.9449 | 133.3064 | 196.6672 | 246.9168 | 306.3914 | 367.7027 | 432.771 | 507.1569 | 594.6353 | 676.6255 | 762.7668 | 909.0346 | 959.067 | 1052.9034 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 |  | 217.3105 | 168.2289 | 201.826 | 229.9801 | 254.9365 | 294.1419 | 329.5915 | 378.6953 | 429.8828 | 471.7382 | 511.2284 | 569.7428 | 612.3426 | 655.2556 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882
60% | 573.2972 | 175.3008 | 411.757 | 599.321 | 821.318 | 1050.171 | 1293.0474 | 1570.7031 | 1897.2283 | 2203.2682 | 2524.8027 | 3070.7675 | 3257.5203 | 3607.7777 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 |  | 442.0796 | 319.3756 | 403.3682 | 473.7535 | 536.1444 | 634.158 | 722.782 | 845.5415 | 973.5103 | 1078.1488 | 1176.8743 | 1323.1602 | 1429.6596 | 1536.9421 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237
55% | 381.0194 |  | 136.1535 | 430.9394 | 863.9541 | 1310.3415 | 1784.0823 | 2325.6616 | 2962.563 | 3559.5068 | 4186.6736 | 5251.6012 | 5615.8706 | 6299.0625 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 |  | 286.4051 | 177.6985 | 252.1097 | 314.4659 | 369.7396 | 456.5724 | 535.0867 | 643.8425 | 757.2134 | 849.9153 | 937.3788 | 1066.9773 | 1161.3279 | 1256.3723 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971
50% |  |  |  | 0.14412 | 203.1188 | 781.1825 | 1629.226 | 2603.733 | 3749.7605 | 4823.8893 | 5952.4007 | 7868.6101 | 8524.0692 | 9753.3911 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 |  | 360.2162 | 119.9202 | 283.539 | 422.9541 | 546.5343 | 740.6737 | 916.215 | 1159.3697 | 1412.8427 | 1620.1043 | 1815.654 | 2105.4085 | 2316.3562 | 2528.8551 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307
45% | [6 empty] | 148.0142 | 781.2185 | 1972.306 | 3126.2423 | 4338.6019 | 6397.1855 | 7101.3451 | 8422.0054 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 |  | 138.3055 |  | 53.4493 | 235.0575 | 492.2929 | 953.0292 | 1369.6278 | 1946.6883 | 2548.2366 | 3040.1146 | 3504.1977 | 4191.8501 | 4692.4761 | 5196.7834 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008
40% | [8 empty] | 179.4633 | 1063.2321 | 2671.8859 | 5729.7119 | 6775.6727 | 8737.3855 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | [5 empty] | 0.49049 | 208.8808 | 693.0821 | 1679.0967 | 2739.4369 | 3606.4631 | 4424.4955 | 5636.61 | 6519.0562 | 7407.9911 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194
35% | [10 empty] | 22.7176 | 1374.291 | 2264.6059 | 4352.5967 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | [8 empty] | 95.7648 | 640.6468 | 1398.5353 | 2223.4418 | 3445.7422 | 4335.6039 | 5232.0089 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458
30% | FY38: 27.4824; FY39: 155.8275; FY40: 155.8275; FY41: 155.8275; FY42: 155.8275; FY43: 155.8275; FY44: 155.8275; FY45: 155.8275; FY46: 155.8275; FY47: 155.8275; FY48: 155.8275; FY49: 155.8275; FY50: 155.8275; FY51: 155.8275; FY52: 155.8275; FY53: 155.8275; FY54: 155.8275 | [10 empty] | 0.49093 | 224.8097 | 1238.6494 | 2424.2493 | 3908.703 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712
25% | [44 empty] | 61.4871 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1858.8794 | 792.7296 | 1335.9441 | 1953.7399 | 2971.8672 | 4390.2575 | 6278.1349 | 8905.3721 | 12620.9206 | 16856.5044 | 22009.3916 | 32398.316 | 36379.9495 | 44293.2304 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | E @ R (MWh) | 2614.363 | 1770.577 | 2306.0705 | 2893.9325 | 3511.7693 | 4746.6157 | 6158.9404 | 8526.3297 | 11471.7175 | 14192.9586 | 17094.1285 | 22074.3763 | 26147.6089 | 30602.4157 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504
Option 3 Summer POE50 W E @ R (MWh) N 2 | 1301.2156 | 554.9107 | 935.1608 | 1367.6179 | 2080.307 | 3073.1803 | 4394.6944 | 6233.7605 | 8834.6444 | 11799.5531 | 15406.5742 | 22678.8212 | 25465.9646 | 31005.2613 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 784.3089 | 531.1731 | 691.8211 | 868.1798 | 1053.5308 | 1423.9847 | 1847.6821 | 2557.8989 | 3441.5153 | 4257.8876 | 5128.2385 | 6622.3129 | 7844.2827 | 9180.7247 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.7244 | 4.29 | 6.3831 | 0.47828 | 3.0641 | 5.3674 | 8.5244 | 11.9739 | 15.5064 | 19.0064 | 22.1185 | 25.5087 | 26.8119 | 31.1901 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 | 35.7177 |  | 10.3325 | 6.9085 | 9.1195 | 3.2473 | 5.7682 | 8.4514 | 11.2718 | 15.2886 | 18.7927 | 22.098 | 25.5326 | 29.6458 | 31.0326 | 35.4672 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009 | 39.6009
98% | 3.6773 | 1.9774 | 3.0134 | 0.090674 | 1.3706 | 2.5107 | 4.0733 | 5.7807 | 7.5292 | 9.2616 | 10.8021 | 12.4801 | 13.1252 | 15.2923 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 | 17.5333 |  | 4.9683 | 3.2735 | 4.3679 | 1.4613 | 2.709 | 4.0372 | 5.4332 | 7.4214 | 9.1559 | 10.7919 | 12.4919 | 14.5279 | 15.2143 | 17.4093 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554 | 19.4554
97% | 6.9849 | 3.6195 | 5.6706 | 0.001821 | 2.4183 | 4.6753 | 7.7688 | 11.149 | 14.6104 | 18.0401 | 21.0897 | 24.4117 | 25.6888 | 29.979 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 | 34.4155 |  | 9.5406 | 6.1854 | 8.352 | 2.5978 | 5.068 | 7.6973 | 10.461 | 14.3971 | 17.8308 | 21.0696 | 24.4351 | 28.4657 | 29.8246 | 34.17 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206 | 38.2206
95% | 9.6454 | 4.675 | 7.7042 |  | 2.9009 | 6.2342 | 10.8032 | 15.7955 | 20.9078 | 25.9731 | 30.4771 | 35.3835 | 37.2696 | 43.6059 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 | 50.1584 |  | 13.4199 | 8.4646 | 11.6645 | 3.166 | 6.8143 | 10.6975 | 14.7794 | 20.5926 | 25.6639 | 30.4474 | 35.4181 | 41.3709 | 43.3778 | 49.7958 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782 | 55.7782
90% | 7.7042 | 2.915 | 5.8338 |  | 1.2056 | 4.4174 | 8.8198 | 13.6301 | 18.5559 | 23.4366 | 27.7764 | 32.5039 | 34.3213 | 40.4265 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 | 46.7401 |  | 11.3411 | 6.5665 | 9.6497 | 1.4611 | 4.9763 | 8.718 | 12.651 | 18.2523 | 23.1387 | 27.7477 | 32.5372 | 38.273 | 40.2068 | 46.3907 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551 | 52.1551
85% | 59.1725 | 6.5594 | 37.941 |  |  | 21.8631 | 71.8361 | 126.4393 | 182.3546 | 237.7572 | 287.0196 | 340.6827 | 361.3122 | 430.6151 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 | 502.2831 |  | 100.4564 | 46.2576 | 81.2564 | 0.14573 | 28.2073 | 70.6801 | 115.3252 | 178.908 | 234.3749 | 286.694 | 341.0612 | 406.1702 | 428.1209 | 498.3171 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75 | 563.75
80% | 66.1755 |  | 19.1279 |  |  | 1.6233 | 96.6887 | 228.2563 | 362.9856 | 496.4795 | 615.1786 | 744.481 | 794.1882 | 961.1753 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 | 1133.8609 |  | 165.6499 | 35.3125 | 119.3871 |  | 6.2891 | 93.9034 | 201.4767 | 354.681 | 488.3297 | 614.3938 | 745.3929 | 902.2747 | 955.1654 | 1124.3048 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967 | 1281.967
75% | 10.2262 | [5 empty] | 50.7088 | 414.6691 | 808.1178 | 1197.9585 | 1544.5943 | 1922.1949 | 2067.3542 | 2555.005 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 | 3059.2971 |  | 231.8404 |  | 99.7224 |  |  | 45.7834 | 336.4648 | 783.8659 | 1174.1589 | 1542.3025 | 1924.858 | 2382.9983 | 2537.4542 | 3031.3905 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096 | 3491.8096
70% | [7 empty] | 281.4841 | 1134.2753 | 1982.2428 | 2736.2322 | 3557.5754 | 3873.3205 | 4934.0409 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 | 6030.9587 |  | 33.4714 | [5 empty] | 147.1344 | 1081.5235 | 1930.4747 | 2731.2473 | 3563.368 | 4559.898 | 4895.865 | 5970.2571 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744 | 6971.744
65% | [8 empty] | 444.5978 | 1345.6814 | 2146.9002 | 3019.6918 | 3355.215 | 4482.3782 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | 5648.0062 | [8 empty] | 389.2406 | 1290.6706 | 2141.603 | 3025.8472 | 4084.7993 | 4441.811 | 5583.5023 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217 | 6647.7217
60% | [8 empty] | 0.25019 | 475.7871 | 1297.2813 | 2192.7307 | 2536.9641 | 3693.3885 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | 4889.2763 | [9 empty] | 422.5506 | 1291.8466 | 2199.0459 | 3285.4884 | 3651.7682 | 4823.0979 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446 | 5914.9446
55% | [10 empty] | 335.3487 | 1317.6462 | 1719.0691 | 3067.6167 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | 4462.184 | [10 empty] | 330.8722 | 1325.0106 | 2591.9499 | 3019.0817 | 4385.0109 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522 | 5658.2522
50% | [11 empty] | 140.758 | 376.2578 | 1737.3735 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | 3259.123 | [11 empty] | 144.0947 | 1218.3267 | 1684.4123 | 3174.9119 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706 | 4564.2706
45% | FY38: 208.2562; FY39: 1593.859; FY40: 1593.859; FY41: 1593.859; FY42: 1593.859; FY43: 1593.859; FY44: 1593.859; FY45: 1593.859; FY46: 1593.859; FY47: 1593.859; FY48: 1593.859; FY49: 1593.859; FY50: 1593.859; FY51: 1593.859; FY52: 1593.859; FY53: 1593.859; FY54: 1593.859 | [12 empty] | 27.774 | 182.4411 | 1491.4139 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081 | 3181.6081
40% | FY39: 12.2661; FY40: 12.2661; FY41: 12.2661; FY42: 12.2661; FY43: 12.2661; FY44: 12.2661; FY45: 12.2661; FY46: 12.2661; FY47: 12.2661; FY48: 12.2661; FY49: 12.2661; FY50: 12.2661; FY51: 12.2661; FY52: 12.2661; FY53: 12.2661; FY54: 12.2661 | [14 empty] | 3.2535 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141 | 842.4141
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 171.3105 | 24.0364 | 85.674 | 0.57077 | 10.9595 | 46.6914 | 259.2231 | 1109.178 | 3009.691 | 5831.6245 | 9074.8187 | 13366.0486 | 15220.8978 | 22230.3433 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | 30775.6796 | E @ R (MWh) | 581.0205 | 112.9686 | 343.5196 | 12.0793 | 59.8322 | 249.9682 | 854.9974 | 2864.1711 | 5635.1414 | 9051.1139 | 13399.0934 | 19611.963 | 21955.7758 | 30268.6928 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919 | 39323.6919
Option 4 Winter POE50 W E @ R (MWh) N 2 | 119.9174 | 16.8255 | 59.9718 | 0.39954 | 7.6717 | 32.684 | 181.4562 | 776.4246 | 2106.7837 | 4082.1372 | 6352.3731 | 9356.234 | 10654.6285 | 15561.2403 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | 21542.9757 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 174.3061 | 33.8906 | 103.0559 | 3.6238 | 17.9497 | 74.9905 | 256.4992 | 859.2513 | 1690.5424 | 2715.3342 | 4019.728 | 5883.5889 | 6586.7327 | 9080.6078 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076 | 11797.1076
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.6735 | 16.2619 | 17.9127 | 13.8401 | 15.0663 | 16.9927 | 18.7346 | 21.1473 | 23.6625 | 25.7191 | 27.6594 | 30.5346 | 32.6278 | 34.7363 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687 | 36.9687
98% | 13.2169 | 10.7854 | 12.2301 | 7.9747 | 9.3308 | 10.7288 | 12.2124 | 13.9084 | 15.903 | 17.7725 | 19.7366 | 23.0716 | 24.2124 | 26.352 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 | 27.9905 |  | 36.6327 | 31.8578 | 35.1263 | 27.063 | 29.4908 | 33.3049 | 36.7536 | 41.5306 | 46.5103 | 50.5821 | 54.4239 | 60.1164 | 64.2607 | 68.4354 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553 | 72.8553
97% | 12.9115 | 10.5047 | 11.9347 | 7.7225 | 9.0648 | 10.4486 | 11.9172 | 13.596 | 15.5703 | 17.4208 | 19.365 | 22.6662 | 23.7954 | 25.9132 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 | 27.5351 |  | 53.8775 | 46.7879 | 51.6408 | 39.6686 | 43.2734 | 48.9364 | 54.0569 | 61.1497 | 68.5435 | 74.5892 | 80.2934 | 88.7455 | 94.8988 | 101.0973 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598 | 107.6598
95% | 12.4534 | 10.0836 | 11.4916 | 7.3442 | 8.6659 | 10.0284 | 11.4743 | 13.1274 | 15.0713 | 16.8933 | 18.8076 | 22.058 | 23.1698 | 25.2551 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 | 26.852 |  | 104.5403 | 90.5793 | 100.1358 | 76.5598 | 83.6585 | 94.8103 | 104.8937 | 118.861 | 133.421 | 145.3266 | 156.5593 | 173.2034 | 185.3207 | 197.527 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501 | 210.4501
90% | 102.4598 | 81.9097 | 94.1198 | 58.1542 | 69.6154 | 81.4306 | 93.9698 | 108.3046 | 125.1624 | 140.9626 | 157.5628 | 185.7498 | 195.3915 | 213.4745 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 | 227.3234 |  | 145.5592 | 125.3812 | 139.1933 | 105.1187 | 115.3785 | 131.4963 | 146.07 | 166.2571 | 187.3009 | 204.5081 | 220.7429 | 244.7989 | 262.3121 | 279.9541 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632 | 298.632
85% | 88.7163 | 69.277 | 80.8271 | 46.8056 | 57.6473 | 68.8238 | 80.6852 | 94.2452 | 110.1918 | 125.1379 | 140.8407 | 167.5041 | 176.6246 | 193.7302 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 | 206.8305 |  | 244.5846 | 208.5309 | 233.2102 | 172.326 | 190.6582 | 219.4572 | 245.4973 | 281.5674 | 319.1681 | 349.9137 | 378.922 | 421.9048 | 453.1972 | 484.7197 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093 | 518.093
80% | 83.3031 | 62.9381 | 75.0382 | 39.3966 | 50.7546 | 62.4634 | 74.8896 | 89.0953 | 105.8012 | 121.4591 | 137.9097 | 165.8427 | 175.3975 | 193.3177 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 | 207.0418 |  | 176.4199 | 148.4252 | 167.588 | 120.3132 | 134.5475 | 156.9092 | 177.1286 | 205.1359 | 234.3318 | 258.2048 | 280.7289 | 314.1037 | 338.4014 | 362.8777 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911 | 388.7911
75% | 108.852 | 78.2428 | 96.4297 | 42.8593 | 59.9307 | 77.5293 | 96.2063 | 117.5578 | 142.6674 | 166.2016 | 190.9274 | 232.9116 | 247.2728 | 274.2073 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 | 294.835 |  | 173.0481 | 142.9932 | 163.5662 | 112.8124 | 128.0943 | 152.1016 | 173.809 | 203.8775 | 235.2219 | 260.8519 | 285.0335 | 320.8646 | 346.9503 | 373.2279 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484 | 401.0484
70% | 242.705 | 160.3811 | 209.295 | 65.2165 | 111.1303 | 158.4621 | 208.6942 | 266.1194 | 333.6519 | 396.9476 | 463.4479 | 576.3653 | 614.9898 | 687.4306 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 | 742.9092 |  | 216.7103 | 174.5365 | 203.4051 | 132.1859 | 153.6299 | 187.3175 | 217.7779 | 259.9708 | 303.9542 | 339.9188 | 373.8511 | 424.1301 | 460.7344 | 497.6078 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462 | 536.6462
65% | 239.9449 | 133.3064 | 196.6672 | 15.7289 | 69.5093 | 130.8206 | 195.8889 | 270.2748 | 357.7532 | 439.7434 | 525.8847 | 672.1525 | 722.1849 | 816.0213 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 | 887.8856 |  | 217.3105 | 168.2289 | 201.826 | 118.9416 | 143.898 | 183.1034 | 218.553 | 267.6568 | 318.8444 | 360.6997 | 400.1899 | 458.7043 | 501.3041 | 544.2171 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497 | 589.6497
60% | 573.2972 | 175.3008 | 411.757 |  | 17.2089 | 166.2754 | 408.852 | 686.5077 | 1013.0329 | 1319.0728 | 1640.6073 | 2186.5721 | 2373.325 | 2723.5823 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 | 2991.8258 |  | 442.0796 | 319.3756 | 403.3682 | 196.1573 | 258.5482 | 356.5618 | 445.1858 | 567.9453 | 695.9141 | 800.5525 | 899.2781 | 1045.564 | 1152.0634 | 1259.3459 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275 | 1372.9275
55% | 381.0194 |  | 136.1535 |  |  |  | 132.8234 | 601.0009 | 1237.9022 | 1834.846 | 2462.0128 | 3526.9404 | 3891.2098 | 4574.4018 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 | 5097.622 |  | 286.4051 | 177.6985 | 252.1097 | 68.5362 | 123.8099 | 210.6427 | 289.157 | 397.9128 | 511.2837 | 603.9856 | 691.4491 | 821.0476 | 915.3982 | 1010.4426 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674 | 1111.0674
50% | [7 empty] | 34.8127 | 663.8869 | 1720.5691 | 2849.0806 | 4765.29 | 5420.7491 | 6650.071 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 | 7591.5431 |  | 360.2162 | 119.9202 | 283.539 | 0.71067 | 36.6729 | 190.8276 | 366.3688 | 609.5235 | 862.9966 | 1070.2582 | 1265.8078 | 1555.5624 | 1766.5101 | 1979.0089 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845 | 2203.9845
45% | [9 empty] | 187.0814 | 1011.8558 | 3063.2891 | 3767.4487 | 5088.1091 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 | 6099.5324 |  | 138.3055 |  | 53.4493 |  |  | 3.2411 | 146.7315 | 641.7804 | 1243.3287 | 1735.2068 | 2199.2899 | 2886.9422 | 3387.5683 | 3891.8755 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929 | 4425.7929
40% | [11 empty] | 997.4336 | 1840.8359 | 3785.206 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | 5287.5771 | [8 empty] | 27.437 | 518.9165 | 1306.3214 | 2124.3538 | 3336.4683 | 4218.9145 | 5107.8494 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776 | 6048.9776
35% | FY38: 282.662; FY39: 1059.3797; FY40: 1059.3797; FY41: 1059.3797; FY42: 1059.3797; FY43: 1059.3797; FY44: 1059.3797; FY45: 1059.3797; FY46: 1059.3797; FY47: 1059.3797; FY48: 1059.3797; FY49: 1059.3797; FY50: 1059.3797; FY51: 1059.3797; FY52: 1059.3797; FY53: 1059.3797; FY54: 1059.3797 | [10 empty] | 16.9431 | 269.2952 | 1135.0463 | 2016.1333 | 2912.5383 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751 | 3861.5751
30% | [43 empty] | 131.1992 | 703.2253 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081 | 1749.1081
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1858.8794 | 792.7296 | 1335.9441 | 291.2026 | 462.8581 | 777.011 | 1327.6133 | 2308.5502 | 4136.5946 | 6504.1081 | 9638.0388 | 16607.8471 | 19496.6072 | 25559.7341 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | 30776.6831 | E @ R (MWh) | 2614.363 | 1770.577 | 2306.0705 | 1184.2335 | 1456.7265 | 1985.7026 | 2640.7178 | 3871.7532 | 5703.3981 | 7603.5817 | 9707.8783 | 13317.7371 | 16327.7943 | 19808.6864 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275 | 23934.2275
Option 4 Summer POE50 W E @ R (MWh) N 2 | 1301.2156 | 554.9107 | 935.1608 | 203.8418 | 324.0007 | 543.9077 | 929.3293 | 1615.9851 | 2895.6162 | 4552.8756 | 6746.6272 | 11625.493 | 13647.625 | 17891.8139 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | 21543.6782 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 784.3089 | 531.1731 | 691.8211 | 355.27 | 437.0179 | 595.7108 | 792.2153 | 1161.526 | 1711.0194 | 2281.0745 | 2912.3635 | 3995.3211 | 4898.3383 | 5942.6059 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682 | 7180.2682
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.7244 | 4.29 | 6.3831 | 9.0539 | 11.6398 | 13.9431 | 17.1001 | 20.5496 | 24.082 | 27.5821 | 30.6942 | 34.0844 | 35.3876 | 39.7658 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 |  | 10.3325 | 6.9085 | 9.1195 | 11.823 | 14.3438 | 17.0271 | 19.8475 | 23.8643 | 27.3684 | 30.6736 | 34.1083 | 38.2215 | 39.6082 | 44.0428 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765
98% | 3.6773 | 1.9774 | 3.0134 | 4.3354 | 5.6153 | 6.7554 | 8.318 | 10.0255 | 11.7739 | 13.5064 | 15.0468 | 16.7248 | 17.3699 | 19.537 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 |  | 4.9683 | 3.2735 | 4.3679 | 5.706 | 6.9538 | 8.2819 | 9.6779 | 11.6662 | 13.4006 | 15.0366 | 16.7367 | 18.7726 | 19.459 | 21.654 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001
97% | 6.9849 | 3.6195 | 5.6706 | 8.2877 | 10.8216 | 13.0786 | 16.1721 | 19.5523 | 23.0137 | 26.4434 | 29.493 | 32.815 | 34.0921 | 38.3822 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 |  | 9.5406 | 6.1854 | 8.352 | 11.0011 | 13.4713 | 16.1006 | 18.8643 | 22.8004 | 26.234 | 29.4728 | 32.8384 | 36.869 | 38.2278 | 42.5733 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239
95% | 9.6454 | 4.675 | 7.7042 | 11.5696 | 15.3119 | 18.6453 | 23.2142 | 28.2065 | 33.3188 | 38.3841 | 42.8881 | 47.7945 | 49.6806 | 56.0169 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 |  | 13.4199 | 8.4646 | 11.6645 | 15.577 | 19.2253 | 23.1085 | 27.1904 | 33.0036 | 38.0749 | 42.8584 | 47.8291 | 53.7819 | 55.7888 | 62.2068 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892
90% | 7.7042 | 2.915 | 5.8338 | 9.5582 | 13.1641 | 16.3759 | 20.7783 | 25.5886 | 30.5145 | 35.3952 | 39.735 | 44.4624 | 46.2798 | 52.385 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 |  | 11.3411 | 6.5665 | 9.6497 | 13.4196 | 16.9348 | 20.6765 | 24.6095 | 30.2108 | 35.0972 | 39.7063 | 44.4958 | 50.2316 | 52.1653 | 58.3493 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136
85% | 59.1725 | 6.5594 | 37.941 | 80.2181 | 121.15 | 157.6086 | 207.5815 | 262.1847 | 318.1 | 373.5026 | 422.7651 | 476.4282 | 497.0576 | 566.3606 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 |  | 100.4564 | 46.2576 | 81.2564 | 124.05 | 163.9527 | 206.4256 | 251.0706 | 314.6534 | 370.1203 | 422.4394 | 476.8066 | 541.9157 | 563.8663 | 634.0625 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954
80% | 66.1755 |  | 19.1279 | 116.8852 | 215.5116 | 303.3595 | 423.7706 | 555.3382 | 690.0675 | 823.5613 | 942.2604 | 1071.5629 | 1121.27 | 1288.2572 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 |  | 165.6499 | 35.3125 | 119.3871 | 222.4994 | 318.6459 | 420.9852 | 528.5585 | 681.7629 | 815.4116 | 941.4757 | 1072.4748 | 1229.3566 | 1282.2472 | 1451.3867 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488
75% | 10.2262 |  |  | 93.5568 | 377.4509 | 633.9922 | 985.6274 | 1369.8429 | 1763.2916 | 2153.1324 | 2499.7681 | 2877.3687 | 3022.528 | 3510.1789 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 |  | 231.8404 |  | 99.7224 | 397.8571 | 678.6328 | 977.4934 | 1291.6386 | 1739.0397 | 2129.3327 | 2497.4763 | 2880.0318 | 3338.1721 | 3492.628 | 3986.5643 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834
70% |  |  |  |  | 212.4458 | 755.5237 | 1520.3879 | 2356.1194 | 3211.9346 | 4059.9021 | 4813.8914 | 5635.2347 | 5950.9798 | 7011.7001 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 |  | 33.4714 |  |  | 249.167 | 852.6245 | 1502.6951 | 2186.0122 | 3159.1828 | 4008.134 | 4808.9065 | 5641.0272 | 6637.5573 | 6973.5242 | 8047.9163 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033
65% | [5 empty] | 124.667 | 854.8962 | 1742.9773 | 2652.4003 | 3553.4839 | 4354.7027 | 5227.4943 | 5563.0175 | 6690.1807 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | [5 empty] | 188.8845 | 836.0951 | 1562.2148 | 2596.3441 | 3498.4731 | 4349.4055 | 5233.6497 | 6292.6018 | 6649.6135 | 7791.3048 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242
60% | [6 empty] | 108.2178 | 882.8726 | 1815.9042 | 2740.38 | 3562.3985 | 4457.8479 | 4802.0813 | 5958.5057 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | [6 empty] | 99.1317 | 697.4174 | 1758.3928 | 2683.9411 | 3556.9639 | 4464.1631 | 5550.6057 | 5916.8854 | 7088.2151 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618
55% | [7 empty] | 77.7648 | 878.2155 | 1956.2796 | 2914.8646 | 3959.0799 | 4360.5028 | 5709.0504 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | [7 empty] | 20.0065 | 811.1494 | 1890.4642 | 2908.5271 | 3966.4443 | 5233.3836 | 5660.5155 | 7026.4447 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859
50% | [8 empty] | 11.6315 | 564.915 | 1570.6907 | 2710.1367 | 3148.1687 | 4619.7015 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | [8 empty] | 4.4119 | 509.0069 | 1563.7752 | 2718.1727 | 4100.6547 | 4566.7403 | 6057.2399 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986
45% | [10 empty] | 132.5918 | 960.492 | 1458.8799 | 3249.0414 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | [10 empty] | 129.8083 | 968.7958 | 2617.6063 | 3184.6126 | 4997.8477 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419
40% | [12 empty] | 1.595 | 904.5952 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | [12 empty] | 405.0509 | 845.1405 | 3175.0768 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163
35% | FY39: 23.8357; FY40: 23.8357; FY41: 23.8357; FY42: 23.8357; FY43: 23.8357; FY44: 23.8357; FY45: 23.8357; FY46: 23.8357; FY47: 23.8357; FY48: 23.8357; FY49: 23.8357; FY50: 23.8357; FY51: 23.8357; FY52: 23.8357; FY53: 23.8357; FY54: 23.8357 | [14 empty] | 13.9282 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 171.3105 | 24.0364 | 85.674 | 333.4649 | 983.111 | 2043.9492 | 4186.0642 | 7351.0223 | 11464.2481 | 16366.4681 | 21371.7903 | 27551.5264 | 30108.8907 | 39713.6588 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | E @ R (MWh) | 581.0205 | 112.9686 | 343.5196 | 1051.1003 | 2273.6695 | 4128.0206 | 6637.1083 | 11186.4823 | 16045.0591 | 21336.5256 | 27597.5743 | 36144.7813 | 39341.0228 | 50498.8132 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421
Option 5 Winter POE50 W E @ R (MWh) N 2 | 119.9174 | 16.8255 | 59.9718 | 233.4254 | 688.1777 | 1430.7644 | 2930.2449 | 5145.7156 | 8024.9736 | 11456.5276 | 14960.2532 | 19286.0685 | 21076.2235 | 27799.5611 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 174.3061 | 33.8906 | 103.0559 | 315.3301 | 682.1008 | 1238.4062 | 1991.1325 | 3355.9447 | 4813.5177 | 6400.9577 | 8279.2723 | 10843.4344 | 11802.3068 | 15149.644 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.6735 | 16.2619 | 17.9127 | 19.2961 | 20.5223 | 22.4487 | 24.1905 | 26.6033 | 29.1184 | 31.175 | 33.1154 | 35.9906 | 38.0837 | 40.1923 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247
98% | 13.2169 | 10.7854 | 12.2301 | 13.3759 | 14.7319 | 16.1299 | 17.6135 | 19.3096 | 21.3042 | 23.1736 | 25.1377 | 28.4728 | 29.6135 | 31.7531 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 |  | 36.6327 | 31.8578 | 35.1263 | 37.8652 | 40.2931 | 44.1071 | 47.5558 | 52.3328 | 57.3126 | 61.3844 | 65.2262 | 70.9187 | 75.063 | 79.2377 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576
97% | 12.9115 | 10.5047 | 11.9347 | 13.0688 | 14.4111 | 15.7949 | 17.2635 | 18.9423 | 20.9166 | 22.7671 | 24.7113 | 28.0125 | 29.1417 | 31.2595 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 |  | 53.8775 | 46.7879 | 51.6408 | 55.7075 | 59.3123 | 64.9753 | 70.0958 | 77.1886 | 84.5824 | 90.6281 | 96.3323 | 104.7844 | 110.9376 | 117.1362 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987
95% | 12.4534 | 10.0836 | 11.4916 | 12.6083 | 13.93 | 15.2924 | 16.7384 | 18.3914 | 20.3354 | 22.1574 | 24.0716 | 27.322 | 28.4339 | 30.5191 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 |  | 104.5403 | 90.5793 | 100.1358 | 108.1441 | 115.2428 | 126.3946 | 136.478 | 150.4453 | 165.0053 | 176.9108 | 188.1436 | 204.7877 | 216.905 | 229.1113 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344
90% | 102.4598 | 81.9097 | 94.1198 | 103.8034 | 115.2646 | 127.0798 | 139.619 | 153.9538 | 170.8116 | 186.6118 | 203.2119 | 231.399 | 241.0406 | 259.1237 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 |  | 145.5592 | 125.3812 | 139.1933 | 150.7678 | 161.0276 | 177.1454 | 191.7192 | 211.9063 | 232.95 | 250.1572 | 266.3921 | 290.448 | 307.9613 | 325.6033 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811
85% | 88.7163 | 69.277 | 80.8271 | 89.9872 | 100.8289 | 112.0055 | 123.8669 | 137.4268 | 153.3734 | 168.3195 | 184.0224 | 210.6858 | 219.8063 | 236.9119 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 |  | 244.5846 | 208.5309 | 233.2102 | 253.8913 | 272.2235 | 301.0225 | 327.0627 | 363.1327 | 400.7334 | 431.4791 | 460.4873 | 503.4701 | 534.7625 | 566.285 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584
80% | 83.3031 | 62.9381 | 75.0382 | 84.6345 | 95.9925 | 107.7013 | 120.1275 | 134.3332 | 151.0391 | 166.697 | 183.1476 | 211.0806 | 220.6354 | 238.5556 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 |  | 176.4199 | 148.4252 | 167.588 | 183.6462 | 197.8806 | 220.2422 | 240.4616 | 268.469 | 297.6648 | 321.5379 | 344.0619 | 377.4368 | 401.7344 | 426.2108 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242
75% | 108.852 | 78.2428 | 96.4297 | 110.8532 | 127.9246 | 145.5233 | 164.2003 | 185.5518 | 210.6613 | 234.1955 | 258.9213 | 300.9056 | 315.2667 | 342.2012 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 |  | 173.0481 | 142.9932 | 163.5662 | 180.8063 | 196.0882 | 220.0955 | 241.8029 | 271.8714 | 303.2159 | 328.8458 | 353.0275 | 388.8585 | 414.9443 | 441.2219 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423
70% | 242.705 | 160.3811 | 209.295 | 248.0873 | 294.0011 | 341.3328 | 391.565 | 448.9902 | 516.5227 | 579.8184 | 646.3187 | 759.2361 | 797.8606 | 870.3014 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 |  | 216.7103 | 174.5365 | 203.4051 | 227.5968 | 249.0408 | 282.7284 | 313.1888 | 355.3817 | 399.365 | 435.3296 | 469.262 | 519.541 | 556.1452 | 593.0186 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057
65% | 239.9449 | 133.3064 | 196.6672 | 246.9168 | 306.3914 | 367.7027 | 432.771 | 507.1569 | 594.6353 | 676.6255 | 762.7668 | 909.0346 | 959.067 | 1052.9034 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 |  | 217.3105 | 168.2289 | 201.826 | 229.9801 | 254.9365 | 294.1419 | 329.5915 | 378.6953 | 429.8828 | 471.7382 | 511.2284 | 569.7428 | 612.3426 | 655.2556 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882
60% | 573.2972 | 175.3008 | 411.757 | 599.321 | 821.318 | 1050.171 | 1293.0474 | 1570.7031 | 1897.2283 | 2203.2682 | 2524.8027 | 3070.7675 | 3257.5203 | 3607.7777 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 |  | 442.0796 | 319.3756 | 403.3682 | 473.7535 | 536.1444 | 634.158 | 722.782 | 845.5415 | 973.5103 | 1078.1488 | 1176.8743 | 1323.1602 | 1429.6596 | 1536.9421 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237
55% | 381.0194 |  | 136.1535 | 430.9394 | 863.9541 | 1310.3415 | 1784.0823 | 2325.6616 | 2962.563 | 3559.5068 | 4186.6736 | 5251.6012 | 5615.8706 | 6299.0625 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 |  | 286.4051 | 177.6985 | 252.1097 | 314.4659 | 369.7396 | 456.5724 | 535.0867 | 643.8425 | 757.2134 | 849.9153 | 937.3788 | 1066.9773 | 1161.3279 | 1256.3723 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971
50% |  |  |  | 0.14412 | 203.1188 | 781.1825 | 1629.226 | 2603.733 | 3749.7605 | 4823.8893 | 5952.4007 | 7868.6101 | 8524.0692 | 9753.3911 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 |  | 360.2162 | 119.9202 | 283.539 | 422.9541 | 546.5343 | 740.6737 | 916.215 | 1159.3697 | 1412.8427 | 1620.1043 | 1815.654 | 2105.4085 | 2316.3562 | 2528.8551 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307
45% | [6 empty] | 148.0142 | 781.2185 | 1972.306 | 3126.2423 | 4338.6019 | 6397.1855 | 7101.3451 | 8422.0054 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 |  | 138.3055 |  | 53.4493 | 235.0575 | 492.2929 | 953.0292 | 1369.6278 | 1946.6883 | 2548.2366 | 3040.1146 | 3504.1977 | 4191.8501 | 4692.4761 | 5196.7834 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008
40% | [8 empty] | 179.4633 | 1063.2321 | 2671.8859 | 5729.7119 | 6775.6727 | 8737.3855 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | [5 empty] | 0.49049 | 208.8808 | 693.0821 | 1679.0967 | 2739.4369 | 3606.4631 | 4424.4955 | 5636.61 | 6519.0562 | 7407.9911 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194
35% | [10 empty] | 22.7176 | 1374.291 | 2264.6059 | 4352.5967 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | [8 empty] | 95.7648 | 640.6468 | 1398.5353 | 2223.4418 | 3445.7422 | 4335.6039 | 5232.0089 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458
30% | FY38: 27.4824; FY39: 155.8275; FY40: 155.8275; FY41: 155.8275; FY42: 155.8275; FY43: 155.8275; FY44: 155.8275; FY45: 155.8275; FY46: 155.8275; FY47: 155.8275; FY48: 155.8275; FY49: 155.8275; FY50: 155.8275; FY51: 155.8275; FY52: 155.8275; FY53: 155.8275; FY54: 155.8275 | [10 empty] | 0.49093 | 224.8097 | 1238.6494 | 2424.2493 | 3908.703 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712
25% | [44 empty] | 61.4871 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1858.8794 | 792.7296 | 1335.9441 | 1953.7399 | 2971.8672 | 4390.2575 | 6278.1349 | 8905.3721 | 12620.9206 | 16856.5044 | 22009.3916 | 32398.316 | 36379.9495 | 44293.2304 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | E @ R (MWh) | 2614.363 | 1770.577 | 2306.0705 | 2893.9325 | 3511.7693 | 4746.6157 | 6158.9404 | 8526.3297 | 11471.7175 | 14192.9586 | 17094.1285 | 22074.3763 | 26147.6089 | 30602.4157 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504
Option 5 Summer POE50 W E @ R (MWh) N 2 | 1301.2156 | 554.9107 | 935.1608 | 1367.6179 | 2080.307 | 3073.1803 | 4394.6944 | 6233.7605 | 8834.6444 | 11799.5531 | 15406.5742 | 22678.8212 | 25465.9646 | 31005.2613 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 784.3089 | 531.1731 | 691.8211 | 868.1798 | 1053.5308 | 1423.9847 | 1847.6821 | 2557.8989 | 3441.5153 | 4257.8876 | 5128.2385 | 6622.3129 | 7844.2827 | 9180.7247 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.7244 | 4.29 | 6.3831 | 9.0539 | 11.6398 | 13.9431 | 17.1001 | 20.5496 | 24.082 | 27.5821 | 30.6942 | 34.0844 | 35.3876 | 39.7658 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 |  | 10.3325 | 6.9085 | 9.1195 | 11.823 | 14.3438 | 17.0271 | 19.8475 | 23.8643 | 27.3684 | 30.6736 | 34.1083 | 38.2215 | 39.6082 | 44.0428 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765
98% | 3.6773 | 1.9774 | 3.0134 | 4.3354 | 5.6153 | 6.7554 | 8.318 | 10.0255 | 11.7739 | 13.5064 | 15.0468 | 16.7248 | 17.3699 | 19.537 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 |  | 4.9683 | 3.2735 | 4.3679 | 5.706 | 6.9538 | 8.2819 | 9.6779 | 11.6662 | 13.4006 | 15.0366 | 16.7367 | 18.7726 | 19.459 | 21.654 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001
97% | 6.9849 | 3.6195 | 5.6706 | 8.2877 | 10.8216 | 13.0786 | 16.1721 | 19.5523 | 23.0137 | 26.4434 | 29.493 | 32.815 | 34.0921 | 38.3822 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 |  | 9.5406 | 6.1854 | 8.352 | 11.0011 | 13.4713 | 16.1006 | 18.8643 | 22.8004 | 26.234 | 29.4728 | 32.8384 | 36.869 | 38.2278 | 42.5733 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239
95% | 9.6454 | 4.675 | 7.7042 | 11.5696 | 15.3119 | 18.6453 | 23.2142 | 28.2065 | 33.3188 | 38.3841 | 42.8881 | 47.7945 | 49.6806 | 56.0169 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 |  | 13.4199 | 8.4646 | 11.6645 | 15.577 | 19.2253 | 23.1085 | 27.1904 | 33.0036 | 38.0749 | 42.8584 | 47.8291 | 53.7819 | 55.7888 | 62.2068 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892
90% | 7.7042 | 2.915 | 5.8338 | 9.5582 | 13.1641 | 16.3759 | 20.7783 | 25.5886 | 30.5145 | 35.3952 | 39.735 | 44.4624 | 46.2798 | 52.385 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 |  | 11.3411 | 6.5665 | 9.6497 | 13.4196 | 16.9348 | 20.6765 | 24.6095 | 30.2108 | 35.0972 | 39.7063 | 44.4958 | 50.2316 | 52.1653 | 58.3493 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136
85% | 59.1725 | 6.5594 | 37.941 | 80.2181 | 121.15 | 157.6086 | 207.5815 | 262.1847 | 318.1 | 373.5026 | 422.7651 | 476.4282 | 497.0576 | 566.3606 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 |  | 100.4564 | 46.2576 | 81.2564 | 124.05 | 163.9527 | 206.4256 | 251.0706 | 314.6534 | 370.1203 | 422.4394 | 476.8066 | 541.9157 | 563.8663 | 634.0625 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954
80% | 66.1755 |  | 19.1279 | 116.8852 | 215.5116 | 303.3595 | 423.7706 | 555.3382 | 690.0675 | 823.5613 | 942.2604 | 1071.5629 | 1121.27 | 1288.2572 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 |  | 165.6499 | 35.3125 | 119.3871 | 222.4994 | 318.6459 | 420.9852 | 528.5585 | 681.7629 | 815.4116 | 941.4757 | 1072.4748 | 1229.3566 | 1282.2472 | 1451.3867 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488
75% | 10.2262 |  |  | 93.5568 | 377.4509 | 633.9922 | 985.6274 | 1369.8429 | 1763.2916 | 2153.1324 | 2499.7681 | 2877.3687 | 3022.528 | 3510.1789 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 |  | 231.8404 |  | 99.7224 | 397.8571 | 678.6328 | 977.4934 | 1291.6386 | 1739.0397 | 2129.3327 | 2497.4763 | 2880.0318 | 3338.1721 | 3492.628 | 3986.5643 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834
70% |  |  |  |  | 212.4458 | 755.5237 | 1520.3879 | 2356.1194 | 3211.9346 | 4059.9021 | 4813.8914 | 5635.2347 | 5950.9798 | 7011.7001 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 |  | 33.4714 |  |  | 249.167 | 852.6245 | 1502.6951 | 2186.0122 | 3159.1828 | 4008.134 | 4808.9065 | 5641.0272 | 6637.5573 | 6973.5242 | 8047.9163 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033
65% | [5 empty] | 124.667 | 854.8962 | 1742.9773 | 2652.4003 | 3553.4839 | 4354.7027 | 5227.4943 | 5563.0175 | 6690.1807 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | [5 empty] | 188.8845 | 836.0951 | 1562.2148 | 2596.3441 | 3498.4731 | 4349.4055 | 5233.6497 | 6292.6018 | 6649.6135 | 7791.3048 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242
60% | [6 empty] | 108.2178 | 882.8726 | 1815.9042 | 2740.38 | 3562.3985 | 4457.8479 | 4802.0813 | 5958.5057 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | [6 empty] | 99.1317 | 697.4174 | 1758.3928 | 2683.9411 | 3556.9639 | 4464.1631 | 5550.6057 | 5916.8854 | 7088.2151 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618
55% | [7 empty] | 77.7648 | 878.2155 | 1956.2796 | 2914.8646 | 3959.0799 | 4360.5028 | 5709.0504 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | [7 empty] | 20.0065 | 811.1494 | 1890.4642 | 2908.5271 | 3966.4443 | 5233.3836 | 5660.5155 | 7026.4447 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859
50% | [8 empty] | 11.6315 | 564.915 | 1570.6907 | 2710.1367 | 3148.1687 | 4619.7015 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | [8 empty] | 4.4119 | 509.0069 | 1563.7752 | 2718.1727 | 4100.6547 | 4566.7403 | 6057.2399 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986
45% | [10 empty] | 132.5918 | 960.492 | 1458.8799 | 3249.0414 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | [10 empty] | 129.8083 | 968.7958 | 2617.6063 | 3184.6126 | 4997.8477 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419
40% | [12 empty] | 1.595 | 904.5952 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | [12 empty] | 405.0509 | 845.1405 | 3175.0768 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163
35% | FY39: 23.8357; FY40: 23.8357; FY41: 23.8357; FY42: 23.8357; FY43: 23.8357; FY44: 23.8357; FY45: 23.8357; FY46: 23.8357; FY47: 23.8357; FY48: 23.8357; FY49: 23.8357; FY50: 23.8357; FY51: 23.8357; FY52: 23.8357; FY53: 23.8357; FY54: 23.8357 | [14 empty] | 13.9282 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 171.3105 | 24.0364 | 85.674 | 333.4649 | 983.111 | 2043.9492 | 4186.0642 | 7351.0223 | 11464.2481 | 16366.4681 | 21371.7903 | 27551.5264 | 30108.8907 | 39713.6588 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | E @ R (MWh) | 581.0205 | 112.9686 | 343.5196 | 1051.1003 | 2273.6695 | 4128.0206 | 6637.1083 | 11186.4823 | 16045.0591 | 21336.5256 | 27597.5743 | 36144.7813 | 39341.0228 | 50498.8132 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421
Option 6 Winter POE50 W E @ R (MWh) N 2 | 119.9174 | 16.8255 | 59.9718 | 233.4254 | 688.1777 | 1430.7644 | 2930.2449 | 5145.7156 | 8024.9736 | 11456.5276 | 14960.2532 | 19286.0685 | 21076.2235 | 27799.5611 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 174.3061 | 33.8906 | 103.0559 | 315.3301 | 682.1008 | 1238.4062 | 1991.1325 | 3355.9447 | 4813.5177 | 6400.9577 | 8279.2723 | 10843.4344 | 11802.3068 | 15149.644 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.6735 | 16.2619 | 17.9127 | 19.2961 | 20.5223 | 22.4487 | 24.1905 | 26.6033 | 29.1184 | 31.175 | 33.1154 | 35.9906 | 38.0837 | 40.1923 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247
98% | 13.2169 | 10.7854 | 12.2301 | 13.3759 | 14.7319 | 16.1299 | 17.6135 | 19.3096 | 21.3042 | 23.1736 | 25.1377 | 28.4728 | 29.6135 | 31.7531 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 |  | 36.6327 | 31.8578 | 35.1263 | 37.8652 | 40.2931 | 44.1071 | 47.5558 | 52.3328 | 57.3126 | 61.3844 | 65.2262 | 70.9187 | 75.063 | 79.2377 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576
97% | 12.9115 | 10.5047 | 11.9347 | 13.0688 | 14.4111 | 15.7949 | 17.2635 | 18.9423 | 20.9166 | 22.7671 | 24.7113 | 28.0125 | 29.1417 | 31.2595 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 |  | 53.8775 | 46.7879 | 51.6408 | 55.7075 | 59.3123 | 64.9753 | 70.0958 | 77.1886 | 84.5824 | 90.6281 | 96.3323 | 104.7844 | 110.9376 | 117.1362 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987
95% | 12.4534 | 10.0836 | 11.4916 | 12.6083 | 13.93 | 15.2924 | 16.7384 | 18.3914 | 20.3354 | 22.1574 | 24.0716 | 27.322 | 28.4339 | 30.5191 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 |  | 104.5403 | 90.5793 | 100.1358 | 108.1441 | 115.2428 | 126.3946 | 136.478 | 150.4453 | 165.0053 | 176.9108 | 188.1436 | 204.7877 | 216.905 | 229.1113 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344
90% | 102.4598 | 81.9097 | 94.1198 | 103.8034 | 115.2646 | 127.0798 | 139.619 | 153.9538 | 170.8116 | 186.6118 | 203.2119 | 231.399 | 241.0406 | 259.1237 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 |  | 145.5592 | 125.3812 | 139.1933 | 150.7678 | 161.0276 | 177.1454 | 191.7192 | 211.9063 | 232.95 | 250.1572 | 266.3921 | 290.448 | 307.9613 | 325.6033 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811
85% | 88.7163 | 69.277 | 80.8271 | 89.9872 | 100.8289 | 112.0055 | 123.8669 | 137.4268 | 153.3734 | 168.3195 | 184.0224 | 210.6858 | 219.8063 | 236.9119 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 |  | 244.5846 | 208.5309 | 233.2102 | 253.8913 | 272.2235 | 301.0225 | 327.0627 | 363.1327 | 400.7334 | 431.4791 | 460.4873 | 503.4701 | 534.7625 | 566.285 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584
80% | 83.3031 | 62.9381 | 75.0382 | 84.6345 | 95.9925 | 107.7013 | 120.1275 | 134.3332 | 151.0391 | 166.697 | 183.1476 | 211.0806 | 220.6354 | 238.5556 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 |  | 176.4199 | 148.4252 | 167.588 | 183.6462 | 197.8806 | 220.2422 | 240.4616 | 268.469 | 297.6648 | 321.5379 | 344.0619 | 377.4368 | 401.7344 | 426.2108 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242
75% | 108.852 | 78.2428 | 96.4297 | 110.8532 | 127.9246 | 145.5233 | 164.2003 | 185.5518 | 210.6613 | 234.1955 | 258.9213 | 300.9056 | 315.2667 | 342.2012 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 |  | 173.0481 | 142.9932 | 163.5662 | 180.8063 | 196.0882 | 220.0955 | 241.8029 | 271.8714 | 303.2159 | 328.8458 | 353.0275 | 388.8585 | 414.9443 | 441.2219 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423
70% | 242.705 | 160.3811 | 209.295 | 248.0873 | 294.0011 | 341.3328 | 391.565 | 448.9902 | 516.5227 | 579.8184 | 646.3187 | 759.2361 | 797.8606 | 870.3014 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 |  | 216.7103 | 174.5365 | 203.4051 | 227.5968 | 249.0408 | 282.7284 | 313.1888 | 355.3817 | 399.365 | 435.3296 | 469.262 | 519.541 | 556.1452 | 593.0186 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057
65% | 239.9449 | 133.3064 | 196.6672 | 246.9168 | 306.3914 | 367.7027 | 432.771 | 507.1569 | 594.6353 | 676.6255 | 762.7668 | 909.0346 | 959.067 | 1052.9034 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 |  | 217.3105 | 168.2289 | 201.826 | 229.9801 | 254.9365 | 294.1419 | 329.5915 | 378.6953 | 429.8828 | 471.7382 | 511.2284 | 569.7428 | 612.3426 | 655.2556 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882
60% | 573.2972 | 175.3008 | 411.757 | 599.321 | 821.318 | 1050.171 | 1293.0474 | 1570.7031 | 1897.2283 | 2203.2682 | 2524.8027 | 3070.7675 | 3257.5203 | 3607.7777 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 |  | 442.0796 | 319.3756 | 403.3682 | 473.7535 | 536.1444 | 634.158 | 722.782 | 845.5415 | 973.5103 | 1078.1488 | 1176.8743 | 1323.1602 | 1429.6596 | 1536.9421 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237
55% | 381.0194 |  | 136.1535 | 430.9394 | 863.9541 | 1310.3415 | 1784.0823 | 2325.6616 | 2962.563 | 3559.5068 | 4186.6736 | 5251.6012 | 5615.8706 | 6299.0625 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 |  | 286.4051 | 177.6985 | 252.1097 | 314.4659 | 369.7396 | 456.5724 | 535.0867 | 643.8425 | 757.2134 | 849.9153 | 937.3788 | 1066.9773 | 1161.3279 | 1256.3723 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971
50% |  |  |  | 0.14412 | 203.1188 | 781.1825 | 1629.226 | 2603.733 | 3749.7605 | 4823.8893 | 5952.4007 | 7868.6101 | 8524.0692 | 9753.3911 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 |  | 360.2162 | 119.9202 | 283.539 | 422.9541 | 546.5343 | 740.6737 | 916.215 | 1159.3697 | 1412.8427 | 1620.1043 | 1815.654 | 2105.4085 | 2316.3562 | 2528.8551 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307
45% | [6 empty] | 148.0142 | 781.2185 | 1972.306 | 3126.2423 | 4338.6019 | 6397.1855 | 7101.3451 | 8422.0054 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 |  | 138.3055 |  | 53.4493 | 235.0575 | 492.2929 | 953.0292 | 1369.6278 | 1946.6883 | 2548.2366 | 3040.1146 | 3504.1977 | 4191.8501 | 4692.4761 | 5196.7834 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008
40% | [8 empty] | 179.4633 | 1063.2321 | 2671.8859 | 5729.7119 | 6775.6727 | 8737.3855 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | [5 empty] | 0.49049 | 208.8808 | 693.0821 | 1679.0967 | 2739.4369 | 3606.4631 | 4424.4955 | 5636.61 | 6519.0562 | 7407.9911 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194
35% | [10 empty] | 22.7176 | 1374.291 | 2264.6059 | 4352.5967 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | [8 empty] | 95.7648 | 640.6468 | 1398.5353 | 2223.4418 | 3445.7422 | 4335.6039 | 5232.0089 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458
30% | FY38: 27.4824; FY39: 155.8275; FY40: 155.8275; FY41: 155.8275; FY42: 155.8275; FY43: 155.8275; FY44: 155.8275; FY45: 155.8275; FY46: 155.8275; FY47: 155.8275; FY48: 155.8275; FY49: 155.8275; FY50: 155.8275; FY51: 155.8275; FY52: 155.8275; FY53: 155.8275; FY54: 155.8275 | [10 empty] | 0.49093 | 224.8097 | 1238.6494 | 2424.2493 | 3908.703 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712
25% | [44 empty] | 61.4871 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1858.8794 | 792.7296 | 1335.9441 | 1953.7399 | 2971.8672 | 4390.2575 | 6278.1349 | 8905.3721 | 12620.9206 | 16856.5044 | 22009.3916 | 32398.316 | 36379.9495 | 44293.2304 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | E @ R (MWh) | 2614.363 | 1770.577 | 2306.0705 | 2893.9325 | 3511.7693 | 4746.6157 | 6158.9404 | 8526.3297 | 11471.7175 | 14192.9586 | 17094.1285 | 22074.3763 | 26147.6089 | 30602.4157 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504
Option 6 Summer POE50 W E @ R (MWh) N 2 | 1301.2156 | 554.9107 | 935.1608 | 1367.6179 | 2080.307 | 3073.1803 | 4394.6944 | 6233.7605 | 8834.6444 | 11799.5531 | 15406.5742 | 22678.8212 | 25465.9646 | 31005.2613 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 784.3089 | 531.1731 | 691.8211 | 868.1798 | 1053.5308 | 1423.9847 | 1847.6821 | 2557.8989 | 3441.5153 | 4257.8876 | 5128.2385 | 6622.3129 | 7844.2827 | 9180.7247 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.7244 | 4.29 | 6.3831 | 9.0539 | 11.6398 | 13.9431 | 17.1001 | 20.5496 | 24.082 | 27.5821 | 30.6942 | 34.0844 | 35.3876 | 39.7658 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 |  | 10.3325 | 6.9085 | 9.1195 | 11.823 | 14.3438 | 17.0271 | 19.8475 | 23.8643 | 27.3684 | 30.6736 | 34.1083 | 38.2215 | 39.6082 | 44.0428 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765
98% | 3.6773 | 1.9774 | 3.0134 | 4.3354 | 5.6153 | 6.7554 | 8.318 | 10.0255 | 11.7739 | 13.5064 | 15.0468 | 16.7248 | 17.3699 | 19.537 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 |  | 4.9683 | 3.2735 | 4.3679 | 5.706 | 6.9538 | 8.2819 | 9.6779 | 11.6662 | 13.4006 | 15.0366 | 16.7367 | 18.7726 | 19.459 | 21.654 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001
97% | 6.9849 | 3.6195 | 5.6706 | 8.2877 | 10.8216 | 13.0786 | 16.1721 | 19.5523 | 23.0137 | 26.4434 | 29.493 | 32.815 | 34.0921 | 38.3822 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 |  | 9.5406 | 6.1854 | 8.352 | 11.0011 | 13.4713 | 16.1006 | 18.8643 | 22.8004 | 26.234 | 29.4728 | 32.8384 | 36.869 | 38.2278 | 42.5733 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239
95% | 9.6454 | 4.675 | 7.7042 | 11.5696 | 15.3119 | 18.6453 | 23.2142 | 28.2065 | 33.3188 | 38.3841 | 42.8881 | 47.7945 | 49.6806 | 56.0169 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 |  | 13.4199 | 8.4646 | 11.6645 | 15.577 | 19.2253 | 23.1085 | 27.1904 | 33.0036 | 38.0749 | 42.8584 | 47.8291 | 53.7819 | 55.7888 | 62.2068 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892
90% | 7.7042 | 2.915 | 5.8338 | 9.5582 | 13.1641 | 16.3759 | 20.7783 | 25.5886 | 30.5145 | 35.3952 | 39.735 | 44.4624 | 46.2798 | 52.385 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 |  | 11.3411 | 6.5665 | 9.6497 | 13.4196 | 16.9348 | 20.6765 | 24.6095 | 30.2108 | 35.0972 | 39.7063 | 44.4958 | 50.2316 | 52.1653 | 58.3493 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136
85% | 59.1725 | 6.5594 | 37.941 | 80.2181 | 121.15 | 157.6086 | 207.5815 | 262.1847 | 318.1 | 373.5026 | 422.7651 | 476.4282 | 497.0576 | 566.3606 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 |  | 100.4564 | 46.2576 | 81.2564 | 124.05 | 163.9527 | 206.4256 | 251.0706 | 314.6534 | 370.1203 | 422.4394 | 476.8066 | 541.9157 | 563.8663 | 634.0625 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954
80% | 66.1755 |  | 19.1279 | 116.8852 | 215.5116 | 303.3595 | 423.7706 | 555.3382 | 690.0675 | 823.5613 | 942.2604 | 1071.5629 | 1121.27 | 1288.2572 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 |  | 165.6499 | 35.3125 | 119.3871 | 222.4994 | 318.6459 | 420.9852 | 528.5585 | 681.7629 | 815.4116 | 941.4757 | 1072.4748 | 1229.3566 | 1282.2472 | 1451.3867 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488
75% | 10.2262 |  |  | 93.5568 | 377.4509 | 633.9922 | 985.6274 | 1369.8429 | 1763.2916 | 2153.1324 | 2499.7681 | 2877.3687 | 3022.528 | 3510.1789 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 |  | 231.8404 |  | 99.7224 | 397.8571 | 678.6328 | 977.4934 | 1291.6386 | 1739.0397 | 2129.3327 | 2497.4763 | 2880.0318 | 3338.1721 | 3492.628 | 3986.5643 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834
70% |  |  |  |  | 212.4458 | 755.5237 | 1520.3879 | 2356.1194 | 3211.9346 | 4059.9021 | 4813.8914 | 5635.2347 | 5950.9798 | 7011.7001 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 |  | 33.4714 |  |  | 249.167 | 852.6245 | 1502.6951 | 2186.0122 | 3159.1828 | 4008.134 | 4808.9065 | 5641.0272 | 6637.5573 | 6973.5242 | 8047.9163 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033
65% | [5 empty] | 124.667 | 854.8962 | 1742.9773 | 2652.4003 | 3553.4839 | 4354.7027 | 5227.4943 | 5563.0175 | 6690.1807 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | [5 empty] | 188.8845 | 836.0951 | 1562.2148 | 2596.3441 | 3498.4731 | 4349.4055 | 5233.6497 | 6292.6018 | 6649.6135 | 7791.3048 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242
60% | [6 empty] | 108.2178 | 882.8726 | 1815.9042 | 2740.38 | 3562.3985 | 4457.8479 | 4802.0813 | 5958.5057 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | [6 empty] | 99.1317 | 697.4174 | 1758.3928 | 2683.9411 | 3556.9639 | 4464.1631 | 5550.6057 | 5916.8854 | 7088.2151 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618
55% | [7 empty] | 77.7648 | 878.2155 | 1956.2796 | 2914.8646 | 3959.0799 | 4360.5028 | 5709.0504 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | [7 empty] | 20.0065 | 811.1494 | 1890.4642 | 2908.5271 | 3966.4443 | 5233.3836 | 5660.5155 | 7026.4447 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859
50% | [8 empty] | 11.6315 | 564.915 | 1570.6907 | 2710.1367 | 3148.1687 | 4619.7015 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | [8 empty] | 4.4119 | 509.0069 | 1563.7752 | 2718.1727 | 4100.6547 | 4566.7403 | 6057.2399 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986
45% | [10 empty] | 132.5918 | 960.492 | 1458.8799 | 3249.0414 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | [10 empty] | 129.8083 | 968.7958 | 2617.6063 | 3184.6126 | 4997.8477 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419
40% | [12 empty] | 1.595 | 904.5952 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | [12 empty] | 405.0509 | 845.1405 | 3175.0768 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163
35% | FY39: 23.8357; FY40: 23.8357; FY41: 23.8357; FY42: 23.8357; FY43: 23.8357; FY44: 23.8357; FY45: 23.8357; FY46: 23.8357; FY47: 23.8357; FY48: 23.8357; FY49: 23.8357; FY50: 23.8357; FY51: 23.8357; FY52: 23.8357; FY53: 23.8357; FY54: 23.8357 | [14 empty] | 13.9282 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 171.3105 | 24.0364 | 85.674 | 333.4649 | 983.111 | 2043.9492 | 4186.0642 | 7351.0223 | 11464.2481 | 16366.4681 | 21371.7903 | 27551.5264 | 30108.8907 | 39713.6588 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | E @ R (MWh) | 581.0205 | 112.9686 | 343.5196 | 1051.1003 | 2273.6695 | 4128.0206 | 6637.1083 | 11186.4823 | 16045.0591 | 21336.5256 | 27597.5743 | 36144.7813 | 39341.0228 | 50498.8132 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421
Option 7 Winter POE50 W E @ R (MWh) N 2 | 119.9174 | 16.8255 | 59.9718 | 233.4254 | 688.1777 | 1430.7644 | 2930.2449 | 5145.7156 | 8024.9736 | 11456.5276 | 14960.2532 | 19286.0685 | 21076.2235 | 27799.5611 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 174.3061 | 33.8906 | 103.0559 | 315.3301 | 682.1008 | 1238.4062 | 1991.1325 | 3355.9447 | 4813.5177 | 6400.9577 | 8279.2723 | 10843.4344 | 11802.3068 | 15149.644 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.6735 | 16.2619 | 17.9127 | 19.2961 | 20.5223 | 22.4487 | 24.1905 | 26.6033 | 29.1184 | 31.175 | 33.1154 | 35.9906 | 38.0837 | 40.1923 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247
98% | 13.2169 | 10.7854 | 12.2301 | 13.3759 | 14.7319 | 16.1299 | 17.6135 | 19.3096 | 21.3042 | 23.1736 | 25.1377 | 28.4728 | 29.6135 | 31.7531 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 |  | 36.6327 | 31.8578 | 35.1263 | 37.8652 | 40.2931 | 44.1071 | 47.5558 | 52.3328 | 57.3126 | 61.3844 | 65.2262 | 70.9187 | 75.063 | 79.2377 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576
97% | 12.9115 | 10.5047 | 11.9347 | 13.0688 | 14.4111 | 15.7949 | 17.2635 | 18.9423 | 20.9166 | 22.7671 | 24.7113 | 28.0125 | 29.1417 | 31.2595 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 |  | 53.8775 | 46.7879 | 51.6408 | 55.7075 | 59.3123 | 64.9753 | 70.0958 | 77.1886 | 84.5824 | 90.6281 | 96.3323 | 104.7844 | 110.9376 | 117.1362 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987
95% | 12.4534 | 10.0836 | 11.4916 | 12.6083 | 13.93 | 15.2924 | 16.7384 | 18.3914 | 20.3354 | 22.1574 | 24.0716 | 27.322 | 28.4339 | 30.5191 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 |  | 104.5403 | 90.5793 | 100.1358 | 108.1441 | 115.2428 | 126.3946 | 136.478 | 150.4453 | 165.0053 | 176.9108 | 188.1436 | 204.7877 | 216.905 | 229.1113 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344
90% | 102.4598 | 81.9097 | 94.1198 | 103.8034 | 115.2646 | 127.0798 | 139.619 | 153.9538 | 170.8116 | 186.6118 | 203.2119 | 231.399 | 241.0406 | 259.1237 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 |  | 145.5592 | 125.3812 | 139.1933 | 150.7678 | 161.0276 | 177.1454 | 191.7192 | 211.9063 | 232.95 | 250.1572 | 266.3921 | 290.448 | 307.9613 | 325.6033 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811
85% | 88.7163 | 69.277 | 80.8271 | 89.9872 | 100.8289 | 112.0055 | 123.8669 | 137.4268 | 153.3734 | 168.3195 | 184.0224 | 210.6858 | 219.8063 | 236.9119 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 |  | 244.5846 | 208.5309 | 233.2102 | 253.8913 | 272.2235 | 301.0225 | 327.0627 | 363.1327 | 400.7334 | 431.4791 | 460.4873 | 503.4701 | 534.7625 | 566.285 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584
80% | 83.3031 | 62.9381 | 75.0382 | 84.6345 | 95.9925 | 107.7013 | 120.1275 | 134.3332 | 151.0391 | 166.697 | 183.1476 | 211.0806 | 220.6354 | 238.5556 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 |  | 176.4199 | 148.4252 | 167.588 | 183.6462 | 197.8806 | 220.2422 | 240.4616 | 268.469 | 297.6648 | 321.5379 | 344.0619 | 377.4368 | 401.7344 | 426.2108 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242
75% | 108.852 | 78.2428 | 96.4297 | 110.8532 | 127.9246 | 145.5233 | 164.2003 | 185.5518 | 210.6613 | 234.1955 | 258.9213 | 300.9056 | 315.2667 | 342.2012 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 |  | 173.0481 | 142.9932 | 163.5662 | 180.8063 | 196.0882 | 220.0955 | 241.8029 | 271.8714 | 303.2159 | 328.8458 | 353.0275 | 388.8585 | 414.9443 | 441.2219 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423
70% | 242.705 | 160.3811 | 209.295 | 248.0873 | 294.0011 | 341.3328 | 391.565 | 448.9902 | 516.5227 | 579.8184 | 646.3187 | 759.2361 | 797.8606 | 870.3014 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 |  | 216.7103 | 174.5365 | 203.4051 | 227.5968 | 249.0408 | 282.7284 | 313.1888 | 355.3817 | 399.365 | 435.3296 | 469.262 | 519.541 | 556.1452 | 593.0186 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057
65% | 239.9449 | 133.3064 | 196.6672 | 246.9168 | 306.3914 | 367.7027 | 432.771 | 507.1569 | 594.6353 | 676.6255 | 762.7668 | 909.0346 | 959.067 | 1052.9034 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 |  | 217.3105 | 168.2289 | 201.826 | 229.9801 | 254.9365 | 294.1419 | 329.5915 | 378.6953 | 429.8828 | 471.7382 | 511.2284 | 569.7428 | 612.3426 | 655.2556 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882
60% | 573.2972 | 175.3008 | 411.757 | 599.321 | 821.318 | 1050.171 | 1293.0474 | 1570.7031 | 1897.2283 | 2203.2682 | 2524.8027 | 3070.7675 | 3257.5203 | 3607.7777 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 |  | 442.0796 | 319.3756 | 403.3682 | 473.7535 | 536.1444 | 634.158 | 722.782 | 845.5415 | 973.5103 | 1078.1488 | 1176.8743 | 1323.1602 | 1429.6596 | 1536.9421 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237
55% | 381.0194 |  | 136.1535 | 430.9394 | 863.9541 | 1310.3415 | 1784.0823 | 2325.6616 | 2962.563 | 3559.5068 | 4186.6736 | 5251.6012 | 5615.8706 | 6299.0625 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 |  | 286.4051 | 177.6985 | 252.1097 | 314.4659 | 369.7396 | 456.5724 | 535.0867 | 643.8425 | 757.2134 | 849.9153 | 937.3788 | 1066.9773 | 1161.3279 | 1256.3723 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971
50% |  |  |  | 0.14412 | 203.1188 | 781.1825 | 1629.226 | 2603.733 | 3749.7605 | 4823.8893 | 5952.4007 | 7868.6101 | 8524.0692 | 9753.3911 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 |  | 360.2162 | 119.9202 | 283.539 | 422.9541 | 546.5343 | 740.6737 | 916.215 | 1159.3697 | 1412.8427 | 1620.1043 | 1815.654 | 2105.4085 | 2316.3562 | 2528.8551 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307
45% | [6 empty] | 148.0142 | 781.2185 | 1972.306 | 3126.2423 | 4338.6019 | 6397.1855 | 7101.3451 | 8422.0054 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 |  | 138.3055 |  | 53.4493 | 235.0575 | 492.2929 | 953.0292 | 1369.6278 | 1946.6883 | 2548.2366 | 3040.1146 | 3504.1977 | 4191.8501 | 4692.4761 | 5196.7834 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008
40% | [8 empty] | 179.4633 | 1063.2321 | 2671.8859 | 5729.7119 | 6775.6727 | 8737.3855 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | [5 empty] | 0.49049 | 208.8808 | 693.0821 | 1679.0967 | 2739.4369 | 3606.4631 | 4424.4955 | 5636.61 | 6519.0562 | 7407.9911 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194
35% | [10 empty] | 22.7176 | 1374.291 | 2264.6059 | 4352.5967 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | [8 empty] | 95.7648 | 640.6468 | 1398.5353 | 2223.4418 | 3445.7422 | 4335.6039 | 5232.0089 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458
30% | FY38: 27.4824; FY39: 155.8275; FY40: 155.8275; FY41: 155.8275; FY42: 155.8275; FY43: 155.8275; FY44: 155.8275; FY45: 155.8275; FY46: 155.8275; FY47: 155.8275; FY48: 155.8275; FY49: 155.8275; FY50: 155.8275; FY51: 155.8275; FY52: 155.8275; FY53: 155.8275; FY54: 155.8275 | [10 empty] | 0.49093 | 224.8097 | 1238.6494 | 2424.2493 | 3908.703 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712
25% | [44 empty] | 61.4871 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1858.8794 | 792.7296 | 1335.9441 | 1953.7399 | 2971.8672 | 4390.2575 | 6278.1349 | 8905.3721 | 12620.9206 | 16856.5044 | 22009.3916 | 32398.316 | 36379.9495 | 44293.2304 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | E @ R (MWh) | 2614.363 | 1770.577 | 2306.0705 | 2893.9325 | 3511.7693 | 4746.6157 | 6158.9404 | 8526.3297 | 11471.7175 | 14192.9586 | 17094.1285 | 22074.3763 | 26147.6089 | 30602.4157 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504
Option 7 Summer POE50 W E @ R (MWh) N 2 | 1301.2156 | 554.9107 | 935.1608 | 1367.6179 | 2080.307 | 3073.1803 | 4394.6944 | 6233.7605 | 8834.6444 | 11799.5531 | 15406.5742 | 22678.8212 | 25465.9646 | 31005.2613 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 784.3089 | 531.1731 | 691.8211 | 868.1798 | 1053.5308 | 1423.9847 | 1847.6821 | 2557.8989 | 3441.5153 | 4257.8876 | 5128.2385 | 6622.3129 | 7844.2827 | 9180.7247 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 7.7244 | 4.29 | 6.3831 | 9.0539 | 11.6398 | 13.9431 | 17.1001 | 20.5496 | 24.082 | 27.5821 | 30.6942 | 34.0844 | 35.3876 | 39.7658 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 | 44.2934 |  | 10.3325 | 6.9085 | 9.1195 | 11.823 | 14.3438 | 17.0271 | 19.8475 | 23.8643 | 27.3684 | 30.6736 | 34.1083 | 38.2215 | 39.6082 | 44.0428 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765 | 48.1765
98% | 3.6773 | 1.9774 | 3.0134 | 4.3354 | 5.6153 | 6.7554 | 8.318 | 10.0255 | 11.7739 | 13.5064 | 15.0468 | 16.7248 | 17.3699 | 19.537 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 | 21.7781 |  | 4.9683 | 3.2735 | 4.3679 | 5.706 | 6.9538 | 8.2819 | 9.6779 | 11.6662 | 13.4006 | 15.0366 | 16.7367 | 18.7726 | 19.459 | 21.654 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001 | 23.7001
97% | 6.9849 | 3.6195 | 5.6706 | 8.2877 | 10.8216 | 13.0786 | 16.1721 | 19.5523 | 23.0137 | 26.4434 | 29.493 | 32.815 | 34.0921 | 38.3822 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 | 42.8188 |  | 9.5406 | 6.1854 | 8.352 | 11.0011 | 13.4713 | 16.1006 | 18.8643 | 22.8004 | 26.234 | 29.4728 | 32.8384 | 36.869 | 38.2278 | 42.5733 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239 | 46.6239
95% | 9.6454 | 4.675 | 7.7042 | 11.5696 | 15.3119 | 18.6453 | 23.2142 | 28.2065 | 33.3188 | 38.3841 | 42.8881 | 47.7945 | 49.6806 | 56.0169 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 | 62.5694 |  | 13.4199 | 8.4646 | 11.6645 | 15.577 | 19.2253 | 23.1085 | 27.1904 | 33.0036 | 38.0749 | 42.8584 | 47.8291 | 53.7819 | 55.7888 | 62.2068 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892 | 68.1892
90% | 7.7042 | 2.915 | 5.8338 | 9.5582 | 13.1641 | 16.3759 | 20.7783 | 25.5886 | 30.5145 | 35.3952 | 39.735 | 44.4624 | 46.2798 | 52.385 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 | 58.6986 |  | 11.3411 | 6.5665 | 9.6497 | 13.4196 | 16.9348 | 20.6765 | 24.6095 | 30.2108 | 35.0972 | 39.7063 | 44.4958 | 50.2316 | 52.1653 | 58.3493 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136 | 64.1136
85% | 59.1725 | 6.5594 | 37.941 | 80.2181 | 121.15 | 157.6086 | 207.5815 | 262.1847 | 318.1 | 373.5026 | 422.7651 | 476.4282 | 497.0576 | 566.3606 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 | 638.0285 |  | 100.4564 | 46.2576 | 81.2564 | 124.05 | 163.9527 | 206.4256 | 251.0706 | 314.6534 | 370.1203 | 422.4394 | 476.8066 | 541.9157 | 563.8663 | 634.0625 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954 | 699.4954
80% | 66.1755 |  | 19.1279 | 116.8852 | 215.5116 | 303.3595 | 423.7706 | 555.3382 | 690.0675 | 823.5613 | 942.2604 | 1071.5629 | 1121.27 | 1288.2572 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 | 1460.9428 |  | 165.6499 | 35.3125 | 119.3871 | 222.4994 | 318.6459 | 420.9852 | 528.5585 | 681.7629 | 815.4116 | 941.4757 | 1072.4748 | 1229.3566 | 1282.2472 | 1451.3867 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488 | 1609.0488
75% | 10.2262 |  |  | 93.5568 | 377.4509 | 633.9922 | 985.6274 | 1369.8429 | 1763.2916 | 2153.1324 | 2499.7681 | 2877.3687 | 3022.528 | 3510.1789 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 | 4014.4709 |  | 231.8404 |  | 99.7224 | 397.8571 | 678.6328 | 977.4934 | 1291.6386 | 1739.0397 | 2129.3327 | 2497.4763 | 2880.0318 | 3338.1721 | 3492.628 | 3986.5643 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834 | 4446.9834
70% |  |  |  |  | 212.4458 | 755.5237 | 1520.3879 | 2356.1194 | 3211.9346 | 4059.9021 | 4813.8914 | 5635.2347 | 5950.9798 | 7011.7001 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 | 8108.6179 |  | 33.4714 |  |  | 249.167 | 852.6245 | 1502.6951 | 2186.0122 | 3159.1828 | 4008.134 | 4808.9065 | 5641.0272 | 6637.5573 | 6973.5242 | 8047.9163 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033 | 9049.4033
65% | [5 empty] | 124.667 | 854.8962 | 1742.9773 | 2652.4003 | 3553.4839 | 4354.7027 | 5227.4943 | 5563.0175 | 6690.1807 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | 7855.8087 | [5 empty] | 188.8845 | 836.0951 | 1562.2148 | 2596.3441 | 3498.4731 | 4349.4055 | 5233.6497 | 6292.6018 | 6649.6135 | 7791.3048 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242 | 8855.5242
60% | [6 empty] | 108.2178 | 882.8726 | 1815.9042 | 2740.38 | 3562.3985 | 4457.8479 | 4802.0813 | 5958.5057 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | 7154.3936 | [6 empty] | 99.1317 | 697.4174 | 1758.3928 | 2683.9411 | 3556.9639 | 4464.1631 | 5550.6057 | 5916.8854 | 7088.2151 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618 | 8180.0618
55% | [7 empty] | 77.7648 | 878.2155 | 1956.2796 | 2914.8646 | 3959.0799 | 4360.5028 | 5709.0504 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | 7103.6177 | [7 empty] | 20.0065 | 811.1494 | 1890.4642 | 2908.5271 | 3966.4443 | 5233.3836 | 5660.5155 | 7026.4447 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859 | 8299.6859
50% | [8 empty] | 11.6315 | 564.915 | 1570.6907 | 2710.1367 | 3148.1687 | 4619.7015 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | 6141.451 | [8 empty] | 4.4119 | 509.0069 | 1563.7752 | 2718.1727 | 4100.6547 | 4566.7403 | 6057.2399 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986 | 7446.5986
45% | [10 empty] | 132.5918 | 960.492 | 1458.8799 | 3249.0414 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | 5100.2928 | [10 empty] | 129.8083 | 968.7958 | 2617.6063 | 3184.6126 | 4997.8477 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419 | 6688.0419
40% | [12 empty] | 1.595 | 904.5952 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | 3332.2872 | [12 empty] | 405.0509 | 845.1405 | 3175.0768 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163 | 5768.8163
35% | FY39: 23.8357; FY40: 23.8357; FY41: 23.8357; FY42: 23.8357; FY43: 23.8357; FY44: 23.8357; FY45: 23.8357; FY46: 23.8357; FY47: 23.8357; FY48: 23.8357; FY49: 23.8357; FY50: 23.8357; FY51: 23.8357; FY52: 23.8357; FY53: 23.8357; FY54: 23.8357 | [14 empty] | 13.9282 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791 | 493.9791
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 171.3105 | 24.0364 | 85.674 | 333.4649 | 983.111 | 2043.9492 | 4186.0642 | 7351.0223 | 11464.2481 | 16366.4681 | 21371.7903 | 27551.5264 | 30108.8907 | 39713.6588 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | 51163.9052 | E @ R (MWh) | 581.0205 | 112.9686 | 343.5196 | 1051.1003 | 2273.6695 | 4128.0206 | 6637.1083 | 11186.4823 | 16045.0591 | 21336.5256 | 27597.5743 | 36144.7813 | 39341.0228 | 50498.8132 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421 | 61788.4421
Option 8 Winter POE50 W E @ R (MWh) N 2 | 119.9174 | 16.8255 | 59.9718 | 233.4254 | 688.1777 | 1430.7644 | 2930.2449 | 5145.7156 | 8024.9736 | 11456.5276 | 14960.2532 | 19286.0685 | 21076.2235 | 27799.5611 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | 35814.7336 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 174.3061 | 33.8906 | 103.0559 | 315.3301 | 682.1008 | 1238.4062 | 1991.1325 | 3355.9447 | 4813.5177 | 6400.9577 | 8279.2723 | 10843.4344 | 11802.3068 | 15149.644 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326 | 18536.5326
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.6735 | 16.2619 | 17.9127 | 19.2961 | 20.5223 | 22.4487 | 24.1905 | 26.6033 | 29.1184 | 31.175 | 33.1154 | 35.9906 | 38.0837 | 40.1923 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247 | 42.4247
98% | 13.2169 | 10.7854 | 12.2301 | 13.3759 | 14.7319 | 16.1299 | 17.6135 | 19.3096 | 21.3042 | 23.1736 | 25.1377 | 28.4728 | 29.6135 | 31.7531 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 | 33.3917 |  | 36.6327 | 31.8578 | 35.1263 | 37.8652 | 40.2931 | 44.1071 | 47.5558 | 52.3328 | 57.3126 | 61.3844 | 65.2262 | 70.9187 | 75.063 | 79.2377 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576 | 83.6576
97% | 12.9115 | 10.5047 | 11.9347 | 13.0688 | 14.4111 | 15.7949 | 17.2635 | 18.9423 | 20.9166 | 22.7671 | 24.7113 | 28.0125 | 29.1417 | 31.2595 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 | 32.8814 |  | 53.8775 | 46.7879 | 51.6408 | 55.7075 | 59.3123 | 64.9753 | 70.0958 | 77.1886 | 84.5824 | 90.6281 | 96.3323 | 104.7844 | 110.9376 | 117.1362 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987 | 123.6987
95% | 12.4534 | 10.0836 | 11.4916 | 12.6083 | 13.93 | 15.2924 | 16.7384 | 18.3914 | 20.3354 | 22.1574 | 24.0716 | 27.322 | 28.4339 | 30.5191 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 | 32.1161 |  | 104.5403 | 90.5793 | 100.1358 | 108.1441 | 115.2428 | 126.3946 | 136.478 | 150.4453 | 165.0053 | 176.9108 | 188.1436 | 204.7877 | 216.905 | 229.1113 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344 | 242.0344
90% | 102.4598 | 81.9097 | 94.1198 | 103.8034 | 115.2646 | 127.0798 | 139.619 | 153.9538 | 170.8116 | 186.6118 | 203.2119 | 231.399 | 241.0406 | 259.1237 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 | 272.9725 |  | 145.5592 | 125.3812 | 139.1933 | 150.7678 | 161.0276 | 177.1454 | 191.7192 | 211.9063 | 232.95 | 250.1572 | 266.3921 | 290.448 | 307.9613 | 325.6033 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811 | 344.2811
85% | 88.7163 | 69.277 | 80.8271 | 89.9872 | 100.8289 | 112.0055 | 123.8669 | 137.4268 | 153.3734 | 168.3195 | 184.0224 | 210.6858 | 219.8063 | 236.9119 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 | 250.0121 |  | 244.5846 | 208.5309 | 233.2102 | 253.8913 | 272.2235 | 301.0225 | 327.0627 | 363.1327 | 400.7334 | 431.4791 | 460.4873 | 503.4701 | 534.7625 | 566.285 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584 | 599.6584
80% | 83.3031 | 62.9381 | 75.0382 | 84.6345 | 95.9925 | 107.7013 | 120.1275 | 134.3332 | 151.0391 | 166.697 | 183.1476 | 211.0806 | 220.6354 | 238.5556 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 | 252.2797 |  | 176.4199 | 148.4252 | 167.588 | 183.6462 | 197.8806 | 220.2422 | 240.4616 | 268.469 | 297.6648 | 321.5379 | 344.0619 | 377.4368 | 401.7344 | 426.2108 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242 | 452.1242
75% | 108.852 | 78.2428 | 96.4297 | 110.8532 | 127.9246 | 145.5233 | 164.2003 | 185.5518 | 210.6613 | 234.1955 | 258.9213 | 300.9056 | 315.2667 | 342.2012 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 | 362.8289 |  | 173.0481 | 142.9932 | 163.5662 | 180.8063 | 196.0882 | 220.0955 | 241.8029 | 271.8714 | 303.2159 | 328.8458 | 353.0275 | 388.8585 | 414.9443 | 441.2219 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423 | 469.0423
70% | 242.705 | 160.3811 | 209.295 | 248.0873 | 294.0011 | 341.3328 | 391.565 | 448.9902 | 516.5227 | 579.8184 | 646.3187 | 759.2361 | 797.8606 | 870.3014 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 | 925.78 |  | 216.7103 | 174.5365 | 203.4051 | 227.5968 | 249.0408 | 282.7284 | 313.1888 | 355.3817 | 399.365 | 435.3296 | 469.262 | 519.541 | 556.1452 | 593.0186 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057 | 632.057
65% | 239.9449 | 133.3064 | 196.6672 | 246.9168 | 306.3914 | 367.7027 | 432.771 | 507.1569 | 594.6353 | 676.6255 | 762.7668 | 909.0346 | 959.067 | 1052.9034 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 | 1124.7677 |  | 217.3105 | 168.2289 | 201.826 | 229.9801 | 254.9365 | 294.1419 | 329.5915 | 378.6953 | 429.8828 | 471.7382 | 511.2284 | 569.7428 | 612.3426 | 655.2556 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882 | 700.6882
60% | 573.2972 | 175.3008 | 411.757 | 599.321 | 821.318 | 1050.171 | 1293.0474 | 1570.7031 | 1897.2283 | 2203.2682 | 2524.8027 | 3070.7675 | 3257.5203 | 3607.7777 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 | 3876.0211 |  | 442.0796 | 319.3756 | 403.3682 | 473.7535 | 536.1444 | 634.158 | 722.782 | 845.5415 | 973.5103 | 1078.1488 | 1176.8743 | 1323.1602 | 1429.6596 | 1536.9421 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237 | 1650.5237
55% | 381.0194 |  | 136.1535 | 430.9394 | 863.9541 | 1310.3415 | 1784.0823 | 2325.6616 | 2962.563 | 3559.5068 | 4186.6736 | 5251.6012 | 5615.8706 | 6299.0625 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 | 6822.2828 |  | 286.4051 | 177.6985 | 252.1097 | 314.4659 | 369.7396 | 456.5724 | 535.0867 | 643.8425 | 757.2134 | 849.9153 | 937.3788 | 1066.9773 | 1161.3279 | 1256.3723 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971 | 1356.9971
50% |  |  |  | 0.14412 | 203.1188 | 781.1825 | 1629.226 | 2603.733 | 3749.7605 | 4823.8893 | 5952.4007 | 7868.6101 | 8524.0692 | 9753.3911 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 | 10694.8632 |  | 360.2162 | 119.9202 | 283.539 | 422.9541 | 546.5343 | 740.6737 | 916.215 | 1159.3697 | 1412.8427 | 1620.1043 | 1815.654 | 2105.4085 | 2316.3562 | 2528.8551 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307 | 2753.8307
45% | [6 empty] | 148.0142 | 781.2185 | 1972.306 | 3126.2423 | 4338.6019 | 6397.1855 | 7101.3451 | 8422.0054 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 | 9433.4287 |  | 138.3055 |  | 53.4493 | 235.0575 | 492.2929 | 953.0292 | 1369.6278 | 1946.6883 | 2548.2366 | 3040.1146 | 3504.1977 | 4191.8501 | 4692.4761 | 5196.7834 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008 | 5730.7008
40% | [8 empty] | 179.4633 | 1063.2321 | 2671.8859 | 5729.7119 | 6775.6727 | 8737.3855 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | 10239.7566 | [5 empty] | 0.49049 | 208.8808 | 693.0821 | 1679.0967 | 2739.4369 | 3606.4631 | 4424.4955 | 5636.61 | 6519.0562 | 7407.9911 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194 | 8349.1194
35% | [10 empty] | 22.7176 | 1374.291 | 2264.6059 | 4352.5967 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | 6004.4772 | [8 empty] | 95.7648 | 640.6468 | 1398.5353 | 2223.4418 | 3445.7422 | 4335.6039 | 5232.0089 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458 | 6181.0458
30% | FY38: 27.4824; FY39: 155.8275; FY40: 155.8275; FY41: 155.8275; FY42: 155.8275; FY43: 155.8275; FY44: 155.8275; FY45: 155.8275; FY46: 155.8275; FY47: 155.8275; FY48: 155.8275; FY49: 155.8275; FY50: 155.8275; FY51: 155.8275; FY52: 155.8275; FY53: 155.8275; FY54: 155.8275 | [10 empty] | 0.49093 | 224.8097 | 1238.6494 | 2424.2493 | 3908.703 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712 | 5517.9712
25% | [44 empty] | 61.4871 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954 | 530.6954
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 1858.8794 | 792.7296 | 1335.9441 | 1953.7399 | 2971.8672 | 4390.2575 | 6278.1349 | 8905.3721 | 12620.9206 | 16856.5044 | 22009.3916 | 32398.316 | 36379.9495 | 44293.2304 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | 50513.6872 | E @ R (MWh) | 2614.363 | 1770.577 | 2306.0705 | 2893.9325 | 3511.7693 | 4746.6157 | 6158.9404 | 8526.3297 | 11471.7175 | 14192.9586 | 17094.1285 | 22074.3763 | 26147.6089 | 30602.4157 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504 | 35760.5504
Option 8 Summer POE50 W E @ R (MWh) N 2 | 1301.2156 | 554.9107 | 935.1608 | 1367.6179 | 2080.307 | 3073.1803 | 4394.6944 | 6233.7605 | 8834.6444 | 11799.5531 | 15406.5742 | 22678.8212 | 25465.9646 | 31005.2613 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | 35359.581 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 784.3089 | 531.1731 | 691.8211 | 868.1798 | 1053.5308 | 1423.9847 | 1847.6821 | 2557.8989 | 3441.5153 | 4257.8876 | 5128.2385 | 6622.3129 | 7844.2827 | 9180.7247 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651 | 10728.1651

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-CLN-TRNFMR-9000006730 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 2 Pof | DS-CLN-TRNFMR-9000001306 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 3 Pof | DS-CLN-TRNFMR-XXXXXXXXXXXX | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543% | 0.1543%
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.3954% | 0.3997% | 0.4449% | 0.4933% | 0.545% | 0.6% | 0.6585% | 0.7205% | 0.7861% | 0.8553% | 0.9283% | 1.005% | 1.086% | 1.17% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259% | 1.259%
N-1 Risk |  | 0.1525% | 0.1542% | 0.1716% | 0.1903% | 0.2103% | 0.2315% | 0.254% | 0.278% | 0.3033% | 0.33% | 0.3581% | 0.3878% | 0.4189% | 0.4515% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856% | 0.4856%
N-2 Risk |  | 9.757e-05% | 0.0001015% | 0.0001271% | 0.0001578% | 0.0001945% | 0.000238% | 0.0002892% | 0.0003491% | 0.0004187% | 0.0004994% | 0.0005922% | 0.0006986% | 0.0008201% | 0.0009581% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114% | 0.001114%
N Risk |  | 99.85% | 99.85% | 99.83% | 99.81% | 99.79% | 99.77% | 99.75% | 99.72% | 99.7% | 99.67% | 99.64% | 99.61% | 99.58% | 99.55% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51% | 99.51%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21807 | 10.3902 | 25.1544 | 47.0621 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0069571 | 0 | 0.002473 | 0.015326 | 0.035438 | 0.087998 | 0.1673 | 0.333 | 0.61415 | 0.9775 | 1.4865 | 2.6085 | 3.5805 | 5.6824 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0030306 | 0.0015236 | 0.0029834 | 0.0056717 | 0.01112 | 0.021414 | 0.040092 | 0.074351 | 0.12912 | 0.20741 | 0.31725 | 0.5101 | 0.66798 | 0.97704 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674
Total EUE (MWh) - Option 1 | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Cost of EUE ($) - Option 1 | 440.1284 | 67.1404 | 240.4469 | 925.2826 | 2051.671 | 4821.4687 | 9139.1494 | 17950.7134 | 32753.385 | 52215.3874 | 89096.8517 | 595292.1162 | 1295691.5485 | 2367341.3146 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247
Hours at Risk pA. (Hrs) (N) | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 0.5944 | 1.7289 | 8.5358 | 14.9646 | 14.9646 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589 | 20.2589
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9247 | 13.8741 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151 | 31.5151
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0069571 | 0 | 0.002473 | 0 | 4.3923e-05 | 0.012211 | 0.043475 | 0.126 | 0.27145 | 0.47104 | 0.77272 | 1.462 | 2.0449 | 3.0895 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445 | 4.7445
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0030306 | 0.0015236 | 0.0029834 | 0.0018702 | 0.0034204 | 0.0069436 | 0.014642 | 0.033002 | 0.066797 | 0.1186 | 0.19503 | 0.338 | 0.45356 | 0.69421 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075 | 1.0075
Total EUE (MWh) - Option 2 | 0.0099877 | 0.0015236 | 0.0054564 | 0.0018702 | 0.0034643 | 0.019155 | 0.058117 | 0.159 | 0.33825 | 0.58964 | 0.96775 | 1.8 | 5.4231 | 17.6578 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672 | 37.2672
Cost of EUE ($) - Option 2 | 440.1284 | 67.1404 | 240.4469 | 82.4141 | 152.6601 | 844.0924 | 2561.0457 | 7006.6169 | 14905.6693 | 25983.7493 | 42645.8249 | 79318.915 | 238980.6329 | 778124.8034 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122 | 1642250.0122
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21807 | 10.3902 | 25.1544 | 47.0621 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0069571 | 0 | 0.002473 | 0.015326 | 0.035438 | 0.087998 | 0.1673 | 0.333 | 0.61415 | 0.9775 | 1.4865 | 2.6085 | 3.5805 | 5.6824 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0030306 | 0.0015236 | 0.0029834 | 0.0056717 | 0.01112 | 0.021414 | 0.040092 | 0.074351 | 0.12912 | 0.20741 | 0.31725 | 0.5101 | 0.66798 | 0.97704 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674
Total EUE (MWh) - Option 3 | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Cost of EUE ($) - Option 3 | 440.1284 | 67.1404 | 240.4469 | 925.2826 | 2051.671 | 4821.4687 | 9139.1494 | 17950.7134 | 32753.385 | 52215.3874 | 89096.8517 | 595292.1162 | 1295691.5485 | 2367341.3146 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019683 | 4.0219 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659 | 16.659
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0069571 | 0 | 0.002473 | 0 | 0 | 0.00011951 | 0.01238 | 0.062827 | 0.16991 | 0.31127 | 0.52665 | 1.063 | 1.5397 | 2.3288 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676 | 3.4676
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0030306 | 0.0015236 | 0.0029834 | 0.0011808 | 0.0020252 | 0.003897 | 0.0080526 | 0.019347 | 0.043623 | 0.083744 | 0.14548 | 0.26545 | 0.36204 | 0.57048 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551 | 0.84551
Total EUE (MWh) - Option 4 | 0.0099877 | 0.0015236 | 0.0054564 | 0.0011808 | 0.0020252 | 0.0040166 | 0.020433 | 0.082174 | 0.21353 | 0.39501 | 0.67214 | 1.3284 | 1.9215 | 6.9212 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721 | 20.9721
Cost of EUE ($) - Option 4 | 440.1284 | 67.1404 | 240.4469 | 52.0331 | 89.2453 | 176.9972 | 900.4 | 3621.157 | 9409.8073 | 17407.0753 | 29619.0115 | 58540.5141 | 84672.7967 | 304995.434 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296 | 924175.296
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21807 | 10.3902 | 25.1544 | 47.0621 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0069571 | 0 | 0.002473 | 0.015326 | 0.035438 | 0.087998 | 0.1673 | 0.333 | 0.61415 | 0.9775 | 1.4865 | 2.6085 | 3.5805 | 5.6824 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0030306 | 0.0015236 | 0.0029834 | 0.0056717 | 0.01112 | 0.021414 | 0.040092 | 0.074351 | 0.12912 | 0.20741 | 0.31725 | 0.5101 | 0.66798 | 0.97704 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674
Total EUE (MWh) - Option 5 | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Cost of EUE ($) - Option 5 | 440.1284 | 67.1404 | 240.4469 | 925.2826 | 2051.671 | 4821.4687 | 9139.1494 | 17950.7134 | 32753.385 | 52215.3874 | 89096.8517 | 595292.1162 | 1295691.5485 | 2367341.3146 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21807 | 10.3902 | 25.1544 | 47.0621 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0069571 | 0 | 0.002473 | 0.015326 | 0.035438 | 0.087998 | 0.1673 | 0.333 | 0.61415 | 0.9775 | 1.4865 | 2.6085 | 3.5805 | 5.6824 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0030306 | 0.0015236 | 0.0029834 | 0.0056717 | 0.01112 | 0.021414 | 0.040092 | 0.074351 | 0.12912 | 0.20741 | 0.31725 | 0.5101 | 0.66798 | 0.97704 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674
Total EUE (MWh) - Option 6 | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Cost of EUE ($) - Option 6 | 440.1284 | 67.1404 | 240.4469 | 925.2826 | 2051.671 | 4821.4687 | 9139.1494 | 17950.7134 | 32753.385 | 52215.3874 | 89096.8517 | 595292.1162 | 1295691.5485 | 2367341.3146 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21807 | 10.3902 | 25.1544 | 47.0621 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0069571 | 0 | 0.002473 | 0.015326 | 0.035438 | 0.087998 | 0.1673 | 0.333 | 0.61415 | 0.9775 | 1.4865 | 2.6085 | 3.5805 | 5.6824 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0030306 | 0.0015236 | 0.0029834 | 0.0056717 | 0.01112 | 0.021414 | 0.040092 | 0.074351 | 0.12912 | 0.20741 | 0.31725 | 0.5101 | 0.66798 | 0.97704 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674
Total EUE (MWh) - Option 7 | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Cost of EUE ($) - Option 7 | 440.1284 | 67.1404 | 240.4469 | 925.2826 | 2051.671 | 4821.4687 | 9139.1494 | 17950.7134 | 32753.385 | 52215.3874 | 89096.8517 | 595292.1162 | 1295691.5485 | 2367341.3146 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21807 | 10.3902 | 25.1544 | 47.0621 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651 | 79.4651
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0069571 | 0 | 0.002473 | 0.015326 | 0.035438 | 0.087998 | 0.1673 | 0.333 | 0.61415 | 0.9775 | 1.4865 | 2.6085 | 3.5805 | 5.6824 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321 | 9.3321
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0030306 | 0.0015236 | 0.0029834 | 0.0056717 | 0.01112 | 0.021414 | 0.040092 | 0.074351 | 0.12912 | 0.20741 | 0.31725 | 0.5101 | 0.66798 | 0.97704 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674 | 1.3674
Total EUE (MWh) - Option 8 | 0.0099877 | 0.0015236 | 0.0054564 | 0.020997 | 0.046558 | 0.10941 | 0.20739 | 0.40735 | 0.74326 | 1.1849 | 2.0219 | 13.5088 | 29.4028 | 53.7215 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646 | 90.1646
Cost of EUE ($) - Option 8 | 440.1284 | 67.1404 | 240.4469 | 925.2826 | 2051.671 | 4821.4687 | 9139.1494 | 17950.7134 | 32753.385 | 52215.3874 | 89096.8517 | 595292.1162 | 1295691.5485 | 2367341.3146 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247 | 3973277.6247