## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 34378474.2948 | 37.17% | 18.2965
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 31576189.3656 | 34.14% | 11.7393
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 10621047.2058 | 11.48% | 3.8453
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 15925855.934 | 17.22% | 3.8307
[5 empty] | 92501566.8003 |  | 37.7119
Customer No. and Vol per Feeder | [6 empty] | 37711.8651 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 31576189.3656 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 192.2577 | E@R MWh | 192.2577
RESIDENTL | 34378474.2948 | [14 empty] | cost of EUE ($) | 7250394.8946 | cost of EUE ($M) | 7.2504
FARM | 15925855.934
INDUSTRIAL | 10621047.2058
Forecast (FCT)
Forecast | 2031
Summer POE50 | 31.5616
Summer POE10 | 33.5865
Winter POE50 | 30.3426
Winter POE10 | 32.5932
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 0 |  | Summer POE50 | 31.5616 |  |  | 100% | 0 | 31.5616 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 33.5865 |  |  | 99% | 0.37816 | 31.2459 | 99% |  | 99% | 11.8758 | 99% | 11.8758
Embedded Generation |  |  | Winter POE50 | 30.3426 |  |  | 98% | 0.37816 | 30.9303 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 32.5932 |  |  | 97% | 0.75633 | 30.6147 | 97% |  | 97% | 11.6371 | 97% | 11.6371
Year | 2031 | [5 empty] | 95% | 0.75633 | 29.9835 | 95% |  | 95% | 0 | 95% | 0
Capacity | 0 | [5 empty] | 90% | 3.7816 | 28.4054 | 90% |  | 90% | 88.3224 | 90% | 88.3224
[7 empty] | 85% | 13.6139 | 26.8273 | 85% |  | 85% | 271.5316 | 85% | 271.5316
Demand Mangement | [6 empty] | 80% | 35.1693 | 25.2493 | 80% |  | 80% | 561.2649 | 80% | 561.2649
[7 empty] | 75% | 80.549 | 23.6712 | 75% |  | 75% | 1109.9975 | 75% | 1109.9975
Year | 2031 | [5 empty] | 70% | 192.1075 | 22.0931 | 70% |  | 70% | 2552.6958 | 70% | 2552.6958
Capacity | 0 | [5 empty] | 65% | 403.1231 | 20.515 | 65% |  | 65% | 4495.4898 | 65% | 4495.4898
[7 empty] | 60% | 739.3112 | 18.9369 | 60% |  | 60% | 6631.6381 | 60% | 6631.6381
LDC | [6 empty] | 55% | 1204.8314 | 17.3589 | 55% |  | 55% | 8448.2147 | 55% | 8448.2147
[7 empty] | 50% | 1783.0446 | 15.7808 | 50% |  | 50% | 9580.8895 | 50% | 9580.8895
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2370.3337 | 14.2027 | 45% |  | 45% | 8804.488 | 45% | 8804.488
100% | 0% | 0 |  |  |  |  | 40% | 2864.2163 | 12.6246 | 40% |  | 40% | 6624.7753 | 40% | 6624.7753
99% | 0.00861% | 0.37816 |  |  |  |  | 35% | 3297.9707 | 11.0465 | 35% |  | 35% | 5133.7383 | 35% | 5133.7383
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3579.7031 | 9.4685 | 30% |  | 30% | 2889.8725 | 30% | 2889.8725
97% | 0.01722% | 0.75633 |  |  |  |  | 25% | 3796.3913 | 7.8904 | 25% |  | 25% | 1880.7296 | 25% | 1880.7296
95% | 0.01722% | 0.75633 |  |  |  |  | 20% | 3975.6411 | 6.3123 | 20% |  | 20% | 1272.9165 | 20% | 1272.9165
90% | 0.0861% | 3.7816 |  |  |  |  | 15% | 4117.4527 | 4.7342 | 15% |  | 15% | 783.2643 | 15% | 783.2643
85% | 0.31% | 13.6139 |  |  |  |  | 10% | 4224.8514 | 3.1562 | 10% |  | 10% | 423.7087 | 10% | 423.7087
80% | 0.8008% | 35.1693 |  |  |  |  | 5% | 4310.3165 | 1.5781 | 5% |  | 5% | 202.306 | 5% | 202.306
75% | 1.834% | 80.549 |  |  |  |  | 9.992e-14% | 4382.5459 | 3.1536e-14 | 9.992e-14% |  | 9.992e-14% | 56.9918 | 9.992e-14% | 56.9918
70% | 4.374% | 192.1075 | [7 empty] | Total E@R | 0 | Total E@R | 61217.9846 | Total E@R | 61217.9846
65% | 9.179% | 403.1231 | [7 empty] | Total WE@R | 0 | Total WE@R | 66.7345 | Total WE@R | 0
60% | 16.83% | 739.3112 |  |  |  |  | MD Weighted LDC
55% | 27.43% | 1204.8314
50% | 40.6% | 1783.0446 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 53.97% | 2370.3337 |  |  |  |  | 100% | 0 | 33.5865 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 65.21% | 2864.2163 |  |  |  |  | 99% | 1.1345 | 33.2507
35% | 75.09% | 3297.9707 |  |  |  |  | 98% | 1.8908 | 32.9148 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 81.51% | 3579.7031 |  |  |  |  | 97% | 2.269 | 32.5789 | 100% |  | 100% |  | 100%
25% | 86.44% | 3796.3913 |  |  |  |  | 95% | 4.1598 | 31.9072 | 99% |  | 99% | 37.9131 | 99% | 37.9131
20% | 90.52% | 3975.6411 |  |  |  |  | 90% | 15.5047 | 30.2279 | 98% |  | 98% | 25.0214 | 98% | 25.0214
15% | 93.75% | 4117.4527 |  |  |  |  | 85% | 31.3876 | 28.5485 | 97% |  | 97% | 12.3837 | 97% | 12.3837
10% | 96.19% | 4224.8514 |  |  |  |  | 80% | 57.8591 | 26.8692 | 95% |  | 95% | 60.9659 | 95% | 60.9659
5% | 98.14% | 4310.3165 |  |  |  |  | 75% | 121.3907 | 25.1899 | 90% |  | 90% | 352.4589 | 90% | 352.4589
9.992e-14% | 99.78% | 4382.5459 |  |  |  |  | 70% | 273.4128 | 23.5106 | 85% |  | 85% | 466.7699 | 85% | 466.7699
[7 empty] | 65% | 529.43 | 21.8312 | 80% |  | 80% | 733.4956 | 80% | 733.4956
[7 empty] | 60% | 918.9392 | 20.1519 | 75% |  | 75% | 1653.6992 | 75% | 1653.6992
[7 empty] | 55% | 1454.0417 | 18.4726 | 70% |  | 70% | 3701.7713 | 70% | 3701.7713
LDC | [6 empty] | 50% | 2105.2406 | 16.7933 | 65% |  | 65% | 5804.1412 | 65% | 5804.1412
[7 empty] | 45% | 2758.3303 | 15.1139 | 60% |  | 60% | 8176.4121 | 60% | 8176.4121
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 3348.2666 | 13.4346 | 55% |  | 55% | 10334.0323 | 55% | 10334.0323
100% | 0% | 0 |  |  |  |  | 35% | 3816.434 | 11.7553 | 50% |  | 50% | 11482.5404 | 50% | 11482.5404
99% | 0.02583% | 1.1345 |  |  |  |  | 30% | 4067.1569 | 10.076 | 45% |  | 45% | 10419.1305 | 45% | 10419.1305
98% | 0.04305% | 1.8908 |  |  |  |  | 25% | 4236.9526 | 8.3966 | 40% |  | 40% | 8420.9106 | 40% | 8420.9106
97% | 0.05166% | 2.269 |  |  |  |  | 20% | 4332.6282 | 6.7173 | 35% |  | 35% | 5896.5426 | 35% | 5896.5426
95% | 0.09471% | 4.1598 |  |  |  |  | 15% | 4361.7469 | 5.038 | 30% |  | 30% | 2736.796 | 30% | 2736.796
90% | 0.353% | 15.5047 |  |  |  |  | 10% | 4375.7389 | 3.3587 | 25% |  | 25% | 1568.2835 | 25% | 1568.2835
85% | 0.7147% | 31.3876 |  |  |  |  | 5% | 4378.0079 | 1.6793 | 20% |  | 20% | 723.0171 | 20% | 723.0171
80% | 1.317% | 57.8591 |  |  |  |  | 9.992e-14% | 4379.1424 | 3.356e-14 | 15% |  | 15% | 171.149 | 15% | 171.149
75% | 2.764% | 121.3907 | [7 empty] | 10% |  | 10% | 58.7432 | 10% | 58.7432
70% | 6.225% | 273.4128 | [7 empty] | 5% |  | 5% | 5.7156 | 5% | 5.7156
65% | 12.05% | 529.43 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0.95259 | 9.992e-14% | 0.95259
60% | 20.92% | 918.9392 | [7 empty] | Total E@R | 0 | Total E@R | 72114.4172 | Total E@R | 72114.4172
55% | 33.11% | 1454.0417 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 33.6912 | Total WE@R | 0
50% | 47.93% | 2105.2406
45% | 62.8% | 2758.3303 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 76.24% | 3348.2666 |  |  |  |  | 100% | 0 | 30.3426
35% | 86.9% | 3816.434 |  |  |  |  | 99% | 0.2972 | 30.0392 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 92.6% | 4067.1569 |  |  |  |  | 98% | 0.8916 | 29.7357
25% | 96.47% | 4236.9526 |  |  |  |  | 97% | 1.7832 | 29.4323 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 98.65% | 4332.6282 |  |  |  |  | 95% | 4.458 | 28.8254 | 100% |  | 100% |  | 100%
15% | 99.31% | 4361.7469 |  |  |  |  | 90% | 15.1571 | 27.3083 | 99% |  | 99% | 8.9727 | 99% | 8.9727
10% | 99.63% | 4375.7389 |  |  |  |  | 85% | 39.5274 | 25.7912 | 98% |  | 98% | 17.765 | 98% | 17.765
5% | 99.68% | 4378.0079 |  |  |  |  | 80% | 110.5579 | 24.2741 | 97% |  | 97% | 26.377 | 97% | 26.377
9.992e-14% | 99.71% | 4379.1424 |  |  |  |  | 75% | 244.2972 | 22.7569 | 95% |  | 95% | 77.9135 | 95% | 77.9135
[7 empty] | 70% | 444.0146 | 21.2398 | 90% |  | 90% | 300.2917 | 90% | 300.2917
[7 empty] | 65% | 770.3386 | 19.7227 | 85% |  | 85% | 647.025 | 85% | 647.025
[7 empty] | 60% | 1209.3009 | 18.2055 | 80% |  | 80% | 1778.0788 | 80% | 1778.0788
LDC | [6 empty] | 55% | 1757.6322 | 16.6884 | 75% |  | 75% | 3144.9473 | 75% | 3144.9473
[7 empty] | 50% | 2378.4799 | 15.1713 | 70% |  | 70% | 4393.4576 | 70% | 4393.4576
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 3003.7856 | 13.6542 | 65% |  | 65% | 6683.5203 | 65% | 6683.5203
100% | 0% | 0 |  |  |  |  | 40% | 3548.2533 | 12.137 | 60% |  | 60% | 8324.529 | 60% | 8324.529
99% | 0.006767% | 0.2972 |  |  |  |  | 35% | 3927.7759 | 10.6199 | 55% |  | 55% | 9566.7268 | 55% | 9566.7268
98% | 0.0203% | 0.8916 |  |  |  |  | 30% | 4135.8149 | 9.1028 | 50% |  | 50% | 9890.0138 | 50% | 9890.0138
97% | 0.0406% | 1.7832 |  |  |  |  | 25% | 4252.0195 | 7.5856 | 45% |  | 45% | 9012.3594 | 45% | 9012.3594
95% | 0.1015% | 4.458 |  |  |  |  | 20% | 4325.4275 | 6.0685 | 40% |  | 40% | 7021.2357 | 40% | 7021.2357
90% | 0.3451% | 15.1571 |  |  |  |  | 15% | 4360.497 | 4.5514 | 35% |  | 35% | 4318.3846 | 35% | 4318.3846
85% | 0.9% | 39.5274 |  |  |  |  | 10% | 4373.8709 | 3.0343 | 30% |  | 30% | 2051.5427 | 30% | 2051.5427
80% | 2.517% | 110.5579 |  |  |  |  | 5% | 4381.8952 | 1.5171 | 25% |  | 25% | 969.6357 | 25% | 969.6357
75% | 5.562% | 244.2972 |  |  |  |  | 9.992e-14% | 4391.7028 | 3.0318e-14 | 20% |  | 20% | 501.1626 | 20% | 501.1626
70% | 10.11% | 444.0146 | [7 empty] | 15% |  | 15% | 186.217 | 15% | 186.217
65% | 17.54% | 770.3386 | [7 empty] | 10% |  | 10% | 50.725 | 10% | 50.725
60% | 27.53% | 1209.3009 | [7 empty] | 5% |  | 5% | 18.261 | 5% | 18.261
55% | 40.02% | 1757.6322 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 7.4397 | 9.992e-14% | 7.4397
50% | 54.15% | 2378.4799 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 68306.6159 | Total E@R | 68306.6159
45% | 68.39% | 3003.7856 | [7 empty] | Total WE@R | 0 | Total WE@R | 63.2646 | Total WE@R | 0
40% | 80.79% | 3548.2533 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 89.43% | 3927.7759 |  |  |  |  | 100% | 0 | 32.5932 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 94.17% | 4135.8149 |  |  |  |  | 99% | 0.2972 | 32.2673
25% | 96.81% | 4252.0195 |  |  |  |  | 98% | 0.8916 | 31.9413 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 98.48% | 4325.4275 |  |  |  |  | 97% | 2.0804 | 31.6154 | 100% |  | 100% |  | 100%
15% | 99.28% | 4360.497 |  |  |  |  | 95% | 4.1608 | 30.9635 | 99% |  | 99% | 9.6382 | 99% | 9.6382
10% | 99.59% | 4373.8709 |  |  |  |  | 90% | 11.5907 | 29.3339 | 98% |  | 98% | 19.0827 | 98% | 19.0827
5% | 99.77% | 4381.8952 |  |  |  |  | 85% | 32.6918 | 27.7042 | 97% |  | 97% | 37.778 | 97% | 37.778
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 84.1072 | 26.0746 | 95% |  | 95% | 65.0943 | 95% | 65.0943
[7 empty] | 75% | 202.095 | 24.4449 | 90% |  | 90% | 224.0039 | 90% | 224.0039
[7 empty] | 70% | 388.1413 | 22.8152 | 85% |  | 85% | 601.7834 | 85% | 601.7834
[7 empty] | 65% | 669.8855 | 21.1856 | 80% |  | 80% | 1382.5277 | 80% | 1382.5277
LDC | [6 empty] | 60% | 1104.687 | 19.5559 | 75% |  | 75% | 2980.3413 | 75% | 2980.3413
[7 empty] | 55% | 1631.62 | 17.9263 | 70% |  | 70% | 4396.288 | 70% | 4396.288
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 2253.9537 | 16.2966 | 65% |  | 65% | 6198.4901 | 65% | 6198.4901
100% | 0% | 0 |  |  |  |  | 45% | 2892.3362 | 14.6669 | 60% |  | 60% | 8857.2345 | 60% | 8857.2345
99% | 0.006767% | 0.2972 |  |  |  |  | 40% | 3473.3593 | 13.0373 | 55% |  | 55% | 9875.3018 | 55% | 9875.3018
98% | 0.0203% | 0.8916 |  |  |  |  | 35% | 3882.8989 | 11.4076 | 50% |  | 50% | 10649.0233 | 50% | 10649.0233
97% | 0.04737% | 2.0804 |  |  |  |  | 30% | 4127.1961 | 9.778 | 45% |  | 45% | 9883.2933 | 45% | 9883.2933
95% | 0.09474% | 4.1608 |  |  |  |  | 25% | 4245.1839 | 8.1483 | 40% |  | 40% | 8048.3988 | 40% | 8048.3988
90% | 0.2639% | 11.5907 |  |  |  |  | 20% | 4322.1583 | 6.5186 | 35% |  | 35% | 5005.5786 | 35% | 5005.5786
85% | 0.7443% | 32.6918 |  |  |  |  | 15% | 4354.2558 | 4.889 | 30% |  | 30% | 2587.7897 | 30% | 2587.7897
80% | 1.915% | 84.1072 |  |  |  |  | 10% | 4366.1437 | 3.2593 | 25% |  | 25% | 1057.5405 | 25% | 1057.5405
75% | 4.601% | 202.095 |  |  |  |  | 5% | 4374.4653 | 1.6297 | 20% |  | 20% | 564.4898 | 20% | 564.4898
70% | 8.837% | 388.1413 |  |  |  |  | 9.992e-14% | 4375.9513 | 3.2567e-14 | 15% |  | 15% | 183.0778 | 15% | 183.0778
65% | 15.25% | 669.8855 | [7 empty] | 10% |  | 10% | 48.4333 | 10% | 48.4333
60% | 25.15% | 1104.687 | [7 empty] | 5% |  | 5% | 20.342 | 5% | 20.342
55% | 37.15% | 1631.62 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 1.2108 | 9.992e-14% | 1.2108
50% | 51.32% | 2253.9537 | [7 empty] | Total E@R | 0 | Total E@R | 71969.7744 | Total E@R | 71969.7744
45% | 65.85% | 2892.3362 | [7 empty] | Total WE@R | 0 | Total WE@R | 28.5674 | Total WE@R | 0
40% | 79.08% | 3473.3593
35% | 88.41% | 3882.8989
30% | 93.97% | 4127.1961
25% | 96.66% | 4245.1839
20% | 98.41% | 4322.1583
15% | 99.14% | 4354.2558
10% | 99.41% | 4366.1437
5% | 99.6% | 4374.4653
9.992e-14% | 99.63% | 4375.9513
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 47.4 |  |  | Year | 2031
SCR (N-1) | 0 |  |  | SCR (N) | 47.4
SCR (N-2) | 0 |  |  | SCR (N-1) | 0
WCR (N) | 48.3 |  |  | SCR (N-2) | 0
WCR (N-1) | 0 |  |  | WCR (N) | 48.3
WCR (N-2) | 0 |  |  | WCR (N-1) | 0
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 0.99
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 3.2839 | 3.7184 | 4.8172 | 5.3324 | 5.8731 | 6.4947 | 7.2504 | 8.0108 | 8.7172 | 9.4643 | 10.2807 | 11.1321 | 11.8595 | 12.8673 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727
Total EUE (MWh) | 87.0787 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Residual Values
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.2778 | 3.7184 | 4.8172 | 5.3324 | 5.8731 | 6.4947 | 7.2504 | 8.0108 | 8.7172 | 9.4643 | 10.2807 | 11.1321 | 11.8595 | 12.8673 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727
Total EUE (MWh) | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.2778 | 3.7184 | 4.8172 | 5.3324 | 5.8731 | 6.4947 | 7.2504 | 8.0108 | 8.7172 | 9.4643 | 10.2807 | 11.1321 | 11.8595 | 12.8673 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727
Total EUE (MWh) | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.2778 | 3.7184 | 4.8172 | 5.3324 | 5.8731 | 6.4947 | 7.2504 | 8.0108 | 8.7172 | 9.4643 | 10.2807 | 11.1321 | 11.8595 | 12.8673 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727
Total EUE (MWh) | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.2778 | 3.7184 | 4.8172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | 86.9159 | 98.6015 | 127.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 2.8149 | 3.1978 | 4.1547 | 4.6044 | 5.0737 | 5.6176 | 6.2828 | 6.9507 | 7.5608 | 8.2129 | 8.9231 | 9.6681 | 10.2873 | 11.1846 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732 | 11.8732
Total EUE (MWh) | 74.6417 | 84.7959 | 110.1691 | 122.0953 | 134.5378 | 148.9608 | 166.5993 | 184.3113 | 200.4876 | 217.7793 | 236.6113 | 256.3663 | 272.7872 | 296.5803 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.2778 | 3.7184 | 4.8172 | 5.3324 | 5.8731 | 6.4947 | 7.2504 | 8.0108 | 8.7172 | 9.4643 | 10.2807 | 11.1321 | 11.8595 | 12.8673 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727
Total EUE (MWh) | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.2778 | 3.7184 | 4.8172 | 5.3324 | 5.8731 | 6.4947 | 7.2504 | 8.0108 | 8.7172 | 9.4643 | 10.2807 | 11.1321 | 11.8595 | 12.8673 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727 | 13.6727
Total EUE (MWh) | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565

## Key Model Assumption & Inputs
Select ZSS & Region | LLG | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity | #NAME?
Base | 100% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1A New PHS ZSS + Four new feeders | 1A New PHS ZSS + Four new feeders
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Option 6 - Non Network | Non Network
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N |  |  |  | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Added Capacity (MVA) Option 5 N-1 |  |  |  | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | 3.2101 | 3.6106 | 4.1576 | 4.1502 | 4.155 | 4.17 | 4.2208 | 4.2548 | 4.2827 | 4.2869 | 4.312 | 4.3209 | 4.3209 | 4.3152 | 4.3139
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | LLG
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234
Summer POE10 | 10 |  |  | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709
Winter POE10 | 10 |  |  | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | LLG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | PowerFactor | 0.99

## Load Duration Curves
Station
LLG
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0.02583% | 1.1345 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.04305% | 1.8908 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.04737% | 2.0804 | 0.05166% | 2.269 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.09474% | 4.1608 | 0.09471% | 4.1598 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.2639% | 11.5907 | 0.353% | 15.5047 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 0.7443% | 32.6918 | 0.7147% | 31.3876 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 1.915% | 84.1072 | 1.317% | 57.8591 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 4.601% | 202.095 | 2.764% | 121.3907 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 8.837% | 388.1413 | 6.225% | 273.4128 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 15.25% | 669.8855 | 12.05% | 529.43 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 25.15% | 1104.687 | 20.92% | 918.9392 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 37.15% | 1631.62 | 33.11% | 1454.0417 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 51.32% | 2253.9537 | 47.93% | 2105.2406 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 65.85% | 2892.3362 | 62.8% | 2758.3303 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 79.08% | 3473.3593 | 76.24% | 3348.2666 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 88.41% | 3882.8989 | 86.9% | 3816.434 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 93.97% | 4127.1961 | 92.6% | 4067.1569 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 96.66% | 4245.1839 | 96.47% | 4236.9526 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 98.41% | 4322.1583 | 98.65% | 4332.6282 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.14% | 4354.2558 | 99.31% | 4361.7469 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.41% | 4366.1437 | 99.63% | 4375.7389 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.6% | 4374.4653 | 99.68% | 4378.0079 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.63% | 4375.9513 | 99.71% | 4379.1424 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.0406% | 1.7832 | 0.01722% | 0.75633 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.1015% | 4.458 | 0.01722% | 0.75633 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.3451% | 15.1571 | 0.0861% | 3.7816 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 0.9% | 39.5274 | 0.31% | 13.6139 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 2.517% | 110.5579 | 0.8008% | 35.1693 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 5.562% | 244.2972 | 1.834% | 80.549 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 10.11% | 444.0146 | 4.374% | 192.1075 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 17.54% | 770.3386 | 9.179% | 403.1231 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 27.53% | 1209.3009 | 16.83% | 739.3112 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 40.02% | 1757.6322 | 27.43% | 1204.8314 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 54.15% | 2378.4799 | 40.6% | 1783.0446 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 68.39% | 3003.7856 | 53.97% | 2370.3337 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 80.79% | 3548.2533 | 65.21% | 2864.2163 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 89.43% | 3927.7759 | 75.09% | 3297.9707 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 94.17% | 4135.8149 | 81.51% | 3579.7031 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 96.81% | 4252.0195 | 86.44% | 3796.3913 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 98.48% | 4325.4275 | 90.52% | 3975.6411 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.28% | 4360.497 | 93.75% | 4117.4527 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.59% | 4373.8709 | 96.19% | 4224.8514 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.77% | 4381.8952 | 98.14% | 4310.3165 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.78% | 4382.5459 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 1 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 2 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 3 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 48.3 | 48.3 | 48.3 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 5 | 47.4 | 47.4 | 47.4 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8
Capacity Added (MVA) | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 6 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 7 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 8 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
SCR N-1 Rating (MVA) - Option 5 | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709
Maximum Demand (MVA) - P10 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234
Maximum Demand (MVA) - P10 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
Option 2 - 1A New PHS ZSS + Four new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
Option 6 - Non Network
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 3.2101 | 3.6106 | 4.1576 | 4.1502 | 4.155 | 4.17 | 4.2208 | 4.2548 | 4.2827 | 4.2869 | 4.312 | 4.3209 | 4.3209 | 4.3152 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139 | 4.3139
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 17.3637 | 20.3053 | 24.2822 | 24.69 | 24.953 | 25.3146 | 26.1218 | 26.7615 | 27.3326 | 27.5386 | 27.7536 | 27.409 | 27.586 | 28.4238 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 19.5604 | 22.5119 | 26.5253 | 26.8988 | 27.1513 | 27.4014 | 28.3724 | 28.9357 | 29.5187 | 29.7924 | 29.9133 | 29.3976 | 29.6622 | 30.6835 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 20.298 | 22.487 | 26.2999 | 26.2745 | 26.2401 | 26.6977 | 27.3408 | 27.7822 | 27.1764 | 27.2297 | 27.48 | 28.5618 | 27.5283 | 27.4734 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 22.3339 | 25.1205 | 28.9258 | 28.8747 | 28.9082 | 29.0122 | 29.3657 | 29.6025 | 29.7967 | 29.8253 | 30.0004 | 30.0625 | 30.0623 | 30.0222 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 100% | 0 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
99% | 0.2972 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 99% | 0.2972 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
98% | 0.8916 | 20.1623 | 23.4376 | 27.871 | 28.2634 | 28.5259 | 28.8949 | 29.7357 | 30.396 | 30.983 | 31.189 | 31.4243 | 31.0953 | 31.2688 | 32.0842 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 98% | 0.8916 | 22.3151 | 25.6 | 30.0692 | 30.428 | 30.6802 | 30.9399 | 31.9413 | 32.5267 | 33.1254 | 33.3977 | 33.5408 | 33.0442 | 33.3035 | 34.2987 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305
97% | 1.7832 | 19.9566 | 23.1984 | 27.5866 | 27.975 | 28.2348 | 28.6 | 29.4323 | 30.0858 | 30.6669 | 30.8707 | 31.1036 | 30.778 | 30.9497 | 31.7568 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 97% | 2.0804 | 22.0874 | 25.3388 | 29.7624 | 30.1176 | 30.3672 | 30.6242 | 31.6154 | 32.1948 | 32.7874 | 33.0569 | 33.1986 | 32.707 | 32.9637 | 33.9487 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853
95% | 4.458 | 19.5451 | 22.7201 | 27.0178 | 27.3982 | 27.6526 | 28.0103 | 28.8254 | 29.4655 | 30.0346 | 30.2342 | 30.4623 | 30.1434 | 30.3116 | 31.102 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 95% | 4.1608 | 21.632 | 24.8164 | 29.1487 | 29.4966 | 29.7411 | 29.9928 | 30.9635 | 31.531 | 32.1113 | 32.3753 | 32.5141 | 32.0326 | 32.284 | 33.2487 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948
90% | 15.1571 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 90% | 11.5907 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
85% | 39.5274 | 17.4877 | 20.3285 | 24.1738 | 24.5142 | 24.7418 | 25.0619 | 25.7912 | 26.3639 | 26.8731 | 27.0517 | 27.2558 | 26.9704 | 27.1209 | 27.8281 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 85% | 32.6918 | 19.355 | 22.2041 | 26.0804 | 26.3917 | 26.6104 | 26.8357 | 27.7042 | 28.2119 | 28.7312 | 28.9674 | 29.0915 | 28.6608 | 28.8857 | 29.7489 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427
80% | 110.5579 | 16.4591 | 19.1327 | 22.7518 | 23.0722 | 23.2864 | 23.5876 | 24.2741 | 24.813 | 25.2923 | 25.4604 | 25.6525 | 25.3839 | 25.5255 | 26.1912 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 80% | 84.1072 | 18.2164 | 20.898 | 24.5463 | 24.8392 | 25.0451 | 25.2571 | 26.0746 | 26.5524 | 27.0411 | 27.2634 | 27.3803 | 26.9748 | 27.1865 | 27.9989 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167
75% | 244.2972 | 15.4304 | 17.9369 | 21.3298 | 21.6302 | 21.831 | 22.1134 | 22.7569 | 23.2622 | 23.7115 | 23.8691 | 24.0492 | 23.7974 | 23.9302 | 24.5542 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 75% | 202.095 | 17.0779 | 19.5919 | 23.0122 | 23.2868 | 23.4798 | 23.6785 | 24.4449 | 24.8929 | 25.3511 | 25.5595 | 25.669 | 25.2889 | 25.4874 | 26.249 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907
70% | 444.0146 | 14.4017 | 16.7411 | 19.9078 | 20.1881 | 20.3756 | 20.6392 | 21.2398 | 21.7114 | 22.1307 | 22.2778 | 22.4459 | 22.2109 | 22.3349 | 22.9173 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 70% | 388.1413 | 15.9394 | 18.2857 | 21.478 | 21.7343 | 21.9145 | 22.1 | 22.8152 | 23.2334 | 23.661 | 23.8555 | 23.9577 | 23.603 | 23.7882 | 24.4991 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646
65% | 770.3386 | 13.373 | 15.5453 | 18.4859 | 18.7461 | 18.9202 | 19.165 | 19.7227 | 20.1606 | 20.55 | 20.6866 | 20.8426 | 20.6244 | 20.7395 | 21.2803 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 65% | 669.8855 | 14.8008 | 16.9796 | 19.9439 | 20.1819 | 20.3491 | 20.5214 | 21.1856 | 21.5738 | 21.9709 | 22.1515 | 22.2465 | 21.917 | 22.0891 | 22.7491 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386
60% | 1209.3009 | 12.3443 | 14.3496 | 17.0639 | 17.3041 | 17.4648 | 17.6907 | 18.2055 | 18.6098 | 18.9692 | 19.0953 | 19.2394 | 19.038 | 19.1442 | 19.6434 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 60% | 1104.687 | 13.6623 | 15.6735 | 18.4097 | 18.6294 | 18.7838 | 18.9428 | 19.5559 | 19.9143 | 20.2808 | 20.4476 | 20.5352 | 20.2311 | 20.3899 | 20.9992 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125
55% | 1757.6322 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 55% | 1631.62 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
50% | 2378.4799 | 10.2869 | 11.958 | 14.2199 | 14.4201 | 14.554 | 14.7423 | 15.1713 | 15.5081 | 15.8077 | 15.9127 | 16.0328 | 15.865 | 15.9535 | 16.3695 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 50% | 2253.9537 | 11.3853 | 13.0612 | 15.3414 | 15.5245 | 15.6532 | 15.7857 | 16.2966 | 16.5953 | 16.9007 | 17.0396 | 17.1127 | 16.8593 | 16.9916 | 17.4993 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604
45% | 3003.7856 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 45% | 2892.3362 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
40% | 3548.2533 | 8.2295 | 9.5664 | 11.3759 | 11.5361 | 11.6432 | 11.7938 | 12.137 | 12.4065 | 12.6461 | 12.7302 | 12.8262 | 12.692 | 12.7628 | 13.0956 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 40% | 3473.3593 | 9.1082 | 10.449 | 12.2731 | 12.4196 | 12.5226 | 12.6285 | 13.0373 | 13.2762 | 13.5206 | 13.6317 | 13.6901 | 13.4874 | 13.5933 | 13.9995 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084
35% | 3927.7759 | 7.2008 | 8.3706 | 9.9539 | 10.0941 | 10.1878 | 10.3196 | 10.6199 | 10.8557 | 11.0654 | 11.1389 | 11.223 | 11.1055 | 11.1674 | 11.4586 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 35% | 3882.8989 | 7.9697 | 9.1429 | 10.739 | 10.8672 | 10.9572 | 11.05 | 11.4076 | 11.6167 | 11.8305 | 11.9278 | 11.9789 | 11.8015 | 11.8941 | 12.2495 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823
30% | 4135.8149 | 6.1721 | 7.1748 | 8.5319 | 8.6521 | 8.7324 | 8.8454 | 9.1028 | 9.3049 | 9.4846 | 9.5476 | 9.6197 | 9.519 | 9.5721 | 9.8217 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 30% | 4127.1961 | 6.8312 | 7.8367 | 9.2049 | 9.3147 | 9.3919 | 9.4714 | 9.778 | 9.9572 | 10.1404 | 10.2238 | 10.2676 | 10.1156 | 10.1949 | 10.4996 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563
25% | 4252.0195 | 5.1435 | 5.979 | 7.1099 | 7.2101 | 7.277 | 7.3711 | 7.5856 | 7.7541 | 7.9038 | 7.9564 | 8.0164 | 7.9325 | 7.9767 | 8.1847 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 25% | 4245.1839 | 5.6926 | 6.5306 | 7.6707 | 7.7623 | 7.8266 | 7.8928 | 8.1483 | 8.2976 | 8.4504 | 8.5198 | 8.5563 | 8.4296 | 8.4958 | 8.7497 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302
20% | 4325.4275 | 4.1148 | 4.7832 | 5.688 | 5.768 | 5.8216 | 5.8969 | 6.0685 | 6.2033 | 6.3231 | 6.3651 | 6.4131 | 6.346 | 6.3814 | 6.5478 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 20% | 4322.1583 | 4.5541 | 5.2245 | 6.1366 | 6.2098 | 6.2613 | 6.3143 | 6.5186 | 6.6381 | 6.7603 | 6.8159 | 6.8451 | 6.7437 | 6.7966 | 6.9997 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042
15% | 4360.497 | 3.0861 | 3.5874 | 4.266 | 4.326 | 4.3662 | 4.4227 | 4.5514 | 4.6524 | 4.7423 | 4.7738 | 4.8098 | 4.7595 | 4.786 | 4.9108 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 15% | 4354.2558 | 3.4156 | 3.9184 | 4.6024 | 4.6574 | 4.696 | 4.7357 | 4.889 | 4.9786 | 5.0702 | 5.1119 | 5.1338 | 5.0578 | 5.0975 | 5.2498 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781
10% | 4373.8709 | 2.0574 | 2.3916 | 2.844 | 2.884 | 2.9108 | 2.9485 | 3.0343 | 3.1016 | 3.1615 | 3.1825 | 3.2066 | 3.173 | 3.1907 | 3.2739 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 10% | 4366.1437 | 2.2771 | 2.6122 | 3.0683 | 3.1049 | 3.1306 | 3.1571 | 3.2593 | 3.3191 | 3.3801 | 3.4079 | 3.4225 | 3.3719 | 3.3983 | 3.4999 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521
5% | 4381.8952 | 1.0287 | 1.1958 | 1.422 | 1.442 | 1.4554 | 1.4742 | 1.5171 | 1.5508 | 1.5808 | 1.5913 | 1.6033 | 1.5865 | 1.5953 | 1.6369 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 5% | 4374.4653 | 1.1385 | 1.3061 | 1.5341 | 1.5525 | 1.5653 | 1.5786 | 1.6297 | 1.6595 | 1.6901 | 1.704 | 1.7113 | 1.6859 | 1.6992 | 1.7499 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726
9.992e-14% | 4391.7028 | 2.0557e-14 | 2.3897e-14 | 2.8417e-14 | 2.8817e-14 | 2.9085e-14 | 2.9461e-14 | 3.0318e-14 | 3.0992e-14 | 3.159e-14 | 3.18e-14 | 3.204e-14 | 3.1705e-14 | 3.1881e-14 | 3.2713e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 9.992e-14% | 4375.9513 | 2.2752e-14 | 2.6102e-14 | 3.0658e-14 | 3.1024e-14 | 3.1281e-14 | 3.1546e-14 | 3.2567e-14 | 3.3164e-14 | 3.3774e-14 | 3.4052e-14 | 3.4198e-14 | 3.3692e-14 | 3.3956e-14 | 3.4971e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 100% | 0 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
99% | 0.37816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 99% | 1.1345 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
98% | 0.37816 | 23.038 | 25.5757 | 29.8483 | 29.8162 | 29.7873 | 30.2504 | 30.9303 | 31.3963 | 30.8299 | 30.8862 | 31.1562 | 32.2251 | 31.2123 | 31.1528 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 98% | 1.8908 | 25.0331 | 28.1565 | 32.4217 | 32.3644 | 32.402 | 32.5186 | 32.9148 | 33.1802 | 33.3978 | 33.4299 | 33.6262 | 33.6957 | 33.6956 | 33.6506 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411
97% | 0.75633 | 22.8029 | 25.3147 | 29.5437 | 29.512 | 29.4833 | 29.9417 | 30.6147 | 31.0759 | 30.5153 | 30.5711 | 30.8382 | 31.8963 | 30.8938 | 30.8349 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 97% | 2.269 | 24.7777 | 27.8692 | 32.0909 | 32.0342 | 32.0714 | 32.1868 | 32.5789 | 32.8416 | 33.057 | 33.0888 | 33.2831 | 33.3519 | 33.3517 | 33.3073 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978
95% | 0.75633 | 22.3327 | 24.7927 | 28.9346 | 28.9035 | 28.8754 | 29.3244 | 29.9835 | 30.4352 | 29.8861 | 29.9407 | 30.2024 | 31.2386 | 30.2568 | 30.1991 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 95% | 4.1598 | 24.2668 | 27.2946 | 31.4292 | 31.3737 | 31.4101 | 31.5231 | 31.9072 | 32.1644 | 32.3754 | 32.4065 | 32.5968 | 32.6642 | 32.6641 | 32.6205 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112
90% | 3.7816 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 90% | 15.5047 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
85% | 13.6139 | 19.9819 | 22.183 | 25.8888 | 25.861 | 25.8359 | 26.2376 | 26.8273 | 27.2315 | 26.7402 | 26.7891 | 27.0232 | 27.9503 | 27.0719 | 27.0202 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 85% | 31.3876 | 21.7124 | 24.4215 | 28.1209 | 28.0712 | 28.1038 | 28.2049 | 28.5485 | 28.7787 | 28.9675 | 28.9953 | 29.1656 | 29.2259 | 29.2258 | 29.1868 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785
80% | 35.1693 | 18.8065 | 20.8781 | 24.366 | 24.3398 | 24.3161 | 24.6942 | 25.2493 | 25.6296 | 25.1673 | 25.2132 | 25.4336 | 26.3062 | 25.4794 | 25.4308 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 80% | 57.8591 | 20.4352 | 22.9849 | 26.4667 | 26.4199 | 26.4506 | 26.5458 | 26.8692 | 27.0858 | 27.2635 | 27.2897 | 27.4499 | 27.5067 | 27.5066 | 27.4699 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621
75% | 80.549 | 17.6311 | 19.5732 | 22.8431 | 22.8185 | 22.7964 | 23.1508 | 23.6712 | 24.0278 | 23.5943 | 23.6374 | 23.844 | 24.6621 | 23.8869 | 23.8414 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 75% | 121.3907 | 19.158 | 21.5484 | 24.8125 | 24.7687 | 24.7974 | 24.8867 | 25.1899 | 25.393 | 25.5596 | 25.5841 | 25.7343 | 25.7876 | 25.7874 | 25.753 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457
70% | 192.1075 | 16.4557 | 18.2683 | 21.3202 | 21.2973 | 21.2766 | 21.6074 | 22.0931 | 22.4259 | 22.0214 | 22.0616 | 22.2544 | 23.0179 | 22.2945 | 22.252 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 70% | 273.4128 | 17.8808 | 20.1118 | 23.1584 | 23.1174 | 23.1443 | 23.2276 | 23.5106 | 23.7001 | 23.8556 | 23.8785 | 24.0187 | 24.0684 | 24.0683 | 24.0362 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293
65% | 403.1231 | 15.2803 | 16.9635 | 19.7973 | 19.7761 | 19.7569 | 20.064 | 20.515 | 20.8241 | 20.4484 | 20.4858 | 20.6648 | 21.3738 | 20.702 | 20.6625 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 65% | 529.43 | 16.6036 | 18.6752 | 21.5042 | 21.4662 | 21.4911 | 21.5685 | 21.8312 | 22.0073 | 22.1516 | 22.1729 | 22.3031 | 22.3492 | 22.3491 | 22.3193 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313
60% | 739.3112 | 14.1049 | 15.6586 | 18.2745 | 18.2548 | 18.2371 | 18.5206 | 18.9369 | 19.2222 | 18.8755 | 18.9099 | 19.0752 | 19.7296 | 19.1095 | 19.0731 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 60% | 918.9392 | 15.3264 | 17.2387 | 19.85 | 19.8149 | 19.838 | 19.9093 | 20.1519 | 20.3144 | 20.4476 | 20.4673 | 20.5875 | 20.6301 | 20.6299 | 20.6024 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966
55% | 1204.8314 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 55% | 1454.0417 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
50% | 1783.0446 | 11.7541 | 13.0488 | 15.2287 | 15.2123 | 15.1976 | 15.4339 | 15.7808 | 16.0185 | 15.7295 | 15.7583 | 15.896 | 16.4414 | 15.9246 | 15.8943 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 50% | 2105.2406 | 12.772 | 14.3656 | 16.5417 | 16.5125 | 16.5316 | 16.5911 | 16.7933 | 16.9287 | 17.0397 | 17.0561 | 17.1562 | 17.1917 | 17.1916 | 17.1687 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638
45% | 2370.3337 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 45% | 2758.3303 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
40% | 2864.2163 | 9.4033 | 10.4391 | 12.183 | 12.1699 | 12.1581 | 12.3471 | 12.6246 | 12.8148 | 12.5836 | 12.6066 | 12.7168 | 13.1531 | 12.7397 | 12.7154 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 40% | 3348.2666 | 10.2176 | 11.4925 | 13.2333 | 13.21 | 13.2253 | 13.2729 | 13.4346 | 13.5429 | 13.6318 | 13.6448 | 13.725 | 13.7534 | 13.7533 | 13.735 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311
35% | 3297.9707 | 8.2279 | 9.1342 | 10.6601 | 10.6486 | 10.6383 | 10.8037 | 11.0465 | 11.213 | 11.0107 | 11.0308 | 11.1272 | 11.509 | 11.1472 | 11.126 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 35% | 3816.434 | 8.9404 | 10.0559 | 11.5792 | 11.5587 | 11.5721 | 11.6138 | 11.7553 | 11.8501 | 11.9278 | 11.9392 | 12.0093 | 12.0342 | 12.0341 | 12.0181 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147
30% | 3579.7031 | 7.0524 | 7.8293 | 9.1372 | 9.1274 | 9.1186 | 9.2603 | 9.4685 | 9.6111 | 9.4377 | 9.455 | 9.5376 | 9.8648 | 9.5548 | 9.5366 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 30% | 4067.1569 | 7.6632 | 8.6193 | 9.925 | 9.9075 | 9.919 | 9.9547 | 10.076 | 10.1572 | 10.2238 | 10.2336 | 10.2937 | 10.315 | 10.315 | 10.3012 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983
25% | 3796.3913 | 5.877 | 6.5244 | 7.6144 | 7.6062 | 7.5988 | 7.7169 | 7.8904 | 8.0093 | 7.8648 | 7.8791 | 7.948 | 8.2207 | 7.9623 | 7.9471 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 25% | 4236.9526 | 6.386 | 7.1828 | 8.2708 | 8.2562 | 8.2658 | 8.2956 | 8.3966 | 8.4643 | 8.5199 | 8.528 | 8.5781 | 8.5959 | 8.5958 | 8.5843 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819
20% | 3975.6411 | 4.7016 | 5.2195 | 6.0915 | 6.0849 | 6.079 | 6.1735 | 6.3123 | 6.4074 | 6.2918 | 6.3033 | 6.3584 | 6.5765 | 6.3698 | 6.3577 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 20% | 4332.6282 | 5.1088 | 5.7462 | 6.6167 | 6.605 | 6.6127 | 6.6364 | 6.7173 | 6.7715 | 6.8159 | 6.8224 | 6.8625 | 6.8767 | 6.8766 | 6.8675 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655
15% | 4117.4527 | 3.5262 | 3.9146 | 4.5686 | 4.5637 | 4.5593 | 4.6302 | 4.7342 | 4.8056 | 4.7189 | 4.7275 | 4.7688 | 4.9324 | 4.7774 | 4.7683 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 15% | 4361.7469 | 3.8316 | 4.3097 | 4.9625 | 4.9537 | 4.9595 | 4.9773 | 5.038 | 5.0786 | 5.1119 | 5.1168 | 5.1469 | 5.1575 | 5.1575 | 5.1506 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491
10% | 4224.8514 | 2.3508 | 2.6098 | 3.0457 | 3.0425 | 3.0395 | 3.0868 | 3.1562 | 3.2037 | 3.1459 | 3.1517 | 3.1792 | 3.2883 | 3.1849 | 3.1789 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 10% | 4375.7389 | 2.5544 | 2.8731 | 3.3083 | 3.3025 | 3.3063 | 3.3182 | 3.3587 | 3.3857 | 3.4079 | 3.4112 | 3.4312 | 3.4383 | 3.4383 | 3.4337 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328
5% | 4310.3165 | 1.1754 | 1.3049 | 1.5229 | 1.5212 | 1.5198 | 1.5434 | 1.5781 | 1.6019 | 1.573 | 1.5758 | 1.5896 | 1.6441 | 1.5925 | 1.5894 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 5% | 4378.0079 | 1.2772 | 1.4366 | 1.6542 | 1.6512 | 1.6532 | 1.6591 | 1.6793 | 1.6929 | 1.704 | 1.7056 | 1.7156 | 1.7192 | 1.7192 | 1.7169 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164
9.992e-14% | 4382.5459 | 2.3489e-14 | 2.6077e-14 | 3.0433e-14 | 3.04e-14 | 3.0371e-14 | 3.0843e-14 | 3.1536e-14 | 3.2011e-14 | 3.1434e-14 | 3.1491e-14 | 3.1767e-14 | 3.2856e-14 | 3.1824e-14 | 3.1763e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 9.992e-14% | 4379.1424 | 2.5524e-14 | 2.8708e-14 | 3.3057e-14 | 3.2999e-14 | 3.3037e-14 | 3.3156e-14 | 3.356e-14 | 3.383e-14 | 3.4052e-14 | 3.4085e-14 | 3.4285e-14 | 3.4356e-14 | 3.4356e-14 | 3.431e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 100% | 0 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
99% | 0.2972 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 99% | 0.2972 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
98% | 0.8916 | 20.1623 | 23.4376 | 27.871 | 28.2634 | 28.5259 | 28.8949 | 29.7357 | 30.396 | 30.983 | 31.189 | 31.4243 | 31.0953 | 31.2688 | 32.0842 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 98% | 0.8916 | 22.3151 | 25.6 | 30.0692 | 30.428 | 30.6802 | 30.9399 | 31.9413 | 32.5267 | 33.1254 | 33.3977 | 33.5408 | 33.0442 | 33.3035 | 34.2987 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305
97% | 1.7832 | 19.9566 | 23.1984 | 27.5866 | 27.975 | 28.2348 | 28.6 | 29.4323 | 30.0858 | 30.6669 | 30.8707 | 31.1036 | 30.778 | 30.9497 | 31.7568 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 97% | 2.0804 | 22.0874 | 25.3388 | 29.7624 | 30.1176 | 30.3672 | 30.6242 | 31.6154 | 32.1948 | 32.7874 | 33.0569 | 33.1986 | 32.707 | 32.9637 | 33.9487 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853
95% | 4.458 | 19.5451 | 22.7201 | 27.0178 | 27.3982 | 27.6526 | 28.0103 | 28.8254 | 29.4655 | 30.0346 | 30.2342 | 30.4623 | 30.1434 | 30.3116 | 31.102 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 95% | 4.1608 | 21.632 | 24.8164 | 29.1487 | 29.4966 | 29.7411 | 29.9928 | 30.9635 | 31.531 | 32.1113 | 32.3753 | 32.5141 | 32.0326 | 32.284 | 33.2487 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948
90% | 15.1571 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 90% | 11.5907 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
85% | 39.5274 | 17.4877 | 20.3285 | 24.1738 | 24.5142 | 24.7418 | 25.0619 | 25.7912 | 26.3639 | 26.8731 | 27.0517 | 27.2558 | 26.9704 | 27.1209 | 27.8281 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 85% | 32.6918 | 19.355 | 22.2041 | 26.0804 | 26.3917 | 26.6104 | 26.8357 | 27.7042 | 28.2119 | 28.7312 | 28.9674 | 29.0915 | 28.6608 | 28.8857 | 29.7489 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427
80% | 110.5579 | 16.4591 | 19.1327 | 22.7518 | 23.0722 | 23.2864 | 23.5876 | 24.2741 | 24.813 | 25.2923 | 25.4604 | 25.6525 | 25.3839 | 25.5255 | 26.1912 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 80% | 84.1072 | 18.2164 | 20.898 | 24.5463 | 24.8392 | 25.0451 | 25.2571 | 26.0746 | 26.5524 | 27.0411 | 27.2634 | 27.3803 | 26.9748 | 27.1865 | 27.9989 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167
75% | 244.2972 | 15.4304 | 17.9369 | 21.3298 | 21.6302 | 21.831 | 22.1134 | 22.7569 | 23.2622 | 23.7115 | 23.8691 | 24.0492 | 23.7974 | 23.9302 | 24.5542 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 75% | 202.095 | 17.0779 | 19.5919 | 23.0122 | 23.2868 | 23.4798 | 23.6785 | 24.4449 | 24.8929 | 25.3511 | 25.5595 | 25.669 | 25.2889 | 25.4874 | 26.249 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907
70% | 444.0146 | 14.4017 | 16.7411 | 19.9078 | 20.1881 | 20.3756 | 20.6392 | 21.2398 | 21.7114 | 22.1307 | 22.2778 | 22.4459 | 22.2109 | 22.3349 | 22.9173 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 70% | 388.1413 | 15.9394 | 18.2857 | 21.478 | 21.7343 | 21.9145 | 22.1 | 22.8152 | 23.2334 | 23.661 | 23.8555 | 23.9577 | 23.603 | 23.7882 | 24.4991 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646
65% | 770.3386 | 13.373 | 15.5453 | 18.4859 | 18.7461 | 18.9202 | 19.165 | 19.7227 | 20.1606 | 20.55 | 20.6866 | 20.8426 | 20.6244 | 20.7395 | 21.2803 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 65% | 669.8855 | 14.8008 | 16.9796 | 19.9439 | 20.1819 | 20.3491 | 20.5214 | 21.1856 | 21.5738 | 21.9709 | 22.1515 | 22.2465 | 21.917 | 22.0891 | 22.7491 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386
60% | 1209.3009 | 12.3443 | 14.3496 | 17.0639 | 17.3041 | 17.4648 | 17.6907 | 18.2055 | 18.6098 | 18.9692 | 19.0953 | 19.2394 | 19.038 | 19.1442 | 19.6434 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 60% | 1104.687 | 13.6623 | 15.6735 | 18.4097 | 18.6294 | 18.7838 | 18.9428 | 19.5559 | 19.9143 | 20.2808 | 20.4476 | 20.5352 | 20.2311 | 20.3899 | 20.9992 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125
55% | 1757.6322 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 55% | 1631.62 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
50% | 2378.4799 | 10.2869 | 11.958 | 14.2199 | 14.4201 | 14.554 | 14.7423 | 15.1713 | 15.5081 | 15.8077 | 15.9127 | 16.0328 | 15.865 | 15.9535 | 16.3695 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 50% | 2253.9537 | 11.3853 | 13.0612 | 15.3414 | 15.5245 | 15.6532 | 15.7857 | 16.2966 | 16.5953 | 16.9007 | 17.0396 | 17.1127 | 16.8593 | 16.9916 | 17.4993 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604
45% | 3003.7856 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 45% | 2892.3362 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
40% | 3548.2533 | 8.2295 | 9.5664 | 11.3759 | 11.5361 | 11.6432 | 11.7938 | 12.137 | 12.4065 | 12.6461 | 12.7302 | 12.8262 | 12.692 | 12.7628 | 13.0956 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 40% | 3473.3593 | 9.1082 | 10.449 | 12.2731 | 12.4196 | 12.5226 | 12.6285 | 13.0373 | 13.2762 | 13.5206 | 13.6317 | 13.6901 | 13.4874 | 13.5933 | 13.9995 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084
35% | 3927.7759 | 7.2008 | 8.3706 | 9.9539 | 10.0941 | 10.1878 | 10.3196 | 10.6199 | 10.8557 | 11.0654 | 11.1389 | 11.223 | 11.1055 | 11.1674 | 11.4586 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 35% | 3882.8989 | 7.9697 | 9.1429 | 10.739 | 10.8672 | 10.9572 | 11.05 | 11.4076 | 11.6167 | 11.8305 | 11.9278 | 11.9789 | 11.8015 | 11.8941 | 12.2495 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823
30% | 4135.8149 | 6.1721 | 7.1748 | 8.5319 | 8.6521 | 8.7324 | 8.8454 | 9.1028 | 9.3049 | 9.4846 | 9.5476 | 9.6197 | 9.519 | 9.5721 | 9.8217 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 30% | 4127.1961 | 6.8312 | 7.8367 | 9.2049 | 9.3147 | 9.3919 | 9.4714 | 9.778 | 9.9572 | 10.1404 | 10.2238 | 10.2676 | 10.1156 | 10.1949 | 10.4996 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563
25% | 4252.0195 | 5.1435 | 5.979 | 7.1099 | 7.2101 | 7.277 | 7.3711 | 7.5856 | 7.7541 | 7.9038 | 7.9564 | 8.0164 | 7.9325 | 7.9767 | 8.1847 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 25% | 4245.1839 | 5.6926 | 6.5306 | 7.6707 | 7.7623 | 7.8266 | 7.8928 | 8.1483 | 8.2976 | 8.4504 | 8.5198 | 8.5563 | 8.4296 | 8.4958 | 8.7497 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302
20% | 4325.4275 | 4.1148 | 4.7832 | 5.688 | 5.768 | 5.8216 | 5.8969 | 6.0685 | 6.2033 | 6.3231 | 6.3651 | 6.4131 | 6.346 | 6.3814 | 6.5478 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 20% | 4322.1583 | 4.5541 | 5.2245 | 6.1366 | 6.2098 | 6.2613 | 6.3143 | 6.5186 | 6.6381 | 6.7603 | 6.8159 | 6.8451 | 6.7437 | 6.7966 | 6.9997 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042
15% | 4360.497 | 3.0861 | 3.5874 | 4.266 | 4.326 | 4.3662 | 4.4227 | 4.5514 | 4.6524 | 4.7423 | 4.7738 | 4.8098 | 4.7595 | 4.786 | 4.9108 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 15% | 4354.2558 | 3.4156 | 3.9184 | 4.6024 | 4.6574 | 4.696 | 4.7357 | 4.889 | 4.9786 | 5.0702 | 5.1119 | 5.1338 | 5.0578 | 5.0975 | 5.2498 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781
10% | 4373.8709 | 2.0574 | 2.3916 | 2.844 | 2.884 | 2.9108 | 2.9485 | 3.0343 | 3.1016 | 3.1615 | 3.1825 | 3.2066 | 3.173 | 3.1907 | 3.2739 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 10% | 4366.1437 | 2.2771 | 2.6122 | 3.0683 | 3.1049 | 3.1306 | 3.1571 | 3.2593 | 3.3191 | 3.3801 | 3.4079 | 3.4225 | 3.3719 | 3.3983 | 3.4999 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521
5% | 4381.8952 | 1.0287 | 1.1958 | 1.422 | 1.442 | 1.4554 | 1.4742 | 1.5171 | 1.5508 | 1.5808 | 1.5913 | 1.6033 | 1.5865 | 1.5953 | 1.6369 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 5% | 4374.4653 | 1.1385 | 1.3061 | 1.5341 | 1.5525 | 1.5653 | 1.5786 | 1.6297 | 1.6595 | 1.6901 | 1.704 | 1.7113 | 1.6859 | 1.6992 | 1.7499 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726
9.992e-14% | 4391.7028 | 2.0557e-14 | 2.3897e-14 | 2.8417e-14 | 2.8817e-14 | 2.9085e-14 | 2.9461e-14 | 3.0318e-14 | 3.0992e-14 | 3.159e-14 | 3.18e-14 | 3.204e-14 | 3.1705e-14 | 3.1881e-14 | 3.2713e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 9.992e-14% | 4375.9513 | 2.2752e-14 | 2.6102e-14 | 3.0658e-14 | 3.1024e-14 | 3.1281e-14 | 3.1546e-14 | 3.2567e-14 | 3.3164e-14 | 3.3774e-14 | 3.4052e-14 | 3.4198e-14 | 3.3692e-14 | 3.3956e-14 | 3.4971e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 100% | 0 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
99% | 0.37816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 99% | 1.1345 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
98% | 0.37816 | 23.038 | 25.5757 | 29.8483 | 29.8162 | 29.7873 | 30.2504 | 30.9303 | 31.3963 | 30.8299 | 30.8862 | 31.1562 | 32.2251 | 31.2123 | 31.1528 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 98% | 1.8908 | 25.0331 | 28.1565 | 32.4217 | 32.3644 | 32.402 | 32.5186 | 32.9148 | 33.1802 | 33.3978 | 33.4299 | 33.6262 | 33.6957 | 33.6956 | 33.6506 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411
97% | 0.75633 | 22.8029 | 25.3147 | 29.5437 | 29.512 | 29.4833 | 29.9417 | 30.6147 | 31.0759 | 30.5153 | 30.5711 | 30.8382 | 31.8963 | 30.8938 | 30.8349 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 97% | 2.269 | 24.7777 | 27.8692 | 32.0909 | 32.0342 | 32.0714 | 32.1868 | 32.5789 | 32.8416 | 33.057 | 33.0888 | 33.2831 | 33.3519 | 33.3517 | 33.3073 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978
95% | 0.75633 | 22.3327 | 24.7927 | 28.9346 | 28.9035 | 28.8754 | 29.3244 | 29.9835 | 30.4352 | 29.8861 | 29.9407 | 30.2024 | 31.2386 | 30.2568 | 30.1991 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 95% | 4.1598 | 24.2668 | 27.2946 | 31.4292 | 31.3737 | 31.4101 | 31.5231 | 31.9072 | 32.1644 | 32.3754 | 32.4065 | 32.5968 | 32.6642 | 32.6641 | 32.6205 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112
90% | 3.7816 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 90% | 15.5047 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
85% | 13.6139 | 19.9819 | 22.183 | 25.8888 | 25.861 | 25.8359 | 26.2376 | 26.8273 | 27.2315 | 26.7402 | 26.7891 | 27.0232 | 27.9503 | 27.0719 | 27.0202 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 85% | 31.3876 | 21.7124 | 24.4215 | 28.1209 | 28.0712 | 28.1038 | 28.2049 | 28.5485 | 28.7787 | 28.9675 | 28.9953 | 29.1656 | 29.2259 | 29.2258 | 29.1868 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785
80% | 35.1693 | 18.8065 | 20.8781 | 24.366 | 24.3398 | 24.3161 | 24.6942 | 25.2493 | 25.6296 | 25.1673 | 25.2132 | 25.4336 | 26.3062 | 25.4794 | 25.4308 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 80% | 57.8591 | 20.4352 | 22.9849 | 26.4667 | 26.4199 | 26.4506 | 26.5458 | 26.8692 | 27.0858 | 27.2635 | 27.2897 | 27.4499 | 27.5067 | 27.5066 | 27.4699 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621
75% | 80.549 | 17.6311 | 19.5732 | 22.8431 | 22.8185 | 22.7964 | 23.1508 | 23.6712 | 24.0278 | 23.5943 | 23.6374 | 23.844 | 24.6621 | 23.8869 | 23.8414 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 75% | 121.3907 | 19.158 | 21.5484 | 24.8125 | 24.7687 | 24.7974 | 24.8867 | 25.1899 | 25.393 | 25.5596 | 25.5841 | 25.7343 | 25.7876 | 25.7874 | 25.753 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457
70% | 192.1075 | 16.4557 | 18.2683 | 21.3202 | 21.2973 | 21.2766 | 21.6074 | 22.0931 | 22.4259 | 22.0214 | 22.0616 | 22.2544 | 23.0179 | 22.2945 | 22.252 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 70% | 273.4128 | 17.8808 | 20.1118 | 23.1584 | 23.1174 | 23.1443 | 23.2276 | 23.5106 | 23.7001 | 23.8556 | 23.8785 | 24.0187 | 24.0684 | 24.0683 | 24.0362 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293
65% | 403.1231 | 15.2803 | 16.9635 | 19.7973 | 19.7761 | 19.7569 | 20.064 | 20.515 | 20.8241 | 20.4484 | 20.4858 | 20.6648 | 21.3738 | 20.702 | 20.6625 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 65% | 529.43 | 16.6036 | 18.6752 | 21.5042 | 21.4662 | 21.4911 | 21.5685 | 21.8312 | 22.0073 | 22.1516 | 22.1729 | 22.3031 | 22.3492 | 22.3491 | 22.3193 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313
60% | 739.3112 | 14.1049 | 15.6586 | 18.2745 | 18.2548 | 18.2371 | 18.5206 | 18.9369 | 19.2222 | 18.8755 | 18.9099 | 19.0752 | 19.7296 | 19.1095 | 19.0731 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 60% | 918.9392 | 15.3264 | 17.2387 | 19.85 | 19.8149 | 19.838 | 19.9093 | 20.1519 | 20.3144 | 20.4476 | 20.4673 | 20.5875 | 20.6301 | 20.6299 | 20.6024 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966
55% | 1204.8314 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 55% | 1454.0417 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
50% | 1783.0446 | 11.7541 | 13.0488 | 15.2287 | 15.2123 | 15.1976 | 15.4339 | 15.7808 | 16.0185 | 15.7295 | 15.7583 | 15.896 | 16.4414 | 15.9246 | 15.8943 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 50% | 2105.2406 | 12.772 | 14.3656 | 16.5417 | 16.5125 | 16.5316 | 16.5911 | 16.7933 | 16.9287 | 17.0397 | 17.0561 | 17.1562 | 17.1917 | 17.1916 | 17.1687 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638
45% | 2370.3337 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 45% | 2758.3303 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
40% | 2864.2163 | 9.4033 | 10.4391 | 12.183 | 12.1699 | 12.1581 | 12.3471 | 12.6246 | 12.8148 | 12.5836 | 12.6066 | 12.7168 | 13.1531 | 12.7397 | 12.7154 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 40% | 3348.2666 | 10.2176 | 11.4925 | 13.2333 | 13.21 | 13.2253 | 13.2729 | 13.4346 | 13.5429 | 13.6318 | 13.6448 | 13.725 | 13.7534 | 13.7533 | 13.735 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311
35% | 3297.9707 | 8.2279 | 9.1342 | 10.6601 | 10.6486 | 10.6383 | 10.8037 | 11.0465 | 11.213 | 11.0107 | 11.0308 | 11.1272 | 11.509 | 11.1472 | 11.126 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 35% | 3816.434 | 8.9404 | 10.0559 | 11.5792 | 11.5587 | 11.5721 | 11.6138 | 11.7553 | 11.8501 | 11.9278 | 11.9392 | 12.0093 | 12.0342 | 12.0341 | 12.0181 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147
30% | 3579.7031 | 7.0524 | 7.8293 | 9.1372 | 9.1274 | 9.1186 | 9.2603 | 9.4685 | 9.6111 | 9.4377 | 9.455 | 9.5376 | 9.8648 | 9.5548 | 9.5366 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 30% | 4067.1569 | 7.6632 | 8.6193 | 9.925 | 9.9075 | 9.919 | 9.9547 | 10.076 | 10.1572 | 10.2238 | 10.2336 | 10.2937 | 10.315 | 10.315 | 10.3012 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983
25% | 3796.3913 | 5.877 | 6.5244 | 7.6144 | 7.6062 | 7.5988 | 7.7169 | 7.8904 | 8.0093 | 7.8648 | 7.8791 | 7.948 | 8.2207 | 7.9623 | 7.9471 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 25% | 4236.9526 | 6.386 | 7.1828 | 8.2708 | 8.2562 | 8.2658 | 8.2956 | 8.3966 | 8.4643 | 8.5199 | 8.528 | 8.5781 | 8.5959 | 8.5958 | 8.5843 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819
20% | 3975.6411 | 4.7016 | 5.2195 | 6.0915 | 6.0849 | 6.079 | 6.1735 | 6.3123 | 6.4074 | 6.2918 | 6.3033 | 6.3584 | 6.5765 | 6.3698 | 6.3577 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 20% | 4332.6282 | 5.1088 | 5.7462 | 6.6167 | 6.605 | 6.6127 | 6.6364 | 6.7173 | 6.7715 | 6.8159 | 6.8224 | 6.8625 | 6.8767 | 6.8766 | 6.8675 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655
15% | 4117.4527 | 3.5262 | 3.9146 | 4.5686 | 4.5637 | 4.5593 | 4.6302 | 4.7342 | 4.8056 | 4.7189 | 4.7275 | 4.7688 | 4.9324 | 4.7774 | 4.7683 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 15% | 4361.7469 | 3.8316 | 4.3097 | 4.9625 | 4.9537 | 4.9595 | 4.9773 | 5.038 | 5.0786 | 5.1119 | 5.1168 | 5.1469 | 5.1575 | 5.1575 | 5.1506 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491
10% | 4224.8514 | 2.3508 | 2.6098 | 3.0457 | 3.0425 | 3.0395 | 3.0868 | 3.1562 | 3.2037 | 3.1459 | 3.1517 | 3.1792 | 3.2883 | 3.1849 | 3.1789 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 10% | 4375.7389 | 2.5544 | 2.8731 | 3.3083 | 3.3025 | 3.3063 | 3.3182 | 3.3587 | 3.3857 | 3.4079 | 3.4112 | 3.4312 | 3.4383 | 3.4383 | 3.4337 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328
5% | 4310.3165 | 1.1754 | 1.3049 | 1.5229 | 1.5212 | 1.5198 | 1.5434 | 1.5781 | 1.6019 | 1.573 | 1.5758 | 1.5896 | 1.6441 | 1.5925 | 1.5894 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 5% | 4378.0079 | 1.2772 | 1.4366 | 1.6542 | 1.6512 | 1.6532 | 1.6591 | 1.6793 | 1.6929 | 1.704 | 1.7056 | 1.7156 | 1.7192 | 1.7192 | 1.7169 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164
9.992e-14% | 4382.5459 | 2.3489e-14 | 2.6077e-14 | 3.0433e-14 | 3.04e-14 | 3.0371e-14 | 3.0843e-14 | 3.1536e-14 | 3.2011e-14 | 3.1434e-14 | 3.1491e-14 | 3.1767e-14 | 3.2856e-14 | 3.1824e-14 | 3.1763e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 9.992e-14% | 4379.1424 | 2.5524e-14 | 2.8708e-14 | 3.3057e-14 | 3.2999e-14 | 3.3037e-14 | 3.3156e-14 | 3.356e-14 | 3.383e-14 | 3.4052e-14 | 3.4085e-14 | 3.4285e-14 | 3.4356e-14 | 3.4356e-14 | 3.431e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 100% | 0 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
99% | 0.2972 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 99% | 0.2972 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
98% | 0.8916 | 20.1623 | 23.4376 | 27.871 | 28.2634 | 28.5259 | 28.8949 | 29.7357 | 30.396 | 30.983 | 31.189 | 31.4243 | 31.0953 | 31.2688 | 32.0842 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 98% | 0.8916 | 22.3151 | 25.6 | 30.0692 | 30.428 | 30.6802 | 30.9399 | 31.9413 | 32.5267 | 33.1254 | 33.3977 | 33.5408 | 33.0442 | 33.3035 | 34.2987 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305
97% | 1.7832 | 19.9566 | 23.1984 | 27.5866 | 27.975 | 28.2348 | 28.6 | 29.4323 | 30.0858 | 30.6669 | 30.8707 | 31.1036 | 30.778 | 30.9497 | 31.7568 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 97% | 2.0804 | 22.0874 | 25.3388 | 29.7624 | 30.1176 | 30.3672 | 30.6242 | 31.6154 | 32.1948 | 32.7874 | 33.0569 | 33.1986 | 32.707 | 32.9637 | 33.9487 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853
95% | 4.458 | 19.5451 | 22.7201 | 27.0178 | 27.3982 | 27.6526 | 28.0103 | 28.8254 | 29.4655 | 30.0346 | 30.2342 | 30.4623 | 30.1434 | 30.3116 | 31.102 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 95% | 4.1608 | 21.632 | 24.8164 | 29.1487 | 29.4966 | 29.7411 | 29.9928 | 30.9635 | 31.531 | 32.1113 | 32.3753 | 32.5141 | 32.0326 | 32.284 | 33.2487 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948
90% | 15.1571 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 90% | 11.5907 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
85% | 39.5274 | 17.4877 | 20.3285 | 24.1738 | 24.5142 | 24.7418 | 25.0619 | 25.7912 | 26.3639 | 26.8731 | 27.0517 | 27.2558 | 26.9704 | 27.1209 | 27.8281 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 85% | 32.6918 | 19.355 | 22.2041 | 26.0804 | 26.3917 | 26.6104 | 26.8357 | 27.7042 | 28.2119 | 28.7312 | 28.9674 | 29.0915 | 28.6608 | 28.8857 | 29.7489 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427
80% | 110.5579 | 16.4591 | 19.1327 | 22.7518 | 23.0722 | 23.2864 | 23.5876 | 24.2741 | 24.813 | 25.2923 | 25.4604 | 25.6525 | 25.3839 | 25.5255 | 26.1912 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 80% | 84.1072 | 18.2164 | 20.898 | 24.5463 | 24.8392 | 25.0451 | 25.2571 | 26.0746 | 26.5524 | 27.0411 | 27.2634 | 27.3803 | 26.9748 | 27.1865 | 27.9989 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167
75% | 244.2972 | 15.4304 | 17.9369 | 21.3298 | 21.6302 | 21.831 | 22.1134 | 22.7569 | 23.2622 | 23.7115 | 23.8691 | 24.0492 | 23.7974 | 23.9302 | 24.5542 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 75% | 202.095 | 17.0779 | 19.5919 | 23.0122 | 23.2868 | 23.4798 | 23.6785 | 24.4449 | 24.8929 | 25.3511 | 25.5595 | 25.669 | 25.2889 | 25.4874 | 26.249 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907
70% | 444.0146 | 14.4017 | 16.7411 | 19.9078 | 20.1881 | 20.3756 | 20.6392 | 21.2398 | 21.7114 | 22.1307 | 22.2778 | 22.4459 | 22.2109 | 22.3349 | 22.9173 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 70% | 388.1413 | 15.9394 | 18.2857 | 21.478 | 21.7343 | 21.9145 | 22.1 | 22.8152 | 23.2334 | 23.661 | 23.8555 | 23.9577 | 23.603 | 23.7882 | 24.4991 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646
65% | 770.3386 | 13.373 | 15.5453 | 18.4859 | 18.7461 | 18.9202 | 19.165 | 19.7227 | 20.1606 | 20.55 | 20.6866 | 20.8426 | 20.6244 | 20.7395 | 21.2803 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 65% | 669.8855 | 14.8008 | 16.9796 | 19.9439 | 20.1819 | 20.3491 | 20.5214 | 21.1856 | 21.5738 | 21.9709 | 22.1515 | 22.2465 | 21.917 | 22.0891 | 22.7491 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386
60% | 1209.3009 | 12.3443 | 14.3496 | 17.0639 | 17.3041 | 17.4648 | 17.6907 | 18.2055 | 18.6098 | 18.9692 | 19.0953 | 19.2394 | 19.038 | 19.1442 | 19.6434 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 60% | 1104.687 | 13.6623 | 15.6735 | 18.4097 | 18.6294 | 18.7838 | 18.9428 | 19.5559 | 19.9143 | 20.2808 | 20.4476 | 20.5352 | 20.2311 | 20.3899 | 20.9992 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125
55% | 1757.6322 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 55% | 1631.62 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
50% | 2378.4799 | 10.2869 | 11.958 | 14.2199 | 14.4201 | 14.554 | 14.7423 | 15.1713 | 15.5081 | 15.8077 | 15.9127 | 16.0328 | 15.865 | 15.9535 | 16.3695 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 50% | 2253.9537 | 11.3853 | 13.0612 | 15.3414 | 15.5245 | 15.6532 | 15.7857 | 16.2966 | 16.5953 | 16.9007 | 17.0396 | 17.1127 | 16.8593 | 16.9916 | 17.4993 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604
45% | 3003.7856 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 45% | 2892.3362 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
40% | 3548.2533 | 8.2295 | 9.5664 | 11.3759 | 11.5361 | 11.6432 | 11.7938 | 12.137 | 12.4065 | 12.6461 | 12.7302 | 12.8262 | 12.692 | 12.7628 | 13.0956 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 40% | 3473.3593 | 9.1082 | 10.449 | 12.2731 | 12.4196 | 12.5226 | 12.6285 | 13.0373 | 13.2762 | 13.5206 | 13.6317 | 13.6901 | 13.4874 | 13.5933 | 13.9995 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084
35% | 3927.7759 | 7.2008 | 8.3706 | 9.9539 | 10.0941 | 10.1878 | 10.3196 | 10.6199 | 10.8557 | 11.0654 | 11.1389 | 11.223 | 11.1055 | 11.1674 | 11.4586 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 35% | 3882.8989 | 7.9697 | 9.1429 | 10.739 | 10.8672 | 10.9572 | 11.05 | 11.4076 | 11.6167 | 11.8305 | 11.9278 | 11.9789 | 11.8015 | 11.8941 | 12.2495 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823
30% | 4135.8149 | 6.1721 | 7.1748 | 8.5319 | 8.6521 | 8.7324 | 8.8454 | 9.1028 | 9.3049 | 9.4846 | 9.5476 | 9.6197 | 9.519 | 9.5721 | 9.8217 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 30% | 4127.1961 | 6.8312 | 7.8367 | 9.2049 | 9.3147 | 9.3919 | 9.4714 | 9.778 | 9.9572 | 10.1404 | 10.2238 | 10.2676 | 10.1156 | 10.1949 | 10.4996 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563
25% | 4252.0195 | 5.1435 | 5.979 | 7.1099 | 7.2101 | 7.277 | 7.3711 | 7.5856 | 7.7541 | 7.9038 | 7.9564 | 8.0164 | 7.9325 | 7.9767 | 8.1847 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 25% | 4245.1839 | 5.6926 | 6.5306 | 7.6707 | 7.7623 | 7.8266 | 7.8928 | 8.1483 | 8.2976 | 8.4504 | 8.5198 | 8.5563 | 8.4296 | 8.4958 | 8.7497 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302
20% | 4325.4275 | 4.1148 | 4.7832 | 5.688 | 5.768 | 5.8216 | 5.8969 | 6.0685 | 6.2033 | 6.3231 | 6.3651 | 6.4131 | 6.346 | 6.3814 | 6.5478 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 20% | 4322.1583 | 4.5541 | 5.2245 | 6.1366 | 6.2098 | 6.2613 | 6.3143 | 6.5186 | 6.6381 | 6.7603 | 6.8159 | 6.8451 | 6.7437 | 6.7966 | 6.9997 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042
15% | 4360.497 | 3.0861 | 3.5874 | 4.266 | 4.326 | 4.3662 | 4.4227 | 4.5514 | 4.6524 | 4.7423 | 4.7738 | 4.8098 | 4.7595 | 4.786 | 4.9108 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 15% | 4354.2558 | 3.4156 | 3.9184 | 4.6024 | 4.6574 | 4.696 | 4.7357 | 4.889 | 4.9786 | 5.0702 | 5.1119 | 5.1338 | 5.0578 | 5.0975 | 5.2498 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781
10% | 4373.8709 | 2.0574 | 2.3916 | 2.844 | 2.884 | 2.9108 | 2.9485 | 3.0343 | 3.1016 | 3.1615 | 3.1825 | 3.2066 | 3.173 | 3.1907 | 3.2739 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 10% | 4366.1437 | 2.2771 | 2.6122 | 3.0683 | 3.1049 | 3.1306 | 3.1571 | 3.2593 | 3.3191 | 3.3801 | 3.4079 | 3.4225 | 3.3719 | 3.3983 | 3.4999 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521
5% | 4381.8952 | 1.0287 | 1.1958 | 1.422 | 1.442 | 1.4554 | 1.4742 | 1.5171 | 1.5508 | 1.5808 | 1.5913 | 1.6033 | 1.5865 | 1.5953 | 1.6369 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 5% | 4374.4653 | 1.1385 | 1.3061 | 1.5341 | 1.5525 | 1.5653 | 1.5786 | 1.6297 | 1.6595 | 1.6901 | 1.704 | 1.7113 | 1.6859 | 1.6992 | 1.7499 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726
9.992e-14% | 4391.7028 | 2.0557e-14 | 2.3897e-14 | 2.8417e-14 | 2.8817e-14 | 2.9085e-14 | 2.9461e-14 | 3.0318e-14 | 3.0992e-14 | 3.159e-14 | 3.18e-14 | 3.204e-14 | 3.1705e-14 | 3.1881e-14 | 3.2713e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 9.992e-14% | 4375.9513 | 2.2752e-14 | 2.6102e-14 | 3.0658e-14 | 3.1024e-14 | 3.1281e-14 | 3.1546e-14 | 3.2567e-14 | 3.3164e-14 | 3.3774e-14 | 3.4052e-14 | 3.4198e-14 | 3.3692e-14 | 3.3956e-14 | 3.4971e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 100% | 0 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
99% | 0.37816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 99% | 1.1345 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
98% | 0.37816 | 23.038 | 25.5757 | 29.8483 | 29.8162 | 29.7873 | 30.2504 | 30.9303 | 31.3963 | 30.8299 | 30.8862 | 31.1562 | 32.2251 | 31.2123 | 31.1528 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 98% | 1.8908 | 25.0331 | 28.1565 | 32.4217 | 32.3644 | 32.402 | 32.5186 | 32.9148 | 33.1802 | 33.3978 | 33.4299 | 33.6262 | 33.6957 | 33.6956 | 33.6506 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411
97% | 0.75633 | 22.8029 | 25.3147 | 29.5437 | 29.512 | 29.4833 | 29.9417 | 30.6147 | 31.0759 | 30.5153 | 30.5711 | 30.8382 | 31.8963 | 30.8938 | 30.8349 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 97% | 2.269 | 24.7777 | 27.8692 | 32.0909 | 32.0342 | 32.0714 | 32.1868 | 32.5789 | 32.8416 | 33.057 | 33.0888 | 33.2831 | 33.3519 | 33.3517 | 33.3073 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978
95% | 0.75633 | 22.3327 | 24.7927 | 28.9346 | 28.9035 | 28.8754 | 29.3244 | 29.9835 | 30.4352 | 29.8861 | 29.9407 | 30.2024 | 31.2386 | 30.2568 | 30.1991 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 95% | 4.1598 | 24.2668 | 27.2946 | 31.4292 | 31.3737 | 31.4101 | 31.5231 | 31.9072 | 32.1644 | 32.3754 | 32.4065 | 32.5968 | 32.6642 | 32.6641 | 32.6205 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112
90% | 3.7816 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 90% | 15.5047 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
85% | 13.6139 | 19.9819 | 22.183 | 25.8888 | 25.861 | 25.8359 | 26.2376 | 26.8273 | 27.2315 | 26.7402 | 26.7891 | 27.0232 | 27.9503 | 27.0719 | 27.0202 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 85% | 31.3876 | 21.7124 | 24.4215 | 28.1209 | 28.0712 | 28.1038 | 28.2049 | 28.5485 | 28.7787 | 28.9675 | 28.9953 | 29.1656 | 29.2259 | 29.2258 | 29.1868 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785
80% | 35.1693 | 18.8065 | 20.8781 | 24.366 | 24.3398 | 24.3161 | 24.6942 | 25.2493 | 25.6296 | 25.1673 | 25.2132 | 25.4336 | 26.3062 | 25.4794 | 25.4308 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 80% | 57.8591 | 20.4352 | 22.9849 | 26.4667 | 26.4199 | 26.4506 | 26.5458 | 26.8692 | 27.0858 | 27.2635 | 27.2897 | 27.4499 | 27.5067 | 27.5066 | 27.4699 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621
75% | 80.549 | 17.6311 | 19.5732 | 22.8431 | 22.8185 | 22.7964 | 23.1508 | 23.6712 | 24.0278 | 23.5943 | 23.6374 | 23.844 | 24.6621 | 23.8869 | 23.8414 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 75% | 121.3907 | 19.158 | 21.5484 | 24.8125 | 24.7687 | 24.7974 | 24.8867 | 25.1899 | 25.393 | 25.5596 | 25.5841 | 25.7343 | 25.7876 | 25.7874 | 25.753 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457
70% | 192.1075 | 16.4557 | 18.2683 | 21.3202 | 21.2973 | 21.2766 | 21.6074 | 22.0931 | 22.4259 | 22.0214 | 22.0616 | 22.2544 | 23.0179 | 22.2945 | 22.252 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 70% | 273.4128 | 17.8808 | 20.1118 | 23.1584 | 23.1174 | 23.1443 | 23.2276 | 23.5106 | 23.7001 | 23.8556 | 23.8785 | 24.0187 | 24.0684 | 24.0683 | 24.0362 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293
65% | 403.1231 | 15.2803 | 16.9635 | 19.7973 | 19.7761 | 19.7569 | 20.064 | 20.515 | 20.8241 | 20.4484 | 20.4858 | 20.6648 | 21.3738 | 20.702 | 20.6625 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 65% | 529.43 | 16.6036 | 18.6752 | 21.5042 | 21.4662 | 21.4911 | 21.5685 | 21.8312 | 22.0073 | 22.1516 | 22.1729 | 22.3031 | 22.3492 | 22.3491 | 22.3193 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313
60% | 739.3112 | 14.1049 | 15.6586 | 18.2745 | 18.2548 | 18.2371 | 18.5206 | 18.9369 | 19.2222 | 18.8755 | 18.9099 | 19.0752 | 19.7296 | 19.1095 | 19.0731 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 60% | 918.9392 | 15.3264 | 17.2387 | 19.85 | 19.8149 | 19.838 | 19.9093 | 20.1519 | 20.3144 | 20.4476 | 20.4673 | 20.5875 | 20.6301 | 20.6299 | 20.6024 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966
55% | 1204.8314 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 55% | 1454.0417 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
50% | 1783.0446 | 11.7541 | 13.0488 | 15.2287 | 15.2123 | 15.1976 | 15.4339 | 15.7808 | 16.0185 | 15.7295 | 15.7583 | 15.896 | 16.4414 | 15.9246 | 15.8943 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 50% | 2105.2406 | 12.772 | 14.3656 | 16.5417 | 16.5125 | 16.5316 | 16.5911 | 16.7933 | 16.9287 | 17.0397 | 17.0561 | 17.1562 | 17.1917 | 17.1916 | 17.1687 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638
45% | 2370.3337 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 45% | 2758.3303 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
40% | 2864.2163 | 9.4033 | 10.4391 | 12.183 | 12.1699 | 12.1581 | 12.3471 | 12.6246 | 12.8148 | 12.5836 | 12.6066 | 12.7168 | 13.1531 | 12.7397 | 12.7154 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 40% | 3348.2666 | 10.2176 | 11.4925 | 13.2333 | 13.21 | 13.2253 | 13.2729 | 13.4346 | 13.5429 | 13.6318 | 13.6448 | 13.725 | 13.7534 | 13.7533 | 13.735 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311
35% | 3297.9707 | 8.2279 | 9.1342 | 10.6601 | 10.6486 | 10.6383 | 10.8037 | 11.0465 | 11.213 | 11.0107 | 11.0308 | 11.1272 | 11.509 | 11.1472 | 11.126 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 35% | 3816.434 | 8.9404 | 10.0559 | 11.5792 | 11.5587 | 11.5721 | 11.6138 | 11.7553 | 11.8501 | 11.9278 | 11.9392 | 12.0093 | 12.0342 | 12.0341 | 12.0181 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147
30% | 3579.7031 | 7.0524 | 7.8293 | 9.1372 | 9.1274 | 9.1186 | 9.2603 | 9.4685 | 9.6111 | 9.4377 | 9.455 | 9.5376 | 9.8648 | 9.5548 | 9.5366 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 30% | 4067.1569 | 7.6632 | 8.6193 | 9.925 | 9.9075 | 9.919 | 9.9547 | 10.076 | 10.1572 | 10.2238 | 10.2336 | 10.2937 | 10.315 | 10.315 | 10.3012 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983
25% | 3796.3913 | 5.877 | 6.5244 | 7.6144 | 7.6062 | 7.5988 | 7.7169 | 7.8904 | 8.0093 | 7.8648 | 7.8791 | 7.948 | 8.2207 | 7.9623 | 7.9471 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 25% | 4236.9526 | 6.386 | 7.1828 | 8.2708 | 8.2562 | 8.2658 | 8.2956 | 8.3966 | 8.4643 | 8.5199 | 8.528 | 8.5781 | 8.5959 | 8.5958 | 8.5843 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819
20% | 3975.6411 | 4.7016 | 5.2195 | 6.0915 | 6.0849 | 6.079 | 6.1735 | 6.3123 | 6.4074 | 6.2918 | 6.3033 | 6.3584 | 6.5765 | 6.3698 | 6.3577 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 20% | 4332.6282 | 5.1088 | 5.7462 | 6.6167 | 6.605 | 6.6127 | 6.6364 | 6.7173 | 6.7715 | 6.8159 | 6.8224 | 6.8625 | 6.8767 | 6.8766 | 6.8675 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655
15% | 4117.4527 | 3.5262 | 3.9146 | 4.5686 | 4.5637 | 4.5593 | 4.6302 | 4.7342 | 4.8056 | 4.7189 | 4.7275 | 4.7688 | 4.9324 | 4.7774 | 4.7683 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 15% | 4361.7469 | 3.8316 | 4.3097 | 4.9625 | 4.9537 | 4.9595 | 4.9773 | 5.038 | 5.0786 | 5.1119 | 5.1168 | 5.1469 | 5.1575 | 5.1575 | 5.1506 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491
10% | 4224.8514 | 2.3508 | 2.6098 | 3.0457 | 3.0425 | 3.0395 | 3.0868 | 3.1562 | 3.2037 | 3.1459 | 3.1517 | 3.1792 | 3.2883 | 3.1849 | 3.1789 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 10% | 4375.7389 | 2.5544 | 2.8731 | 3.3083 | 3.3025 | 3.3063 | 3.3182 | 3.3587 | 3.3857 | 3.4079 | 3.4112 | 3.4312 | 3.4383 | 3.4383 | 3.4337 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328
5% | 4310.3165 | 1.1754 | 1.3049 | 1.5229 | 1.5212 | 1.5198 | 1.5434 | 1.5781 | 1.6019 | 1.573 | 1.5758 | 1.5896 | 1.6441 | 1.5925 | 1.5894 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 5% | 4378.0079 | 1.2772 | 1.4366 | 1.6542 | 1.6512 | 1.6532 | 1.6591 | 1.6793 | 1.6929 | 1.704 | 1.7056 | 1.7156 | 1.7192 | 1.7192 | 1.7169 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164
9.992e-14% | 4382.5459 | 2.3489e-14 | 2.6077e-14 | 3.0433e-14 | 3.04e-14 | 3.0371e-14 | 3.0843e-14 | 3.1536e-14 | 3.2011e-14 | 3.1434e-14 | 3.1491e-14 | 3.1767e-14 | 3.2856e-14 | 3.1824e-14 | 3.1763e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 9.992e-14% | 4379.1424 | 2.5524e-14 | 2.8708e-14 | 3.3057e-14 | 3.2999e-14 | 3.3037e-14 | 3.3156e-14 | 3.356e-14 | 3.383e-14 | 3.4052e-14 | 3.4085e-14 | 3.4285e-14 | 3.4356e-14 | 3.4356e-14 | 3.431e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 100% | 0 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
99% | 0.2972 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 99% | 0.2972 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
98% | 0.8916 | 20.1623 | 23.4376 | 27.871 | 28.2634 | 28.5259 | 28.8949 | 29.7357 | 30.396 | 30.983 | 31.189 | 31.4243 | 31.0953 | 31.2688 | 32.0842 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 98% | 0.8916 | 22.3151 | 25.6 | 30.0692 | 30.428 | 30.6802 | 30.9399 | 31.9413 | 32.5267 | 33.1254 | 33.3977 | 33.5408 | 33.0442 | 33.3035 | 34.2987 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305
97% | 1.7832 | 19.9566 | 23.1984 | 27.5866 | 27.975 | 28.2348 | 28.6 | 29.4323 | 30.0858 | 30.6669 | 30.8707 | 31.1036 | 30.778 | 30.9497 | 31.7568 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 97% | 2.0804 | 22.0874 | 25.3388 | 29.7624 | 30.1176 | 30.3672 | 30.6242 | 31.6154 | 32.1948 | 32.7874 | 33.0569 | 33.1986 | 32.707 | 32.9637 | 33.9487 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853
95% | 4.458 | 19.5451 | 22.7201 | 27.0178 | 27.3982 | 27.6526 | 28.0103 | 28.8254 | 29.4655 | 30.0346 | 30.2342 | 30.4623 | 30.1434 | 30.3116 | 31.102 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 95% | 4.1608 | 21.632 | 24.8164 | 29.1487 | 29.4966 | 29.7411 | 29.9928 | 30.9635 | 31.531 | 32.1113 | 32.3753 | 32.5141 | 32.0326 | 32.284 | 33.2487 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948
90% | 15.1571 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 90% | 11.5907 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
85% | 39.5274 | 17.4877 | 20.3285 | 24.1738 | 24.5142 | 24.7418 | 25.0619 | 25.7912 | 26.3639 | 26.8731 | 27.0517 | 27.2558 | 26.9704 | 27.1209 | 27.8281 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 85% | 32.6918 | 19.355 | 22.2041 | 26.0804 | 26.3917 | 26.6104 | 26.8357 | 27.7042 | 28.2119 | 28.7312 | 28.9674 | 29.0915 | 28.6608 | 28.8857 | 29.7489 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427
80% | 110.5579 | 16.4591 | 19.1327 | 22.7518 | 23.0722 | 23.2864 | 23.5876 | 24.2741 | 24.813 | 25.2923 | 25.4604 | 25.6525 | 25.3839 | 25.5255 | 26.1912 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 80% | 84.1072 | 18.2164 | 20.898 | 24.5463 | 24.8392 | 25.0451 | 25.2571 | 26.0746 | 26.5524 | 27.0411 | 27.2634 | 27.3803 | 26.9748 | 27.1865 | 27.9989 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167
75% | 244.2972 | 15.4304 | 17.9369 | 21.3298 | 21.6302 | 21.831 | 22.1134 | 22.7569 | 23.2622 | 23.7115 | 23.8691 | 24.0492 | 23.7974 | 23.9302 | 24.5542 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 75% | 202.095 | 17.0779 | 19.5919 | 23.0122 | 23.2868 | 23.4798 | 23.6785 | 24.4449 | 24.8929 | 25.3511 | 25.5595 | 25.669 | 25.2889 | 25.4874 | 26.249 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907
70% | 444.0146 | 14.4017 | 16.7411 | 19.9078 | 20.1881 | 20.3756 | 20.6392 | 21.2398 | 21.7114 | 22.1307 | 22.2778 | 22.4459 | 22.2109 | 22.3349 | 22.9173 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 70% | 388.1413 | 15.9394 | 18.2857 | 21.478 | 21.7343 | 21.9145 | 22.1 | 22.8152 | 23.2334 | 23.661 | 23.8555 | 23.9577 | 23.603 | 23.7882 | 24.4991 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646
65% | 770.3386 | 13.373 | 15.5453 | 18.4859 | 18.7461 | 18.9202 | 19.165 | 19.7227 | 20.1606 | 20.55 | 20.6866 | 20.8426 | 20.6244 | 20.7395 | 21.2803 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 65% | 669.8855 | 14.8008 | 16.9796 | 19.9439 | 20.1819 | 20.3491 | 20.5214 | 21.1856 | 21.5738 | 21.9709 | 22.1515 | 22.2465 | 21.917 | 22.0891 | 22.7491 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386
60% | 1209.3009 | 12.3443 | 14.3496 | 17.0639 | 17.3041 | 17.4648 | 17.6907 | 18.2055 | 18.6098 | 18.9692 | 19.0953 | 19.2394 | 19.038 | 19.1442 | 19.6434 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 60% | 1104.687 | 13.6623 | 15.6735 | 18.4097 | 18.6294 | 18.7838 | 18.9428 | 19.5559 | 19.9143 | 20.2808 | 20.4476 | 20.5352 | 20.2311 | 20.3899 | 20.9992 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125
55% | 1757.6322 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 55% | 1631.62 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
50% | 2378.4799 | 10.2869 | 11.958 | 14.2199 | 14.4201 | 14.554 | 14.7423 | 15.1713 | 15.5081 | 15.8077 | 15.9127 | 16.0328 | 15.865 | 15.9535 | 16.3695 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 50% | 2253.9537 | 11.3853 | 13.0612 | 15.3414 | 15.5245 | 15.6532 | 15.7857 | 16.2966 | 16.5953 | 16.9007 | 17.0396 | 17.1127 | 16.8593 | 16.9916 | 17.4993 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604
45% | 3003.7856 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 45% | 2892.3362 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
40% | 3548.2533 | 8.2295 | 9.5664 | 11.3759 | 11.5361 | 11.6432 | 11.7938 | 12.137 | 12.4065 | 12.6461 | 12.7302 | 12.8262 | 12.692 | 12.7628 | 13.0956 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 40% | 3473.3593 | 9.1082 | 10.449 | 12.2731 | 12.4196 | 12.5226 | 12.6285 | 13.0373 | 13.2762 | 13.5206 | 13.6317 | 13.6901 | 13.4874 | 13.5933 | 13.9995 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084
35% | 3927.7759 | 7.2008 | 8.3706 | 9.9539 | 10.0941 | 10.1878 | 10.3196 | 10.6199 | 10.8557 | 11.0654 | 11.1389 | 11.223 | 11.1055 | 11.1674 | 11.4586 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 35% | 3882.8989 | 7.9697 | 9.1429 | 10.739 | 10.8672 | 10.9572 | 11.05 | 11.4076 | 11.6167 | 11.8305 | 11.9278 | 11.9789 | 11.8015 | 11.8941 | 12.2495 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823
30% | 4135.8149 | 6.1721 | 7.1748 | 8.5319 | 8.6521 | 8.7324 | 8.8454 | 9.1028 | 9.3049 | 9.4846 | 9.5476 | 9.6197 | 9.519 | 9.5721 | 9.8217 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 30% | 4127.1961 | 6.8312 | 7.8367 | 9.2049 | 9.3147 | 9.3919 | 9.4714 | 9.778 | 9.9572 | 10.1404 | 10.2238 | 10.2676 | 10.1156 | 10.1949 | 10.4996 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563
25% | 4252.0195 | 5.1435 | 5.979 | 7.1099 | 7.2101 | 7.277 | 7.3711 | 7.5856 | 7.7541 | 7.9038 | 7.9564 | 8.0164 | 7.9325 | 7.9767 | 8.1847 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 25% | 4245.1839 | 5.6926 | 6.5306 | 7.6707 | 7.7623 | 7.8266 | 7.8928 | 8.1483 | 8.2976 | 8.4504 | 8.5198 | 8.5563 | 8.4296 | 8.4958 | 8.7497 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302
20% | 4325.4275 | 4.1148 | 4.7832 | 5.688 | 5.768 | 5.8216 | 5.8969 | 6.0685 | 6.2033 | 6.3231 | 6.3651 | 6.4131 | 6.346 | 6.3814 | 6.5478 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 20% | 4322.1583 | 4.5541 | 5.2245 | 6.1366 | 6.2098 | 6.2613 | 6.3143 | 6.5186 | 6.6381 | 6.7603 | 6.8159 | 6.8451 | 6.7437 | 6.7966 | 6.9997 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042
15% | 4360.497 | 3.0861 | 3.5874 | 4.266 | 4.326 | 4.3662 | 4.4227 | 4.5514 | 4.6524 | 4.7423 | 4.7738 | 4.8098 | 4.7595 | 4.786 | 4.9108 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 15% | 4354.2558 | 3.4156 | 3.9184 | 4.6024 | 4.6574 | 4.696 | 4.7357 | 4.889 | 4.9786 | 5.0702 | 5.1119 | 5.1338 | 5.0578 | 5.0975 | 5.2498 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781
10% | 4373.8709 | 2.0574 | 2.3916 | 2.844 | 2.884 | 2.9108 | 2.9485 | 3.0343 | 3.1016 | 3.1615 | 3.1825 | 3.2066 | 3.173 | 3.1907 | 3.2739 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 10% | 4366.1437 | 2.2771 | 2.6122 | 3.0683 | 3.1049 | 3.1306 | 3.1571 | 3.2593 | 3.3191 | 3.3801 | 3.4079 | 3.4225 | 3.3719 | 3.3983 | 3.4999 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521
5% | 4381.8952 | 1.0287 | 1.1958 | 1.422 | 1.442 | 1.4554 | 1.4742 | 1.5171 | 1.5508 | 1.5808 | 1.5913 | 1.6033 | 1.5865 | 1.5953 | 1.6369 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 5% | 4374.4653 | 1.1385 | 1.3061 | 1.5341 | 1.5525 | 1.5653 | 1.5786 | 1.6297 | 1.6595 | 1.6901 | 1.704 | 1.7113 | 1.6859 | 1.6992 | 1.7499 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726
9.992e-14% | 4391.7028 | 2.0557e-14 | 2.3897e-14 | 2.8417e-14 | 2.8817e-14 | 2.9085e-14 | 2.9461e-14 | 3.0318e-14 | 3.0992e-14 | 3.159e-14 | 3.18e-14 | 3.204e-14 | 3.1705e-14 | 3.1881e-14 | 3.2713e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 9.992e-14% | 4375.9513 | 2.2752e-14 | 2.6102e-14 | 3.0658e-14 | 3.1024e-14 | 3.1281e-14 | 3.1546e-14 | 3.2567e-14 | 3.3164e-14 | 3.3774e-14 | 3.4052e-14 | 3.4198e-14 | 3.3692e-14 | 3.3956e-14 | 3.4971e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 100% | 0 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
99% | 0.37816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 99% | 1.1345 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
98% | 0.37816 | 23.038 | 25.5757 | 29.8483 | 29.8162 | 29.7873 | 30.2504 | 30.9303 | 31.3963 | 30.8299 | 30.8862 | 31.1562 | 32.2251 | 31.2123 | 31.1528 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 98% | 1.8908 | 25.0331 | 28.1565 | 32.4217 | 32.3644 | 32.402 | 32.5186 | 32.9148 | 33.1802 | 33.3978 | 33.4299 | 33.6262 | 33.6957 | 33.6956 | 33.6506 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411
97% | 0.75633 | 22.8029 | 25.3147 | 29.5437 | 29.512 | 29.4833 | 29.9417 | 30.6147 | 31.0759 | 30.5153 | 30.5711 | 30.8382 | 31.8963 | 30.8938 | 30.8349 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 97% | 2.269 | 24.7777 | 27.8692 | 32.0909 | 32.0342 | 32.0714 | 32.1868 | 32.5789 | 32.8416 | 33.057 | 33.0888 | 33.2831 | 33.3519 | 33.3517 | 33.3073 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978
95% | 0.75633 | 22.3327 | 24.7927 | 28.9346 | 28.9035 | 28.8754 | 29.3244 | 29.9835 | 30.4352 | 29.8861 | 29.9407 | 30.2024 | 31.2386 | 30.2568 | 30.1991 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 95% | 4.1598 | 24.2668 | 27.2946 | 31.4292 | 31.3737 | 31.4101 | 31.5231 | 31.9072 | 32.1644 | 32.3754 | 32.4065 | 32.5968 | 32.6642 | 32.6641 | 32.6205 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112
90% | 3.7816 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 90% | 15.5047 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
85% | 13.6139 | 19.9819 | 22.183 | 25.8888 | 25.861 | 25.8359 | 26.2376 | 26.8273 | 27.2315 | 26.7402 | 26.7891 | 27.0232 | 27.9503 | 27.0719 | 27.0202 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 85% | 31.3876 | 21.7124 | 24.4215 | 28.1209 | 28.0712 | 28.1038 | 28.2049 | 28.5485 | 28.7787 | 28.9675 | 28.9953 | 29.1656 | 29.2259 | 29.2258 | 29.1868 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785
80% | 35.1693 | 18.8065 | 20.8781 | 24.366 | 24.3398 | 24.3161 | 24.6942 | 25.2493 | 25.6296 | 25.1673 | 25.2132 | 25.4336 | 26.3062 | 25.4794 | 25.4308 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 80% | 57.8591 | 20.4352 | 22.9849 | 26.4667 | 26.4199 | 26.4506 | 26.5458 | 26.8692 | 27.0858 | 27.2635 | 27.2897 | 27.4499 | 27.5067 | 27.5066 | 27.4699 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621
75% | 80.549 | 17.6311 | 19.5732 | 22.8431 | 22.8185 | 22.7964 | 23.1508 | 23.6712 | 24.0278 | 23.5943 | 23.6374 | 23.844 | 24.6621 | 23.8869 | 23.8414 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 75% | 121.3907 | 19.158 | 21.5484 | 24.8125 | 24.7687 | 24.7974 | 24.8867 | 25.1899 | 25.393 | 25.5596 | 25.5841 | 25.7343 | 25.7876 | 25.7874 | 25.753 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457
70% | 192.1075 | 16.4557 | 18.2683 | 21.3202 | 21.2973 | 21.2766 | 21.6074 | 22.0931 | 22.4259 | 22.0214 | 22.0616 | 22.2544 | 23.0179 | 22.2945 | 22.252 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 70% | 273.4128 | 17.8808 | 20.1118 | 23.1584 | 23.1174 | 23.1443 | 23.2276 | 23.5106 | 23.7001 | 23.8556 | 23.8785 | 24.0187 | 24.0684 | 24.0683 | 24.0362 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293
65% | 403.1231 | 15.2803 | 16.9635 | 19.7973 | 19.7761 | 19.7569 | 20.064 | 20.515 | 20.8241 | 20.4484 | 20.4858 | 20.6648 | 21.3738 | 20.702 | 20.6625 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 65% | 529.43 | 16.6036 | 18.6752 | 21.5042 | 21.4662 | 21.4911 | 21.5685 | 21.8312 | 22.0073 | 22.1516 | 22.1729 | 22.3031 | 22.3492 | 22.3491 | 22.3193 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313
60% | 739.3112 | 14.1049 | 15.6586 | 18.2745 | 18.2548 | 18.2371 | 18.5206 | 18.9369 | 19.2222 | 18.8755 | 18.9099 | 19.0752 | 19.7296 | 19.1095 | 19.0731 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 60% | 918.9392 | 15.3264 | 17.2387 | 19.85 | 19.8149 | 19.838 | 19.9093 | 20.1519 | 20.3144 | 20.4476 | 20.4673 | 20.5875 | 20.6301 | 20.6299 | 20.6024 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966
55% | 1204.8314 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 55% | 1454.0417 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
50% | 1783.0446 | 11.7541 | 13.0488 | 15.2287 | 15.2123 | 15.1976 | 15.4339 | 15.7808 | 16.0185 | 15.7295 | 15.7583 | 15.896 | 16.4414 | 15.9246 | 15.8943 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 50% | 2105.2406 | 12.772 | 14.3656 | 16.5417 | 16.5125 | 16.5316 | 16.5911 | 16.7933 | 16.9287 | 17.0397 | 17.0561 | 17.1562 | 17.1917 | 17.1916 | 17.1687 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638
45% | 2370.3337 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 45% | 2758.3303 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
40% | 2864.2163 | 9.4033 | 10.4391 | 12.183 | 12.1699 | 12.1581 | 12.3471 | 12.6246 | 12.8148 | 12.5836 | 12.6066 | 12.7168 | 13.1531 | 12.7397 | 12.7154 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 40% | 3348.2666 | 10.2176 | 11.4925 | 13.2333 | 13.21 | 13.2253 | 13.2729 | 13.4346 | 13.5429 | 13.6318 | 13.6448 | 13.725 | 13.7534 | 13.7533 | 13.735 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311
35% | 3297.9707 | 8.2279 | 9.1342 | 10.6601 | 10.6486 | 10.6383 | 10.8037 | 11.0465 | 11.213 | 11.0107 | 11.0308 | 11.1272 | 11.509 | 11.1472 | 11.126 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 35% | 3816.434 | 8.9404 | 10.0559 | 11.5792 | 11.5587 | 11.5721 | 11.6138 | 11.7553 | 11.8501 | 11.9278 | 11.9392 | 12.0093 | 12.0342 | 12.0341 | 12.0181 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147
30% | 3579.7031 | 7.0524 | 7.8293 | 9.1372 | 9.1274 | 9.1186 | 9.2603 | 9.4685 | 9.6111 | 9.4377 | 9.455 | 9.5376 | 9.8648 | 9.5548 | 9.5366 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 30% | 4067.1569 | 7.6632 | 8.6193 | 9.925 | 9.9075 | 9.919 | 9.9547 | 10.076 | 10.1572 | 10.2238 | 10.2336 | 10.2937 | 10.315 | 10.315 | 10.3012 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983
25% | 3796.3913 | 5.877 | 6.5244 | 7.6144 | 7.6062 | 7.5988 | 7.7169 | 7.8904 | 8.0093 | 7.8648 | 7.8791 | 7.948 | 8.2207 | 7.9623 | 7.9471 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 25% | 4236.9526 | 6.386 | 7.1828 | 8.2708 | 8.2562 | 8.2658 | 8.2956 | 8.3966 | 8.4643 | 8.5199 | 8.528 | 8.5781 | 8.5959 | 8.5958 | 8.5843 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819
20% | 3975.6411 | 4.7016 | 5.2195 | 6.0915 | 6.0849 | 6.079 | 6.1735 | 6.3123 | 6.4074 | 6.2918 | 6.3033 | 6.3584 | 6.5765 | 6.3698 | 6.3577 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 20% | 4332.6282 | 5.1088 | 5.7462 | 6.6167 | 6.605 | 6.6127 | 6.6364 | 6.7173 | 6.7715 | 6.8159 | 6.8224 | 6.8625 | 6.8767 | 6.8766 | 6.8675 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655
15% | 4117.4527 | 3.5262 | 3.9146 | 4.5686 | 4.5637 | 4.5593 | 4.6302 | 4.7342 | 4.8056 | 4.7189 | 4.7275 | 4.7688 | 4.9324 | 4.7774 | 4.7683 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 15% | 4361.7469 | 3.8316 | 4.3097 | 4.9625 | 4.9537 | 4.9595 | 4.9773 | 5.038 | 5.0786 | 5.1119 | 5.1168 | 5.1469 | 5.1575 | 5.1575 | 5.1506 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491
10% | 4224.8514 | 2.3508 | 2.6098 | 3.0457 | 3.0425 | 3.0395 | 3.0868 | 3.1562 | 3.2037 | 3.1459 | 3.1517 | 3.1792 | 3.2883 | 3.1849 | 3.1789 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 10% | 4375.7389 | 2.5544 | 2.8731 | 3.3083 | 3.3025 | 3.3063 | 3.3182 | 3.3587 | 3.3857 | 3.4079 | 3.4112 | 3.4312 | 3.4383 | 3.4383 | 3.4337 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328
5% | 4310.3165 | 1.1754 | 1.3049 | 1.5229 | 1.5212 | 1.5198 | 1.5434 | 1.5781 | 1.6019 | 1.573 | 1.5758 | 1.5896 | 1.6441 | 1.5925 | 1.5894 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 5% | 4378.0079 | 1.2772 | 1.4366 | 1.6542 | 1.6512 | 1.6532 | 1.6591 | 1.6793 | 1.6929 | 1.704 | 1.7056 | 1.7156 | 1.7192 | 1.7192 | 1.7169 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164
9.992e-14% | 4382.5459 | 2.3489e-14 | 2.6077e-14 | 3.0433e-14 | 3.04e-14 | 3.0371e-14 | 3.0843e-14 | 3.1536e-14 | 3.2011e-14 | 3.1434e-14 | 3.1491e-14 | 3.1767e-14 | 3.2856e-14 | 3.1824e-14 | 3.1763e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 9.992e-14% | 4379.1424 | 2.5524e-14 | 2.8708e-14 | 3.3057e-14 | 3.2999e-14 | 3.3037e-14 | 3.3156e-14 | 3.356e-14 | 3.383e-14 | 3.4052e-14 | 3.4085e-14 | 3.4285e-14 | 3.4356e-14 | 3.4356e-14 | 3.431e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 100% | 0 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
99% | 0.2972 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 99% | 0.2972 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
98% | 0.8916 | 20.1623 | 23.4376 | 27.871 | 28.2634 | 28.5259 | 28.8949 | 29.7357 | 30.396 | 30.983 | 31.189 | 31.4243 | 31.0953 | 31.2688 | 32.0842 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 98% | 0.8916 | 22.3151 | 25.6 | 30.0692 | 30.428 | 30.6802 | 30.9399 | 31.9413 | 32.5267 | 33.1254 | 33.3977 | 33.5408 | 33.0442 | 33.3035 | 34.2987 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305
97% | 1.7832 | 19.9566 | 23.1984 | 27.5866 | 27.975 | 28.2348 | 28.6 | 29.4323 | 30.0858 | 30.6669 | 30.8707 | 31.1036 | 30.778 | 30.9497 | 31.7568 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 97% | 2.0804 | 22.0874 | 25.3388 | 29.7624 | 30.1176 | 30.3672 | 30.6242 | 31.6154 | 32.1948 | 32.7874 | 33.0569 | 33.1986 | 32.707 | 32.9637 | 33.9487 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853
95% | 4.458 | 19.5451 | 22.7201 | 27.0178 | 27.3982 | 27.6526 | 28.0103 | 28.8254 | 29.4655 | 30.0346 | 30.2342 | 30.4623 | 30.1434 | 30.3116 | 31.102 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 95% | 4.1608 | 21.632 | 24.8164 | 29.1487 | 29.4966 | 29.7411 | 29.9928 | 30.9635 | 31.531 | 32.1113 | 32.3753 | 32.5141 | 32.0326 | 32.284 | 33.2487 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948
90% | 15.1571 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 90% | 11.5907 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
85% | 39.5274 | 17.4877 | 20.3285 | 24.1738 | 24.5142 | 24.7418 | 25.0619 | 25.7912 | 26.3639 | 26.8731 | 27.0517 | 27.2558 | 26.9704 | 27.1209 | 27.8281 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 85% | 32.6918 | 19.355 | 22.2041 | 26.0804 | 26.3917 | 26.6104 | 26.8357 | 27.7042 | 28.2119 | 28.7312 | 28.9674 | 29.0915 | 28.6608 | 28.8857 | 29.7489 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427
80% | 110.5579 | 16.4591 | 19.1327 | 22.7518 | 23.0722 | 23.2864 | 23.5876 | 24.2741 | 24.813 | 25.2923 | 25.4604 | 25.6525 | 25.3839 | 25.5255 | 26.1912 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 80% | 84.1072 | 18.2164 | 20.898 | 24.5463 | 24.8392 | 25.0451 | 25.2571 | 26.0746 | 26.5524 | 27.0411 | 27.2634 | 27.3803 | 26.9748 | 27.1865 | 27.9989 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167
75% | 244.2972 | 15.4304 | 17.9369 | 21.3298 | 21.6302 | 21.831 | 22.1134 | 22.7569 | 23.2622 | 23.7115 | 23.8691 | 24.0492 | 23.7974 | 23.9302 | 24.5542 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 75% | 202.095 | 17.0779 | 19.5919 | 23.0122 | 23.2868 | 23.4798 | 23.6785 | 24.4449 | 24.8929 | 25.3511 | 25.5595 | 25.669 | 25.2889 | 25.4874 | 26.249 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907
70% | 444.0146 | 14.4017 | 16.7411 | 19.9078 | 20.1881 | 20.3756 | 20.6392 | 21.2398 | 21.7114 | 22.1307 | 22.2778 | 22.4459 | 22.2109 | 22.3349 | 22.9173 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 70% | 388.1413 | 15.9394 | 18.2857 | 21.478 | 21.7343 | 21.9145 | 22.1 | 22.8152 | 23.2334 | 23.661 | 23.8555 | 23.9577 | 23.603 | 23.7882 | 24.4991 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646
65% | 770.3386 | 13.373 | 15.5453 | 18.4859 | 18.7461 | 18.9202 | 19.165 | 19.7227 | 20.1606 | 20.55 | 20.6866 | 20.8426 | 20.6244 | 20.7395 | 21.2803 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 65% | 669.8855 | 14.8008 | 16.9796 | 19.9439 | 20.1819 | 20.3491 | 20.5214 | 21.1856 | 21.5738 | 21.9709 | 22.1515 | 22.2465 | 21.917 | 22.0891 | 22.7491 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386
60% | 1209.3009 | 12.3443 | 14.3496 | 17.0639 | 17.3041 | 17.4648 | 17.6907 | 18.2055 | 18.6098 | 18.9692 | 19.0953 | 19.2394 | 19.038 | 19.1442 | 19.6434 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 60% | 1104.687 | 13.6623 | 15.6735 | 18.4097 | 18.6294 | 18.7838 | 18.9428 | 19.5559 | 19.9143 | 20.2808 | 20.4476 | 20.5352 | 20.2311 | 20.3899 | 20.9992 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125
55% | 1757.6322 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 55% | 1631.62 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
50% | 2378.4799 | 10.2869 | 11.958 | 14.2199 | 14.4201 | 14.554 | 14.7423 | 15.1713 | 15.5081 | 15.8077 | 15.9127 | 16.0328 | 15.865 | 15.9535 | 16.3695 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 50% | 2253.9537 | 11.3853 | 13.0612 | 15.3414 | 15.5245 | 15.6532 | 15.7857 | 16.2966 | 16.5953 | 16.9007 | 17.0396 | 17.1127 | 16.8593 | 16.9916 | 17.4993 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604
45% | 3003.7856 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 45% | 2892.3362 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
40% | 3548.2533 | 8.2295 | 9.5664 | 11.3759 | 11.5361 | 11.6432 | 11.7938 | 12.137 | 12.4065 | 12.6461 | 12.7302 | 12.8262 | 12.692 | 12.7628 | 13.0956 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 40% | 3473.3593 | 9.1082 | 10.449 | 12.2731 | 12.4196 | 12.5226 | 12.6285 | 13.0373 | 13.2762 | 13.5206 | 13.6317 | 13.6901 | 13.4874 | 13.5933 | 13.9995 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084
35% | 3927.7759 | 7.2008 | 8.3706 | 9.9539 | 10.0941 | 10.1878 | 10.3196 | 10.6199 | 10.8557 | 11.0654 | 11.1389 | 11.223 | 11.1055 | 11.1674 | 11.4586 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 35% | 3882.8989 | 7.9697 | 9.1429 | 10.739 | 10.8672 | 10.9572 | 11.05 | 11.4076 | 11.6167 | 11.8305 | 11.9278 | 11.9789 | 11.8015 | 11.8941 | 12.2495 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823
30% | 4135.8149 | 6.1721 | 7.1748 | 8.5319 | 8.6521 | 8.7324 | 8.8454 | 9.1028 | 9.3049 | 9.4846 | 9.5476 | 9.6197 | 9.519 | 9.5721 | 9.8217 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 30% | 4127.1961 | 6.8312 | 7.8367 | 9.2049 | 9.3147 | 9.3919 | 9.4714 | 9.778 | 9.9572 | 10.1404 | 10.2238 | 10.2676 | 10.1156 | 10.1949 | 10.4996 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563
25% | 4252.0195 | 5.1435 | 5.979 | 7.1099 | 7.2101 | 7.277 | 7.3711 | 7.5856 | 7.7541 | 7.9038 | 7.9564 | 8.0164 | 7.9325 | 7.9767 | 8.1847 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 25% | 4245.1839 | 5.6926 | 6.5306 | 7.6707 | 7.7623 | 7.8266 | 7.8928 | 8.1483 | 8.2976 | 8.4504 | 8.5198 | 8.5563 | 8.4296 | 8.4958 | 8.7497 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302
20% | 4325.4275 | 4.1148 | 4.7832 | 5.688 | 5.768 | 5.8216 | 5.8969 | 6.0685 | 6.2033 | 6.3231 | 6.3651 | 6.4131 | 6.346 | 6.3814 | 6.5478 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 20% | 4322.1583 | 4.5541 | 5.2245 | 6.1366 | 6.2098 | 6.2613 | 6.3143 | 6.5186 | 6.6381 | 6.7603 | 6.8159 | 6.8451 | 6.7437 | 6.7966 | 6.9997 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042
15% | 4360.497 | 3.0861 | 3.5874 | 4.266 | 4.326 | 4.3662 | 4.4227 | 4.5514 | 4.6524 | 4.7423 | 4.7738 | 4.8098 | 4.7595 | 4.786 | 4.9108 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 15% | 4354.2558 | 3.4156 | 3.9184 | 4.6024 | 4.6574 | 4.696 | 4.7357 | 4.889 | 4.9786 | 5.0702 | 5.1119 | 5.1338 | 5.0578 | 5.0975 | 5.2498 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781
10% | 4373.8709 | 2.0574 | 2.3916 | 2.844 | 2.884 | 2.9108 | 2.9485 | 3.0343 | 3.1016 | 3.1615 | 3.1825 | 3.2066 | 3.173 | 3.1907 | 3.2739 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 10% | 4366.1437 | 2.2771 | 2.6122 | 3.0683 | 3.1049 | 3.1306 | 3.1571 | 3.2593 | 3.3191 | 3.3801 | 3.4079 | 3.4225 | 3.3719 | 3.3983 | 3.4999 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521
5% | 4381.8952 | 1.0287 | 1.1958 | 1.422 | 1.442 | 1.4554 | 1.4742 | 1.5171 | 1.5508 | 1.5808 | 1.5913 | 1.6033 | 1.5865 | 1.5953 | 1.6369 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 5% | 4374.4653 | 1.1385 | 1.3061 | 1.5341 | 1.5525 | 1.5653 | 1.5786 | 1.6297 | 1.6595 | 1.6901 | 1.704 | 1.7113 | 1.6859 | 1.6992 | 1.7499 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726
9.992e-14% | 4391.7028 | 2.0557e-14 | 2.3897e-14 | 2.8417e-14 | 2.8817e-14 | 2.9085e-14 | 2.9461e-14 | 3.0318e-14 | 3.0992e-14 | 3.159e-14 | 3.18e-14 | 3.204e-14 | 3.1705e-14 | 3.1881e-14 | 3.2713e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 9.992e-14% | 4375.9513 | 2.2752e-14 | 2.6102e-14 | 3.0658e-14 | 3.1024e-14 | 3.1281e-14 | 3.1546e-14 | 3.2567e-14 | 3.3164e-14 | 3.3774e-14 | 3.4052e-14 | 3.4198e-14 | 3.3692e-14 | 3.3956e-14 | 3.4971e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 100% | 0 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
99% | 0.37816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 99% | 1.1345 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
98% | 0.37816 | 23.038 | 25.5757 | 29.8483 | 29.8162 | 29.7873 | 30.2504 | 30.9303 | 31.3963 | 30.8299 | 30.8862 | 31.1562 | 32.2251 | 31.2123 | 31.1528 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 98% | 1.8908 | 25.0331 | 28.1565 | 32.4217 | 32.3644 | 32.402 | 32.5186 | 32.9148 | 33.1802 | 33.3978 | 33.4299 | 33.6262 | 33.6957 | 33.6956 | 33.6506 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411
97% | 0.75633 | 22.8029 | 25.3147 | 29.5437 | 29.512 | 29.4833 | 29.9417 | 30.6147 | 31.0759 | 30.5153 | 30.5711 | 30.8382 | 31.8963 | 30.8938 | 30.8349 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 97% | 2.269 | 24.7777 | 27.8692 | 32.0909 | 32.0342 | 32.0714 | 32.1868 | 32.5789 | 32.8416 | 33.057 | 33.0888 | 33.2831 | 33.3519 | 33.3517 | 33.3073 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978
95% | 0.75633 | 22.3327 | 24.7927 | 28.9346 | 28.9035 | 28.8754 | 29.3244 | 29.9835 | 30.4352 | 29.8861 | 29.9407 | 30.2024 | 31.2386 | 30.2568 | 30.1991 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 95% | 4.1598 | 24.2668 | 27.2946 | 31.4292 | 31.3737 | 31.4101 | 31.5231 | 31.9072 | 32.1644 | 32.3754 | 32.4065 | 32.5968 | 32.6642 | 32.6641 | 32.6205 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112
90% | 3.7816 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 90% | 15.5047 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
85% | 13.6139 | 19.9819 | 22.183 | 25.8888 | 25.861 | 25.8359 | 26.2376 | 26.8273 | 27.2315 | 26.7402 | 26.7891 | 27.0232 | 27.9503 | 27.0719 | 27.0202 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 85% | 31.3876 | 21.7124 | 24.4215 | 28.1209 | 28.0712 | 28.1038 | 28.2049 | 28.5485 | 28.7787 | 28.9675 | 28.9953 | 29.1656 | 29.2259 | 29.2258 | 29.1868 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785
80% | 35.1693 | 18.8065 | 20.8781 | 24.366 | 24.3398 | 24.3161 | 24.6942 | 25.2493 | 25.6296 | 25.1673 | 25.2132 | 25.4336 | 26.3062 | 25.4794 | 25.4308 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 80% | 57.8591 | 20.4352 | 22.9849 | 26.4667 | 26.4199 | 26.4506 | 26.5458 | 26.8692 | 27.0858 | 27.2635 | 27.2897 | 27.4499 | 27.5067 | 27.5066 | 27.4699 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621
75% | 80.549 | 17.6311 | 19.5732 | 22.8431 | 22.8185 | 22.7964 | 23.1508 | 23.6712 | 24.0278 | 23.5943 | 23.6374 | 23.844 | 24.6621 | 23.8869 | 23.8414 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 75% | 121.3907 | 19.158 | 21.5484 | 24.8125 | 24.7687 | 24.7974 | 24.8867 | 25.1899 | 25.393 | 25.5596 | 25.5841 | 25.7343 | 25.7876 | 25.7874 | 25.753 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457
70% | 192.1075 | 16.4557 | 18.2683 | 21.3202 | 21.2973 | 21.2766 | 21.6074 | 22.0931 | 22.4259 | 22.0214 | 22.0616 | 22.2544 | 23.0179 | 22.2945 | 22.252 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 70% | 273.4128 | 17.8808 | 20.1118 | 23.1584 | 23.1174 | 23.1443 | 23.2276 | 23.5106 | 23.7001 | 23.8556 | 23.8785 | 24.0187 | 24.0684 | 24.0683 | 24.0362 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293
65% | 403.1231 | 15.2803 | 16.9635 | 19.7973 | 19.7761 | 19.7569 | 20.064 | 20.515 | 20.8241 | 20.4484 | 20.4858 | 20.6648 | 21.3738 | 20.702 | 20.6625 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 65% | 529.43 | 16.6036 | 18.6752 | 21.5042 | 21.4662 | 21.4911 | 21.5685 | 21.8312 | 22.0073 | 22.1516 | 22.1729 | 22.3031 | 22.3492 | 22.3491 | 22.3193 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313
60% | 739.3112 | 14.1049 | 15.6586 | 18.2745 | 18.2548 | 18.2371 | 18.5206 | 18.9369 | 19.2222 | 18.8755 | 18.9099 | 19.0752 | 19.7296 | 19.1095 | 19.0731 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 60% | 918.9392 | 15.3264 | 17.2387 | 19.85 | 19.8149 | 19.838 | 19.9093 | 20.1519 | 20.3144 | 20.4476 | 20.4673 | 20.5875 | 20.6301 | 20.6299 | 20.6024 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966
55% | 1204.8314 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 55% | 1454.0417 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
50% | 1783.0446 | 11.7541 | 13.0488 | 15.2287 | 15.2123 | 15.1976 | 15.4339 | 15.7808 | 16.0185 | 15.7295 | 15.7583 | 15.896 | 16.4414 | 15.9246 | 15.8943 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 50% | 2105.2406 | 12.772 | 14.3656 | 16.5417 | 16.5125 | 16.5316 | 16.5911 | 16.7933 | 16.9287 | 17.0397 | 17.0561 | 17.1562 | 17.1917 | 17.1916 | 17.1687 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638
45% | 2370.3337 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 45% | 2758.3303 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
40% | 2864.2163 | 9.4033 | 10.4391 | 12.183 | 12.1699 | 12.1581 | 12.3471 | 12.6246 | 12.8148 | 12.5836 | 12.6066 | 12.7168 | 13.1531 | 12.7397 | 12.7154 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 40% | 3348.2666 | 10.2176 | 11.4925 | 13.2333 | 13.21 | 13.2253 | 13.2729 | 13.4346 | 13.5429 | 13.6318 | 13.6448 | 13.725 | 13.7534 | 13.7533 | 13.735 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311
35% | 3297.9707 | 8.2279 | 9.1342 | 10.6601 | 10.6486 | 10.6383 | 10.8037 | 11.0465 | 11.213 | 11.0107 | 11.0308 | 11.1272 | 11.509 | 11.1472 | 11.126 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 35% | 3816.434 | 8.9404 | 10.0559 | 11.5792 | 11.5587 | 11.5721 | 11.6138 | 11.7553 | 11.8501 | 11.9278 | 11.9392 | 12.0093 | 12.0342 | 12.0341 | 12.0181 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147
30% | 3579.7031 | 7.0524 | 7.8293 | 9.1372 | 9.1274 | 9.1186 | 9.2603 | 9.4685 | 9.6111 | 9.4377 | 9.455 | 9.5376 | 9.8648 | 9.5548 | 9.5366 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 30% | 4067.1569 | 7.6632 | 8.6193 | 9.925 | 9.9075 | 9.919 | 9.9547 | 10.076 | 10.1572 | 10.2238 | 10.2336 | 10.2937 | 10.315 | 10.315 | 10.3012 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983
25% | 3796.3913 | 5.877 | 6.5244 | 7.6144 | 7.6062 | 7.5988 | 7.7169 | 7.8904 | 8.0093 | 7.8648 | 7.8791 | 7.948 | 8.2207 | 7.9623 | 7.9471 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 25% | 4236.9526 | 6.386 | 7.1828 | 8.2708 | 8.2562 | 8.2658 | 8.2956 | 8.3966 | 8.4643 | 8.5199 | 8.528 | 8.5781 | 8.5959 | 8.5958 | 8.5843 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819
20% | 3975.6411 | 4.7016 | 5.2195 | 6.0915 | 6.0849 | 6.079 | 6.1735 | 6.3123 | 6.4074 | 6.2918 | 6.3033 | 6.3584 | 6.5765 | 6.3698 | 6.3577 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 20% | 4332.6282 | 5.1088 | 5.7462 | 6.6167 | 6.605 | 6.6127 | 6.6364 | 6.7173 | 6.7715 | 6.8159 | 6.8224 | 6.8625 | 6.8767 | 6.8766 | 6.8675 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655
15% | 4117.4527 | 3.5262 | 3.9146 | 4.5686 | 4.5637 | 4.5593 | 4.6302 | 4.7342 | 4.8056 | 4.7189 | 4.7275 | 4.7688 | 4.9324 | 4.7774 | 4.7683 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 15% | 4361.7469 | 3.8316 | 4.3097 | 4.9625 | 4.9537 | 4.9595 | 4.9773 | 5.038 | 5.0786 | 5.1119 | 5.1168 | 5.1469 | 5.1575 | 5.1575 | 5.1506 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491
10% | 4224.8514 | 2.3508 | 2.6098 | 3.0457 | 3.0425 | 3.0395 | 3.0868 | 3.1562 | 3.2037 | 3.1459 | 3.1517 | 3.1792 | 3.2883 | 3.1849 | 3.1789 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 10% | 4375.7389 | 2.5544 | 2.8731 | 3.3083 | 3.3025 | 3.3063 | 3.3182 | 3.3587 | 3.3857 | 3.4079 | 3.4112 | 3.4312 | 3.4383 | 3.4383 | 3.4337 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328
5% | 4310.3165 | 1.1754 | 1.3049 | 1.5229 | 1.5212 | 1.5198 | 1.5434 | 1.5781 | 1.6019 | 1.573 | 1.5758 | 1.5896 | 1.6441 | 1.5925 | 1.5894 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 5% | 4378.0079 | 1.2772 | 1.4366 | 1.6542 | 1.6512 | 1.6532 | 1.6591 | 1.6793 | 1.6929 | 1.704 | 1.7056 | 1.7156 | 1.7192 | 1.7192 | 1.7169 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164
9.992e-14% | 4382.5459 | 2.3489e-14 | 2.6077e-14 | 3.0433e-14 | 3.04e-14 | 3.0371e-14 | 3.0843e-14 | 3.1536e-14 | 3.2011e-14 | 3.1434e-14 | 3.1491e-14 | 3.1767e-14 | 3.2856e-14 | 3.1824e-14 | 3.1763e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 9.992e-14% | 4379.1424 | 2.5524e-14 | 2.8708e-14 | 3.3057e-14 | 3.2999e-14 | 3.3037e-14 | 3.3156e-14 | 3.356e-14 | 3.383e-14 | 3.4052e-14 | 3.4085e-14 | 3.4285e-14 | 3.4356e-14 | 3.4356e-14 | 3.431e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 17.3637 | 20.3053 | 24.2822 | 24.69 | 24.953 | 25.3146 | 26.1218 | 26.7615 | 27.3326 | 27.5386 | 27.7536 | 27.409 | 27.586 | 28.4238 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 28.057 | 100% | 0 | 19.5604 | 22.5119 | 26.5253 | 26.8988 | 27.1513 | 27.4014 | 28.3724 | 28.9357 | 29.5187 | 29.7924 | 29.9133 | 29.3976 | 29.6622 | 30.6835 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069 | 30.2069
99% | 0.2972 | 17.1901 | 20.1022 | 24.0394 | 24.4431 | 24.7035 | 25.0614 | 25.8606 | 26.4939 | 27.0593 | 27.2633 | 27.476 | 27.1349 | 27.3102 | 28.1395 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 27.7764 | 99% | 0.2972 | 19.3648 | 22.2867 | 26.2601 | 26.6298 | 26.8798 | 27.1274 | 28.0887 | 28.6463 | 29.2235 | 29.4945 | 29.6142 | 29.1036 | 29.3656 | 30.3767 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049 | 29.9049
98% | 0.8916 | 17.0164 | 19.8992 | 23.7966 | 24.1962 | 24.4539 | 24.8083 | 25.5993 | 26.2262 | 26.786 | 26.9879 | 27.1985 | 26.8608 | 27.0343 | 27.8553 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 27.4959 | 98% | 0.8916 | 19.1692 | 22.0616 | 25.9948 | 26.3608 | 26.6083 | 26.8533 | 27.805 | 28.357 | 28.9283 | 29.1966 | 29.3151 | 28.8096 | 29.069 | 30.0698 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028 | 29.6028
97% | 1.7832 | 16.8428 | 19.6961 | 23.5537 | 23.9493 | 24.2044 | 24.5551 | 25.3381 | 25.9586 | 26.5126 | 26.7125 | 26.921 | 26.5867 | 26.7584 | 27.5711 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 27.2153 | 97% | 2.0804 | 18.9736 | 21.8365 | 25.7295 | 26.0918 | 26.3368 | 26.5793 | 27.5212 | 28.0676 | 28.6331 | 28.8987 | 29.0159 | 28.5157 | 28.7724 | 29.763 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007 | 29.3007
95% | 4.458 | 16.4955 | 19.29 | 23.0681 | 23.4555 | 23.7053 | 24.0488 | 24.8157 | 25.4234 | 25.966 | 26.1617 | 26.3659 | 26.0385 | 26.2067 | 27.0026 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 26.6541 | 95% | 4.1608 | 18.5824 | 21.3863 | 25.199 | 25.5539 | 25.7938 | 26.0313 | 26.9538 | 27.4889 | 28.0427 | 28.3028 | 28.4177 | 27.9277 | 28.1791 | 29.1493 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966 | 28.6966
90% | 15.1571 | 15.6273 | 18.2748 | 21.854 | 22.221 | 22.4577 | 22.7831 | 23.5096 | 24.0853 | 24.5994 | 24.7848 | 24.9782 | 24.6681 | 24.8274 | 25.5814 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 25.2513 | 90% | 11.5907 | 17.6044 | 20.2607 | 23.8728 | 24.2089 | 24.4362 | 24.6612 | 25.5352 | 26.0421 | 26.5668 | 26.8132 | 26.922 | 26.4578 | 26.696 | 27.6152 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863 | 27.1863
85% | 39.5274 | 14.7592 | 17.2595 | 20.6399 | 20.9865 | 21.21 | 21.5174 | 22.2035 | 22.7472 | 23.2327 | 23.4078 | 23.5905 | 23.2976 | 23.4481 | 24.1602 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 23.8484 | 85% | 32.6918 | 16.6264 | 19.1351 | 22.5465 | 22.864 | 23.0786 | 23.2912 | 24.1165 | 24.5953 | 25.0909 | 25.3236 | 25.4263 | 24.988 | 25.2129 | 26.081 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759 | 25.6759
80% | 110.5579 | 13.891 | 16.2442 | 19.4258 | 19.752 | 19.9624 | 20.2517 | 20.8974 | 21.4092 | 21.8661 | 22.0309 | 22.2029 | 21.9272 | 22.0688 | 22.739 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 22.4456 | 80% | 84.1072 | 15.6483 | 18.0095 | 21.2202 | 21.519 | 21.7211 | 21.9211 | 22.6979 | 23.1485 | 23.6149 | 23.8339 | 23.9307 | 23.5181 | 23.7298 | 24.5468 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656 | 24.1656
75% | 244.2972 | 13.0228 | 15.229 | 18.2117 | 18.5175 | 18.7147 | 18.9859 | 19.5913 | 20.0711 | 20.4995 | 20.654 | 20.8152 | 20.5567 | 20.6895 | 21.3178 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 21.0427 | 75% | 202.095 | 14.6703 | 16.8839 | 19.894 | 20.1741 | 20.3635 | 20.551 | 21.2793 | 21.7018 | 22.139 | 22.3443 | 22.435 | 22.0482 | 22.2467 | 23.0126 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552 | 22.6552
70% | 444.0146 | 12.1546 | 14.2137 | 16.9975 | 17.283 | 17.4671 | 17.7202 | 18.2852 | 18.733 | 19.1328 | 19.2771 | 19.4275 | 19.1863 | 19.3102 | 19.8966 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 19.6399 | 70% | 388.1413 | 13.6923 | 15.7583 | 18.5677 | 18.8292 | 19.0059 | 19.181 | 19.8607 | 20.255 | 20.6631 | 20.8547 | 20.9393 | 20.5783 | 20.7636 | 21.4785 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449 | 21.1449
65% | 770.3386 | 11.2864 | 13.1984 | 15.7834 | 16.0485 | 16.2194 | 16.4545 | 16.9792 | 17.395 | 17.7662 | 17.9001 | 18.0398 | 17.8158 | 17.9309 | 18.4755 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 18.237 | 65% | 669.8855 | 12.7143 | 14.6327 | 17.2414 | 17.4842 | 17.6484 | 17.8109 | 18.4421 | 18.8082 | 19.1871 | 19.3651 | 19.4437 | 19.1084 | 19.2805 | 19.9443 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345 | 19.6345
60% | 1209.3009 | 10.4182 | 12.1832 | 14.5693 | 14.814 | 14.9718 | 15.1887 | 15.6731 | 16.0569 | 16.3996 | 16.5232 | 16.6521 | 16.4454 | 16.5516 | 17.0543 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 16.8342 | 60% | 1104.687 | 11.7363 | 13.5071 | 15.9152 | 16.1393 | 16.2908 | 16.4408 | 17.0234 | 17.3614 | 17.7112 | 17.8755 | 17.948 | 17.6386 | 17.7973 | 18.4101 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242 | 18.1242
55% | 1757.6322 | 9.55 | 11.1679 | 13.3552 | 13.5795 | 13.7241 | 13.923 | 14.367 | 14.7188 | 15.0329 | 15.1463 | 15.2645 | 15.0749 | 15.1723 | 15.6331 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 15.4313 | 55% | 1631.62 | 10.7582 | 12.3815 | 14.5889 | 14.7943 | 14.9332 | 15.0708 | 15.6048 | 15.9146 | 16.2353 | 16.3858 | 16.4523 | 16.1687 | 16.3142 | 16.8759 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138
50% | 2378.4799 | 8.6819 | 10.1526 | 12.1411 | 12.345 | 12.4765 | 12.6573 | 13.0609 | 13.3807 | 13.6663 | 13.7693 | 13.8768 | 13.7045 | 13.793 | 14.2119 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 14.0285 | 50% | 2253.9537 | 9.7802 | 11.2559 | 13.2627 | 13.4494 | 13.5757 | 13.7007 | 14.1862 | 14.4678 | 14.7593 | 14.8962 | 14.9567 | 14.6988 | 14.8311 | 15.3418 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035 | 15.1035
45% | 3003.7856 | 7.8137 | 9.1374 | 10.927 | 11.1105 | 11.2288 | 11.3916 | 11.7548 | 12.0427 | 12.2997 | 12.3924 | 12.4891 | 12.334 | 12.4137 | 12.7907 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 12.6256 | 45% | 2892.3362 | 8.8022 | 10.1303 | 11.9364 | 12.1045 | 12.2181 | 12.3306 | 12.7676 | 13.0211 | 13.2834 | 13.4066 | 13.461 | 13.2289 | 13.348 | 13.8076 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931 | 13.5931
40% | 3548.2533 | 6.9455 | 8.1221 | 9.7129 | 9.876 | 9.9812 | 10.1258 | 10.4487 | 10.7046 | 10.933 | 11.0155 | 11.1014 | 10.9636 | 11.0344 | 11.3695 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 11.2228 | 40% | 3473.3593 | 7.8242 | 9.0047 | 10.6101 | 10.7595 | 10.8605 | 10.9605 | 11.349 | 11.5743 | 11.8075 | 11.917 | 11.9653 | 11.759 | 11.8649 | 12.2734 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828 | 12.0828
35% | 3927.7759 | 6.0773 | 7.1069 | 8.4988 | 8.6415 | 8.7335 | 8.8601 | 9.1426 | 9.3665 | 9.5664 | 9.6385 | 9.7137 | 9.5931 | 9.6551 | 9.9483 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 9.8199 | 35% | 3882.8989 | 6.8462 | 7.8792 | 9.2839 | 9.4146 | 9.503 | 9.5905 | 9.9303 | 10.1275 | 10.3315 | 10.4274 | 10.4697 | 10.2892 | 10.3818 | 10.7392 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724 | 10.5724
30% | 4135.8149 | 5.2091 | 6.0916 | 7.2847 | 7.407 | 7.4859 | 7.5944 | 7.8365 | 8.0284 | 8.1998 | 8.2616 | 8.3261 | 8.2227 | 8.2758 | 8.5271 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 8.4171 | 30% | 4127.1961 | 5.8681 | 6.7536 | 7.9576 | 8.0696 | 8.1454 | 8.2204 | 8.5117 | 8.6807 | 8.8556 | 8.9377 | 8.974 | 8.8193 | 8.8987 | 9.2051 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621 | 9.0621
25% | 4252.0195 | 4.3409 | 5.0763 | 6.0706 | 6.1725 | 6.2382 | 6.3286 | 6.5304 | 6.6904 | 6.8332 | 6.8847 | 6.9384 | 6.8522 | 6.8965 | 7.1059 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 7.0142 | 25% | 4245.1839 | 4.8901 | 5.628 | 6.6313 | 6.7247 | 6.7878 | 6.8503 | 7.0931 | 7.2339 | 7.3797 | 7.4481 | 7.4783 | 7.3494 | 7.4156 | 7.6709 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517 | 7.5517
20% | 4325.4275 | 3.4727 | 4.0611 | 4.8564 | 4.938 | 4.9906 | 5.0629 | 5.2244 | 5.3523 | 5.4665 | 5.5077 | 5.5507 | 5.4818 | 5.5172 | 5.6848 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 5.6114 | 20% | 4322.1583 | 3.9121 | 4.5024 | 5.3051 | 5.3798 | 5.4303 | 5.4803 | 5.6745 | 5.7871 | 5.9037 | 5.9585 | 5.9827 | 5.8795 | 5.9324 | 6.1367 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414 | 6.0414
15% | 4360.497 | 2.6046 | 3.0458 | 3.6423 | 3.7035 | 3.7429 | 3.7972 | 3.9183 | 4.0142 | 4.0999 | 4.1308 | 4.163 | 4.1113 | 4.1379 | 4.2636 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 4.2085 | 15% | 4354.2558 | 2.9341 | 3.3768 | 3.9788 | 4.0348 | 4.0727 | 4.1102 | 4.2559 | 4.3404 | 4.4278 | 4.4689 | 4.487 | 4.4096 | 4.4493 | 4.6025 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531 | 4.531
10% | 4373.8709 | 1.7364 | 2.0305 | 2.4282 | 2.469 | 2.4953 | 2.5315 | 2.6122 | 2.6761 | 2.7333 | 2.7539 | 2.7754 | 2.7409 | 2.7586 | 2.8424 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 2.8057 | 10% | 4366.1437 | 1.956 | 2.2512 | 2.6525 | 2.6899 | 2.7151 | 2.7401 | 2.8372 | 2.8936 | 2.9519 | 2.9792 | 2.9913 | 2.9398 | 2.9662 | 3.0684 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207 | 3.0207
5% | 4381.8952 | 0.86819 | 1.0153 | 1.2141 | 1.2345 | 1.2476 | 1.2657 | 1.3061 | 1.3381 | 1.3666 | 1.3769 | 1.3877 | 1.3704 | 1.3793 | 1.4212 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 1.4028 | 5% | 4374.4653 | 0.97802 | 1.1256 | 1.3263 | 1.3449 | 1.3576 | 1.3701 | 1.4186 | 1.4468 | 1.4759 | 1.4896 | 1.4957 | 1.4699 | 1.4831 | 1.5342 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103 | 1.5103
9.992e-14% | 4391.7028 | 1.735e-14 | 2.0289e-14 | 2.4263e-14 | 2.467e-14 | 2.4933e-14 | 2.5294e-14 | 2.6101e-14 | 2.674e-14 | 2.7311e-14 | 2.7517e-14 | 2.7731e-14 | 2.7387e-14 | 2.7564e-14 | 2.8401e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 2.8035e-14 | 9.992e-14% | 4375.9513 | 1.9545e-14 | 2.2494e-14 | 2.6504e-14 | 2.6877e-14 | 2.713e-14 | 2.7379e-14 | 2.835e-14 | 2.8913e-14 | 2.9495e-14 | 2.9769e-14 | 2.9889e-14 | 2.9374e-14 | 2.9639e-14 | 3.0659e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14 | 3.0183e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 20.298 | 22.487 | 26.2999 | 26.2745 | 26.2401 | 26.6977 | 27.3408 | 27.7822 | 27.1764 | 27.2297 | 27.48 | 28.5618 | 27.5283 | 27.4734 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 27.4094 | 100% | 0 | 22.3339 | 25.1205 | 28.9258 | 28.8747 | 28.9082 | 29.0122 | 29.3657 | 29.6025 | 29.7967 | 29.8253 | 30.0004 | 30.0625 | 30.0623 | 30.0222 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137 | 30.0137
99% | 0.37816 | 20.0951 | 22.2621 | 26.0369 | 26.0117 | 25.9777 | 26.4308 | 27.0674 | 27.5044 | 26.9046 | 26.9574 | 27.2052 | 28.2762 | 27.253 | 27.1986 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 27.1353 | 99% | 1.1345 | 22.1106 | 24.8693 | 28.6365 | 28.5859 | 28.6191 | 28.7221 | 29.0721 | 29.3065 | 29.4987 | 29.527 | 29.7004 | 29.7618 | 29.7617 | 29.722 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136 | 29.7136
98% | 0.37816 | 19.8921 | 22.0373 | 25.7739 | 25.749 | 25.7153 | 26.1638 | 26.794 | 27.2266 | 26.6328 | 26.6851 | 26.9304 | 27.9906 | 26.9778 | 26.9239 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 26.8613 | 98% | 1.8908 | 21.8872 | 24.6181 | 28.3473 | 28.2972 | 28.3301 | 28.432 | 28.7784 | 29.0104 | 29.2007 | 29.2288 | 29.4004 | 29.4612 | 29.4611 | 29.4218 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134 | 29.4134
97% | 0.75633 | 19.6891 | 21.8124 | 25.5109 | 25.4862 | 25.4529 | 25.8968 | 26.5205 | 26.9487 | 26.3611 | 26.4128 | 26.6556 | 27.7049 | 26.7025 | 26.6492 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 26.5872 | 97% | 2.269 | 21.6639 | 24.3669 | 28.058 | 28.0084 | 28.041 | 28.1419 | 28.4848 | 28.7144 | 28.9028 | 28.9305 | 29.1004 | 29.1606 | 29.1604 | 29.1216 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133 | 29.1133
95% | 0.75633 | 19.2831 | 21.3626 | 24.9849 | 24.9607 | 24.9281 | 25.3629 | 25.9737 | 26.3931 | 25.8175 | 25.8682 | 26.106 | 27.1337 | 26.1519 | 26.0997 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 26.039 | 95% | 4.1598 | 21.2172 | 23.8645 | 27.4795 | 27.431 | 27.4628 | 27.5616 | 27.8974 | 28.1224 | 28.3068 | 28.334 | 28.5004 | 28.5593 | 28.5592 | 28.5211 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513 | 28.513
90% | 3.7816 | 18.2682 | 20.2383 | 23.6699 | 23.647 | 23.6161 | 24.028 | 24.6067 | 25.004 | 24.4587 | 24.5067 | 24.732 | 25.7056 | 24.7755 | 24.726 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 24.6685 | 90% | 15.5047 | 20.1005 | 22.6085 | 26.0332 | 25.9872 | 26.0174 | 26.111 | 26.4292 | 26.6422 | 26.817 | 26.8427 | 27.0004 | 27.0562 | 27.0561 | 27.02 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123 | 27.0123
85% | 13.6139 | 17.2533 | 19.1139 | 22.3549 | 22.3333 | 22.3041 | 22.6931 | 23.2397 | 23.6149 | 23.0999 | 23.1453 | 23.358 | 24.2775 | 23.3991 | 23.3524 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 23.298 | 85% | 31.3876 | 18.9838 | 21.3524 | 24.5869 | 24.5435 | 24.572 | 24.6604 | 24.9609 | 25.1621 | 25.3272 | 25.3515 | 25.5003 | 25.5531 | 25.553 | 25.5189 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116 | 25.5116
80% | 35.1693 | 16.2384 | 17.9896 | 21.0399 | 21.0196 | 20.9921 | 21.3582 | 21.8726 | 22.2258 | 21.7411 | 21.7838 | 21.984 | 22.8494 | 22.0227 | 21.9787 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 21.9276 | 80% | 57.8591 | 17.8671 | 20.0964 | 23.1406 | 23.0997 | 23.1266 | 23.2098 | 23.4926 | 23.682 | 23.8373 | 23.8602 | 24.0003 | 24.05 | 24.0499 | 24.0178 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011 | 24.011
75% | 80.549 | 15.2235 | 16.8652 | 19.7249 | 19.7059 | 19.6801 | 20.0233 | 20.5056 | 20.8366 | 20.3823 | 20.4223 | 20.61 | 21.4213 | 20.6462 | 20.605 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 20.5571 | 75% | 121.3907 | 16.7504 | 18.8404 | 21.6943 | 21.656 | 21.6812 | 21.7592 | 22.0243 | 22.2019 | 22.3475 | 22.369 | 22.5003 | 22.5469 | 22.5467 | 22.5167 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103 | 22.5103
70% | 192.1075 | 14.2086 | 15.7409 | 18.4099 | 18.3921 | 18.3681 | 18.6884 | 19.1385 | 19.4475 | 19.0234 | 19.0608 | 19.236 | 19.9933 | 19.2698 | 19.2314 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 19.1866 | 70% | 273.4128 | 15.6337 | 17.5844 | 20.2481 | 20.2123 | 20.2358 | 20.3086 | 20.556 | 20.7217 | 20.8577 | 20.8777 | 21.0003 | 21.0437 | 21.0436 | 21.0156 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096 | 21.0096
65% | 403.1231 | 13.1937 | 14.6165 | 17.0949 | 17.0784 | 17.0561 | 17.3535 | 17.7715 | 18.0584 | 17.6646 | 17.6993 | 17.862 | 18.5652 | 17.8934 | 17.8577 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 17.8161 | 65% | 529.43 | 14.517 | 16.3283 | 18.8018 | 18.7685 | 18.7903 | 18.858 | 19.0877 | 19.2416 | 19.3678 | 19.3864 | 19.5003 | 19.5406 | 19.5405 | 19.5144 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089 | 19.5089
60% | 739.3112 | 12.1788 | 13.4922 | 15.7799 | 15.7647 | 15.7441 | 16.0186 | 16.4045 | 16.6693 | 16.3058 | 16.3378 | 16.488 | 17.1371 | 16.517 | 16.484 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 16.4457 | 60% | 918.9392 | 13.4003 | 15.0723 | 17.3555 | 17.3248 | 17.3449 | 17.4073 | 17.6194 | 17.7615 | 17.878 | 17.8952 | 18.0002 | 18.0375 | 18.0374 | 18.0133 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082 | 18.0082
55% | 1204.8314 | 11.1639 | 12.3678 | 14.4649 | 14.451 | 14.4321 | 14.6838 | 15.0374 | 15.2802 | 14.947 | 14.9763 | 15.114 | 15.709 | 15.1406 | 15.1104 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 15.0752 | 55% | 1454.0417 | 12.2836 | 13.8163 | 15.9092 | 15.8811 | 15.8995 | 15.9567 | 16.1511 | 16.2814 | 16.3882 | 16.4039 | 16.5002 | 16.5344 | 16.5343 | 16.5122 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075 | 16.5075
50% | 1783.0446 | 10.149 | 11.2435 | 13.1499 | 13.1372 | 13.1201 | 13.3489 | 13.6704 | 13.8911 | 13.5882 | 13.6149 | 13.74 | 14.2809 | 13.7642 | 13.7367 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 13.7047 | 50% | 2105.2406 | 11.167 | 12.5603 | 14.4629 | 14.4373 | 14.4541 | 14.5061 | 14.6829 | 14.8012 | 14.8983 | 14.9126 | 15.0002 | 15.0312 | 15.0312 | 15.0111 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068 | 15.0068
45% | 2370.3337 | 9.1341 | 10.1191 | 11.8349 | 11.8235 | 11.8081 | 12.014 | 12.3033 | 12.502 | 12.2294 | 12.2534 | 12.366 | 12.8528 | 12.3877 | 12.363 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 45% | 2758.3303 | 10.0503 | 11.3042 | 13.0166 | 12.9936 | 13.0087 | 13.0555 | 13.2146 | 13.3211 | 13.4085 | 13.4214 | 13.5002 | 13.5281 | 13.528 | 13.51 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062 | 13.5062
40% | 2864.2163 | 8.1192 | 8.9948 | 10.52 | 10.5098 | 10.4961 | 10.6791 | 10.9363 | 11.1129 | 10.8705 | 10.8919 | 10.992 | 11.4247 | 11.0113 | 10.9893 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 10.9638 | 40% | 3348.2666 | 8.9336 | 10.0482 | 11.5703 | 11.5499 | 11.5633 | 11.6049 | 11.7463 | 11.841 | 11.9187 | 11.9301 | 12.0002 | 12.025 | 12.0249 | 12.0089 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055 | 12.0055
35% | 3297.9707 | 7.1043 | 7.8704 | 9.205 | 9.1961 | 9.184 | 9.3442 | 9.5693 | 9.7238 | 9.5117 | 9.5304 | 9.618 | 9.9966 | 9.6349 | 9.6157 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 9.5933 | 35% | 3816.434 | 7.8169 | 8.7922 | 10.124 | 10.1061 | 10.1179 | 10.1543 | 10.278 | 10.3609 | 10.4288 | 10.4388 | 10.5001 | 10.5219 | 10.5218 | 10.5078 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048 | 10.5048
30% | 3579.7031 | 6.0894 | 6.7461 | 7.89 | 7.8823 | 7.872 | 8.0093 | 8.2022 | 8.3347 | 8.1529 | 8.1689 | 8.244 | 8.5685 | 8.2585 | 8.242 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 30% | 4067.1569 | 6.7002 | 7.5362 | 8.6777 | 8.6624 | 8.6725 | 8.7037 | 8.8097 | 8.8807 | 8.939 | 8.9476 | 9.0001 | 9.0187 | 9.0187 | 9.0067 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041 | 9.0041
25% | 3796.3913 | 5.0745 | 5.6217 | 6.575 | 6.5686 | 6.56 | 6.6744 | 6.8352 | 6.9455 | 6.7941 | 6.8074 | 6.87 | 7.1404 | 6.8821 | 6.8683 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 6.8524 | 25% | 4236.9526 | 5.5835 | 6.2801 | 7.2314 | 7.2187 | 7.2271 | 7.2531 | 7.3414 | 7.4006 | 7.4492 | 7.4563 | 7.5001 | 7.5156 | 7.5156 | 7.5056 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034 | 7.5034
20% | 3975.6411 | 4.0596 | 4.4974 | 5.26 | 5.2549 | 5.248 | 5.3395 | 5.4682 | 5.5564 | 5.4353 | 5.4459 | 5.496 | 5.7124 | 5.5057 | 5.4947 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 5.4819 | 20% | 4332.6282 | 4.4668 | 5.0241 | 5.7852 | 5.7749 | 5.7816 | 5.8024 | 5.8731 | 5.9205 | 5.9593 | 5.9651 | 6.0001 | 6.0125 | 6.0125 | 6.0044 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027 | 6.0027
15% | 4117.4527 | 3.0447 | 3.373 | 3.945 | 3.9412 | 3.936 | 4.0047 | 4.1011 | 4.1673 | 4.0765 | 4.0845 | 4.122 | 4.2843 | 4.1292 | 4.121 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 15% | 4361.7469 | 3.3501 | 3.7681 | 4.3389 | 4.3312 | 4.3362 | 4.3518 | 4.4049 | 4.4404 | 4.4695 | 4.4738 | 4.5001 | 4.5094 | 4.5093 | 4.5033 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021 | 4.5021
10% | 4224.8514 | 2.0298 | 2.2487 | 2.63 | 2.6274 | 2.624 | 2.6698 | 2.7341 | 2.7782 | 2.7176 | 2.723 | 2.748 | 2.8562 | 2.7528 | 2.7473 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 2.7409 | 10% | 4375.7389 | 2.2334 | 2.5121 | 2.8926 | 2.8875 | 2.8908 | 2.9012 | 2.9366 | 2.9602 | 2.9797 | 2.9825 | 3 | 3.0062 | 3.0062 | 3.0022 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014 | 3.0014
5% | 4310.3165 | 1.0149 | 1.1243 | 1.315 | 1.3137 | 1.312 | 1.3349 | 1.367 | 1.3891 | 1.3588 | 1.3615 | 1.374 | 1.4281 | 1.3764 | 1.3737 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 1.3705 | 5% | 4378.0079 | 1.1167 | 1.256 | 1.4463 | 1.4437 | 1.4454 | 1.4506 | 1.4683 | 1.4801 | 1.4898 | 1.4913 | 1.5 | 1.5031 | 1.5031 | 1.5011 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007 | 1.5007
9.992e-14% | 4382.5459 | 2.0282e-14 | 2.2469e-14 | 2.6279e-14 | 2.6253e-14 | 2.6219e-14 | 2.6676e-14 | 2.7319e-14 | 2.776e-14 | 2.7155e-14 | 2.7208e-14 | 2.7458e-14 | 2.8539e-14 | 2.7506e-14 | 2.7451e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 2.7388e-14 | 9.992e-14% | 4379.1424 | 2.2316e-14 | 2.51e-14 | 2.8903e-14 | 2.8852e-14 | 2.8885e-14 | 2.8989e-14 | 2.9342e-14 | 2.9579e-14 | 2.9773e-14 | 2.9801e-14 | 2.9976e-14 | 3.0038e-14 | 3.0038e-14 | 2.9998e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14 | 2.999e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 100% | 0 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
99% | 0.2972 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 99% | 0.2972 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
98% | 0.8916 | 20.1623 | 23.4376 | 27.871 | 28.2634 | 28.5259 | 28.8949 | 29.7357 | 30.396 | 30.983 | 31.189 | 31.4243 | 31.0953 | 31.2688 | 32.0842 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 98% | 0.8916 | 22.3151 | 25.6 | 30.0692 | 30.428 | 30.6802 | 30.9399 | 31.9413 | 32.5267 | 33.1254 | 33.3977 | 33.5408 | 33.0442 | 33.3035 | 34.2987 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305
97% | 1.7832 | 19.9566 | 23.1984 | 27.5866 | 27.975 | 28.2348 | 28.6 | 29.4323 | 30.0858 | 30.6669 | 30.8707 | 31.1036 | 30.778 | 30.9497 | 31.7568 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 97% | 2.0804 | 22.0874 | 25.3388 | 29.7624 | 30.1176 | 30.3672 | 30.6242 | 31.6154 | 32.1948 | 32.7874 | 33.0569 | 33.1986 | 32.707 | 32.9637 | 33.9487 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853
95% | 4.458 | 19.5451 | 22.7201 | 27.0178 | 27.3982 | 27.6526 | 28.0103 | 28.8254 | 29.4655 | 30.0346 | 30.2342 | 30.4623 | 30.1434 | 30.3116 | 31.102 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 95% | 4.1608 | 21.632 | 24.8164 | 29.1487 | 29.4966 | 29.7411 | 29.9928 | 30.9635 | 31.531 | 32.1113 | 32.3753 | 32.5141 | 32.0326 | 32.284 | 33.2487 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948
90% | 15.1571 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 90% | 11.5907 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
85% | 39.5274 | 17.4877 | 20.3285 | 24.1738 | 24.5142 | 24.7418 | 25.0619 | 25.7912 | 26.3639 | 26.8731 | 27.0517 | 27.2558 | 26.9704 | 27.1209 | 27.8281 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 85% | 32.6918 | 19.355 | 22.2041 | 26.0804 | 26.3917 | 26.6104 | 26.8357 | 27.7042 | 28.2119 | 28.7312 | 28.9674 | 29.0915 | 28.6608 | 28.8857 | 29.7489 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427
80% | 110.5579 | 16.4591 | 19.1327 | 22.7518 | 23.0722 | 23.2864 | 23.5876 | 24.2741 | 24.813 | 25.2923 | 25.4604 | 25.6525 | 25.3839 | 25.5255 | 26.1912 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 80% | 84.1072 | 18.2164 | 20.898 | 24.5463 | 24.8392 | 25.0451 | 25.2571 | 26.0746 | 26.5524 | 27.0411 | 27.2634 | 27.3803 | 26.9748 | 27.1865 | 27.9989 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167
75% | 244.2972 | 15.4304 | 17.9369 | 21.3298 | 21.6302 | 21.831 | 22.1134 | 22.7569 | 23.2622 | 23.7115 | 23.8691 | 24.0492 | 23.7974 | 23.9302 | 24.5542 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 75% | 202.095 | 17.0779 | 19.5919 | 23.0122 | 23.2868 | 23.4798 | 23.6785 | 24.4449 | 24.8929 | 25.3511 | 25.5595 | 25.669 | 25.2889 | 25.4874 | 26.249 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907
70% | 444.0146 | 14.4017 | 16.7411 | 19.9078 | 20.1881 | 20.3756 | 20.6392 | 21.2398 | 21.7114 | 22.1307 | 22.2778 | 22.4459 | 22.2109 | 22.3349 | 22.9173 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 70% | 388.1413 | 15.9394 | 18.2857 | 21.478 | 21.7343 | 21.9145 | 22.1 | 22.8152 | 23.2334 | 23.661 | 23.8555 | 23.9577 | 23.603 | 23.7882 | 24.4991 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646
65% | 770.3386 | 13.373 | 15.5453 | 18.4859 | 18.7461 | 18.9202 | 19.165 | 19.7227 | 20.1606 | 20.55 | 20.6866 | 20.8426 | 20.6244 | 20.7395 | 21.2803 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 65% | 669.8855 | 14.8008 | 16.9796 | 19.9439 | 20.1819 | 20.3491 | 20.5214 | 21.1856 | 21.5738 | 21.9709 | 22.1515 | 22.2465 | 21.917 | 22.0891 | 22.7491 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386
60% | 1209.3009 | 12.3443 | 14.3496 | 17.0639 | 17.3041 | 17.4648 | 17.6907 | 18.2055 | 18.6098 | 18.9692 | 19.0953 | 19.2394 | 19.038 | 19.1442 | 19.6434 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 60% | 1104.687 | 13.6623 | 15.6735 | 18.4097 | 18.6294 | 18.7838 | 18.9428 | 19.5559 | 19.9143 | 20.2808 | 20.4476 | 20.5352 | 20.2311 | 20.3899 | 20.9992 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125
55% | 1757.6322 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 55% | 1631.62 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
50% | 2378.4799 | 10.2869 | 11.958 | 14.2199 | 14.4201 | 14.554 | 14.7423 | 15.1713 | 15.5081 | 15.8077 | 15.9127 | 16.0328 | 15.865 | 15.9535 | 16.3695 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 50% | 2253.9537 | 11.3853 | 13.0612 | 15.3414 | 15.5245 | 15.6532 | 15.7857 | 16.2966 | 16.5953 | 16.9007 | 17.0396 | 17.1127 | 16.8593 | 16.9916 | 17.4993 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604
45% | 3003.7856 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 45% | 2892.3362 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
40% | 3548.2533 | 8.2295 | 9.5664 | 11.3759 | 11.5361 | 11.6432 | 11.7938 | 12.137 | 12.4065 | 12.6461 | 12.7302 | 12.8262 | 12.692 | 12.7628 | 13.0956 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 40% | 3473.3593 | 9.1082 | 10.449 | 12.2731 | 12.4196 | 12.5226 | 12.6285 | 13.0373 | 13.2762 | 13.5206 | 13.6317 | 13.6901 | 13.4874 | 13.5933 | 13.9995 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084
35% | 3927.7759 | 7.2008 | 8.3706 | 9.9539 | 10.0941 | 10.1878 | 10.3196 | 10.6199 | 10.8557 | 11.0654 | 11.1389 | 11.223 | 11.1055 | 11.1674 | 11.4586 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 35% | 3882.8989 | 7.9697 | 9.1429 | 10.739 | 10.8672 | 10.9572 | 11.05 | 11.4076 | 11.6167 | 11.8305 | 11.9278 | 11.9789 | 11.8015 | 11.8941 | 12.2495 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823
30% | 4135.8149 | 6.1721 | 7.1748 | 8.5319 | 8.6521 | 8.7324 | 8.8454 | 9.1028 | 9.3049 | 9.4846 | 9.5476 | 9.6197 | 9.519 | 9.5721 | 9.8217 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 30% | 4127.1961 | 6.8312 | 7.8367 | 9.2049 | 9.3147 | 9.3919 | 9.4714 | 9.778 | 9.9572 | 10.1404 | 10.2238 | 10.2676 | 10.1156 | 10.1949 | 10.4996 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563
25% | 4252.0195 | 5.1435 | 5.979 | 7.1099 | 7.2101 | 7.277 | 7.3711 | 7.5856 | 7.7541 | 7.9038 | 7.9564 | 8.0164 | 7.9325 | 7.9767 | 8.1847 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 25% | 4245.1839 | 5.6926 | 6.5306 | 7.6707 | 7.7623 | 7.8266 | 7.8928 | 8.1483 | 8.2976 | 8.4504 | 8.5198 | 8.5563 | 8.4296 | 8.4958 | 8.7497 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302
20% | 4325.4275 | 4.1148 | 4.7832 | 5.688 | 5.768 | 5.8216 | 5.8969 | 6.0685 | 6.2033 | 6.3231 | 6.3651 | 6.4131 | 6.346 | 6.3814 | 6.5478 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 20% | 4322.1583 | 4.5541 | 5.2245 | 6.1366 | 6.2098 | 6.2613 | 6.3143 | 6.5186 | 6.6381 | 6.7603 | 6.8159 | 6.8451 | 6.7437 | 6.7966 | 6.9997 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042
15% | 4360.497 | 3.0861 | 3.5874 | 4.266 | 4.326 | 4.3662 | 4.4227 | 4.5514 | 4.6524 | 4.7423 | 4.7738 | 4.8098 | 4.7595 | 4.786 | 4.9108 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 15% | 4354.2558 | 3.4156 | 3.9184 | 4.6024 | 4.6574 | 4.696 | 4.7357 | 4.889 | 4.9786 | 5.0702 | 5.1119 | 5.1338 | 5.0578 | 5.0975 | 5.2498 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781
10% | 4373.8709 | 2.0574 | 2.3916 | 2.844 | 2.884 | 2.9108 | 2.9485 | 3.0343 | 3.1016 | 3.1615 | 3.1825 | 3.2066 | 3.173 | 3.1907 | 3.2739 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 10% | 4366.1437 | 2.2771 | 2.6122 | 3.0683 | 3.1049 | 3.1306 | 3.1571 | 3.2593 | 3.3191 | 3.3801 | 3.4079 | 3.4225 | 3.3719 | 3.3983 | 3.4999 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521
5% | 4381.8952 | 1.0287 | 1.1958 | 1.422 | 1.442 | 1.4554 | 1.4742 | 1.5171 | 1.5508 | 1.5808 | 1.5913 | 1.6033 | 1.5865 | 1.5953 | 1.6369 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 5% | 4374.4653 | 1.1385 | 1.3061 | 1.5341 | 1.5525 | 1.5653 | 1.5786 | 1.6297 | 1.6595 | 1.6901 | 1.704 | 1.7113 | 1.6859 | 1.6992 | 1.7499 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726
9.992e-14% | 4391.7028 | 2.0557e-14 | 2.3897e-14 | 2.8417e-14 | 2.8817e-14 | 2.9085e-14 | 2.9461e-14 | 3.0318e-14 | 3.0992e-14 | 3.159e-14 | 3.18e-14 | 3.204e-14 | 3.1705e-14 | 3.1881e-14 | 3.2713e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 9.992e-14% | 4375.9513 | 2.2752e-14 | 2.6102e-14 | 3.0658e-14 | 3.1024e-14 | 3.1281e-14 | 3.1546e-14 | 3.2567e-14 | 3.3164e-14 | 3.3774e-14 | 3.4052e-14 | 3.4198e-14 | 3.3692e-14 | 3.3956e-14 | 3.4971e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 100% | 0 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
99% | 0.37816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 99% | 1.1345 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
98% | 0.37816 | 23.038 | 25.5757 | 29.8483 | 29.8162 | 29.7873 | 30.2504 | 30.9303 | 31.3963 | 30.8299 | 30.8862 | 31.1562 | 32.2251 | 31.2123 | 31.1528 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 98% | 1.8908 | 25.0331 | 28.1565 | 32.4217 | 32.3644 | 32.402 | 32.5186 | 32.9148 | 33.1802 | 33.3978 | 33.4299 | 33.6262 | 33.6957 | 33.6956 | 33.6506 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411
97% | 0.75633 | 22.8029 | 25.3147 | 29.5437 | 29.512 | 29.4833 | 29.9417 | 30.6147 | 31.0759 | 30.5153 | 30.5711 | 30.8382 | 31.8963 | 30.8938 | 30.8349 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 97% | 2.269 | 24.7777 | 27.8692 | 32.0909 | 32.0342 | 32.0714 | 32.1868 | 32.5789 | 32.8416 | 33.057 | 33.0888 | 33.2831 | 33.3519 | 33.3517 | 33.3073 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978
95% | 0.75633 | 22.3327 | 24.7927 | 28.9346 | 28.9035 | 28.8754 | 29.3244 | 29.9835 | 30.4352 | 29.8861 | 29.9407 | 30.2024 | 31.2386 | 30.2568 | 30.1991 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 95% | 4.1598 | 24.2668 | 27.2946 | 31.4292 | 31.3737 | 31.4101 | 31.5231 | 31.9072 | 32.1644 | 32.3754 | 32.4065 | 32.5968 | 32.6642 | 32.6641 | 32.6205 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112
90% | 3.7816 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 90% | 15.5047 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
85% | 13.6139 | 19.9819 | 22.183 | 25.8888 | 25.861 | 25.8359 | 26.2376 | 26.8273 | 27.2315 | 26.7402 | 26.7891 | 27.0232 | 27.9503 | 27.0719 | 27.0202 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 85% | 31.3876 | 21.7124 | 24.4215 | 28.1209 | 28.0712 | 28.1038 | 28.2049 | 28.5485 | 28.7787 | 28.9675 | 28.9953 | 29.1656 | 29.2259 | 29.2258 | 29.1868 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785
80% | 35.1693 | 18.8065 | 20.8781 | 24.366 | 24.3398 | 24.3161 | 24.6942 | 25.2493 | 25.6296 | 25.1673 | 25.2132 | 25.4336 | 26.3062 | 25.4794 | 25.4308 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 80% | 57.8591 | 20.4352 | 22.9849 | 26.4667 | 26.4199 | 26.4506 | 26.5458 | 26.8692 | 27.0858 | 27.2635 | 27.2897 | 27.4499 | 27.5067 | 27.5066 | 27.4699 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621
75% | 80.549 | 17.6311 | 19.5732 | 22.8431 | 22.8185 | 22.7964 | 23.1508 | 23.6712 | 24.0278 | 23.5943 | 23.6374 | 23.844 | 24.6621 | 23.8869 | 23.8414 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 75% | 121.3907 | 19.158 | 21.5484 | 24.8125 | 24.7687 | 24.7974 | 24.8867 | 25.1899 | 25.393 | 25.5596 | 25.5841 | 25.7343 | 25.7876 | 25.7874 | 25.753 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457
70% | 192.1075 | 16.4557 | 18.2683 | 21.3202 | 21.2973 | 21.2766 | 21.6074 | 22.0931 | 22.4259 | 22.0214 | 22.0616 | 22.2544 | 23.0179 | 22.2945 | 22.252 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 70% | 273.4128 | 17.8808 | 20.1118 | 23.1584 | 23.1174 | 23.1443 | 23.2276 | 23.5106 | 23.7001 | 23.8556 | 23.8785 | 24.0187 | 24.0684 | 24.0683 | 24.0362 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293
65% | 403.1231 | 15.2803 | 16.9635 | 19.7973 | 19.7761 | 19.7569 | 20.064 | 20.515 | 20.8241 | 20.4484 | 20.4858 | 20.6648 | 21.3738 | 20.702 | 20.6625 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 65% | 529.43 | 16.6036 | 18.6752 | 21.5042 | 21.4662 | 21.4911 | 21.5685 | 21.8312 | 22.0073 | 22.1516 | 22.1729 | 22.3031 | 22.3492 | 22.3491 | 22.3193 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313
60% | 739.3112 | 14.1049 | 15.6586 | 18.2745 | 18.2548 | 18.2371 | 18.5206 | 18.9369 | 19.2222 | 18.8755 | 18.9099 | 19.0752 | 19.7296 | 19.1095 | 19.0731 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 60% | 918.9392 | 15.3264 | 17.2387 | 19.85 | 19.8149 | 19.838 | 19.9093 | 20.1519 | 20.3144 | 20.4476 | 20.4673 | 20.5875 | 20.6301 | 20.6299 | 20.6024 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966
55% | 1204.8314 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 55% | 1454.0417 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
50% | 1783.0446 | 11.7541 | 13.0488 | 15.2287 | 15.2123 | 15.1976 | 15.4339 | 15.7808 | 16.0185 | 15.7295 | 15.7583 | 15.896 | 16.4414 | 15.9246 | 15.8943 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 50% | 2105.2406 | 12.772 | 14.3656 | 16.5417 | 16.5125 | 16.5316 | 16.5911 | 16.7933 | 16.9287 | 17.0397 | 17.0561 | 17.1562 | 17.1917 | 17.1916 | 17.1687 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638
45% | 2370.3337 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 45% | 2758.3303 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
40% | 2864.2163 | 9.4033 | 10.4391 | 12.183 | 12.1699 | 12.1581 | 12.3471 | 12.6246 | 12.8148 | 12.5836 | 12.6066 | 12.7168 | 13.1531 | 12.7397 | 12.7154 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 40% | 3348.2666 | 10.2176 | 11.4925 | 13.2333 | 13.21 | 13.2253 | 13.2729 | 13.4346 | 13.5429 | 13.6318 | 13.6448 | 13.725 | 13.7534 | 13.7533 | 13.735 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311
35% | 3297.9707 | 8.2279 | 9.1342 | 10.6601 | 10.6486 | 10.6383 | 10.8037 | 11.0465 | 11.213 | 11.0107 | 11.0308 | 11.1272 | 11.509 | 11.1472 | 11.126 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 35% | 3816.434 | 8.9404 | 10.0559 | 11.5792 | 11.5587 | 11.5721 | 11.6138 | 11.7553 | 11.8501 | 11.9278 | 11.9392 | 12.0093 | 12.0342 | 12.0341 | 12.0181 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147
30% | 3579.7031 | 7.0524 | 7.8293 | 9.1372 | 9.1274 | 9.1186 | 9.2603 | 9.4685 | 9.6111 | 9.4377 | 9.455 | 9.5376 | 9.8648 | 9.5548 | 9.5366 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 30% | 4067.1569 | 7.6632 | 8.6193 | 9.925 | 9.9075 | 9.919 | 9.9547 | 10.076 | 10.1572 | 10.2238 | 10.2336 | 10.2937 | 10.315 | 10.315 | 10.3012 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983
25% | 3796.3913 | 5.877 | 6.5244 | 7.6144 | 7.6062 | 7.5988 | 7.7169 | 7.8904 | 8.0093 | 7.8648 | 7.8791 | 7.948 | 8.2207 | 7.9623 | 7.9471 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 25% | 4236.9526 | 6.386 | 7.1828 | 8.2708 | 8.2562 | 8.2658 | 8.2956 | 8.3966 | 8.4643 | 8.5199 | 8.528 | 8.5781 | 8.5959 | 8.5958 | 8.5843 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819
20% | 3975.6411 | 4.7016 | 5.2195 | 6.0915 | 6.0849 | 6.079 | 6.1735 | 6.3123 | 6.4074 | 6.2918 | 6.3033 | 6.3584 | 6.5765 | 6.3698 | 6.3577 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 20% | 4332.6282 | 5.1088 | 5.7462 | 6.6167 | 6.605 | 6.6127 | 6.6364 | 6.7173 | 6.7715 | 6.8159 | 6.8224 | 6.8625 | 6.8767 | 6.8766 | 6.8675 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655
15% | 4117.4527 | 3.5262 | 3.9146 | 4.5686 | 4.5637 | 4.5593 | 4.6302 | 4.7342 | 4.8056 | 4.7189 | 4.7275 | 4.7688 | 4.9324 | 4.7774 | 4.7683 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 15% | 4361.7469 | 3.8316 | 4.3097 | 4.9625 | 4.9537 | 4.9595 | 4.9773 | 5.038 | 5.0786 | 5.1119 | 5.1168 | 5.1469 | 5.1575 | 5.1575 | 5.1506 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491
10% | 4224.8514 | 2.3508 | 2.6098 | 3.0457 | 3.0425 | 3.0395 | 3.0868 | 3.1562 | 3.2037 | 3.1459 | 3.1517 | 3.1792 | 3.2883 | 3.1849 | 3.1789 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 10% | 4375.7389 | 2.5544 | 2.8731 | 3.3083 | 3.3025 | 3.3063 | 3.3182 | 3.3587 | 3.3857 | 3.4079 | 3.4112 | 3.4312 | 3.4383 | 3.4383 | 3.4337 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328
5% | 4310.3165 | 1.1754 | 1.3049 | 1.5229 | 1.5212 | 1.5198 | 1.5434 | 1.5781 | 1.6019 | 1.573 | 1.5758 | 1.5896 | 1.6441 | 1.5925 | 1.5894 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 5% | 4378.0079 | 1.2772 | 1.4366 | 1.6542 | 1.6512 | 1.6532 | 1.6591 | 1.6793 | 1.6929 | 1.704 | 1.7056 | 1.7156 | 1.7192 | 1.7192 | 1.7169 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164
9.992e-14% | 4382.5459 | 2.3489e-14 | 2.6077e-14 | 3.0433e-14 | 3.04e-14 | 3.0371e-14 | 3.0843e-14 | 3.1536e-14 | 3.2011e-14 | 3.1434e-14 | 3.1491e-14 | 3.1767e-14 | 3.2856e-14 | 3.1824e-14 | 3.1763e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 9.992e-14% | 4379.1424 | 2.5524e-14 | 2.8708e-14 | 3.3057e-14 | 3.2999e-14 | 3.3037e-14 | 3.3156e-14 | 3.356e-14 | 3.383e-14 | 3.4052e-14 | 3.4085e-14 | 3.4285e-14 | 3.4356e-14 | 3.4356e-14 | 3.431e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 32.3709 | 100% | 0 | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209 | 34.5209
99% | 0.2972 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 99% | 0.2972 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
98% | 0.8916 | 20.1623 | 23.4376 | 27.871 | 28.2634 | 28.5259 | 28.8949 | 29.7357 | 30.396 | 30.983 | 31.189 | 31.4243 | 31.0953 | 31.2688 | 32.0842 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 31.7235 | 98% | 0.8916 | 22.3151 | 25.6 | 30.0692 | 30.428 | 30.6802 | 30.9399 | 31.9413 | 32.5267 | 33.1254 | 33.3977 | 33.5408 | 33.0442 | 33.3035 | 34.2987 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305 | 33.8305
97% | 1.7832 | 19.9566 | 23.1984 | 27.5866 | 27.975 | 28.2348 | 28.6 | 29.4323 | 30.0858 | 30.6669 | 30.8707 | 31.1036 | 30.778 | 30.9497 | 31.7568 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 31.3998 | 97% | 2.0804 | 22.0874 | 25.3388 | 29.7624 | 30.1176 | 30.3672 | 30.6242 | 31.6154 | 32.1948 | 32.7874 | 33.0569 | 33.1986 | 32.707 | 32.9637 | 33.9487 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853 | 33.4853
95% | 4.458 | 19.5451 | 22.7201 | 27.0178 | 27.3982 | 27.6526 | 28.0103 | 28.8254 | 29.4655 | 30.0346 | 30.2342 | 30.4623 | 30.1434 | 30.3116 | 31.102 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 30.7524 | 95% | 4.1608 | 21.632 | 24.8164 | 29.1487 | 29.4966 | 29.7411 | 29.9928 | 30.9635 | 31.531 | 32.1113 | 32.3753 | 32.5141 | 32.0326 | 32.284 | 33.2487 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948 | 32.7948
90% | 15.1571 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 90% | 11.5907 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
85% | 39.5274 | 17.4877 | 20.3285 | 24.1738 | 24.5142 | 24.7418 | 25.0619 | 25.7912 | 26.3639 | 26.8731 | 27.0517 | 27.2558 | 26.9704 | 27.1209 | 27.8281 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 27.5153 | 85% | 32.6918 | 19.355 | 22.2041 | 26.0804 | 26.3917 | 26.6104 | 26.8357 | 27.7042 | 28.2119 | 28.7312 | 28.9674 | 29.0915 | 28.6608 | 28.8857 | 29.7489 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427 | 29.3427
80% | 110.5579 | 16.4591 | 19.1327 | 22.7518 | 23.0722 | 23.2864 | 23.5876 | 24.2741 | 24.813 | 25.2923 | 25.4604 | 25.6525 | 25.3839 | 25.5255 | 26.1912 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 25.8967 | 80% | 84.1072 | 18.2164 | 20.898 | 24.5463 | 24.8392 | 25.0451 | 25.2571 | 26.0746 | 26.5524 | 27.0411 | 27.2634 | 27.3803 | 26.9748 | 27.1865 | 27.9989 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167 | 27.6167
75% | 244.2972 | 15.4304 | 17.9369 | 21.3298 | 21.6302 | 21.831 | 22.1134 | 22.7569 | 23.2622 | 23.7115 | 23.8691 | 24.0492 | 23.7974 | 23.9302 | 24.5542 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 24.2782 | 75% | 202.095 | 17.0779 | 19.5919 | 23.0122 | 23.2868 | 23.4798 | 23.6785 | 24.4449 | 24.8929 | 25.3511 | 25.5595 | 25.669 | 25.2889 | 25.4874 | 26.249 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907 | 25.8907
70% | 444.0146 | 14.4017 | 16.7411 | 19.9078 | 20.1881 | 20.3756 | 20.6392 | 21.2398 | 21.7114 | 22.1307 | 22.2778 | 22.4459 | 22.2109 | 22.3349 | 22.9173 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 22.6597 | 70% | 388.1413 | 15.9394 | 18.2857 | 21.478 | 21.7343 | 21.9145 | 22.1 | 22.8152 | 23.2334 | 23.661 | 23.8555 | 23.9577 | 23.603 | 23.7882 | 24.4991 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646 | 24.1646
65% | 770.3386 | 13.373 | 15.5453 | 18.4859 | 18.7461 | 18.9202 | 19.165 | 19.7227 | 20.1606 | 20.55 | 20.6866 | 20.8426 | 20.6244 | 20.7395 | 21.2803 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 21.0411 | 65% | 669.8855 | 14.8008 | 16.9796 | 19.9439 | 20.1819 | 20.3491 | 20.5214 | 21.1856 | 21.5738 | 21.9709 | 22.1515 | 22.2465 | 21.917 | 22.0891 | 22.7491 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386 | 22.4386
60% | 1209.3009 | 12.3443 | 14.3496 | 17.0639 | 17.3041 | 17.4648 | 17.6907 | 18.2055 | 18.6098 | 18.9692 | 19.0953 | 19.2394 | 19.038 | 19.1442 | 19.6434 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 19.4226 | 60% | 1104.687 | 13.6623 | 15.6735 | 18.4097 | 18.6294 | 18.7838 | 18.9428 | 19.5559 | 19.9143 | 20.2808 | 20.4476 | 20.5352 | 20.2311 | 20.3899 | 20.9992 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125 | 20.7125
55% | 1757.6322 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 55% | 1631.62 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
50% | 2378.4799 | 10.2869 | 11.958 | 14.2199 | 14.4201 | 14.554 | 14.7423 | 15.1713 | 15.5081 | 15.8077 | 15.9127 | 16.0328 | 15.865 | 15.9535 | 16.3695 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 16.1855 | 50% | 2253.9537 | 11.3853 | 13.0612 | 15.3414 | 15.5245 | 15.6532 | 15.7857 | 16.2966 | 16.5953 | 16.9007 | 17.0396 | 17.1127 | 16.8593 | 16.9916 | 17.4993 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604 | 17.2604
45% | 3003.7856 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 45% | 2892.3362 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
40% | 3548.2533 | 8.2295 | 9.5664 | 11.3759 | 11.5361 | 11.6432 | 11.7938 | 12.137 | 12.4065 | 12.6461 | 12.7302 | 12.8262 | 12.692 | 12.7628 | 13.0956 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 12.9484 | 40% | 3473.3593 | 9.1082 | 10.449 | 12.2731 | 12.4196 | 12.5226 | 12.6285 | 13.0373 | 13.2762 | 13.5206 | 13.6317 | 13.6901 | 13.4874 | 13.5933 | 13.9995 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084 | 13.8084
35% | 3927.7759 | 7.2008 | 8.3706 | 9.9539 | 10.0941 | 10.1878 | 10.3196 | 10.6199 | 10.8557 | 11.0654 | 11.1389 | 11.223 | 11.1055 | 11.1674 | 11.4586 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 11.3298 | 35% | 3882.8989 | 7.9697 | 9.1429 | 10.739 | 10.8672 | 10.9572 | 11.05 | 11.4076 | 11.6167 | 11.8305 | 11.9278 | 11.9789 | 11.8015 | 11.8941 | 12.2495 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823 | 12.0823
30% | 4135.8149 | 6.1721 | 7.1748 | 8.5319 | 8.6521 | 8.7324 | 8.8454 | 9.1028 | 9.3049 | 9.4846 | 9.5476 | 9.6197 | 9.519 | 9.5721 | 9.8217 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 9.7113 | 30% | 4127.1961 | 6.8312 | 7.8367 | 9.2049 | 9.3147 | 9.3919 | 9.4714 | 9.778 | 9.9572 | 10.1404 | 10.2238 | 10.2676 | 10.1156 | 10.1949 | 10.4996 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563 | 10.3563
25% | 4252.0195 | 5.1435 | 5.979 | 7.1099 | 7.2101 | 7.277 | 7.3711 | 7.5856 | 7.7541 | 7.9038 | 7.9564 | 8.0164 | 7.9325 | 7.9767 | 8.1847 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 8.0927 | 25% | 4245.1839 | 5.6926 | 6.5306 | 7.6707 | 7.7623 | 7.8266 | 7.8928 | 8.1483 | 8.2976 | 8.4504 | 8.5198 | 8.5563 | 8.4296 | 8.4958 | 8.7497 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302 | 8.6302
20% | 4325.4275 | 4.1148 | 4.7832 | 5.688 | 5.768 | 5.8216 | 5.8969 | 6.0685 | 6.2033 | 6.3231 | 6.3651 | 6.4131 | 6.346 | 6.3814 | 6.5478 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 6.4742 | 20% | 4322.1583 | 4.5541 | 5.2245 | 6.1366 | 6.2098 | 6.2613 | 6.3143 | 6.5186 | 6.6381 | 6.7603 | 6.8159 | 6.8451 | 6.7437 | 6.7966 | 6.9997 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042 | 6.9042
15% | 4360.497 | 3.0861 | 3.5874 | 4.266 | 4.326 | 4.3662 | 4.4227 | 4.5514 | 4.6524 | 4.7423 | 4.7738 | 4.8098 | 4.7595 | 4.786 | 4.9108 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 4.8556 | 15% | 4354.2558 | 3.4156 | 3.9184 | 4.6024 | 4.6574 | 4.696 | 4.7357 | 4.889 | 4.9786 | 5.0702 | 5.1119 | 5.1338 | 5.0578 | 5.0975 | 5.2498 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781 | 5.1781
10% | 4373.8709 | 2.0574 | 2.3916 | 2.844 | 2.884 | 2.9108 | 2.9485 | 3.0343 | 3.1016 | 3.1615 | 3.1825 | 3.2066 | 3.173 | 3.1907 | 3.2739 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 3.2371 | 10% | 4366.1437 | 2.2771 | 2.6122 | 3.0683 | 3.1049 | 3.1306 | 3.1571 | 3.2593 | 3.3191 | 3.3801 | 3.4079 | 3.4225 | 3.3719 | 3.3983 | 3.4999 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521 | 3.4521
5% | 4381.8952 | 1.0287 | 1.1958 | 1.422 | 1.442 | 1.4554 | 1.4742 | 1.5171 | 1.5508 | 1.5808 | 1.5913 | 1.6033 | 1.5865 | 1.5953 | 1.6369 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 1.6185 | 5% | 4374.4653 | 1.1385 | 1.3061 | 1.5341 | 1.5525 | 1.5653 | 1.5786 | 1.6297 | 1.6595 | 1.6901 | 1.704 | 1.7113 | 1.6859 | 1.6992 | 1.7499 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726 | 1.726
9.992e-14% | 4391.7028 | 2.0557e-14 | 2.3897e-14 | 2.8417e-14 | 2.8817e-14 | 2.9085e-14 | 2.9461e-14 | 3.0318e-14 | 3.0992e-14 | 3.159e-14 | 3.18e-14 | 3.204e-14 | 3.1705e-14 | 3.1881e-14 | 3.2713e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 3.2345e-14 | 9.992e-14% | 4375.9513 | 2.2752e-14 | 2.6102e-14 | 3.0658e-14 | 3.1024e-14 | 3.1281e-14 | 3.1546e-14 | 3.2567e-14 | 3.3164e-14 | 3.3774e-14 | 3.4052e-14 | 3.4198e-14 | 3.3692e-14 | 3.3956e-14 | 3.4971e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14 | 3.4493e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 31.7234 | 100% | 0 | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276 | 34.3276
99% | 0.37816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 99% | 1.1345 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
98% | 0.37816 | 23.038 | 25.5757 | 29.8483 | 29.8162 | 29.7873 | 30.2504 | 30.9303 | 31.3963 | 30.8299 | 30.8862 | 31.1562 | 32.2251 | 31.2123 | 31.1528 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 31.0889 | 98% | 1.8908 | 25.0331 | 28.1565 | 32.4217 | 32.3644 | 32.402 | 32.5186 | 32.9148 | 33.1802 | 33.3978 | 33.4299 | 33.6262 | 33.6957 | 33.6956 | 33.6506 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411 | 33.6411
97% | 0.75633 | 22.8029 | 25.3147 | 29.5437 | 29.512 | 29.4833 | 29.9417 | 30.6147 | 31.0759 | 30.5153 | 30.5711 | 30.8382 | 31.8963 | 30.8938 | 30.8349 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 30.7717 | 97% | 2.269 | 24.7777 | 27.8692 | 32.0909 | 32.0342 | 32.0714 | 32.1868 | 32.5789 | 32.8416 | 33.057 | 33.0888 | 33.2831 | 33.3519 | 33.3517 | 33.3073 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978 | 33.2978
95% | 0.75633 | 22.3327 | 24.7927 | 28.9346 | 28.9035 | 28.8754 | 29.3244 | 29.9835 | 30.4352 | 29.8861 | 29.9407 | 30.2024 | 31.2386 | 30.2568 | 30.1991 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 30.1372 | 95% | 4.1598 | 24.2668 | 27.2946 | 31.4292 | 31.3737 | 31.4101 | 31.5231 | 31.9072 | 32.1644 | 32.3754 | 32.4065 | 32.5968 | 32.6642 | 32.6641 | 32.6205 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112 | 32.6112
90% | 3.7816 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 90% | 15.5047 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
85% | 13.6139 | 19.9819 | 22.183 | 25.8888 | 25.861 | 25.8359 | 26.2376 | 26.8273 | 27.2315 | 26.7402 | 26.7891 | 27.0232 | 27.9503 | 27.0719 | 27.0202 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 26.9649 | 85% | 31.3876 | 21.7124 | 24.4215 | 28.1209 | 28.0712 | 28.1038 | 28.2049 | 28.5485 | 28.7787 | 28.9675 | 28.9953 | 29.1656 | 29.2259 | 29.2258 | 29.1868 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785 | 29.1785
80% | 35.1693 | 18.8065 | 20.8781 | 24.366 | 24.3398 | 24.3161 | 24.6942 | 25.2493 | 25.6296 | 25.1673 | 25.2132 | 25.4336 | 26.3062 | 25.4794 | 25.4308 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 25.3787 | 80% | 57.8591 | 20.4352 | 22.9849 | 26.4667 | 26.4199 | 26.4506 | 26.5458 | 26.8692 | 27.0858 | 27.2635 | 27.2897 | 27.4499 | 27.5067 | 27.5066 | 27.4699 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621 | 27.4621
75% | 80.549 | 17.6311 | 19.5732 | 22.8431 | 22.8185 | 22.7964 | 23.1508 | 23.6712 | 24.0278 | 23.5943 | 23.6374 | 23.844 | 24.6621 | 23.8869 | 23.8414 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 23.7925 | 75% | 121.3907 | 19.158 | 21.5484 | 24.8125 | 24.7687 | 24.7974 | 24.8867 | 25.1899 | 25.393 | 25.5596 | 25.5841 | 25.7343 | 25.7876 | 25.7874 | 25.753 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457 | 25.7457
70% | 192.1075 | 16.4557 | 18.2683 | 21.3202 | 21.2973 | 21.2766 | 21.6074 | 22.0931 | 22.4259 | 22.0214 | 22.0616 | 22.2544 | 23.0179 | 22.2945 | 22.252 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 22.2064 | 70% | 273.4128 | 17.8808 | 20.1118 | 23.1584 | 23.1174 | 23.1443 | 23.2276 | 23.5106 | 23.7001 | 23.8556 | 23.8785 | 24.0187 | 24.0684 | 24.0683 | 24.0362 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293 | 24.0293
65% | 403.1231 | 15.2803 | 16.9635 | 19.7973 | 19.7761 | 19.7569 | 20.064 | 20.515 | 20.8241 | 20.4484 | 20.4858 | 20.6648 | 21.3738 | 20.702 | 20.6625 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 20.6202 | 65% | 529.43 | 16.6036 | 18.6752 | 21.5042 | 21.4662 | 21.4911 | 21.5685 | 21.8312 | 22.0073 | 22.1516 | 22.1729 | 22.3031 | 22.3492 | 22.3491 | 22.3193 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313 | 22.313
60% | 739.3112 | 14.1049 | 15.6586 | 18.2745 | 18.2548 | 18.2371 | 18.5206 | 18.9369 | 19.2222 | 18.8755 | 18.9099 | 19.0752 | 19.7296 | 19.1095 | 19.0731 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 19.034 | 60% | 918.9392 | 15.3264 | 17.2387 | 19.85 | 19.8149 | 19.838 | 19.9093 | 20.1519 | 20.3144 | 20.4476 | 20.4673 | 20.5875 | 20.6301 | 20.6299 | 20.6024 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966 | 20.5966
55% | 1204.8314 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 55% | 1454.0417 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
50% | 1783.0446 | 11.7541 | 13.0488 | 15.2287 | 15.2123 | 15.1976 | 15.4339 | 15.7808 | 16.0185 | 15.7295 | 15.7583 | 15.896 | 16.4414 | 15.9246 | 15.8943 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 15.8617 | 50% | 2105.2406 | 12.772 | 14.3656 | 16.5417 | 16.5125 | 16.5316 | 16.5911 | 16.7933 | 16.9287 | 17.0397 | 17.0561 | 17.1562 | 17.1917 | 17.1916 | 17.1687 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638 | 17.1638
45% | 2370.3337 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 45% | 2758.3303 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
40% | 2864.2163 | 9.4033 | 10.4391 | 12.183 | 12.1699 | 12.1581 | 12.3471 | 12.6246 | 12.8148 | 12.5836 | 12.6066 | 12.7168 | 13.1531 | 12.7397 | 12.7154 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 12.6893 | 40% | 3348.2666 | 10.2176 | 11.4925 | 13.2333 | 13.21 | 13.2253 | 13.2729 | 13.4346 | 13.5429 | 13.6318 | 13.6448 | 13.725 | 13.7534 | 13.7533 | 13.735 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311 | 13.7311
35% | 3297.9707 | 8.2279 | 9.1342 | 10.6601 | 10.6486 | 10.6383 | 10.8037 | 11.0465 | 11.213 | 11.0107 | 11.0308 | 11.1272 | 11.509 | 11.1472 | 11.126 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 11.1032 | 35% | 3816.434 | 8.9404 | 10.0559 | 11.5792 | 11.5587 | 11.5721 | 11.6138 | 11.7553 | 11.8501 | 11.9278 | 11.9392 | 12.0093 | 12.0342 | 12.0341 | 12.0181 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147 | 12.0147
30% | 3579.7031 | 7.0524 | 7.8293 | 9.1372 | 9.1274 | 9.1186 | 9.2603 | 9.4685 | 9.6111 | 9.4377 | 9.455 | 9.5376 | 9.8648 | 9.5548 | 9.5366 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 9.517 | 30% | 4067.1569 | 7.6632 | 8.6193 | 9.925 | 9.9075 | 9.919 | 9.9547 | 10.076 | 10.1572 | 10.2238 | 10.2336 | 10.2937 | 10.315 | 10.315 | 10.3012 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983 | 10.2983
25% | 3796.3913 | 5.877 | 6.5244 | 7.6144 | 7.6062 | 7.5988 | 7.7169 | 7.8904 | 8.0093 | 7.8648 | 7.8791 | 7.948 | 8.2207 | 7.9623 | 7.9471 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 7.9308 | 25% | 4236.9526 | 6.386 | 7.1828 | 8.2708 | 8.2562 | 8.2658 | 8.2956 | 8.3966 | 8.4643 | 8.5199 | 8.528 | 8.5781 | 8.5959 | 8.5958 | 8.5843 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819 | 8.5819
20% | 3975.6411 | 4.7016 | 5.2195 | 6.0915 | 6.0849 | 6.079 | 6.1735 | 6.3123 | 6.4074 | 6.2918 | 6.3033 | 6.3584 | 6.5765 | 6.3698 | 6.3577 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 6.3447 | 20% | 4332.6282 | 5.1088 | 5.7462 | 6.6167 | 6.605 | 6.6127 | 6.6364 | 6.7173 | 6.7715 | 6.8159 | 6.8224 | 6.8625 | 6.8767 | 6.8766 | 6.8675 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655 | 6.8655
15% | 4117.4527 | 3.5262 | 3.9146 | 4.5686 | 4.5637 | 4.5593 | 4.6302 | 4.7342 | 4.8056 | 4.7189 | 4.7275 | 4.7688 | 4.9324 | 4.7774 | 4.7683 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 4.7585 | 15% | 4361.7469 | 3.8316 | 4.3097 | 4.9625 | 4.9537 | 4.9595 | 4.9773 | 5.038 | 5.0786 | 5.1119 | 5.1168 | 5.1469 | 5.1575 | 5.1575 | 5.1506 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491 | 5.1491
10% | 4224.8514 | 2.3508 | 2.6098 | 3.0457 | 3.0425 | 3.0395 | 3.0868 | 3.1562 | 3.2037 | 3.1459 | 3.1517 | 3.1792 | 3.2883 | 3.1849 | 3.1789 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 3.1723 | 10% | 4375.7389 | 2.5544 | 2.8731 | 3.3083 | 3.3025 | 3.3063 | 3.3182 | 3.3587 | 3.3857 | 3.4079 | 3.4112 | 3.4312 | 3.4383 | 3.4383 | 3.4337 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328 | 3.4328
5% | 4310.3165 | 1.1754 | 1.3049 | 1.5229 | 1.5212 | 1.5198 | 1.5434 | 1.5781 | 1.6019 | 1.573 | 1.5758 | 1.5896 | 1.6441 | 1.5925 | 1.5894 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 1.5862 | 5% | 4378.0079 | 1.2772 | 1.4366 | 1.6542 | 1.6512 | 1.6532 | 1.6591 | 1.6793 | 1.6929 | 1.704 | 1.7056 | 1.7156 | 1.7192 | 1.7192 | 1.7169 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164 | 1.7164
9.992e-14% | 4382.5459 | 2.3489e-14 | 2.6077e-14 | 3.0433e-14 | 3.04e-14 | 3.0371e-14 | 3.0843e-14 | 3.1536e-14 | 3.2011e-14 | 3.1434e-14 | 3.1491e-14 | 3.1767e-14 | 3.2856e-14 | 3.1824e-14 | 3.1763e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 3.1698e-14 | 9.992e-14% | 4379.1424 | 2.5524e-14 | 2.8708e-14 | 3.3057e-14 | 3.2999e-14 | 3.3037e-14 | 3.3156e-14 | 3.356e-14 | 3.383e-14 | 3.4052e-14 | 3.4085e-14 | 3.4285e-14 | 3.4356e-14 | 3.4356e-14 | 3.431e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14 | 3.43e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 34378474.2948 | 37.17% | 18.2965
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 31576189.3656 | 34.14% | 11.7393
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 10621047.2058 | 11.48% | 3.8453
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 15925855.934 | 17.22% | 3.8307
|  | 92501566.8003 |  | 37.7119 | KW/h
|  |  |  | 37711.8651 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 1 Winter POE50 W E @ R (MWh) N 1 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 55400.1444 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 1 Summer POE50 W E @ R (MWh) N 1 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 16620.0433 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 2 Winter POE50 W E @ R (MWh) N 1 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 2 Summer POE50 W E @ R (MWh) N 1 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 3 Winter POE50 W E @ R (MWh) N 1 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 3 Summer POE50 W E @ R (MWh) N 1 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 4 Winter POE50 W E @ R (MWh) N 1 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 4 Summer POE50 W E @ R (MWh) N 1 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 6.0839; FY26: 7.0722; FY27: 8.41 |  | 6.7335 | 7.7247 | 9.0733
98% | FY25: 12.0456; FY26: 14.0023; FY27: 16.651 |  | 13.3317 | 15.2942 | 17.9642
97% | FY25: 17.8849; FY26: 20.7902; FY27: 24.7229 |  | 26.3927 | 30.2779 | 35.5637
95% | FY25: 52.8294; FY26: 61.4112; FY27: 73.0275 |  | 45.4767 | 52.1712 | 61.279
90% | FY25: 203.6131; FY26: 236.689; FY27: 281.4602 |  | 156.4954 | 179.5324 | 210.8747
85% | FY25: 438.716; FY26: 509.983; FY27: 606.4496 |  | 420.4229 | 482.3115 | 566.512
80% | FY25: 1205.6283; FY26: 1401.4759; FY27: 1666.5743 |  | 965.8729 | 1108.0548 | 1301.4958
75% | FY25: 2132.4349; FY26: 2478.8373; FY27: 2947.7256 |  | 2082.1506 | 2388.6548 | 2805.6592
70% | FY25: 2978.9887; FY26: 3462.909; FY27: 4117.9409 |  | 3071.3709 | 3523.4938 | 4138.6152
65% | FY25: 4531.7682; FY26: 5267.929; FY27: 6264.3923 |  | 4330.4401 | 4967.905 | 5835.1876
60% | FY25: 5644.4559; FY26: 6561.3667; FY27: 7802.4922 |  | 6187.914 | 7098.8094 | 8338.0992
55% | FY25: 6486.7295; FY26: 7540.463; FY27: 8966.791 |  | 6899.1646 | 7914.7601 | 9296.4961
50% | FY25: 6705.9346; FY26: 7795.2768; FY27: 9269.8045 |  | 7439.7083 | 8534.8748 | 10024.8687
45% | FY25: 6110.8401; FY26: 7103.5124; FY27: 8447.1884 |  | 6904.7477 | 7921.165 | 9304.0192
40% | FY25: 4760.7565; FY26: 5534.1152; FY27: 6580.9294 |  | 5622.8386 | 6450.5518 | 7576.6706
35% | FY25: 2928.0854; FY26: 3403.7368; FY27: 4047.5759 |  | 3497.0385 | 4011.822 | 4712.1944
30% | FY25: 1391.0507; FY26: 1617.0193; FY27: 1922.8891 |  | 1807.9029 | 2074.0363 | 2436.1156
25% | FY25: 657.4626; FY26: 764.2637; FY27: 908.8292 |  | 738.8276 | 847.5872 | 995.5565
20% | FY25: 339.8138; FY26: 395.0147; FY27: 469.7343 |  | 394.3685 | 452.4217 | 531.4042
15% | FY25: 126.2646; FY26: 146.7756; FY27: 174.5392 |  | 127.9033 | 146.7314 | 172.3473
10% | FY25: 34.3941; FY26: 39.9812; FY27: 47.544 |  | 33.8369 | 38.8178 | 45.5945
5% | FY25: 12.3819; FY26: 14.3932; FY27: 17.1158 |  | 14.2115 | 16.3035 | 19.1497
9.992e-14% | FY25: 5.0445; FY26: 5.8639; FY27: 6.9731 |  | 0.84592 | 0.97045 | 1.1399
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) N 1 | 32420.7626 | 37687.3371 | 44816.144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 15084.0347 | 17304.4887 | 20325.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 8.8455; FY26: 9.8198; FY27: 11.4603 |  | 28.8346 | 32.4323 | 37.3452
98% | FY25: 0; FY26: 0; FY27: 0 |  | 19.0299 | 21.4042 | 24.6466
97% | FY25: 8.6677; FY26: 9.6225; FY27: 11.23 |  | 9.4183 | 10.5935 | 12.1982
95% | FY25: 0; FY26: 0; FY27: 0 |  | 46.3672 | 52.1525 | 60.0525
90% | FY25: 65.7856; FY26: 73.032; FY27: 85.2326 |  | 268.0603 | 301.5064 | 347.1788
85% | FY25: 202.2462; FY26: 224.5241; FY27: 262.0327 |  | 354.9988 | 399.2922 | 459.7773
80% | FY25: 418.0495; FY26: 464.0987; FY27: 541.6302 |  | 557.8552 | 627.4592 | 722.5072
75% | FY25: 826.7645; FY26: 917.8347; FY27: 1071.1666 |  | 1257.71 | 1414.6354 | 1628.9254
70% | FY25: 1901.3361; FY26: 2110.773; FY27: 2463.3952 |  | 2815.3577 | 3166.632 | 3646.3157
65% | FY25: 3348.3963; FY26: 3717.2305; FY27: 4338.2246 |  | 4414.3012 | 4965.0768 | 5717.1903
60% | FY25: 4939.4735; FY26: 5483.5688; FY27: 6399.6444 |  | 6218.5161 | 6994.405 | 8053.9225
55% | FY25: 6292.5225; FY26: 6985.6595; FY27: 8152.6718 |  | 7859.4799 | 8840.113 | 10179.2197
50% | FY25: 7136.1779; FY26: 7922.2457; FY27: 9245.7224 |  | 8732.9701 | 9822.5892 | 11310.5222
45% | FY25: 6557.8873; FY26: 7280.2548; FY27: 8496.4817 |  | 7924.2008 | 8912.9091 | 10263.0431
40% | FY25: 4934.3618; FY26: 5477.894; FY27: 6393.0216 |  | 6404.4679 | 7203.558 | 8294.7582
35% | FY25: 3823.7859; FY26: 4244.9854; FY27: 4954.1454 |  | 4484.5765 | 5044.1204 | 5808.2074
30% | FY25: 2152.477; FY26: 2389.5777; FY27: 2788.7764 |  | 2081.4521 | 2341.1564 | 2695.7964
25% | FY25: 1400.8325; FY26: 1555.1376; FY27: 1814.9363 |  | 1192.7476 | 1341.5676 | 1544.7893
20% | FY25: 948.1122; FY26: 1052.5491; FY27: 1228.3862 |  | 549.8859 | 618.4955 | 712.1857
15% | FY25: 583.4024; FY26: 647.6656; FY27: 755.8635 |  | 130.1662 | 146.4072 | 168.585
10% | FY25: 315.5929; FY26: 350.3563; FY27: 408.8862 |  | 44.6767 | 50.2511 | 57.8631
5% | FY25: 150.6845; FY26: 167.2828; FY27: 195.2287 |  | 4.3469 | 4.8893 | 5.6299
9.992e-14% | FY25: 42.4495; FY26: 47.1254; FY27: 54.9981 |  | 0.72449 | 0.81488 | 0.93832
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) N 1 | 31918.0908 | 35433.9478 | 41353.4824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 16453.8429 | 18506.8009 | 21310.2246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.1347 | 6.0045 | 7.1806 | 7.3011 | 7.3789 | 7.4858 | 7.7245 | 7.9137 | 8.0826 | 8.1435 | 8.2071 | 8.1052 | 8.1575 | 8.4053 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 |  | 5.7843 | 6.657 | 7.8439 | 7.9543 | 8.029 | 8.1029 | 8.3901 | 8.5566 | 8.729 | 8.81 | 8.8457 | 8.6932 | 8.7715 | 9.0735 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326
98% | 10.1661 | 11.8884 | 14.2168 | 14.4555 | 14.6095 | 14.8212 | 15.2938 | 15.6683 | 16.0027 | 16.1234 | 16.2492 | 16.0474 | 16.1511 | 16.6416 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 |  | 11.4523 | 13.1803 | 15.5301 | 15.7487 | 15.8966 | 16.043 | 16.6115 | 16.9413 | 17.2826 | 17.4429 | 17.5137 | 17.2117 | 17.3667 | 17.9646 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856
97% | 15.0944 | 17.6515 | 21.1087 | 21.4631 | 21.6918 | 22.0061 | 22.7078 | 23.2639 | 23.7604 | 23.9395 | 24.1263 | 23.8268 | 23.9807 | 24.709 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 |  | 22.672 | 26.0929 | 30.7448 | 31.1777 | 31.4704 | 31.7602 | 32.8857 | 33.5386 | 34.2143 | 34.5316 | 34.6718 | 34.074 | 34.3807 | 35.5645 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121
95% | 44.5865 | 52.1398 | 62.3517 | 63.3988 | 64.0742 | 65.0026 | 67.0754 | 68.718 | 70.1846 | 70.7136 | 71.2655 | 70.3806 | 70.8352 | 72.9865 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 |  | 39.0656 | 44.9601 | 52.9757 | 53.7216 | 54.2259 | 54.7253 | 56.6646 | 57.7896 | 58.9539 | 59.5007 | 59.7421 | 58.7121 | 59.2407 | 61.2803 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285
90% | 171.8437 | 200.9556 | 240.314 | 244.3497 | 246.9526 | 250.531 | 258.5197 | 264.8505 | 270.503 | 272.542 | 274.6691 | 271.2587 | 273.0108 | 281.302 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 |  | 134.4333 | 154.7176 | 182.3009 | 184.8678 | 186.6034 | 188.3218 | 194.9955 | 198.8667 | 202.8734 | 204.755 | 205.5858 | 202.0413 | 203.8601 | 210.8791 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038
85% | 370.2638 | 432.99 | 517.7937 | 526.4892 | 532.0976 | 539.8077 | 557.0207 | 570.6614 | 582.8405 | 587.234 | 591.817 | 584.4689 | 588.2439 | 606.1086 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 |  | 361.1533 | 415.6468 | 489.7489 | 496.6449 | 501.3076 | 505.9241 | 523.8529 | 534.2528 | 545.0166 | 550.0715 | 552.3034 | 542.7812 | 547.6675 | 566.5239 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247
80% | 1017.516 | 1189.8928 | 1422.9403 | 1446.8363 | 1462.2486 | 1483.4368 | 1530.7395 | 1568.2254 | 1601.6945 | 1613.7681 | 1626.3625 | 1606.1695 | 1616.5436 | 1665.637 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 |  | 829.7079 | 954.9004 | 1125.1415 | 1140.9843 | 1151.6962 | 1162.3021 | 1203.4913 | 1227.3839 | 1252.1126 | 1263.7255 | 1268.8531 | 1246.9771 | 1258.2027 | 1301.5232 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308
75% | 1799.7145 | 2104.603 | 2516.8021 | 2559.0676 | 2586.328 | 2623.8041 | 2707.47 | 2773.7725 | 2832.9705 | 2854.3254 | 2876.6016 | 2840.8855 | 2859.2345 | 2946.0678 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 |  | 1788.6172 | 2058.497 | 2425.4889 | 2459.6415 | 2482.7334 | 2505.5967 | 2594.3891 | 2645.8949 | 2699.203 | 2724.2372 | 2735.2908 | 2688.1323 | 2712.3315 | 2805.7183 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14
70% | 2514.1818 | 2940.1078 | 3515.9454 | 3574.9899 | 3613.0724 | 3665.4261 | 3782.3065 | 3874.9304 | 3957.6293 | 3987.4619 | 4018.5815 | 3968.6865 | 3994.3199 | 4115.625 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 |  | 2638.3811 | 3036.4796 | 3577.8277 | 3628.206 | 3662.2688 | 3695.9944 | 3826.9717 | 3902.9475 | 3981.5821 | 4018.5099 | 4034.815 | 3965.2518 | 4000.948 | 4138.7023 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202
65% | 3824.6835 | 4472.6209 | 5348.6103 | 5438.4314 | 5496.3641 | 5576.0069 | 5753.8104 | 5894.714 | 6020.5191 | 6065.9018 | 6113.2423 | 6037.3399 | 6076.3345 | 6260.8692 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 |  | 3719.9517 | 4281.2455 | 5044.5124 | 5115.5427 | 5163.5691 | 5211.12 | 5395.7898 | 5502.9109 | 5613.7808 | 5665.8466 | 5688.8358 | 5590.7561 | 5641.0854 | 5835.3104 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767
60% | 4763.7603 | 5570.7861 | 6661.8578 | 6773.7327 | 6845.8896 | 6945.0872 | 7166.5469 | 7342.0466 | 7498.7408 | 7555.2663 | 7614.2303 | 7519.6915 | 7568.2606 | 7798.1041 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 |  | 5315.5662 | 6117.6182 | 7208.2764 | 7309.7739 | 7378.4005 | 7446.3477 | 7710.2286 | 7863.2977 | 8021.7234 | 8096.1221 | 8128.9721 | 7988.8226 | 8060.7399 | 8338.2746 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765
55% | 5474.6153 | 6402.0666 | 7655.9495 | 7784.5186 | 7867.4428 | 7981.4428 | 8235.9491 | 8437.637 | 8617.7133 | 8682.6737 | 8750.4364 | 8641.7904 | 8697.6069 | 8961.7481 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 |  | 5926.5475 | 6820.7889 | 8036.8094 | 8149.9732 | 8226.4878 | 8302.245 | 8596.4569 | 8767.1201 | 8943.7556 | 9026.7057 | 9063.3316 | 8907.073 | 8987.2566 | 9296.6917 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961
50% | 5659.6182 | 6618.4107 | 7914.6659 | 8047.5797 | 8133.3062 | 8251.1585 | 8514.2653 | 8722.7689 | 8908.9305 | 8976.0861 | 9046.1387 | 8933.8212 | 8991.524 | 9264.5911 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 |  | 6390.8875 | 7355.1919 | 8666.4866 | 8788.5167 | 8871.0262 | 8952.7188 | 9269.982 | 9454.0165 | 9644.4912 | 9733.9404 | 9773.4359 | 9604.9346 | 9691.4006 | 10025.0796 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707
45% | 5157.3753 | 6031.0832 | 7212.3067 | 7333.4256 | 7411.5446 | 7518.9385 | 7758.6968 | 7948.6975 | 8118.3388 | 8179.5349 | 8243.3709 | 8141.0207 | 8193.6028 | 8442.4376 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 |  | 5931.3435 | 6826.3085 | 8043.3131 | 8156.5685 | 8233.1451 | 8308.9635 | 8603.4135 | 8774.2148 | 8950.9932 | 9034.0105 | 9070.666 | 8914.281 | 8994.5295 | 9304.215 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025
40% | 4017.9432 | 4698.6205 | 5618.8733 | 5713.2331 | 5774.0931 | 5857.7602 | 6044.5481 | 6192.5714 | 6324.7335 | 6372.4093 | 6422.1419 | 6342.4041 | 6383.3692 | 6577.2283 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 |  | 4830.1529 | 5558.9622 | 6550.0223 | 6642.2512 | 6704.6108 | 6766.3531 | 7006.1366 | 7145.2276 | 7289.186 | 7356.7906 | 7386.6408 | 7259.2896 | 7324.6395 | 7576.83 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471
35% | 2471.2208 | 2889.8689 | 3455.8669 | 3513.9025 | 3551.3342 | 3602.7934 | 3717.6765 | 3808.7177 | 3890.0035 | 3919.3264 | 3949.9142 | 3900.8718 | 3926.0672 | 4045.2995 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 |  | 3004.0398 | 3457.3115 | 4073.6862 | 4131.0465 | 4169.8302 | 4208.2298 | 4357.3595 | 4443.865 | 4533.3978 | 4575.4434 | 4594.0083 | 4514.8042 | 4555.4475 | 4712.2935 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025
30% | 1174.0073 | 1372.8952 | 1641.7849 | 1669.3559 | 1687.1387 | 1711.5855 | 1766.1632 | 1809.4143 | 1848.0309 | 1861.9614 | 1876.4928 | 1853.1941 | 1865.1637 | 1921.8076 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 |  | 1553.0319 | 1787.3648 | 2106.0189 | 2135.6731 | 2155.7235 | 2175.5754 | 2252.6727 | 2297.3944 | 2343.6811 | 2365.4179 | 2375.0156 | 2334.0686 | 2355.0804 | 2436.1668 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284
25% | 554.8797 | 648.8815 | 775.9689 | 789 | 797.4048 | 808.9592 | 834.7547 | 855.1968 | 873.4485 | 880.0325 | 886.9006 | 875.8888 | 881.5461 | 908.3181 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 |  | 634.6706 | 730.4344 | 860.6574 | 872.776 | 880.9699 | 889.0827 | 920.5897 | 938.8659 | 957.7817 | 966.6648 | 970.587 | 953.8534 | 962.4402 | 995.5774 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142
20% | 286.7932 | 335.3787 | 401.0646 | 407.7998 | 412.1439 | 418.1159 | 431.4484 | 442.0141 | 451.4475 | 454.8506 | 458.4004 | 452.7088 | 455.6329 | 469.4702 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 |  | 338.772 | 389.8884 | 459.3983 | 465.8669 | 470.2406 | 474.5711 | 491.3887 | 501.1441 | 511.2409 | 515.9825 | 518.0761 | 509.1441 | 513.7275 | 531.4154 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615
15% | 106.5637 | 124.6166 | 149.0235 | 151.5262 | 153.1403 | 155.3593 | 160.3133 | 164.2391 | 167.7443 | 169.0088 | 170.3278 | 168.213 | 169.2995 | 174.441 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 |  | 109.872 | 126.4503 | 148.994 | 151.092 | 152.5105 | 153.9149 | 159.3693 | 162.5332 | 165.8079 | 167.3457 | 168.0247 | 165.1278 | 166.6143 | 172.3509 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674
10% | 29.0277 | 33.9452 | 40.5936 | 41.2753 | 41.715 | 42.3194 | 43.6689 | 44.7383 | 45.6931 | 46.0375 | 46.3968 | 45.8207 | 46.1167 | 47.5172 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 |  | 29.0667 | 33.4525 | 39.4164 | 39.9714 | 40.3467 | 40.7182 | 42.1612 | 42.9982 | 43.8645 | 44.2713 | 44.451 | 43.6846 | 44.0779 | 45.5955 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873
5% | 10.45 | 12.2203 | 14.6137 | 14.8591 | 15.0174 | 15.235 | 15.7208 | 16.1058 | 16.4495 | 16.5735 | 16.7028 | 16.4955 | 16.602 | 17.1062 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 |  | 12.208 | 14.05 | 16.5549 | 16.788 | 16.9456 | 17.1017 | 17.7077 | 18.0592 | 18.4231 | 18.594 | 18.6694 | 18.3475 | 18.5127 | 19.1501 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527
9.992e-14% | 4.2574 | 4.9786 | 5.9537 | 6.0537 | 6.1182 | 6.2068 | 6.4048 | 6.5616 | 6.7017 | 6.7522 | 6.8049 | 6.7204 | 6.7638 | 6.9692 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 |  | 0.72667 | 0.83631 | 0.98541 | 0.99929 | 1.0087 | 1.018 | 1.054 | 1.075 | 1.0966 | 1.1068 | 1.1113 | 1.0921 | 1.1019 | 1.1399 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222
E @ R (MWh) | 39088.86 | 45710.8803 | 54663.6286 | 55581.6146 | 56173.6951 | 56987.657 | 58804.837 | 60244.893 | 61530.6414 | 61994.4595 | 62478.2867 | 61702.552 | 62101.0833 | 63987.056 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | E @ R (MWh) | 43191.8229 | 49708.9248 | 58571.1067 | 59395.8285 | 59953.456 | 60505.5633 | 62649.7371 | 63893.5056 | 65180.7996 | 65785.3284 | 66052.2524 | 64913.4626 | 65497.8291 | 67752.9475 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127
Option 6 Winter POE50 W E @ R (MWh) N 1 | 27362.202 | 31997.6162 | 38264.54 | 38907.1302 | 39321.5866 | 39891.3599 | 41163.3859 | 42171.4251 | 43071.449 | 43396.1217 | 43734.8007 | 43191.7864 | 43470.7583 | 44790.9392 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 12957.5469 | 14912.6774 | 17571.332 | 17818.7485 | 17986.0368 | 18151.669 | 18794.9211 | 19168.0517 | 19554.2399 | 19735.5985 | 19815.6757 | 19474.0388 | 19649.3487 | 20325.8842 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.6376 | 8.4613 | 9.8959 | 9.8864 | 9.8735 | 10.0457 | 10.2876 | 10.4537 | 10.2257 | 10.2458 | 10.34 | 10.747 | 10.3582 | 10.3375 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 |  | 25.211 | 28.3566 | 32.652 | 32.5943 | 32.6322 | 32.7496 | 33.1486 | 33.4159 | 33.6351 | 33.6674 | 33.8651 | 33.9351 | 33.935 | 33.8897 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16.6384 | 18.7144 | 21.5492 | 21.5112 | 21.5362 | 21.6137 | 21.877 | 22.0534 | 22.198 | 22.2193 | 22.3498 | 22.3961 | 22.3959 | 22.3661 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597
97% | 7.4841 | 8.2912 | 9.697 | 9.6877 | 9.675 | 9.8437 | 10.0808 | 10.2436 | 10.0202 | 10.0399 | 10.1321 | 10.531 | 10.15 | 10.1297 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 |  | 8.2347 | 9.2622 | 10.6652 | 10.6464 | 10.6588 | 10.6971 | 10.8274 | 10.9147 | 10.9863 | 10.9969 | 11.0615 | 11.0843 | 11.0843 | 11.0695 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40.5403 | 45.5985 | 52.5058 | 52.413 | 52.4739 | 52.6627 | 53.3043 | 53.7341 | 54.0866 | 54.1385 | 54.4564 | 54.5691 | 54.5688 | 54.496 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805
90% | 56.8024 | 62.928 | 73.598 | 73.5269 | 73.4308 | 74.7114 | 76.5108 | 77.7461 | 76.0507 | 76.2001 | 76.9004 | 79.9278 | 77.0357 | 76.8819 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 |  | 234.3733 | 263.6163 | 303.549 | 303.0126 | 303.3646 | 304.4562 | 308.1656 | 310.6502 | 312.688 | 312.9881 | 314.826 | 315.4774 | 315.4757 | 315.0549 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655
85% | 174.6289 | 193.461 | 226.2641 | 226.0455 | 225.7501 | 229.6871 | 235.2191 | 239.0168 | 233.8046 | 234.2637 | 236.4168 | 245.7239 | 236.8327 | 236.3599 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 |  | 310.3863 | 349.1134 | 401.9974 | 401.287 | 401.7531 | 403.1988 | 408.1112 | 411.4016 | 414.1004 | 414.4978 | 416.9317 | 417.7943 | 417.7922 | 417.2349 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165
80% | 360.9637 | 399.8903 | 467.6954 | 467.2436 | 466.6329 | 474.7707 | 486.2056 | 494.0557 | 483.2818 | 484.2307 | 488.6813 | 507.9195 | 489.5409 | 488.5637 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 |  | 487.7499 | 548.6068 | 631.7102 | 630.5939 | 631.3263 | 633.5981 | 641.3176 | 646.4883 | 650.7292 | 651.3537 | 655.1785 | 656.534 | 656.5305 | 655.6549 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688
75% | 713.8676 | 790.8515 | 924.9479 | 924.0543 | 922.8465 | 938.9405 | 961.555 | 977.0798 | 955.7727 | 957.6493 | 966.4511 | 1004.4978 | 968.1511 | 966.2185 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 |  | 1099.6543 | 1236.859 | 1424.2193 | 1421.7026 | 1423.3537 | 1428.4758 | 1445.8798 | 1457.5372 | 1467.0985 | 1468.5064 | 1477.1296 | 1480.1857 | 1480.1779 | 1478.2037 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841
70% | 1641.7036 | 1818.7459 | 2127.1316 | 2125.0764 | 2122.2988 | 2159.3107 | 2211.3181 | 2247.0208 | 2198.0202 | 2202.336 | 2222.5777 | 2310.075 | 2226.4872 | 2222.0429 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 |  | 2461.5533 | 2768.6831 | 3188.0853 | 3182.4517 | 3186.1478 | 3197.6134 | 3236.5719 | 3262.6667 | 3284.0696 | 3287.2212 | 3306.524 | 3313.3649 | 3313.3476 | 3308.9284 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891
65% | 2891.1638 | 3202.9487 | 3746.0391 | 3742.4198 | 3737.5283 | 3802.7089 | 3894.2979 | 3957.1731 | 3870.8793 | 3878.4798 | 3914.1268 | 4068.2162 | 3921.0118 | 3913.185 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 |  | 3859.5585 | 4341.1185 | 4998.7143 | 4989.8812 | 4995.6765 | 5013.6538 | 5074.7382 | 5115.6532 | 5149.2115 | 5154.1531 | 5184.4187 | 5195.1447 | 5195.1176 | 5188.1885 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157
60% | 4264.9751 | 4724.9127 | 5526.0665 | 5520.7275 | 5513.5116 | 5609.6646 | 5744.7743 | 5837.5264 | 5710.2279 | 5721.4399 | 5774.0255 | 6001.3345 | 5784.1821 | 5772.6362 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 |  | 5437.0388 | 6115.4221 | 7041.7907 | 7029.3474 | 7037.5113 | 7062.8363 | 7148.8871 | 7206.525 | 7253.7993 | 7260.7605 | 7303.3963 | 7318.5063 | 7318.4681 | 7308.707 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322
55% | 5433.2616 | 6019.188 | 7039.7985 | 7032.997 | 7023.8045 | 7146.2962 | 7318.416 | 7436.5752 | 7274.4064 | 7288.6896 | 7355.6798 | 7645.2546 | 7368.6186 | 7353.9099 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 |  | 6871.7836 | 7729.1811 | 8900.0031 | 8884.2761 | 8894.5944 | 8926.6023 | 9035.3604 | 9108.208 | 9167.9572 | 9176.7554 | 9230.642 | 9249.7393 | 9249.691 | 9237.3541 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319
50% | 6161.7136 | 6826.1967 | 7983.6432 | 7975.9298 | 7965.5048 | 8104.4193 | 8299.6157 | 8433.6169 | 8249.7056 | 8265.9038 | 8341.8756 | 8670.2744 | 8356.5491 | 8339.8684 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 |  | 7635.5028 | 8588.1901 | 9889.1354 | 9871.6605 | 9883.1256 | 9918.6908 | 10039.5361 | 10120.4799 | 10186.8695 | 10196.6455 | 10256.521 | 10277.7408 | 10277.6871 | 10263.9791 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654
45% | 5662.3901 | 6273.0258 | 7336.6769 | 7329.5886 | 7320.0084 | 7447.6658 | 7627.0442 | 7750.1863 | 7581.1786 | 7596.0642 | 7665.8795 | 7967.666 | 7679.3638 | 7664.0349 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 |  | 6928.371 | 7792.829 | 8973.2924 | 8957.4359 | 8967.8391 | 9000.1106 | 9109.7644 | 9183.2118 | 9243.4531 | 9252.3237 | 9306.6541 | 9325.9086 | 9325.8599 | 9313.4214 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776
40% | 4260.5614 | 4720.023 | 5520.3478 | 5515.0143 | 5507.8058 | 5603.8593 | 5738.8293 | 5831.4853 | 5704.3185 | 5715.5189 | 5768.0501 | 5995.1239 | 5778.1962 | 5766.6623 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 |  | 5599.6221 | 6298.2911 | 7252.3608 | 7239.5453 | 7247.9534 | 7274.0357 | 7362.6597 | 7422.0211 | 7470.709 | 7477.8784 | 7521.7891 | 7537.351 | 7537.3116 | 7527.2586 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218
35% | 3301.6376 | 3657.6883 | 4277.8841 | 4273.7511 | 4268.165 | 4342.5997 | 4447.192 | 4518.994 | 4420.4486 | 4429.1281 | 4469.8362 | 4645.8024 | 4477.6987 | 4468.7607 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 |  | 3921.0024 | 4410.2287 | 5078.2933 | 5069.3196 | 5075.2072 | 5093.4707 | 5155.5275 | 5197.0939 | 5231.1865 | 5236.2067 | 5266.9541 | 5277.851 | 5277.8234 | 5270.784 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878
30% | 1858.5504 | 2058.9777 | 2408.0969 | 2405.7704 | 2402.6259 | 2444.5265 | 2503.4034 | 2543.822 | 2488.349 | 2493.2349 | 2516.1502 | 2615.2047 | 2520.5761 | 2515.5447 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 |  | 1819.8772 | 2046.9446 | 2357.0172 | 2352.8522 | 2355.5848 | 2364.0616 | 2392.8644 | 2412.1568 | 2427.9804 | 2430.3105 | 2444.5815 | 2449.6391 | 2449.6263 | 2446.359 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646
25% | 1209.545 | 1339.9831 | 1567.19 | 1565.6758 | 1563.6294 | 1590.8983 | 1629.2154 | 1655.5199 | 1619.4181 | 1622.5978 | 1637.511 | 1701.9758 | 1640.3914 | 1637.117 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 |  | 1042.8557 | 1172.9736 | 1350.6565 | 1348.2698 | 1349.8357 | 1354.6932 | 1371.1982 | 1382.2535 | 1391.321 | 1392.6562 | 1400.8339 | 1403.7321 | 1403.7248 | 1401.8526 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546
20% | 818.6449 | 906.9281 | 1060.7064 | 1059.6816 | 1058.2965 | 1076.7527 | 1102.6865 | 1120.4899 | 1096.0554 | 1098.2075 | 1108.3011 | 1151.9322 | 1110.2507 | 1108.0345 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 |  | 480.782 | 540.7696 | 622.6857 | 621.5854 | 622.3073 | 624.5467 | 632.156 | 637.2527 | 641.433 | 642.0486 | 645.8188 | 647.1549 | 647.1515 | 646.2884 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049
15% | 503.7372 | 558.0606 | 652.685 | 652.0544 | 651.2022 | 662.5588 | 678.5167 | 689.4716 | 674.4364 | 675.7606 | 681.9715 | 708.819 | 683.1711 | 681.8074 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 |  | 113.8083 | 128.0083 | 147.399 | 147.1386 | 147.3095 | 147.8396 | 149.6408 | 150.8473 | 151.8368 | 151.9825 | 152.875 | 153.1913 | 153.1905 | 152.9861 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427
10% | 272.4978 | 301.8842 | 353.0715 | 352.7304 | 352.2694 | 358.4128 | 367.0452 | 372.9713 | 364.838 | 365.5543 | 368.9141 | 383.4373 | 369.563 | 368.8253 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 |  | 39.0622 | 43.936 | 50.5915 | 50.5021 | 50.5608 | 50.7427 | 51.3609 | 51.775 | 52.1147 | 52.1647 | 52.471 | 52.5796 | 52.5793 | 52.5092 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943
5% | 130.1081 | 144.1391 | 168.5792 | 168.4163 | 168.1962 | 171.1295 | 175.2512 | 178.0807 | 174.1973 | 174.5393 | 176.1435 | 183.0778 | 176.4533 | 176.1011 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 |  | 3.8006 | 4.2749 | 4.9224 | 4.9137 | 4.9194 | 4.9371 | 4.9973 | 5.0376 | 5.0706 | 5.0755 | 5.1053 | 5.1158 | 5.1158 | 5.109 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075
9.992e-14% | 36.6529 | 40.6055 | 47.4906 | 47.4447 | 47.3827 | 48.209 | 49.3702 | 50.1673 | 49.0733 | 49.1696 | 49.6215 | 51.575 | 49.7088 | 49.6096 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 |  | 0.63344 | 0.71248 | 0.8204 | 0.81895 | 0.8199 | 0.82285 | 0.83288 | 0.8396 | 0.8451 | 0.84591 | 0.85088 | 0.85264 | 0.85264 | 0.8515 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126
E @ R (MWh) | 39370.8423 | 43616.6189 | 51012.2308 | 50962.9454 | 50896.3339 | 51783.9411 | 53031.1667 | 53887.3794 | 52712.2612 | 52815.7613 | 53301.1901 | 55399.5246 | 53394.9474 | 53288.3649 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | E @ R (MWh) | 47953.6599 | 53936.8732 | 62107.27 | 61997.5219 | 62069.5263 | 62292.8884 | 63051.84 | 63560.1953 | 63977.1458 | 64038.5427 | 64414.5818 | 64547.8494 | 64547.5123 | 64461.421 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222
Option 6 Summer POE50 W E @ R (MWh) N 1 | 27559.5896 | 30531.6333 | 35708.5616 | 35674.0618 | 35627.4337 | 36248.7588 | 37121.8167 | 37721.1656 | 36898.5828 | 36971.0329 | 37310.833 | 38779.6672 | 37376.4632 | 37301.8554 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 14386.098 | 16181.062 | 18632.181 | 18599.2566 | 18620.8579 | 18687.8665 | 18915.552 | 19068.0586 | 19193.1437 | 19211.5628 | 19324.3745 | 19364.3548 | 19364.2537 | 19338.4263 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 7 Winter POE50 W E @ R (MWh) N 1 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 7 Summer POE50 W E @ R (MWh) N 1 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 8 Winter POE50 W E @ R (MWh) N 1 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 8 Summer POE50 W E @ R (MWh) N 1 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 1 Winter POE50 W E @ R (MWh) N 2 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 1 Summer POE50 W E @ R (MWh) N 2 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 2 Winter POE50 W E @ R (MWh) N 2 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 2 Summer POE50 W E @ R (MWh) N 2 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 3 Winter POE50 W E @ R (MWh) N 2 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 3 Summer POE50 W E @ R (MWh) N 2 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 4 Winter POE50 W E @ R (MWh) N 2 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 4 Summer POE50 W E @ R (MWh) N 2 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 5 Winter POE50 W E @ R (MWh) N 2 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 5 Summer POE50 W E @ R (MWh) N 2 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.1347 | 6.0045 | 7.1806 | 7.3011 | 7.3789 | 7.4858 | 7.7245 | 7.9137 | 8.0826 | 8.1435 | 8.2071 | 8.1052 | 8.1575 | 8.4053 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 | 8.2968 |  | 5.7843 | 6.657 | 7.8439 | 7.9543 | 8.029 | 8.1029 | 8.3901 | 8.5566 | 8.729 | 8.81 | 8.8457 | 8.6932 | 8.7715 | 9.0735 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326 | 8.9326
98% | 10.1661 | 11.8884 | 14.2168 | 14.4555 | 14.6095 | 14.8212 | 15.2938 | 15.6683 | 16.0027 | 16.1234 | 16.2492 | 16.0474 | 16.1511 | 16.6416 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 | 16.4268 |  | 11.4523 | 13.1803 | 15.5301 | 15.7487 | 15.8966 | 16.043 | 16.6115 | 16.9413 | 17.2826 | 17.4429 | 17.5137 | 17.2117 | 17.3667 | 17.9646 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856 | 17.6856
97% | 15.0944 | 17.6515 | 21.1087 | 21.4631 | 21.6918 | 22.0061 | 22.7078 | 23.2639 | 23.7604 | 23.9395 | 24.1263 | 23.8268 | 23.9807 | 24.709 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 | 24.3901 |  | 22.672 | 26.0929 | 30.7448 | 31.1777 | 31.4704 | 31.7602 | 32.8857 | 33.5386 | 34.2143 | 34.5316 | 34.6718 | 34.074 | 34.3807 | 35.5645 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121 | 35.0121
95% | 44.5865 | 52.1398 | 62.3517 | 63.3988 | 64.0742 | 65.0026 | 67.0754 | 68.718 | 70.1846 | 70.7136 | 71.2655 | 70.3806 | 70.8352 | 72.9865 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 | 72.0446 |  | 39.0656 | 44.9601 | 52.9757 | 53.7216 | 54.2259 | 54.7253 | 56.6646 | 57.7896 | 58.9539 | 59.5007 | 59.7421 | 58.7121 | 59.2407 | 61.2803 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285 | 60.3285
90% | 171.8437 | 200.9556 | 240.314 | 244.3497 | 246.9526 | 250.531 | 258.5197 | 264.8505 | 270.503 | 272.542 | 274.6691 | 271.2587 | 273.0108 | 281.302 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 | 277.672 |  | 134.4333 | 154.7176 | 182.3009 | 184.8678 | 186.6034 | 188.3218 | 194.9955 | 198.8667 | 202.8734 | 204.755 | 205.5858 | 202.0413 | 203.8601 | 210.8791 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038 | 207.6038
85% | 370.2638 | 432.99 | 517.7937 | 526.4892 | 532.0976 | 539.8077 | 557.0207 | 570.6614 | 582.8405 | 587.234 | 591.817 | 584.4689 | 588.2439 | 606.1086 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 | 598.2873 |  | 361.1533 | 415.6468 | 489.7489 | 496.6449 | 501.3076 | 505.9241 | 523.8529 | 534.2528 | 545.0166 | 550.0715 | 552.3034 | 542.7812 | 547.6675 | 566.5239 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247 | 557.7247
80% | 1017.516 | 1189.8928 | 1422.9403 | 1446.8363 | 1462.2486 | 1483.4368 | 1530.7395 | 1568.2254 | 1601.6945 | 1613.7681 | 1626.3625 | 1606.1695 | 1616.5436 | 1665.637 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 | 1644.1436 |  | 829.7079 | 954.9004 | 1125.1415 | 1140.9843 | 1151.6962 | 1162.3021 | 1203.4913 | 1227.3839 | 1252.1126 | 1263.7255 | 1268.8531 | 1246.9771 | 1258.2027 | 1301.5232 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308 | 1281.308
75% | 1799.7145 | 2104.603 | 2516.8021 | 2559.0676 | 2586.328 | 2623.8041 | 2707.47 | 2773.7725 | 2832.9705 | 2854.3254 | 2876.6016 | 2840.8855 | 2859.2345 | 2946.0678 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 | 2908.0516 |  | 1788.6172 | 2058.497 | 2425.4889 | 2459.6415 | 2482.7334 | 2505.5967 | 2594.3891 | 2645.8949 | 2699.203 | 2724.2372 | 2735.2908 | 2688.1323 | 2712.3315 | 2805.7183 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14 | 2762.14
70% | 2514.1818 | 2940.1078 | 3515.9454 | 3574.9899 | 3613.0724 | 3665.4261 | 3782.3065 | 3874.9304 | 3957.6293 | 3987.4619 | 4018.5815 | 3968.6865 | 3994.3199 | 4115.625 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 | 4062.5168 |  | 2638.3811 | 3036.4796 | 3577.8277 | 3628.206 | 3662.2688 | 3695.9944 | 3826.9717 | 3902.9475 | 3981.5821 | 4018.5099 | 4034.815 | 3965.2518 | 4000.948 | 4138.7023 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202 | 4074.4202
65% | 3824.6835 | 4472.6209 | 5348.6103 | 5438.4314 | 5496.3641 | 5576.0069 | 5753.8104 | 5894.714 | 6020.5191 | 6065.9018 | 6113.2423 | 6037.3399 | 6076.3345 | 6260.8692 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 | 6180.0787 |  | 3719.9517 | 4281.2455 | 5044.5124 | 5115.5427 | 5163.5691 | 5211.12 | 5395.7898 | 5502.9109 | 5613.7808 | 5665.8466 | 5688.8358 | 5590.7561 | 5641.0854 | 5835.3104 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767 | 5744.6767
60% | 4763.7603 | 5570.7861 | 6661.8578 | 6773.7327 | 6845.8896 | 6945.0872 | 7166.5469 | 7342.0466 | 7498.7408 | 7555.2663 | 7614.2303 | 7519.6915 | 7568.2606 | 7798.1041 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 | 7697.4771 |  | 5315.5662 | 6117.6182 | 7208.2764 | 7309.7739 | 7378.4005 | 7446.3477 | 7710.2286 | 7863.2977 | 8021.7234 | 8096.1221 | 8128.9721 | 7988.8226 | 8060.7399 | 8338.2746 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765 | 8208.765
55% | 5474.6153 | 6402.0666 | 7655.9495 | 7784.5186 | 7867.4428 | 7981.4428 | 8235.9491 | 8437.637 | 8617.7133 | 8682.6737 | 8750.4364 | 8641.7904 | 8697.6069 | 8961.7481 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 | 8846.1053 |  | 5926.5475 | 6820.7889 | 8036.8094 | 8149.9732 | 8226.4878 | 8302.245 | 8596.4569 | 8767.1201 | 8943.7556 | 9026.7057 | 9063.3316 | 8907.073 | 8987.2566 | 9296.6917 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961 | 9152.2961
50% | 5659.6182 | 6618.4107 | 7914.6659 | 8047.5797 | 8133.3062 | 8251.1585 | 8514.2653 | 8722.7689 | 8908.9305 | 8976.0861 | 9046.1387 | 8933.8212 | 8991.524 | 9264.5911 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 | 9145.0405 |  | 6390.8875 | 7355.1919 | 8666.4866 | 8788.5167 | 8871.0262 | 8952.7188 | 9269.982 | 9454.0165 | 9644.4912 | 9733.9404 | 9773.4359 | 9604.9346 | 9691.4006 | 10025.0796 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707 | 9869.3707
45% | 5157.3753 | 6031.0832 | 7212.3067 | 7333.4256 | 7411.5446 | 7518.9385 | 7758.6968 | 7948.6975 | 8118.3388 | 8179.5349 | 8243.3709 | 8141.0207 | 8193.6028 | 8442.4376 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 | 8333.4961 |  | 5931.3435 | 6826.3085 | 8043.3131 | 8156.5685 | 8233.1451 | 8308.9635 | 8603.4135 | 8774.2148 | 8950.9932 | 9034.0105 | 9070.666 | 8914.281 | 8994.5295 | 9304.215 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025 | 9159.7025
40% | 4017.9432 | 4698.6205 | 5618.8733 | 5713.2331 | 5774.0931 | 5857.7602 | 6044.5481 | 6192.5714 | 6324.7335 | 6372.4093 | 6422.1419 | 6342.4041 | 6383.3692 | 6577.2283 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 | 6492.3555 |  | 4830.1529 | 5558.9622 | 6550.0223 | 6642.2512 | 6704.6108 | 6766.3531 | 7006.1366 | 7145.2276 | 7289.186 | 7356.7906 | 7386.6408 | 7259.2896 | 7324.6395 | 7576.83 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471 | 7459.1471
35% | 2471.2208 | 2889.8689 | 3455.8669 | 3513.9025 | 3551.3342 | 3602.7934 | 3717.6765 | 3808.7177 | 3890.0035 | 3919.3264 | 3949.9142 | 3900.8718 | 3926.0672 | 4045.2995 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 | 3993.0988 |  | 3004.0398 | 3457.3115 | 4073.6862 | 4131.0465 | 4169.8302 | 4208.2298 | 4357.3595 | 4443.865 | 4533.3978 | 4575.4434 | 4594.0083 | 4514.8042 | 4555.4475 | 4712.2935 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025 | 4639.1025
30% | 1174.0073 | 1372.8952 | 1641.7849 | 1669.3559 | 1687.1387 | 1711.5855 | 1766.1632 | 1809.4143 | 1848.0309 | 1861.9614 | 1876.4928 | 1853.1941 | 1865.1637 | 1921.8076 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 | 1897.0086 |  | 1553.0319 | 1787.3648 | 2106.0189 | 2135.6731 | 2155.7235 | 2175.5754 | 2252.6727 | 2297.3944 | 2343.6811 | 2365.4179 | 2375.0156 | 2334.0686 | 2355.0804 | 2436.1668 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284 | 2398.3284
25% | 554.8797 | 648.8815 | 775.9689 | 789 | 797.4048 | 808.9592 | 834.7547 | 855.1968 | 873.4485 | 880.0325 | 886.9006 | 875.8888 | 881.5461 | 908.3181 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 | 896.5971 |  | 634.6706 | 730.4344 | 860.6574 | 872.776 | 880.9699 | 889.0827 | 920.5897 | 938.8659 | 957.7817 | 966.6648 | 970.587 | 953.8534 | 962.4402 | 995.5774 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142 | 980.1142
20% | 286.7932 | 335.3787 | 401.0646 | 407.7998 | 412.1439 | 418.1159 | 431.4484 | 442.0141 | 451.4475 | 454.8506 | 458.4004 | 452.7088 | 455.6329 | 469.4702 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 | 463.4121 |  | 338.772 | 389.8884 | 459.3983 | 465.8669 | 470.2406 | 474.5711 | 491.3887 | 501.1441 | 511.2409 | 515.9825 | 518.0761 | 509.1441 | 513.7275 | 531.4154 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615 | 523.1615
15% | 106.5637 | 124.6166 | 149.0235 | 151.5262 | 153.1403 | 155.3593 | 160.3133 | 164.2391 | 167.7443 | 169.0088 | 170.3278 | 168.213 | 169.2995 | 174.441 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 | 172.19 |  | 109.872 | 126.4503 | 148.994 | 151.092 | 152.5105 | 153.9149 | 159.3693 | 162.5332 | 165.8079 | 167.3457 | 168.0247 | 165.1278 | 166.6143 | 172.3509 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674 | 169.674
10% | 29.0277 | 33.9452 | 40.5936 | 41.2753 | 41.715 | 42.3194 | 43.6689 | 44.7383 | 45.6931 | 46.0375 | 46.3968 | 45.8207 | 46.1167 | 47.5172 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 | 46.9041 |  | 29.0667 | 33.4525 | 39.4164 | 39.9714 | 40.3467 | 40.7182 | 42.1612 | 42.9982 | 43.8645 | 44.2713 | 44.451 | 43.6846 | 44.0779 | 45.5955 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873 | 44.8873
5% | 10.45 | 12.2203 | 14.6137 | 14.8591 | 15.0174 | 15.235 | 15.7208 | 16.1058 | 16.4495 | 16.5735 | 16.7028 | 16.4955 | 16.602 | 17.1062 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 | 16.8855 |  | 12.208 | 14.05 | 16.5549 | 16.788 | 16.9456 | 17.1017 | 17.7077 | 18.0592 | 18.4231 | 18.594 | 18.6694 | 18.3475 | 18.5127 | 19.1501 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527 | 18.8527
9.992e-14% | 4.2574 | 4.9786 | 5.9537 | 6.0537 | 6.1182 | 6.2068 | 6.4048 | 6.5616 | 6.7017 | 6.7522 | 6.8049 | 6.7204 | 6.7638 | 6.9692 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 | 6.8793 |  | 0.72667 | 0.83631 | 0.98541 | 0.99929 | 1.0087 | 1.018 | 1.054 | 1.075 | 1.0966 | 1.1068 | 1.1113 | 1.0921 | 1.1019 | 1.1399 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222 | 1.1222
E @ R (MWh) | 39088.86 | 45710.8803 | 54663.6286 | 55581.6146 | 56173.6951 | 56987.657 | 58804.837 | 60244.893 | 61530.6414 | 61994.4595 | 62478.2867 | 61702.552 | 62101.0833 | 63987.056 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | 63161.3647 | E @ R (MWh) | 43191.8229 | 49708.9248 | 58571.1067 | 59395.8285 | 59953.456 | 60505.5633 | 62649.7371 | 63893.5056 | 65180.7996 | 65785.3284 | 66052.2524 | 64913.4626 | 65497.8291 | 67752.9475 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127 | 66700.6127
Option 6 Winter POE50 W E @ R (MWh) N 2 | 27362.202 | 31997.6162 | 38264.54 | 38907.1302 | 39321.5866 | 39891.3599 | 41163.3859 | 42171.4251 | 43071.449 | 43396.1217 | 43734.8007 | 43191.7864 | 43470.7583 | 44790.9392 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | 44212.9553 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 12957.5469 | 14912.6774 | 17571.332 | 17818.7485 | 17986.0368 | 18151.669 | 18794.9211 | 19168.0517 | 19554.2399 | 19735.5985 | 19815.6757 | 19474.0388 | 19649.3487 | 20325.8842 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838 | 20010.1838
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.6376 | 8.4613 | 9.8959 | 9.8864 | 9.8735 | 10.0457 | 10.2876 | 10.4537 | 10.2257 | 10.2458 | 10.34 | 10.747 | 10.3582 | 10.3375 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 | 10.3134 |  | 25.211 | 28.3566 | 32.652 | 32.5943 | 32.6322 | 32.7496 | 33.1486 | 33.4159 | 33.6351 | 33.6674 | 33.8651 | 33.9351 | 33.935 | 33.8897 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801 | 33.8801
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 16.6384 | 18.7144 | 21.5492 | 21.5112 | 21.5362 | 21.6137 | 21.877 | 22.0534 | 22.198 | 22.2193 | 22.3498 | 22.3961 | 22.3959 | 22.3661 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597 | 22.3597
97% | 7.4841 | 8.2912 | 9.697 | 9.6877 | 9.675 | 9.8437 | 10.0808 | 10.2436 | 10.0202 | 10.0399 | 10.1321 | 10.531 | 10.15 | 10.1297 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 | 10.1061 |  | 8.2347 | 9.2622 | 10.6652 | 10.6464 | 10.6588 | 10.6971 | 10.8274 | 10.9147 | 10.9863 | 10.9969 | 11.0615 | 11.0843 | 11.0843 | 11.0695 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664 | 11.0664
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40.5403 | 45.5985 | 52.5058 | 52.413 | 52.4739 | 52.6627 | 53.3043 | 53.7341 | 54.0866 | 54.1385 | 54.4564 | 54.5691 | 54.5688 | 54.496 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805 | 54.4805
90% | 56.8024 | 62.928 | 73.598 | 73.5269 | 73.4308 | 74.7114 | 76.5108 | 77.7461 | 76.0507 | 76.2001 | 76.9004 | 79.9278 | 77.0357 | 76.8819 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 | 76.703 |  | 234.3733 | 263.6163 | 303.549 | 303.0126 | 303.3646 | 304.4562 | 308.1656 | 310.6502 | 312.688 | 312.9881 | 314.826 | 315.4774 | 315.4757 | 315.0549 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655 | 314.9655
85% | 174.6289 | 193.461 | 226.2641 | 226.0455 | 225.7501 | 229.6871 | 235.2191 | 239.0168 | 233.8046 | 234.2637 | 236.4168 | 245.7239 | 236.8327 | 236.3599 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 | 235.8099 |  | 310.3863 | 349.1134 | 401.9974 | 401.287 | 401.7531 | 403.1988 | 408.1112 | 411.4016 | 414.1004 | 414.4978 | 416.9317 | 417.7943 | 417.7922 | 417.2349 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165 | 417.1165
80% | 360.9637 | 399.8903 | 467.6954 | 467.2436 | 466.6329 | 474.7707 | 486.2056 | 494.0557 | 483.2818 | 484.2307 | 488.6813 | 507.9195 | 489.5409 | 488.5637 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 | 487.4269 |  | 487.7499 | 548.6068 | 631.7102 | 630.5939 | 631.3263 | 633.5981 | 641.3176 | 646.4883 | 650.7292 | 651.3537 | 655.1785 | 656.534 | 656.5305 | 655.6549 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688 | 655.4688
75% | 713.8676 | 790.8515 | 924.9479 | 924.0543 | 922.8465 | 938.9405 | 961.555 | 977.0798 | 955.7727 | 957.6493 | 966.4511 | 1004.4978 | 968.1511 | 966.2185 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 | 963.9702 |  | 1099.6543 | 1236.859 | 1424.2193 | 1421.7026 | 1423.3537 | 1428.4758 | 1445.8798 | 1457.5372 | 1467.0985 | 1468.5064 | 1477.1296 | 1480.1857 | 1480.1779 | 1478.2037 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841 | 1477.7841
70% | 1641.7036 | 1818.7459 | 2127.1316 | 2125.0764 | 2122.2988 | 2159.3107 | 2211.3181 | 2247.0208 | 2198.0202 | 2202.336 | 2222.5777 | 2310.075 | 2226.4872 | 2222.0429 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 | 2216.8724 |  | 2461.5533 | 2768.6831 | 3188.0853 | 3182.4517 | 3186.1478 | 3197.6134 | 3236.5719 | 3262.6667 | 3284.0696 | 3287.2212 | 3306.524 | 3313.3649 | 3313.3476 | 3308.9284 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891 | 3307.9891
65% | 2891.1638 | 3202.9487 | 3746.0391 | 3742.4198 | 3737.5283 | 3802.7089 | 3894.2979 | 3957.1731 | 3870.8793 | 3878.4798 | 3914.1268 | 4068.2162 | 3921.0118 | 3913.185 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 | 3904.0795 |  | 3859.5585 | 4341.1185 | 4998.7143 | 4989.8812 | 4995.6765 | 5013.6538 | 5074.7382 | 5115.6532 | 5149.2115 | 5154.1531 | 5184.4187 | 5195.1447 | 5195.1176 | 5188.1885 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157 | 5186.7157
60% | 4264.9751 | 4724.9127 | 5526.0665 | 5520.7275 | 5513.5116 | 5609.6646 | 5744.7743 | 5837.5264 | 5710.2279 | 5721.4399 | 5774.0255 | 6001.3345 | 5784.1821 | 5772.6362 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 | 5759.204 |  | 5437.0388 | 6115.4221 | 7041.7907 | 7029.3474 | 7037.5113 | 7062.8363 | 7148.8871 | 7206.525 | 7253.7993 | 7260.7605 | 7303.3963 | 7318.5063 | 7318.4681 | 7308.707 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322 | 7306.6322
55% | 5433.2616 | 6019.188 | 7039.7985 | 7032.997 | 7023.8045 | 7146.2962 | 7318.416 | 7436.5752 | 7274.4064 | 7288.6896 | 7355.6798 | 7645.2546 | 7368.6186 | 7353.9099 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 | 7336.7983 |  | 6871.7836 | 7729.1811 | 8900.0031 | 8884.2761 | 8894.5944 | 8926.6023 | 9035.3604 | 9108.208 | 9167.9572 | 9176.7554 | 9230.642 | 9249.7393 | 9249.691 | 9237.3541 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319 | 9234.7319
50% | 6161.7136 | 6826.1967 | 7983.6432 | 7975.9298 | 7965.5048 | 8104.4193 | 8299.6157 | 8433.6169 | 8249.7056 | 8265.9038 | 8341.8756 | 8670.2744 | 8356.5491 | 8339.8684 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 | 8320.4626 |  | 7635.5028 | 8588.1901 | 9889.1354 | 9871.6605 | 9883.1256 | 9918.6908 | 10039.5361 | 10120.4799 | 10186.8695 | 10196.6455 | 10256.521 | 10277.7408 | 10277.6871 | 10263.9791 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654 | 10261.0654
45% | 5662.3901 | 6273.0258 | 7336.6769 | 7329.5886 | 7320.0084 | 7447.6658 | 7627.0442 | 7750.1863 | 7581.1786 | 7596.0642 | 7665.8795 | 7967.666 | 7679.3638 | 7664.0349 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 | 7646.2016 |  | 6928.371 | 7792.829 | 8973.2924 | 8957.4359 | 8967.8391 | 9000.1106 | 9109.7644 | 9183.2118 | 9243.4531 | 9252.3237 | 9306.6541 | 9325.9086 | 9325.8599 | 9313.4214 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776 | 9310.7776
40% | 4260.5614 | 4720.023 | 5520.3478 | 5515.0143 | 5507.8058 | 5603.8593 | 5738.8293 | 5831.4853 | 5704.3185 | 5715.5189 | 5768.0501 | 5995.1239 | 5778.1962 | 5766.6623 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 | 5753.2439 |  | 5599.6221 | 6298.2911 | 7252.3608 | 7239.5453 | 7247.9534 | 7274.0357 | 7362.6597 | 7422.0211 | 7470.709 | 7477.8784 | 7521.7891 | 7537.351 | 7537.3116 | 7527.2586 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218 | 7525.1218
35% | 3301.6376 | 3657.6883 | 4277.8841 | 4273.7511 | 4268.165 | 4342.5997 | 4447.192 | 4518.994 | 4420.4486 | 4429.1281 | 4469.8362 | 4645.8024 | 4477.6987 | 4468.7607 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 | 4458.3624 |  | 3921.0024 | 4410.2287 | 5078.2933 | 5069.3196 | 5075.2072 | 5093.4707 | 5155.5275 | 5197.0939 | 5231.1865 | 5236.2067 | 5266.9541 | 5277.851 | 5277.8234 | 5270.784 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878 | 5269.2878
30% | 1858.5504 | 2058.9777 | 2408.0969 | 2405.7704 | 2402.6259 | 2444.5265 | 2503.4034 | 2543.822 | 2488.349 | 2493.2349 | 2516.1502 | 2615.2047 | 2520.5761 | 2515.5447 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 | 2509.6914 |  | 1819.8772 | 2046.9446 | 2357.0172 | 2352.8522 | 2355.5848 | 2364.0616 | 2392.8644 | 2412.1568 | 2427.9804 | 2430.3105 | 2444.5815 | 2449.6391 | 2449.6263 | 2446.359 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646 | 2445.6646
25% | 1209.545 | 1339.9831 | 1567.19 | 1565.6758 | 1563.6294 | 1590.8983 | 1629.2154 | 1655.5199 | 1619.4181 | 1622.5978 | 1637.511 | 1701.9758 | 1640.3914 | 1637.117 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 | 1633.3077 |  | 1042.8557 | 1172.9736 | 1350.6565 | 1348.2698 | 1349.8357 | 1354.6932 | 1371.1982 | 1382.2535 | 1391.321 | 1392.6562 | 1400.8339 | 1403.7321 | 1403.7248 | 1401.8526 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546 | 1401.4546
20% | 818.6449 | 906.9281 | 1060.7064 | 1059.6816 | 1058.2965 | 1076.7527 | 1102.6865 | 1120.4899 | 1096.0554 | 1098.2075 | 1108.3011 | 1151.9322 | 1110.2507 | 1108.0345 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 | 1105.4562 |  | 480.782 | 540.7696 | 622.6857 | 621.5854 | 622.3073 | 624.5467 | 632.156 | 637.2527 | 641.433 | 642.0486 | 645.8188 | 647.1549 | 647.1515 | 646.2884 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049 | 646.1049
15% | 503.7372 | 558.0606 | 652.685 | 652.0544 | 651.2022 | 662.5588 | 678.5167 | 689.4716 | 674.4364 | 675.7606 | 681.9715 | 708.819 | 683.1711 | 681.8074 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 | 680.2209 |  | 113.8083 | 128.0083 | 147.399 | 147.1386 | 147.3095 | 147.8396 | 149.6408 | 150.8473 | 151.8368 | 151.9825 | 152.875 | 153.1913 | 153.1905 | 152.9861 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427 | 152.9427
10% | 272.4978 | 301.8842 | 353.0715 | 352.7304 | 352.2694 | 358.4128 | 367.0452 | 372.9713 | 364.838 | 365.5543 | 368.9141 | 383.4373 | 369.563 | 368.8253 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 | 367.9671 |  | 39.0622 | 43.936 | 50.5915 | 50.5021 | 50.5608 | 50.7427 | 51.3609 | 51.775 | 52.1147 | 52.1647 | 52.471 | 52.5796 | 52.5793 | 52.5092 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943 | 52.4943
5% | 130.1081 | 144.1391 | 168.5792 | 168.4163 | 168.1962 | 171.1295 | 175.2512 | 178.0807 | 174.1973 | 174.5393 | 176.1435 | 183.0778 | 176.4533 | 176.1011 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 | 175.6914 |  | 3.8006 | 4.2749 | 4.9224 | 4.9137 | 4.9194 | 4.9371 | 4.9973 | 5.0376 | 5.0706 | 5.0755 | 5.1053 | 5.1158 | 5.1158 | 5.109 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075 | 5.1075
9.992e-14% | 36.6529 | 40.6055 | 47.4906 | 47.4447 | 47.3827 | 48.209 | 49.3702 | 50.1673 | 49.0733 | 49.1696 | 49.6215 | 51.575 | 49.7088 | 49.6096 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 | 49.4942 |  | 0.63344 | 0.71248 | 0.8204 | 0.81895 | 0.8199 | 0.82285 | 0.83288 | 0.8396 | 0.8451 | 0.84591 | 0.85088 | 0.85264 | 0.85264 | 0.8515 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126 | 0.85126
E @ R (MWh) | 39370.8423 | 43616.6189 | 51012.2308 | 50962.9454 | 50896.3339 | 51783.9411 | 53031.1667 | 53887.3794 | 52712.2612 | 52815.7613 | 53301.1901 | 55399.5246 | 53394.9474 | 53288.3649 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | 53164.3694 | E @ R (MWh) | 47953.6599 | 53936.8732 | 62107.27 | 61997.5219 | 62069.5263 | 62292.8884 | 63051.84 | 63560.1953 | 63977.1458 | 64038.5427 | 64414.5818 | 64547.8494 | 64547.5123 | 64461.421 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222 | 64443.1222
Option 6 Summer POE50 W E @ R (MWh) N 2 | 27559.5896 | 30531.6333 | 35708.5616 | 35674.0618 | 35627.4337 | 36248.7588 | 37121.8167 | 37721.1656 | 36898.5828 | 36971.0329 | 37310.833 | 38779.6672 | 37376.4632 | 37301.8554 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | 37215.0586 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 14386.098 | 16181.062 | 18632.181 | 18599.2566 | 18620.8579 | 18687.8665 | 18915.552 | 19068.0586 | 19193.1437 | 19211.5628 | 19324.3745 | 19364.3548 | 19364.2537 | 19338.4263 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367 | 19332.9367
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 7 Winter POE50 W E @ R (MWh) N 2 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 7 Summer POE50 W E @ R (MWh) N 2 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.0839 | 7.0722 | 8.41 | 8.5284 | 8.6076 | 8.719 | 8.9727 | 9.1719 | 9.3491 | 9.4112 | 9.4822 | 9.3829 | 9.4353 | 9.6813 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 | 9.5725 |  | 6.7335 | 7.7247 | 9.0733 | 9.1816 | 9.2577 | 9.336 | 9.6382 | 9.8149 | 9.9955 | 10.0777 | 10.1209 | 9.971 | 10.0492 | 10.3495 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083 | 10.2083
98% | 12.0456 | 14.0023 | 16.651 | 16.8854 | 17.0422 | 17.2627 | 17.765 | 18.1595 | 18.5102 | 18.6332 | 18.7738 | 18.5773 | 18.6809 | 19.168 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 | 18.9526 |  | 13.3317 | 15.2942 | 17.9642 | 18.1786 | 18.3293 | 18.4844 | 19.0827 | 19.4324 | 19.7901 | 19.9528 | 20.0383 | 19.7416 | 19.8965 | 20.4911 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113 | 20.2113
97% | 17.8849 | 20.7902 | 24.7229 | 25.071 | 25.3038 | 25.6311 | 26.377 | 26.9626 | 27.4834 | 27.6661 | 27.8748 | 27.583 | 27.7369 | 28.4601 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 | 28.1402 |  | 26.3927 | 30.2779 | 35.5637 | 35.9881 | 36.2864 | 36.5936 | 37.778 | 38.4703 | 39.1783 | 39.5004 | 39.6697 | 39.0823 | 39.389 | 40.5661 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123 | 40.0123
95% | 52.8294 | 61.4112 | 73.0275 | 74.0558 | 74.7435 | 75.7103 | 77.9135 | 79.6435 | 81.1818 | 81.7214 | 82.3379 | 81.4759 | 81.9305 | 84.0669 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 | 83.1219 |  | 45.4767 | 52.1712 | 61.279 | 62.0103 | 62.5243 | 63.0535 | 65.0943 | 66.2872 | 67.5073 | 68.0623 | 68.354 | 67.3418 | 67.8703 | 69.8985 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442 | 68.9442
90% | 203.6131 | 236.689 | 281.4602 | 285.4232 | 288.0738 | 291.8002 | 300.2917 | 306.9593 | 312.888 | 314.9678 | 317.3439 | 314.0219 | 315.7737 | 324.0078 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 | 320.3658 |  | 156.4954 | 179.5324 | 210.8747 | 213.3911 | 215.1598 | 216.981 | 224.0039 | 228.109 | 232.3074 | 234.2173 | 235.2211 | 231.7379 | 233.5566 | 240.536 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522 | 237.2522
85% | 438.716 | 509.983 | 606.4496 | 614.9885 | 620.6997 | 628.7286 | 647.025 | 661.3914 | 674.1656 | 678.6467 | 683.7665 | 676.6087 | 680.3833 | 698.125 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 | 690.2776 |  | 420.4229 | 482.3115 | 566.512 | 573.2724 | 578.024 | 582.9166 | 601.7834 | 612.8116 | 624.0908 | 629.2215 | 631.9182 | 622.5608 | 627.4467 | 646.1967 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748 | 637.3748
80% | 1205.6283 | 1401.4759 | 1666.5743 | 1690.0397 | 1705.7346 | 1727.7989 | 1778.0788 | 1817.5589 | 1852.6636 | 1864.978 | 1879.0476 | 1859.3773 | 1869.7501 | 1918.5058 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 | 1896.9406 |  | 965.8729 | 1108.0548 | 1301.4958 | 1317.0269 | 1327.9433 | 1339.1834 | 1382.5277 | 1407.8638 | 1433.7764 | 1445.5637 | 1451.759 | 1430.2615 | 1441.4861 | 1484.5621 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295 | 1464.295
75% | 2132.4349 | 2478.8373 | 2947.7256 | 2989.2297 | 3016.9896 | 3056.0155 | 3144.9473 | 3214.777 | 3276.8679 | 3298.6488 | 3323.5341 | 3288.7427 | 3307.0894 | 3393.3253 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 | 3355.1821 |  | 2082.1506 | 2388.6548 | 2805.6592 | 2839.14 | 2862.6727 | 2886.9032 | 2980.3413 | 3034.9588 | 3090.8192 | 3116.2292 | 3129.5846 | 3083.2419 | 3107.439 | 3200.2988 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085 | 3156.6085
70% | 2978.9887 | 3462.909 | 4117.9409 | 4175.9217 | 4214.702 | 4269.2208 | 4393.4576 | 4491.0089 | 4577.7492 | 4608.1769 | 4642.9414 | 4594.3381 | 4619.9683 | 4740.4389 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 | 4687.1534 |  | 3071.3709 | 3523.4938 | 4138.6152 | 4188.0026 | 4222.7155 | 4258.4579 | 4396.288 | 4476.854 | 4559.2534 | 4596.7355 | 4616.436 | 4548.0761 | 4583.7692 | 4720.7462 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989 | 4656.2989
65% | 4531.7682 | 5267.929 | 6264.3923 | 6352.5952 | 6411.5895 | 6494.5258 | 6683.5203 | 6831.9196 | 6963.8728 | 7010.1608 | 7063.046 | 6989.1086 | 7028.0983 | 7211.3635 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 | 7130.3032 |  | 4330.4401 | 4967.905 | 5835.1876 | 5904.8206 | 5953.7637 | 6004.1582 | 6198.4901 | 6312.083 | 6428.261 | 6481.1084 | 6508.8849 | 6412.5017 | 6462.8268 | 6655.9558 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891 | 6565.0891
60% | 5644.4559 | 6561.3667 | 7802.4922 | 7912.3516 | 7985.8309 | 8089.1306 | 8324.529 | 8509.3649 | 8673.7166 | 8731.3697 | 8797.2399 | 8705.1486 | 8753.7114 | 8981.9739 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 | 8881.0108 |  | 6187.914 | 7098.8094 | 8338.0992 | 8437.6002 | 8507.5366 | 8579.5471 | 8857.2345 | 9019.5513 | 9185.562 | 9261.0775 | 9300.7683 | 9163.0431 | 9234.9543 | 9510.9229 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804 | 9381.0804
55% | 6486.7295 | 7540.463 | 8966.791 | 9093.0438 | 9177.4877 | 9296.202 | 9566.7268 | 9779.1442 | 9968.0207 | 10034.2769 | 10109.9763 | 10004.143 | 10059.9525 | 10322.2765 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 | 10206.2476 |  | 6899.1646 | 7914.7601 | 9296.4961 | 9407.434 | 9485.4091 | 9565.6966 | 9875.3018 | 10056.2757 | 10241.368 | 10325.5634 | 10369.8162 | 10216.2607 | 10296.4375 | 10604.1264 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596 | 10459.3596
50% | 6705.9346 | 7795.2768 | 9269.8045 | 9400.3237 | 9487.6213 | 9610.3472 | 9890.0138 | 10109.6094 | 10304.8686 | 10373.3638 | 10451.6213 | 10342.2116 | 10399.907 | 10671.0958 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 | 10551.1459 |  | 7439.7083 | 8534.8748 | 10024.8687 | 10144.4985 | 10228.5828 | 10315.1608 | 10649.0233 | 10844.1763 | 11043.7704 | 11134.5625 | 11182.2825 | 11016.696 | 11103.1546 | 11434.9507 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415 | 11278.8415
45% | 6110.8401 | 7103.5124 | 8447.1884 | 8566.1251 | 8645.6757 | 8757.5108 | 9012.3594 | 9212.4677 | 9390.3993 | 9452.8161 | 9524.129 | 9424.4285 | 9477.0039 | 9724.1269 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 | 9614.8216 |  | 6904.7477 | 7921.165 | 9304.0192 | 9415.0469 | 9493.085 | 9573.4375 | 9883.2933 | 10064.4136 | 10249.6557 | 10333.9193 | 10378.2079 | 10224.5281 | 10304.7697 | 10612.7077 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237 | 10467.8237
40% | 4760.7565 | 5534.1152 | 6580.9294 | 6673.5892 | 6735.5645 | 6822.6915 | 7021.2357 | 7177.1336 | 7315.7543 | 7364.3812 | 7419.9388 | 7342.2654 | 7383.2252 | 7575.7507 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 | 7490.5944 |  | 5622.8386 | 6450.5518 | 7576.6706 | 7667.0853 | 7730.6351 | 7796.0697 | 8048.3988 | 8195.893 | 8346.7438 | 8415.3633 | 8451.4295 | 8326.2813 | 8391.6256 | 8642.3929 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076 | 8524.4076
35% | 2928.0854 | 3403.7368 | 4047.5759 | 4104.5659 | 4142.6836 | 4196.2707 | 4318.3846 | 4414.269 | 4499.5272 | 4529.435 | 4563.6054 | 4515.8327 | 4541.0249 | 4659.4369 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 | 4607.0619 |  | 3497.0385 | 4011.822 | 4712.1944 | 4768.4264 | 4807.9503 | 4848.6463 | 5005.5786 | 5097.3103 | 5191.1296 | 5233.8065 | 5256.2373 | 5178.4033 | 5219.0432 | 5375.0041 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249 | 5301.6249
30% | 1391.0507 | 1617.0193 | 1922.8891 | 1949.9634 | 1968.0721 | 1993.5298 | 2051.5427 | 2097.0947 | 2137.5984 | 2151.8067 | 2168.0402 | 2145.3447 | 2157.3128 | 2213.567 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 | 2188.6851 |  | 1807.9029 | 2074.0363 | 2436.1156 | 2465.1865 | 2485.6196 | 2506.6587 | 2587.7897 | 2635.2133 | 2683.7161 | 2705.7792 | 2717.3755 | 2677.1368 | 2698.1469 | 2778.7757 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401 | 2740.8401
25% | 657.4626 | 764.2637 | 908.8292 | 921.6256 | 930.1844 | 942.2167 | 969.6357 | 991.1653 | 1010.3089 | 1017.0243 | 1024.6968 | 1013.9701 | 1019.6266 | 1046.2145 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 | 1034.4544 |  | 738.8276 | 847.5872 | 995.5565 | 1007.4368 | 1015.7871 | 1024.385 | 1057.5405 | 1076.9209 | 1096.7423 | 1105.7587 | 1110.4977 | 1094.0536 | 1102.6397 | 1135.5899 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869 | 1120.0869
20% | 339.8138 | 395.0147 | 469.7343 | 476.3482 | 480.7719 | 486.9909 | 501.1626 | 512.2903 | 522.1848 | 525.6556 | 529.6212 | 524.0771 | 527.0007 | 540.7428 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 | 534.6645 |  | 394.3685 | 452.4217 | 531.4042 | 537.7456 | 542.2028 | 546.7922 | 564.4898 | 574.8346 | 585.4148 | 590.2275 | 592.7571 | 583.9796 | 588.5626 | 606.1507 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756 | 597.8756
15% | 126.2646 | 146.7756 | 174.5392 | 176.9967 | 178.6404 | 180.9512 | 186.217 | 190.3517 | 194.0282 | 195.3178 | 196.7913 | 194.7313 | 195.8176 | 200.9238 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 | 198.6653 |  | 127.9033 | 146.7314 | 172.3473 | 174.404 | 175.8496 | 177.338 | 183.0778 | 186.4328 | 189.8642 | 191.4251 | 192.2455 | 189.3988 | 190.8852 | 196.5894 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056 | 193.9056
10% | 34.3941 | 39.9812 | 47.544 | 48.2134 | 48.6611 | 49.2906 | 50.725 | 51.8512 | 52.8527 | 53.204 | 53.6054 | 53.0442 | 53.3402 | 54.7311 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 | 54.1158 |  | 33.8369 | 38.8178 | 45.5945 | 46.1386 | 46.521 | 46.9148 | 48.4333 | 49.3209 | 50.2286 | 50.6416 | 50.8586 | 50.1055 | 50.4987 | 52.0078 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978 | 51.2978
5% | 12.3819 | 14.3932 | 17.1158 | 17.3568 | 17.518 | 17.7446 | 18.261 | 18.6664 | 19.027 | 19.1534 | 19.2979 | 19.0959 | 19.2025 | 19.7032 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 | 19.4817 |  | 14.2115 | 16.3035 | 19.1497 | 19.3782 | 19.5388 | 19.7042 | 20.342 | 20.7148 | 21.096 | 21.2695 | 21.3606 | 21.0443 | 21.2095 | 21.8433 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451 | 21.5451
9.992e-14% | 5.0445 | 5.8639 | 6.9731 | 7.0713 | 7.137 | 7.2293 | 7.4397 | 7.6048 | 7.7517 | 7.8033 | 7.8621 | 7.7798 | 7.8232 | 8.0272 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 |  | 0.84592 | 0.97045 | 1.1399 | 1.1535 | 1.163 | 1.1729 | 1.2108 | 1.233 | 1.2557 | 1.266 | 1.2715 | 1.2526 | 1.2625 | 1.3002 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824 | 1.2824
E @ R (MWh) | 46315.3751 | 53839.0531 | 64023.0628 | 64924.5101 | 65527.4415 | 66375.0636 | 68306.6159 | 69823.2801 | 71171.862 | 71644.9325 | 72185.428 | 71429.7764 | 71828.2569 | 73701.2558 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | 72872.8069 | E @ R (MWh) | 50280.1156 | 57681.629 | 67751.522 | 68560.0213 | 69128.2922 | 69713.4158 | 71969.7744 | 73288.6857 | 74637.6114 | 75251.2156 | 75573.724 | 74454.6333 | 75038.95 | 77281.3427 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303 | 76226.303
Option 8 Winter POE50 W E @ R (MWh) N 2 | 32420.7626 | 37687.3371 | 44816.144 | 45447.1571 | 45869.209 | 46462.5445 | 47814.6311 | 48876.2961 | 49820.3034 | 50151.4528 | 50529.7996 | 50000.8435 | 50279.7798 | 51590.8791 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | 51010.9648 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 15084.0347 | 17304.4887 | 20325.4566 | 20568.0064 | 20738.4877 | 20914.0247 | 21590.9323 | 21986.6057 | 22391.2834 | 22575.3647 | 22672.1172 | 22336.39 | 22511.685 | 23184.4028 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909 | 22867.8909
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 8.8455 | 9.8198 | 11.4603 | 11.448 | 11.4369 | 11.6147 | 11.8758 | 12.0547 | 11.8372 | 11.8588 | 11.9625 | 12.3729 | 11.984 | 11.9612 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 | 11.9367 |  | 28.8346 | 32.4323 | 37.3452 | 37.2792 | 37.3225 | 37.4568 | 37.9131 | 38.2188 | 38.4695 | 38.5065 | 38.7326 | 38.8127 | 38.8125 | 38.7607 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497 | 38.7497
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 19.0299 | 21.4042 | 24.6466 | 24.603 | 24.6316 | 24.7202 | 25.0214 | 25.2231 | 25.3886 | 25.413 | 25.5622 | 25.6151 | 25.6149 | 25.5808 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735 | 25.5735
97% | 8.6677 | 9.6225 | 11.23 | 11.2179 | 11.207 | 11.3812 | 11.6371 | 11.8124 | 11.5993 | 11.6205 | 11.722 | 12.1242 | 11.7431 | 11.7208 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 | 11.6967 |  | 9.4183 | 10.5935 | 12.1982 | 12.1766 | 12.1908 | 12.2346 | 12.3837 | 12.4835 | 12.5654 | 12.5775 | 12.6513 | 12.6775 | 12.6774 | 12.6605 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569 | 12.6569
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.3672 | 52.1525 | 60.0525 | 59.9464 | 60.0161 | 60.232 | 60.9659 | 61.4574 | 61.8606 | 61.9199 | 62.2835 | 62.4124 | 62.4121 | 62.3288 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111 | 62.3111
90% | 65.7856 | 73.032 | 85.2326 | 85.1409 | 85.0583 | 86.3808 | 88.3224 | 89.6529 | 88.0356 | 88.1964 | 88.9672 | 92.0196 | 89.1274 | 88.9575 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 | 88.7752 |  | 268.0603 | 301.5064 | 347.1788 | 346.5653 | 346.9678 | 348.2164 | 352.4589 | 355.3006 | 357.6314 | 357.9746 | 360.0766 | 360.8216 | 360.8197 | 360.3385 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362 | 360.2362
85% | 202.2462 | 224.5241 | 262.0327 | 261.7509 | 261.4969 | 265.5625 | 271.5316 | 275.6221 | 270.65 | 271.1445 | 273.5142 | 282.898 | 274.0066 | 273.4842 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 | 272.9237 |  | 354.9988 | 399.2922 | 459.7773 | 458.9649 | 459.4979 | 461.1514 | 466.7699 | 470.5333 | 473.6199 | 474.0744 | 476.8582 | 477.8448 | 477.8423 | 477.205 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695 | 477.0695
80% | 418.0495 | 464.0987 | 541.6302 | 541.0477 | 540.5227 | 548.9264 | 561.2649 | 569.72 | 559.4425 | 560.4646 | 565.3628 | 584.7596 | 566.3806 | 565.3009 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 | 564.1423 |  | 557.8552 | 627.4592 | 722.5072 | 721.2305 | 722.0681 | 724.6666 | 733.4956 | 739.4094 | 744.2599 | 744.9741 | 749.3487 | 750.899 | 750.8951 | 749.8936 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807 | 749.6807
75% | 826.7645 | 917.8347 | 1071.1666 | 1070.0146 | 1068.9763 | 1085.5961 | 1109.9975 | 1126.719 | 1106.3936 | 1108.4148 | 1118.1018 | 1156.4623 | 1120.1148 | 1117.9795 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 | 1115.6882 |  | 1257.71 | 1414.6354 | 1628.9254 | 1626.0469 | 1627.9354 | 1633.7937 | 1653.6992 | 1667.0321 | 1677.9678 | 1679.578 | 1689.4407 | 1692.9359 | 1692.9271 | 1690.6691 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892 | 1690.1892
70% | 1901.3361 | 2110.773 | 2463.3952 | 2460.7458 | 2458.3581 | 2496.5793 | 2552.6958 | 2591.1509 | 2544.4078 | 2549.056 | 2571.3336 | 2659.5524 | 2575.9628 | 2571.0524 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 | 2565.7829 |  | 2815.3577 | 3166.632 | 3646.3157 | 3639.8724 | 3644.0997 | 3657.2133 | 3701.7713 | 3731.6169 | 3756.096 | 3759.7006 | 3781.7779 | 3789.602 | 3789.5822 | 3784.5278 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535 | 3783.4535
65% | 3348.3963 | 3717.2305 | 4338.2246 | 4333.5589 | 4329.3539 | 4396.6643 | 4495.4898 | 4563.2121 | 4480.8939 | 4489.0798 | 4528.3123 | 4683.6724 | 4536.4648 | 4527.8171 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 | 4518.5371 |  | 4414.3012 | 4965.0768 | 5717.1903 | 5707.0876 | 5713.7158 | 5734.2771 | 5804.1412 | 5850.9371 | 5889.3188 | 5894.9706 | 5929.5864 | 5941.8541 | 5941.8231 | 5933.8981 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136 | 5932.2136
60% | 4939.4735 | 5483.5688 | 6399.6444 | 6392.7617 | 6386.5586 | 6485.8532 | 6631.6381 | 6731.5405 | 6610.1067 | 6622.1822 | 6680.0571 | 6909.2406 | 6692.0835 | 6679.3266 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 | 6665.637 |  | 6218.5161 | 6994.405 | 8053.9225 | 8039.6906 | 8049.028 | 8077.9931 | 8176.4121 | 8242.3344 | 8296.4035 | 8304.3653 | 8353.1292 | 8370.411 | 8370.3673 | 8359.2032 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303 | 8356.8303
55% | 6292.5225 | 6985.6595 | 8152.6718 | 8143.9038 | 8136.0015 | 8262.4955 | 8448.2147 | 8575.4829 | 8420.7852 | 8436.1685 | 8509.8969 | 8801.8595 | 8525.2175 | 8508.9662 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 | 8491.5267 |  | 7859.4799 | 8840.113 | 10179.2197 | 10161.2323 | 10173.0336 | 10209.6421 | 10334.0323 | 10417.3504 | 10485.6875 | 10495.7503 | 10557.3821 | 10579.2243 | 10579.1691 | 10565.0589 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598 | 10562.0598
50% | 7136.1779 | 7922.2457 | 9245.7224 | 9235.7788 | 9226.817 | 9370.2705 | 9580.8895 | 9725.2209 | 9549.7825 | 9567.2283 | 9650.8416 | 9981.9485 | 9668.2163 | 9649.7862 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 | 9630.0085 |  | 8732.9701 | 9822.5892 | 11310.5222 | 11290.5356 | 11303.6486 | 11344.3256 | 11482.5404 | 11575.1183 | 11651.0503 | 11662.2314 | 11730.7129 | 11754.9827 | 11754.9213 | 11739.2429 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105 | 11735.9105
45% | 6557.8873 | 7280.2548 | 8496.4817 | 8487.3439 | 8479.1084 | 8610.9368 | 8804.488 | 8937.1233 | 8775.9018 | 8791.9339 | 8868.7715 | 9173.0466 | 8884.7382 | 8867.8016 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 | 8849.6266 |  | 7924.2008 | 8912.9091 | 10263.0431 | 10244.9075 | 10256.806 | 10293.716 | 10419.1305 | 10503.1347 | 10572.0345 | 10582.1802 | 10644.3195 | 10666.3416 | 10666.2859 | 10652.0596 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358 | 10649.0358
40% | 4934.3618 | 5477.894 | 6393.0216 | 6386.146 | 6379.9493 | 6479.1412 | 6624.7753 | 6724.5743 | 6603.2661 | 6615.3291 | 6673.1441 | 6902.0904 | 6685.158 | 6672.4144 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 | 6658.739 |  | 6404.4679 | 7203.558 | 8294.7582 | 8280.1008 | 8289.7174 | 8319.5486 | 8420.9106 | 8488.8042 | 8544.4902 | 8552.6901 | 8602.9121 | 8620.7107 | 8620.6657 | 8609.1677 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238 | 8606.7238
35% | 3823.7859 | 4244.9854 | 4954.1454 | 4948.8173 | 4944.0153 | 5020.8821 | 5133.7383 | 5211.0756 | 5117.0702 | 5126.4182 | 5171.2208 | 5348.6382 | 5180.5308 | 5170.6553 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 | 5160.0578 |  | 4484.5765 | 5044.1204 | 5808.2074 | 5797.9439 | 5804.6777 | 5825.5663 | 5896.5426 | 5944.0835 | 5983.0763 | 5988.818 | 6023.9848 | 6036.4479 | 6036.4163 | 6028.3652 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539 | 6026.6539
30% | 2152.477 | 2389.5777 | 2788.7764 | 2785.7771 | 2783.074 | 2826.3437 | 2889.8725 | 2933.407 | 2880.4897 | 2885.7519 | 2910.972 | 3010.8434 | 2916.2127 | 2910.6537 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 | 2904.6882 |  | 2081.4521 | 2341.1564 | 2695.7964 | 2691.0328 | 2694.1581 | 2703.8533 | 2736.796 | 2758.8614 | 2776.9593 | 2779.6243 | 2795.9464 | 2801.731 | 2801.7163 | 2797.9795 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852 | 2797.1852
25% | 1400.8325 | 1555.1376 | 1814.9363 | 1812.9843 | 1811.2251 | 1839.3851 | 1880.7296 | 1909.0619 | 1874.6233 | 1878.0479 | 1894.4612 | 1959.4575 | 1897.8719 | 1894.254 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 | 1890.3717 |  | 1192.7476 | 1341.5676 | 1544.7893 | 1542.0595 | 1543.8505 | 1549.4061 | 1568.2835 | 1580.9278 | 1591.2985 | 1592.8256 | 1602.1788 | 1605.4936 | 1605.4852 | 1603.3439 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887 | 1602.8887
20% | 948.1122 | 1052.5491 | 1228.3862 | 1227.0651 | 1225.8744 | 1244.9336 | 1272.9165 | 1292.0923 | 1268.7836 | 1271.1014 | 1282.2103 | 1326.2011 | 1284.5187 | 1282.0701 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 | 1279.4424 |  | 549.8859 | 618.4955 | 712.1857 | 710.9272 | 711.7529 | 714.3142 | 723.0171 | 728.8464 | 733.6276 | 734.3316 | 738.6437 | 740.1719 | 740.168 | 739.1808 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971 | 738.971
15% | 583.4024 | 647.6656 | 755.8635 | 755.0506 | 754.3179 | 766.0457 | 783.2643 | 795.0638 | 780.7213 | 782.1475 | 788.9831 | 816.052 | 790.4036 | 788.8968 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 | 787.28 |  | 130.1662 | 146.4072 | 168.585 | 168.2871 | 168.4826 | 169.0889 | 171.149 | 172.5289 | 173.6606 | 173.8273 | 174.848 | 175.2098 | 175.2089 | 174.9752 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255 | 174.9255
10% | 315.5929 | 350.3563 | 408.8862 | 408.4464 | 408.0501 | 414.3942 | 423.7087 | 430.0917 | 422.333 | 423.1046 | 426.8023 | 441.4453 | 427.5707 | 426.7556 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 | 425.881 |  | 44.6767 | 50.2511 | 57.8631 | 57.7609 | 57.828 | 58.0361 | 58.7432 | 59.2168 | 59.6052 | 59.6624 | 60.0128 | 60.1369 | 60.1366 | 60.0564 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394 | 60.0394
5% | 150.6845 | 167.2828 | 195.2287 | 195.0188 | 194.8295 | 197.8586 | 202.306 | 205.3536 | 201.6491 | 202.0175 | 203.7831 | 210.7746 | 204.1499 | 203.7608 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 | 203.3432 |  | 4.3469 | 4.8893 | 5.6299 | 5.62 | 5.6265 | 5.6468 | 5.7156 | 5.7616 | 5.7994 | 5.805 | 5.8391 | 5.8512 | 5.8511 | 5.8433 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417 | 5.8417
9.992e-14% | 42.4495 | 47.1254 | 54.9981 | 54.9389 | 54.8856 | 55.7389 | 56.9918 | 57.8504 | 56.8068 | 56.9105 | 57.4079 | 59.3775 | 57.5113 | 57.4016 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 | 57.284 |  | 0.72449 | 0.81488 | 0.93832 | 0.93666 | 0.93775 | 0.94113 | 0.95259 | 0.96027 | 0.96657 | 0.9675 | 0.97318 | 0.97519 | 0.97519 | 0.97389 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361 | 0.97361
E @ R (MWh) | 45597.2725 | 50619.9255 | 59076.4034 | 59012.8679 | 58955.6056 | 59872.2148 | 61217.9846 | 62140.2036 | 61019.2233 | 61130.6953 | 61664.9501 | 63780.5884 | 61775.9675 | 61658.2066 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | 61531.8352 | E @ R (MWh) | 54846.143 | 61689.3365 | 71034.0821 | 70908.5596 | 70990.9134 | 71246.3798 | 72114.4172 | 72695.8395 | 73172.7192 | 73242.9408 | 73673.0288 | 73825.4513 | 73825.0657 | 73726.6003 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714 | 73705.6714
Option 8 Summer POE50 W E @ R (MWh) N 2 | 31918.0908 | 35433.9478 | 41353.4824 | 41309.0076 | 41268.9239 | 41910.5504 | 42852.5893 | 43498.1425 | 42713.4563 | 42791.4867 | 43165.465 | 44646.4119 | 43243.1772 | 43160.7446 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | 43072.2846 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 16453.8429 | 18506.8009 | 21310.2246 | 21272.5679 | 21297.274 | 21373.914 | 21634.3252 | 21808.7518 | 21951.8158 | 21972.8822 | 22101.9086 | 22147.6354 | 22147.5197 | 22117.9801 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014 | 22111.7014

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-LLG-TRNFMR-9000007796 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 2 Pof | bar: FY25 to FY54
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
N-1 Risk |  | 0.07365% | 0.07365% | 0.08139% | 0.08959% | 0.09827% | 0.1074% | 0.1171% | 0.1272% | 0.1379% | 0.1491% | 0.1608% | 0.1731% | 0.1858% | 0.1992% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213%
N-2 Risk | bar: FY25 to FY54
N Risk |  | 99.93% | 99.93% | 99.92% | 99.91% | 99.9% | 99.89% | 99.88% | 99.87% | 99.86% | 99.85% | 99.84% | 99.83% | 99.81% | 99.8% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 87.0787 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 1 | 87.0787 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Cost of EUE ($) - Option 1 | 3283899.7871 | 3718448.0103 | 4817164.5666 | 5332417.2061 | 5873105.2005 | 6494721.6778 | 7250394.8946 | 8010773.3652 | 8717214.8031 | 9464304.0188 | 10280699.3876 | 11132072.7363 | 11859457.7468 | 12867252.9786 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322
Hours at Risk pA. (Hrs) (N) | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 2 | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Cost of EUE ($) - Option 2 | 3277760.4222 | 3718448.0103 | 4817164.5666 | 5332417.2061 | 5873105.2005 | 6494721.6778 | 7250394.8946 | 8010773.3652 | 8717214.8031 | 9464304.0188 | 10280699.3876 | 11132072.7363 | 11859457.7468 | 12867252.9786 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 3 | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Cost of EUE ($) - Option 3 | 3277760.4222 | 3718448.0103 | 4817164.5666 | 5332417.2061 | 5873105.2005 | 6494721.6778 | 7250394.8946 | 8010773.3652 | 8717214.8031 | 9464304.0188 | 10280699.3876 | 11132072.7363 | 11859457.7468 | 12867252.9786 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 4 | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Cost of EUE ($) - Option 4 | 3277760.4222 | 3718448.0103 | 4817164.5666 | 5332417.2061 | 5873105.2005 | 6494721.6778 | 7250394.8946 | 8010773.3652 | 8717214.8031 | 9464304.0188 | 10280699.3876 | 11132072.7363 | 11859457.7468 | 12867252.9786 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 86.9159 | 98.6015 | 127.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 5 | 86.9159 | 98.6015 | 127.736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of EUE ($) - Option 5 | 3277760.4222 | 3718448.0103 | 4817164.5666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 74.6417 | 84.7959 | 110.1691 | 122.0953 | 134.5378 | 148.9608 | 166.5993 | 184.3113 | 200.4876 | 217.7793 | 236.6113 | 256.3663 | 272.7872 | 296.5803 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 6 | 74.6417 | 84.7959 | 110.1691 | 122.0953 | 134.5378 | 148.9608 | 166.5993 | 184.3113 | 200.4876 | 217.7793 | 236.6113 | 256.3663 | 272.7872 | 296.5803 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841 | 314.841
Cost of EUE ($) - Option 6 | 2814877.2986 | 3197810.6198 | 4154681.2323 | 4604441.1505 | 5073671.6094 | 5617589.6585 | 6282769.8594 | 6950722.3729 | 7560760.6784 | 8212864.9335 | 8923054.5399 | 9668053.1901 | 10287313.5965 | 11184595.3285 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182 | 11873242.5182
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 7 | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Cost of EUE ($) - Option 7 | 3277760.4222 | 3718448.0103 | 4817164.5666 | 5332417.2061 | 5873105.2005 | 6494721.6778 | 7250394.8946 | 8010773.3652 | 8717214.8031 | 9464304.0188 | 10280699.3876 | 11132072.7363 | 11859457.7468 | 12867252.9786 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 8 | 86.9159 | 98.6015 | 127.736 | 141.3989 | 155.7363 | 172.2196 | 192.2577 | 212.4205 | 231.1531 | 250.9636 | 272.6118 | 295.1875 | 314.4755 | 341.1991 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565 | 362.5565
Cost of EUE ($) - Option 8 | 3277760.4222 | 3718448.0103 | 4817164.5666 | 5332417.2061 | 5873105.2005 | 6494721.6778 | 7250394.8946 | 8010773.3652 | 8717214.8031 | 9464304.0188 | 10280699.3876 | 11132072.7363 | 11859457.7468 | 12867252.9786 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322 | 13672682.2322