## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 34378474.2948 | 37.17% | 18.2965
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 31576189.3656 | 34.14% | 11.7393
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 10621047.2058 | 11.48% | 3.8453
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 15925855.934 | 17.22% | 3.8307
[5 empty] | 92501566.8003 |  | 37.7119
Customer No. and Vol per Feeder | [6 empty] | 37711.8651 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 31576189.3656 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 211.4834 | E@R MWh | 211.4834
RESIDENTL | 34378474.2948 | [14 empty] | cost of EUE ($) | 7975434.384 | cost of EUE ($M) | 7.9754
FARM | 15925855.934
INDUSTRIAL | 10621047.2058
Forecast (FCT)
Forecast | 2031
Summer POE50 | 34.7177
Summer POE10 | 36.9452
Winter POE50 | 33.3768
Winter POE10 | 35.8525
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 0 |  | Summer POE50 | 34.7177 |  |  | 100% | 0 | 34.7177 | 100% |  | 0% |  | 0%
|  |  | Summer POE10 | 36.9452 |  |  | 99% | 0.37816 | 34.3705 | 99% |  | 0% | 13.0634 | 0% | 13.0634
Embedded Generation |  |  | Winter POE50 | 33.3768 |  |  | 98% | 0.37816 | 34.0234 | 98% |  | 0% | 0 | 0% | 0
|  |  | Winter POE10 | 35.8525 |  |  | 97% | 0.75633 | 33.6762 | 97% |  | 0% | 12.8008 | 0% | 12.8008
Year | 2031 | [5 empty] | 95% | 0.75633 | 32.9818 | 95% |  | 0% | 0 | 0% | 0
Capacity | 0 | [5 empty] | 90% | 3.7816 | 31.2459 | 90% |  | 0% | 97.1546 | 0% | 97.1546
[7 empty] | 85% | 13.6139 | 29.5101 | 85% |  | 0% | 298.6848 | 0% | 298.6848
Demand Mangement | [6 empty] | 80% | 35.1693 | 27.7742 | 80% |  | 0% | 617.3913 | 0% | 617.3913
[7 empty] | 75% | 80.549 | 26.0383 | 75% |  | 0% | 1220.9972 | 0% | 1220.9972
Year | 2031 | [5 empty] | 70% | 192.1075 | 24.3024 | 70% |  | 0% | 2807.9654 | 0% | 2807.9654
Capacity | 0 | [5 empty] | 65% | 403.1231 | 22.5665 | 65% |  | 0% | 4945.0388 | 0% | 4945.0388
[7 empty] | 60% | 739.3112 | 20.8306 | 60% |  | 0% | 7294.802 | 0% | 7294.802
LDC | [6 empty] | 55% | 1204.8314 | 19.0947 | 55% |  | 0% | 9293.0361 | 0% | 9293.0361
[7 empty] | 50% | 1783.0446 | 17.3589 | 50% |  | 0% | 10538.9785 | 0% | 10538.9785
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2370.3337 | 15.623 | 45% |  | 0% | 9684.9369 | 0% | 9684.9369
100% | 0% | 0 |  |  |  |  | 40% | 2864.2163 | 13.8871 | 40% |  | 0% | 7287.2528 | 0% | 7287.2528
99% | 0.00861% | 0.37816 |  |  |  |  | 35% | 3297.9707 | 12.1512 | 35% |  | 0% | 5647.1122 | 0% | 5647.1122
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3579.7031 | 10.4153 | 30% |  | 0% | 3178.8597 | 0% | 3178.8597
97% | 0.01722% | 0.75633 |  |  |  |  | 25% | 3796.3913 | 8.6794 | 25% |  | 0% | 2068.8026 | 0% | 2068.8026
95% | 0.01722% | 0.75633 |  |  |  |  | 20% | 3975.6411 | 6.9435 | 20% |  | 0% | 1400.2081 | 0% | 1400.2081
90% | 0.0861% | 3.7816 |  |  |  |  | 15% | 4117.4527 | 5.2077 | 15% |  | 0% | 861.5908 | 0% | 861.5908
85% | 0.31% | 13.6139 |  |  |  |  | 10% | 4224.8514 | 3.4718 | 10% |  | 0% | 466.0796 | 0% | 466.0796
80% | 0.8008% | 35.1693 |  |  |  |  | 5% | 4310.3165 | 1.7359 | 5% |  | 0% | 222.5366 | 0% | 222.5366
75% | 1.834% | 80.549 |  |  |  |  | 9.992e-14% | 4382.5459 | 3.469e-14 | 9.992e-14% |  | 0% | 62.691 | 0% | 62.691
70% | 4.374% | 192.1075 | [7 empty] | Total E@R | 0 | Total E@R | 67339.7831 | Total E@R | 67339.7831
65% | 9.179% | 403.1231 | [7 empty] | Total WE@R | 0 | Total WE@R | 73.4079 | Total WE@R | 0
60% | 16.83% | 739.3112 |  |  |  |  | MD Weighted LDC
55% | 27.43% | 1204.8314
50% | 40.6% | 1783.0446 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 53.97% | 2370.3337 |  |  |  |  | 100% | 0 | 36.9452 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 65.21% | 2864.2163 |  |  |  |  | 99% | 1.1345 | 36.5757
35% | 75.09% | 3297.9707 |  |  |  |  | 98% | 1.8908 | 36.2063 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 81.51% | 3579.7031 |  |  |  |  | 97% | 2.269 | 35.8368 | 100% |  | 0% |  | 0%
25% | 86.44% | 3796.3913 |  |  |  |  | 95% | 4.1598 | 35.0979 | 99% |  | 0% | 41.7045 | 0% | 41.7045
20% | 90.52% | 3975.6411 |  |  |  |  | 90% | 15.5047 | 33.2507 | 98% |  | 0% | 27.5235 | 0% | 27.5235
15% | 93.75% | 4117.4527 |  |  |  |  | 85% | 31.3876 | 31.4034 | 97% |  | 0% | 13.6221 | 0% | 13.6221
10% | 96.19% | 4224.8514 |  |  |  |  | 80% | 57.8591 | 29.5561 | 95% |  | 0% | 67.0625 | 0% | 67.0625
5% | 98.14% | 4310.3165 |  |  |  |  | 75% | 121.3907 | 27.7089 | 90% |  | 0% | 387.7048 | 0% | 387.7048
9.992e-14% | 99.78% | 4382.5459 |  |  |  |  | 70% | 273.4128 | 25.8616 | 85% |  | 0% | 513.4469 | 0% | 513.4469
[7 empty] | 65% | 529.43 | 24.0144 | 80% |  | 0% | 806.8452 | 0% | 806.8452
[7 empty] | 60% | 918.9392 | 22.1671 | 75% |  | 0% | 1819.0691 | 0% | 1819.0691
[7 empty] | 55% | 1454.0417 | 20.3198 | 70% |  | 0% | 4071.9485 | 0% | 4071.9485
LDC | [6 empty] | 50% | 2105.2406 | 18.4726 | 65% |  | 0% | 6384.5554 | 0% | 6384.5554
[7 empty] | 45% | 2758.3303 | 16.6253 | 60% |  | 0% | 8994.0533 | 0% | 8994.0533
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 3348.2666 | 14.7781 | 55% |  | 0% | 11367.4355 | 0% | 11367.4355
100% | 0% | 0 |  |  |  |  | 35% | 3816.434 | 12.9308 | 50% |  | 0% | 12630.7944 | 0% | 12630.7944
99% | 0.02583% | 1.1345 |  |  |  |  | 30% | 4067.1569 | 11.0836 | 45% |  | 0% | 11461.0435 | 0% | 11461.0435
98% | 0.04305% | 1.8908 |  |  |  |  | 25% | 4236.9526 | 9.2363 | 40% |  | 0% | 9263.0017 | 0% | 9263.0017
97% | 0.05166% | 2.269 |  |  |  |  | 20% | 4332.6282 | 7.389 | 35% |  | 0% | 6486.1969 | 0% | 6486.1969
95% | 0.09471% | 4.1598 |  |  |  |  | 15% | 4361.7469 | 5.5418 | 30% |  | 0% | 3010.4755 | 0% | 3010.4755
90% | 0.353% | 15.5047 |  |  |  |  | 10% | 4375.7389 | 3.6945 | 25% |  | 0% | 1725.1118 | 0% | 1725.1118
85% | 0.7147% | 31.3876 |  |  |  |  | 5% | 4378.0079 | 1.8473 | 20% |  | 0% | 795.3188 | 0% | 795.3188
80% | 1.317% | 57.8591 |  |  |  |  | 9.992e-14% | 4379.1424 | 3.6916e-14 | 15% |  | 0% | 188.2639 | 0% | 188.2639
75% | 2.764% | 121.3907 | [7 empty] | 10% |  | 0% | 64.6175 | 0% | 64.6175
70% | 6.225% | 273.4128 | [7 empty] | 5% |  | 0% | 6.2871 | 0% | 6.2871
65% | 12.05% | 529.43 | [7 empty] | 9.992e-14% |  | 0% | 1.0479 | 0% | 1.0479
60% | 20.92% | 918.9392 | [7 empty] | Total E@R | 0 | Total E@R | 79325.8589 | Total E@R | 79325.8589
55% | 33.11% | 1454.0417 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 37.0603 | Total WE@R | 0
50% | 47.93% | 2105.2406
45% | 62.8% | 2758.3303 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 76.24% | 3348.2666 |  |  |  |  | 100% | 0 | 33.3768
35% | 86.9% | 3816.434 |  |  |  |  | 99% | 0.2972 | 33.0431 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 92.6% | 4067.1569 |  |  |  |  | 98% | 0.8916 | 32.7093
25% | 96.47% | 4236.9526 |  |  |  |  | 97% | 1.7832 | 32.3755 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 98.65% | 4332.6282 |  |  |  |  | 95% | 4.458 | 31.708 | 100% |  | 0% |  | 0%
15% | 99.31% | 4361.7469 |  |  |  |  | 90% | 15.1571 | 30.0392 | 99% |  | 0% | 9.8699 | 0% | 9.8699
10% | 99.63% | 4375.7389 |  |  |  |  | 85% | 39.5274 | 28.3703 | 98% |  | 0% | 19.5415 | 0% | 19.5415
5% | 99.68% | 4378.0079 |  |  |  |  | 80% | 110.5579 | 26.7015 | 97% |  | 0% | 29.0147 | 0% | 29.0147
9.992e-14% | 99.71% | 4379.1424 |  |  |  |  | 75% | 244.2972 | 25.0326 | 95% |  | 0% | 85.7049 | 0% | 85.7049
[7 empty] | 70% | 444.0146 | 23.3638 | 90% |  | 0% | 330.3209 | 0% | 330.3209
[7 empty] | 65% | 770.3386 | 21.6949 | 85% |  | 0% | 711.7275 | 0% | 711.7275
[7 empty] | 60% | 1209.3009 | 20.0261 | 80% |  | 0% | 1955.8867 | 0% | 1955.8867
LDC | [6 empty] | 55% | 1757.6322 | 18.3573 | 75% |  | 0% | 3459.442 | 0% | 3459.442
[7 empty] | 50% | 2378.4799 | 16.6884 | 70% |  | 0% | 4832.8033 | 0% | 4832.8033
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 3003.7856 | 15.0196 | 65% |  | 0% | 7351.8723 | 0% | 7351.8723
100% | 0% | 0 |  |  |  |  | 40% | 3548.2533 | 13.3507 | 60% |  | 0% | 9156.9819 | 0% | 9156.9819
99% | 0.006767% | 0.2972 |  |  |  |  | 35% | 3927.7759 | 11.6819 | 55% |  | 0% | 10523.3995 | 0% | 10523.3995
98% | 0.0203% | 0.8916 |  |  |  |  | 30% | 4135.8149 | 10.0131 | 50% |  | 0% | 10879.0152 | 0% | 10879.0152
97% | 0.0406% | 1.7832 |  |  |  |  | 25% | 4252.0195 | 8.3442 | 45% |  | 0% | 9913.5953 | 0% | 9913.5953
95% | 0.1015% | 4.458 |  |  |  |  | 20% | 4325.4275 | 6.6754 | 40% |  | 0% | 7723.3593 | 0% | 7723.3593
90% | 0.3451% | 15.1571 |  |  |  |  | 15% | 4360.497 | 5.0065 | 35% |  | 0% | 4750.2231 | 0% | 4750.2231
85% | 0.9% | 39.5274 |  |  |  |  | 10% | 4373.8709 | 3.3377 | 30% |  | 0% | 2256.697 | 0% | 2256.697
80% | 2.517% | 110.5579 |  |  |  |  | 5% | 4381.8952 | 1.6688 | 25% |  | 0% | 1066.5993 | 0% | 1066.5993
75% | 5.562% | 244.2972 |  |  |  |  | 9.992e-14% | 4391.7028 | 3.335e-14 | 20% |  | 0% | 551.2788 | 0% | 551.2788
70% | 10.11% | 444.0146 | [7 empty] | 15% |  | 0% | 204.8386 | 0% | 204.8386
65% | 17.54% | 770.3386 | [7 empty] | 10% |  | 0% | 55.7975 | 0% | 55.7975
60% | 27.53% | 1209.3009 | [7 empty] | 5% |  | 0% | 20.0871 | 0% | 20.0871
55% | 40.02% | 1757.6322 | [7 empty] | 9.992e-14% |  | 0% | 8.1836 | 0% | 8.1836
50% | 54.15% | 2378.4799 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 75137.2775 | Total E@R | 75137.2775
45% | 68.39% | 3003.7856 | [7 empty] | Total WE@R | 0 | Total WE@R | 69.591 | Total WE@R | 0
40% | 80.79% | 3548.2533 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 89.43% | 3927.7759 |  |  |  |  | 100% | 0 | 35.8525 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 94.17% | 4135.8149 |  |  |  |  | 99% | 0.2972 | 35.494
25% | 96.81% | 4252.0195 |  |  |  |  | 98% | 0.8916 | 35.1355 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 98.48% | 4325.4275 |  |  |  |  | 97% | 2.0804 | 34.777 | 100% |  | 100% |  | 100%
15% | 99.28% | 4360.497 |  |  |  |  | 95% | 4.1608 | 34.0599 | 99% |  | 99% | 10.602 | 99% | 10.602
10% | 99.59% | 4373.8709 |  |  |  |  | 90% | 11.5907 | 32.2673 | 98% |  | 98% | 20.991 | 98% | 20.991
5% | 99.77% | 4381.8952 |  |  |  |  | 85% | 32.6918 | 30.4747 | 97% |  | 97% | 41.5557 | 97% | 41.5557
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 84.1072 | 28.682 | 95% |  | 95% | 71.6037 | 95% | 71.6037
[7 empty] | 75% | 202.095 | 26.8894 | 90% |  | 90% | 246.4043 | 90% | 246.4043
[7 empty] | 70% | 388.1413 | 25.0968 | 85% |  | 85% | 661.9617 | 85% | 661.9617
[7 empty] | 65% | 669.8855 | 23.3041 | 80% |  | 80% | 1520.7805 | 80% | 1520.7805
LDC | [6 empty] | 60% | 1104.687 | 21.5115 | 75% |  | 75% | 3278.3755 | 75% | 3278.3755
[7 empty] | 55% | 1631.62 | 19.7189 | 70% |  | 70% | 4835.9168 | 70% | 4835.9168
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 2253.9537 | 17.9263 | 65% |  | 65% | 6818.3391 | 65% | 6818.3391
100% | 0% | 0 |  |  |  |  | 45% | 2892.3362 | 16.1336 | 60% |  | 60% | 9742.9579 | 60% | 9742.9579
99% | 0.006767% | 0.2972 |  |  |  |  | 40% | 3473.3593 | 14.341 | 55% |  | 55% | 10862.832 | 55% | 10862.832
98% | 0.0203% | 0.8916 |  |  |  |  | 35% | 3882.8989 | 12.5484 | 50% |  | 50% | 11713.9257 | 50% | 11713.9257
97% | 0.04737% | 2.0804 |  |  |  |  | 30% | 4127.1961 | 10.7558 | 45% |  | 45% | 10871.6227 | 45% | 10871.6227
95% | 0.09474% | 4.1608 |  |  |  |  | 25% | 4245.1839 | 8.9631 | 40% |  | 40% | 8853.2387 | 40% | 8853.2387
90% | 0.2639% | 11.5907 |  |  |  |  | 20% | 4322.1583 | 7.1705 | 35% |  | 35% | 5506.1364 | 35% | 5506.1364
85% | 0.7443% | 32.6918 |  |  |  |  | 15% | 4354.2558 | 5.3779 | 30% |  | 30% | 2846.5687 | 30% | 2846.5687
80% | 1.915% | 84.1072 |  |  |  |  | 10% | 4366.1437 | 3.5853 | 25% |  | 25% | 1163.2945 | 25% | 1163.2945
75% | 4.601% | 202.095 |  |  |  |  | 5% | 4374.4653 | 1.7926 | 20% |  | 20% | 620.9388 | 20% | 620.9388
70% | 8.837% | 388.1413 |  |  |  |  | 9.992e-14% | 4375.9513 | 3.5824e-14 | 15% |  | 15% | 201.3855 | 15% | 201.3855
65% | 15.25% | 669.8855 | [7 empty] | 10% |  | 10% | 53.2766 | 10% | 53.2766
60% | 25.15% | 1104.687 | [7 empty] | 5% |  | 5% | 22.3762 | 5% | 22.3762
55% | 37.15% | 1631.62 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 1.3319 | 9.992e-14% | 1.3319
50% | 51.32% | 2253.9537 | [7 empty] | Total E@R | 0 | Total E@R | 79166.7518 | Total E@R | 79166.7518
45% | 65.85% | 2892.3362 | [7 empty] | Total WE@R | 0 | Total WE@R | 31.4242 | Total WE@R | 0
40% | 79.08% | 3473.3593
35% | 88.41% | 3882.8989
30% | 93.97% | 4127.1961
25% | 96.66% | 4245.1839
20% | 98.41% | 4322.1583
15% | 99.14% | 4354.2558
10% | 99.41% | 4366.1437
5% | 99.6% | 4374.4653
9.992e-14% | 99.63% | 4375.9513
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 47.4 |  |  | Year | 2031
SCR (N-1) | 0 |  |  | SCR (N) | 47.4
SCR (N-2) | 0 |  |  | SCR (N-1) | 0
WCR (N) | 48.3 |  |  | SCR (N-2) | 0
WCR (N-1) | 0 |  |  | WCR (N) | 48.3
WCR (N-2) | 0 |  |  | WCR (N-1) | 0
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 0.99
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 3.6123 | 4.0903 | 5.2989 | 5.8657 | 6.4604 | 7.1442 | 7.9754 | 8.8119 | 9.5889 | 10.4107 | 11.3088 | 12.2453 | 13.0454 | 14.154 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04
Total EUE (MWh) | 95.7866 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Residual Values
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.6055 | 4.0903 | 5.2989 | 5.8657 | 6.4604 | 7.1442 | 7.9754 | 8.8119 | 9.5889 | 10.4107 | 11.3088 | 12.2453 | 13.0454 | 14.154 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04
Total EUE (MWh) | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.6055 | 4.0903 | 5.2989 | 5.8657 | 6.4604 | 7.1442 | 7.9754 | 8.8119 | 9.5889 | 10.4107 | 11.3088 | 12.2453 | 13.0454 | 14.154 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04
Total EUE (MWh) | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.6055 | 4.0903 | 5.2989 | 5.8657 | 6.4604 | 7.1442 | 7.9754 | 8.8119 | 9.5889 | 10.4107 | 11.3088 | 12.2453 | 13.0454 | 14.154 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04
Total EUE (MWh) | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.6055 | 4.0903 | 5.2989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | 95.6075 | 108.4617 | 140.5097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.6055 | 4.0903 | 5.2989 | 5.8657 | 6.4604 | 7.1442 | 7.9754 | 8.8119 | 9.5889 | 10.4107 | 11.3088 | 12.2453 | 13.0454 | 14.154 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04
Total EUE (MWh) | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.6055 | 4.0903 | 5.2989 | 5.8657 | 6.4604 | 7.1442 | 7.9754 | 8.8119 | 9.5889 | 10.4107 | 11.3088 | 12.2453 | 13.0454 | 14.154 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04
Total EUE (MWh) | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 3.6055 | 4.0903 | 5.2989 | 5.8657 | 6.4604 | 7.1442 | 7.9754 | 8.8119 | 9.5889 | 10.4107 | 11.3088 | 12.2453 | 13.0454 | 14.154 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04 | 15.04
Total EUE (MWh) | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122

## Key Model Assumption & Inputs
Select ZSS & Region | LLG | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
High | 110% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1B New PHS ZSS + Three new feeders | 1B New PHS ZSS + Three new feeders
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N |  |  |  | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Added Capacity (MVA) Option 5 N-1 |  |  |  | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | LLG
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234
Summer POE10 | 10 |  |  | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709
Winter POE10 | 10 |  |  | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | LLG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | PowerFactor | 0.99

## Load Duration Curves
Station
LLG
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0.02583% | 1.1345 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.04305% | 1.8908 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.04737% | 2.0804 | 0.05166% | 2.269 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.09474% | 4.1608 | 0.09471% | 4.1598 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.2639% | 11.5907 | 0.353% | 15.5047 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 0.7443% | 32.6918 | 0.7147% | 31.3876 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 1.915% | 84.1072 | 1.317% | 57.8591 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 4.601% | 202.095 | 2.764% | 121.3907 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 8.837% | 388.1413 | 6.225% | 273.4128 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 15.25% | 669.8855 | 12.05% | 529.43 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 25.15% | 1104.687 | 20.92% | 918.9392 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 37.15% | 1631.62 | 33.11% | 1454.0417 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 51.32% | 2253.9537 | 47.93% | 2105.2406 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 65.85% | 2892.3362 | 62.8% | 2758.3303 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 79.08% | 3473.3593 | 76.24% | 3348.2666 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 88.41% | 3882.8989 | 86.9% | 3816.434 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 93.97% | 4127.1961 | 92.6% | 4067.1569 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 96.66% | 4245.1839 | 96.47% | 4236.9526 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 98.41% | 4322.1583 | 98.65% | 4332.6282 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.14% | 4354.2558 | 99.31% | 4361.7469 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.41% | 4366.1437 | 99.63% | 4375.7389 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.6% | 4374.4653 | 99.68% | 4378.0079 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.63% | 4375.9513 | 99.71% | 4379.1424 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.0406% | 1.7832 | 0.01722% | 0.75633 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.1015% | 4.458 | 0.01722% | 0.75633 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.3451% | 15.1571 | 0.0861% | 3.7816 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 0.9% | 39.5274 | 0.31% | 13.6139 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 2.517% | 110.5579 | 0.8008% | 35.1693 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 5.562% | 244.2972 | 1.834% | 80.549 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 10.11% | 444.0146 | 4.374% | 192.1075 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 17.54% | 770.3386 | 9.179% | 403.1231 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 27.53% | 1209.3009 | 16.83% | 739.3112 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 40.02% | 1757.6322 | 27.43% | 1204.8314 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 54.15% | 2378.4799 | 40.6% | 1783.0446 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 68.39% | 3003.7856 | 53.97% | 2370.3337 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 80.79% | 3548.2533 | 65.21% | 2864.2163 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 89.43% | 3927.7759 | 75.09% | 3297.9707 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 94.17% | 4135.8149 | 81.51% | 3579.7031 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 96.81% | 4252.0195 | 86.44% | 3796.3913 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 98.48% | 4325.4275 | 90.52% | 3975.6411 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.28% | 4360.497 | 93.75% | 4117.4527 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.59% | 4373.8709 | 96.19% | 4224.8514 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.77% | 4381.8952 | 98.14% | 4310.3165 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.78% | 4382.5459 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 1 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 2 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 3 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 48.3 | 48.3 | 48.3 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 5 | 47.4 | 47.4 | 47.4 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8
Capacity Added (MVA) | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 6 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 7 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 8 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
SCR N-1 Rating (MVA) - Option 5 | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608
Maximum Demand (MVA) - P10 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957
Maximum Demand (MVA) - P10 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
Option 2 - 1B New PHS ZSS + Three new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 100% | 0 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
99% | 0.2972 | 22.4049 | 26.0444 | 30.9709 | 31.407 | 31.6987 | 32.1087 | 33.0431 | 33.7767 | 34.4291 | 34.658 | 34.9194 | 34.5539 | 34.7466 | 35.6527 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 99% | 0.2972 | 24.7971 | 28.4474 | 33.4137 | 33.8124 | 34.0926 | 34.3812 | 35.494 | 36.1445 | 36.8097 | 37.1123 | 37.2714 | 36.7195 | 37.0077 | 38.1136 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932
98% | 0.8916 | 22.1786 | 25.7814 | 30.6581 | 31.0897 | 31.3785 | 31.7844 | 32.7093 | 33.4356 | 34.0814 | 34.3079 | 34.5667 | 34.2049 | 34.3957 | 35.2926 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 98% | 0.8916 | 24.5466 | 28.16 | 33.0761 | 33.4708 | 33.7483 | 34.0339 | 35.1355 | 35.7794 | 36.4379 | 36.7375 | 36.8949 | 36.3486 | 36.6338 | 37.7286 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135
97% | 1.7832 | 21.9523 | 25.5183 | 30.3452 | 30.7725 | 31.0583 | 31.46 | 32.3755 | 33.0944 | 33.7336 | 33.9578 | 34.214 | 33.8558 | 34.0447 | 34.9324 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 97% | 2.0804 | 24.2962 | 27.8727 | 32.7386 | 33.1293 | 33.4039 | 33.6866 | 34.777 | 35.4143 | 36.0661 | 36.3626 | 36.5184 | 35.9777 | 36.26 | 37.3436 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338
95% | 4.458 | 21.4996 | 24.9921 | 29.7196 | 30.138 | 30.4179 | 30.8114 | 31.708 | 32.412 | 33.038 | 33.2576 | 33.5085 | 33.1578 | 33.3427 | 34.2122 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 95% | 4.1608 | 23.7952 | 27.298 | 32.0636 | 32.4462 | 32.7152 | 32.9921 | 34.0599 | 34.6841 | 35.3225 | 35.6129 | 35.7655 | 35.2359 | 35.5124 | 36.5736 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743
90% | 15.1571 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 90% | 11.5907 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
85% | 39.5274 | 19.2365 | 22.3614 | 26.5912 | 26.9656 | 27.216 | 27.5681 | 28.3703 | 29.0002 | 29.5604 | 29.7568 | 29.9813 | 29.6675 | 29.833 | 30.6109 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 85% | 32.6918 | 21.2905 | 24.4245 | 28.6885 | 29.0308 | 29.2715 | 29.5192 | 30.4747 | 31.0331 | 31.6043 | 31.8641 | 32.0007 | 31.5268 | 31.7743 | 32.7238 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277
80% | 110.5579 | 18.105 | 21.046 | 25.027 | 25.3794 | 25.6151 | 25.9464 | 26.7015 | 27.2943 | 27.8215 | 28.0064 | 28.2177 | 27.9223 | 28.0781 | 28.8103 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 80% | 84.1072 | 20.0381 | 22.9878 | 27.0009 | 27.3231 | 27.5496 | 27.7828 | 28.682 | 29.2076 | 29.7452 | 29.9898 | 30.1183 | 29.6723 | 29.9052 | 30.7988 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784
75% | 244.2972 | 16.9734 | 19.7306 | 23.4628 | 23.7932 | 24.0141 | 24.3248 | 25.0326 | 25.5884 | 26.0827 | 26.256 | 26.4541 | 26.1772 | 26.3232 | 27.0096 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 75% | 202.095 | 18.7857 | 21.5511 | 25.3134 | 25.6154 | 25.8278 | 26.0464 | 26.8894 | 27.3822 | 27.8862 | 28.1154 | 28.2359 | 27.8178 | 28.0361 | 28.8739 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797
70% | 444.0146 | 15.8418 | 18.4153 | 21.8986 | 22.207 | 22.4132 | 22.7031 | 23.3638 | 23.8825 | 24.3438 | 24.5056 | 24.6905 | 24.432 | 24.5683 | 25.209 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 70% | 388.1413 | 17.5333 | 20.1143 | 23.6258 | 23.9077 | 24.1059 | 24.31 | 25.0968 | 25.5567 | 26.0271 | 26.2411 | 26.3535 | 25.9633 | 26.167 | 26.949 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811
65% | 770.3386 | 14.7103 | 17.0999 | 20.3344 | 20.6207 | 20.8122 | 21.0815 | 21.6949 | 22.1767 | 22.605 | 22.7552 | 22.9269 | 22.6869 | 22.8135 | 23.4083 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 65% | 669.8855 | 16.2809 | 18.6776 | 21.9383 | 22.2001 | 22.3841 | 22.5735 | 23.3041 | 23.7312 | 24.168 | 24.3667 | 24.4711 | 24.1088 | 24.298 | 25.0241 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824
60% | 1209.3009 | 13.5787 | 15.7845 | 18.7703 | 19.0345 | 19.2113 | 19.4598 | 20.0261 | 20.4708 | 20.8661 | 21.0048 | 21.1633 | 20.9417 | 21.0586 | 21.6077 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 60% | 1104.687 | 15.0286 | 17.2408 | 20.2507 | 20.4924 | 20.6622 | 20.8371 | 21.5115 | 21.9057 | 22.3089 | 22.4923 | 22.5887 | 22.2542 | 22.4289 | 23.0991 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838
55% | 1757.6322 | 12.4472 | 14.4691 | 17.2061 | 17.4483 | 17.6104 | 17.8382 | 18.3573 | 18.7649 | 19.1273 | 19.2544 | 19.3997 | 19.1966 | 19.3037 | 19.8071 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 55% | 1631.62 | 13.7762 | 15.8041 | 18.5631 | 18.7847 | 18.9404 | 19.1007 | 19.7189 | 20.0803 | 20.4498 | 20.618 | 20.7063 | 20.3997 | 20.5598 | 21.1742 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851
50% | 2378.4799 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 50% | 2253.9537 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
45% | 3003.7856 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 45% | 2892.3362 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
40% | 3548.2533 | 9.0525 | 10.523 | 12.5135 | 12.6897 | 12.8075 | 12.9732 | 13.3507 | 13.6472 | 13.9108 | 14.0032 | 14.1089 | 13.9612 | 14.0391 | 14.4051 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 40% | 3473.3593 | 10.019 | 11.4939 | 13.5005 | 13.6616 | 13.7748 | 13.8914 | 14.341 | 14.6038 | 14.8726 | 14.9949 | 15.0592 | 14.8362 | 14.9526 | 15.3994 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892
35% | 3927.7759 | 7.9209 | 9.2076 | 10.9493 | 11.1035 | 11.2066 | 11.3516 | 11.6819 | 11.9413 | 12.1719 | 12.2528 | 12.3453 | 12.216 | 12.2842 | 12.6045 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 35% | 3882.8989 | 8.7667 | 10.0572 | 11.8129 | 11.9539 | 12.053 | 12.155 | 12.5484 | 12.7783 | 13.0135 | 13.1205 | 13.1768 | 12.9816 | 13.0835 | 13.4745 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905
30% | 4135.8149 | 6.7894 | 7.8923 | 9.3851 | 9.5173 | 9.6057 | 9.7299 | 10.0131 | 10.2354 | 10.4331 | 10.5024 | 10.5816 | 10.4709 | 10.5293 | 10.8038 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 30% | 4127.1961 | 7.5143 | 8.6204 | 10.1253 | 10.2462 | 10.3311 | 10.4186 | 10.7558 | 10.9529 | 11.1545 | 11.2462 | 11.2944 | 11.1271 | 11.2144 | 11.5496 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919
25% | 4252.0195 | 5.6578 | 6.5769 | 7.8209 | 7.9311 | 8.0047 | 8.1083 | 8.3442 | 8.5295 | 8.6942 | 8.752 | 8.818 | 8.7257 | 8.7744 | 9.0032 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 25% | 4245.1839 | 6.2619 | 7.1837 | 8.4378 | 8.5385 | 8.6093 | 8.6821 | 8.9631 | 9.1274 | 9.2954 | 9.3718 | 9.412 | 9.2726 | 9.3454 | 9.6246 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932
20% | 4325.4275 | 4.5262 | 5.2615 | 6.2568 | 6.3448 | 6.4038 | 6.4866 | 6.6754 | 6.8236 | 6.9554 | 7.0016 | 7.0544 | 6.9806 | 7.0195 | 7.2026 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 20% | 4322.1583 | 5.0095 | 5.7469 | 6.7502 | 6.8308 | 6.8874 | 6.9457 | 7.1705 | 7.3019 | 7.4363 | 7.4974 | 7.5296 | 7.4181 | 7.4763 | 7.6997 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946
15% | 4360.497 | 3.3947 | 3.9461 | 4.6926 | 4.7586 | 4.8028 | 4.865 | 5.0065 | 5.1177 | 5.2165 | 5.2512 | 5.2908 | 5.2354 | 5.2646 | 5.4019 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 15% | 4354.2558 | 3.7571 | 4.3102 | 5.0627 | 5.1231 | 5.1656 | 5.2093 | 5.3779 | 5.4764 | 5.5772 | 5.6231 | 5.6472 | 5.5636 | 5.6072 | 5.7748 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959
10% | 4373.8709 | 2.2631 | 2.6308 | 3.1284 | 3.1724 | 3.2019 | 3.2433 | 3.3377 | 3.4118 | 3.4777 | 3.5008 | 3.5272 | 3.4903 | 3.5098 | 3.6013 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 10% | 4366.1437 | 2.5048 | 2.8735 | 3.3751 | 3.4154 | 3.4437 | 3.4729 | 3.5853 | 3.651 | 3.7182 | 3.7487 | 3.7648 | 3.709 | 3.7381 | 3.8499 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973
5% | 4381.8952 | 1.1316 | 1.3154 | 1.5642 | 1.5862 | 1.6009 | 1.6217 | 1.6688 | 1.7059 | 1.7388 | 1.7504 | 1.7636 | 1.7451 | 1.7549 | 1.8006 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 5% | 4374.4653 | 1.2524 | 1.4367 | 1.6876 | 1.7077 | 1.7219 | 1.7364 | 1.7926 | 1.8255 | 1.8591 | 1.8744 | 1.8824 | 1.8545 | 1.8691 | 1.9249 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986
9.992e-14% | 4391.7028 | 2.2613e-14 | 2.6286e-14 | 3.1259e-14 | 3.1699e-14 | 3.1993e-14 | 3.2407e-14 | 3.335e-14 | 3.4091e-14 | 3.4749e-14 | 3.498e-14 | 3.5244e-14 | 3.4875e-14 | 3.507e-14 | 3.5984e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 9.992e-14% | 4375.9513 | 2.5028e-14 | 2.8712e-14 | 3.3724e-14 | 3.4127e-14 | 3.4409e-14 | 3.4701e-14 | 3.5824e-14 | 3.648e-14 | 3.7152e-14 | 3.7457e-14 | 3.7618e-14 | 3.7061e-14 | 3.7352e-14 | 3.8468e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 100% | 0 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
99% | 0.37816 | 25.6004 | 28.4203 | 33.1682 | 33.1325 | 33.1003 | 33.615 | 34.3705 | 34.8883 | 34.259 | 34.3215 | 34.6215 | 35.8093 | 34.6838 | 34.6177 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 99% | 1.1345 | 27.8174 | 31.2882 | 36.0278 | 35.9641 | 36.0059 | 36.1355 | 36.5757 | 36.8706 | 37.1125 | 37.1481 | 37.3662 | 37.4435 | 37.4433 | 37.3934 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828
98% | 0.37816 | 25.3418 | 28.1332 | 32.8331 | 32.7978 | 32.766 | 33.2754 | 34.0234 | 34.5359 | 33.9129 | 33.9749 | 34.2718 | 35.4476 | 34.3335 | 34.268 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 98% | 1.8908 | 27.5364 | 30.9722 | 35.6639 | 35.6008 | 35.6422 | 35.7705 | 36.2063 | 36.4982 | 36.7376 | 36.7729 | 36.9888 | 37.0653 | 37.0651 | 37.0157 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052
97% | 0.75633 | 25.0832 | 27.8462 | 32.4981 | 32.4631 | 32.4316 | 32.9359 | 33.6762 | 34.1835 | 33.5669 | 33.6282 | 33.9221 | 35.0859 | 33.9831 | 33.9184 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 97% | 2.269 | 27.2555 | 30.6561 | 35.3 | 35.2376 | 35.2785 | 35.4055 | 35.8368 | 36.1258 | 36.3627 | 36.3976 | 36.6114 | 36.6871 | 36.6869 | 36.638 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276
95% | 0.75633 | 24.566 | 27.272 | 31.828 | 31.7938 | 31.763 | 32.2568 | 32.9818 | 33.4787 | 32.8748 | 32.9348 | 33.2226 | 34.3625 | 33.2825 | 33.219 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 95% | 4.1598 | 26.6935 | 30.0241 | 34.5721 | 34.511 | 34.5511 | 34.6754 | 35.0979 | 35.3809 | 35.613 | 35.6472 | 35.8565 | 35.9307 | 35.9305 | 35.8826 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724
90% | 3.7816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 90% | 15.5047 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
85% | 13.6139 | 21.9801 | 24.4013 | 28.4777 | 28.4471 | 28.4195 | 28.8613 | 29.5101 | 29.9546 | 29.4143 | 29.468 | 29.7255 | 30.7454 | 29.779 | 29.7223 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 85% | 31.3876 | 23.8836 | 26.8636 | 30.9329 | 30.8783 | 30.9141 | 31.0254 | 31.4034 | 31.6566 | 31.8643 | 31.8948 | 32.0821 | 32.1485 | 32.1483 | 32.1054 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963
80% | 35.1693 | 20.6872 | 22.9659 | 26.8026 | 26.7737 | 26.7478 | 27.1636 | 27.7742 | 28.1926 | 27.684 | 27.7346 | 27.977 | 28.9368 | 28.0273 | 27.9739 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 80% | 57.8591 | 22.4787 | 25.2834 | 29.1134 | 29.0619 | 29.0957 | 29.2004 | 29.5561 | 29.7944 | 29.9899 | 30.0187 | 30.1949 | 30.2574 | 30.2572 | 30.2169 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083
75% | 80.549 | 19.3942 | 21.5305 | 25.1274 | 25.1004 | 25.076 | 25.4659 | 26.0383 | 26.4305 | 25.9538 | 26.0012 | 26.2284 | 27.1283 | 26.2756 | 26.2255 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 75% | 121.3907 | 21.0738 | 23.7032 | 27.2938 | 27.2455 | 27.2772 | 27.3753 | 27.7089 | 27.9323 | 28.1155 | 28.1425 | 28.3078 | 28.3663 | 28.3662 | 28.3283 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203
70% | 192.1075 | 18.1013 | 20.0952 | 23.4522 | 23.427 | 23.4043 | 23.7682 | 24.3024 | 24.6685 | 24.2235 | 24.2678 | 24.4798 | 25.3197 | 24.5239 | 24.4772 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 70% | 273.4128 | 19.6689 | 22.123 | 25.4742 | 25.4292 | 25.4587 | 25.5503 | 25.8616 | 26.0701 | 26.2411 | 26.2663 | 26.4206 | 26.4752 | 26.4751 | 26.4398 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323
65% | 403.1231 | 16.8083 | 18.6598 | 21.7771 | 21.7537 | 21.7325 | 22.0704 | 22.5665 | 22.9065 | 22.4933 | 22.5343 | 22.7313 | 23.5112 | 22.7722 | 22.7288 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 65% | 529.43 | 18.264 | 20.5428 | 23.6546 | 23.6128 | 23.6402 | 23.7253 | 24.0144 | 24.208 | 24.3668 | 24.3902 | 24.5334 | 24.5841 | 24.584 | 24.5512 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443
60% | 739.3112 | 15.5154 | 17.2244 | 20.1019 | 20.0803 | 20.0608 | 20.3727 | 20.8306 | 21.1444 | 20.763 | 20.8009 | 20.9827 | 21.7026 | 21.0205 | 20.9804 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 60% | 918.9392 | 16.859 | 18.9626 | 21.835 | 21.7964 | 21.8218 | 21.9003 | 22.1671 | 22.3458 | 22.4924 | 22.514 | 22.6462 | 22.6931 | 22.6929 | 22.6627 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562
55% | 1204.8314 | 14.2224 | 15.7891 | 18.4268 | 18.4069 | 18.3891 | 18.675 | 19.0947 | 19.3824 | 19.0328 | 19.0675 | 19.2342 | 19.8941 | 19.2688 | 19.2321 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 55% | 1454.0417 | 15.4541 | 17.3823 | 20.0154 | 19.9801 | 20.0033 | 20.0753 | 20.3198 | 20.4837 | 20.618 | 20.6378 | 20.759 | 20.802 | 20.8019 | 20.7741 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682
50% | 1783.0446 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 50% | 2105.2406 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
45% | 2370.3337 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 45% | 2758.3303 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
40% | 2864.2163 | 10.3436 | 11.483 | 13.4013 | 13.3869 | 13.3739 | 13.5818 | 13.8871 | 14.0963 | 13.842 | 13.8673 | 13.9885 | 14.4684 | 14.0137 | 13.987 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 40% | 3348.2666 | 11.2394 | 12.6417 | 14.5567 | 14.531 | 14.5478 | 14.6002 | 14.7781 | 14.8972 | 14.9949 | 15.0093 | 15.0975 | 15.1287 | 15.1286 | 15.1084 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042
35% | 3297.9707 | 9.0506 | 10.0476 | 11.7261 | 11.7135 | 11.7021 | 11.8841 | 12.1512 | 12.3343 | 12.1118 | 12.1339 | 12.2399 | 12.6599 | 12.262 | 12.2386 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 35% | 3816.434 | 9.8344 | 11.0615 | 12.7371 | 12.7146 | 12.7294 | 12.7752 | 12.9308 | 13.0351 | 13.1206 | 13.1332 | 13.2103 | 13.2376 | 13.2375 | 13.2199 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161
30% | 3579.7031 | 7.7577 | 8.6122 | 10.051 | 10.0401 | 10.0304 | 10.1864 | 10.4153 | 10.5722 | 10.3815 | 10.4005 | 10.4914 | 10.8513 | 10.5102 | 10.4902 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 30% | 4067.1569 | 8.4295 | 9.4813 | 10.9175 | 10.8982 | 10.9109 | 10.9501 | 11.0836 | 11.1729 | 11.2462 | 11.257 | 11.3231 | 11.3465 | 11.3465 | 11.3313 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281
25% | 3796.3913 | 6.4647 | 7.1768 | 8.3758 | 8.3668 | 8.3587 | 8.4886 | 8.6794 | 8.8102 | 8.6513 | 8.6671 | 8.7428 | 9.0428 | 8.7585 | 8.7418 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 25% | 4236.9526 | 7.0246 | 7.9011 | 9.0979 | 9.0818 | 9.0924 | 9.1251 | 9.2363 | 9.3108 | 9.3718 | 9.3808 | 9.4359 | 9.4554 | 9.4554 | 9.4428 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401
20% | 3975.6411 | 5.1718 | 5.7415 | 6.7006 | 6.6934 | 6.6869 | 6.7909 | 6.9435 | 7.0481 | 6.921 | 6.9336 | 6.9942 | 7.2342 | 7.0068 | 6.9935 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 20% | 4332.6282 | 5.6197 | 6.3209 | 7.2783 | 7.2655 | 7.2739 | 7.3001 | 7.389 | 7.4486 | 7.4975 | 7.5047 | 7.5487 | 7.5644 | 7.5643 | 7.5542 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521
15% | 4117.4527 | 3.8788 | 4.3061 | 5.0255 | 5.0201 | 5.0152 | 5.0932 | 5.2077 | 5.2861 | 5.1908 | 5.2002 | 5.2457 | 5.4257 | 5.2551 | 5.2451 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 15% | 4361.7469 | 4.2148 | 4.7406 | 5.4588 | 5.4491 | 5.4554 | 5.4751 | 5.5418 | 5.5865 | 5.6231 | 5.6285 | 5.6616 | 5.6733 | 5.6732 | 5.6657 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641
10% | 4224.8514 | 2.5859 | 2.8707 | 3.3503 | 3.3467 | 3.3435 | 3.3955 | 3.4718 | 3.5241 | 3.4605 | 3.4668 | 3.4971 | 3.6171 | 3.5034 | 3.4967 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 10% | 4375.7389 | 2.8098 | 3.1604 | 3.6392 | 3.6327 | 3.637 | 3.65 | 3.6945 | 3.7243 | 3.7487 | 3.7523 | 3.7744 | 3.7822 | 3.7822 | 3.7771 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776
5% | 4310.3165 | 1.2929 | 1.4354 | 1.6752 | 1.6734 | 1.6717 | 1.6977 | 1.7359 | 1.762 | 1.7303 | 1.7334 | 1.7486 | 1.8086 | 1.7517 | 1.7484 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 5% | 4378.0079 | 1.4049 | 1.5802 | 1.8196 | 1.8164 | 1.8185 | 1.825 | 1.8473 | 1.8622 | 1.8744 | 1.8762 | 1.8872 | 1.8911 | 1.8911 | 1.8886 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888
9.992e-14% | 4382.5459 | 2.5838e-14 | 2.8684e-14 | 3.3476e-14 | 3.344e-14 | 3.3408e-14 | 3.3927e-14 | 3.469e-14 | 3.5213e-14 | 3.4577e-14 | 3.4641e-14 | 3.4943e-14 | 3.6142e-14 | 3.5006e-14 | 3.4939e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 9.992e-14% | 4379.1424 | 2.8076e-14 | 3.1579e-14 | 3.6363e-14 | 3.6298e-14 | 3.6341e-14 | 3.6471e-14 | 3.6916e-14 | 3.7213e-14 | 3.7457e-14 | 3.7493e-14 | 3.7714e-14 | 3.7792e-14 | 3.7791e-14 | 3.7741e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 100% | 0 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
99% | 0.2972 | 22.4049 | 26.0444 | 30.9709 | 31.407 | 31.6987 | 32.1087 | 33.0431 | 33.7767 | 34.4291 | 34.658 | 34.9194 | 34.5539 | 34.7466 | 35.6527 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 99% | 0.2972 | 24.7971 | 28.4474 | 33.4137 | 33.8124 | 34.0926 | 34.3812 | 35.494 | 36.1445 | 36.8097 | 37.1123 | 37.2714 | 36.7195 | 37.0077 | 38.1136 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932
98% | 0.8916 | 22.1786 | 25.7814 | 30.6581 | 31.0897 | 31.3785 | 31.7844 | 32.7093 | 33.4356 | 34.0814 | 34.3079 | 34.5667 | 34.2049 | 34.3957 | 35.2926 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 98% | 0.8916 | 24.5466 | 28.16 | 33.0761 | 33.4708 | 33.7483 | 34.0339 | 35.1355 | 35.7794 | 36.4379 | 36.7375 | 36.8949 | 36.3486 | 36.6338 | 37.7286 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135
97% | 1.7832 | 21.9523 | 25.5183 | 30.3452 | 30.7725 | 31.0583 | 31.46 | 32.3755 | 33.0944 | 33.7336 | 33.9578 | 34.214 | 33.8558 | 34.0447 | 34.9324 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 97% | 2.0804 | 24.2962 | 27.8727 | 32.7386 | 33.1293 | 33.4039 | 33.6866 | 34.777 | 35.4143 | 36.0661 | 36.3626 | 36.5184 | 35.9777 | 36.26 | 37.3436 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338
95% | 4.458 | 21.4996 | 24.9921 | 29.7196 | 30.138 | 30.4179 | 30.8114 | 31.708 | 32.412 | 33.038 | 33.2576 | 33.5085 | 33.1578 | 33.3427 | 34.2122 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 95% | 4.1608 | 23.7952 | 27.298 | 32.0636 | 32.4462 | 32.7152 | 32.9921 | 34.0599 | 34.6841 | 35.3225 | 35.6129 | 35.7655 | 35.2359 | 35.5124 | 36.5736 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743
90% | 15.1571 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 90% | 11.5907 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
85% | 39.5274 | 19.2365 | 22.3614 | 26.5912 | 26.9656 | 27.216 | 27.5681 | 28.3703 | 29.0002 | 29.5604 | 29.7568 | 29.9813 | 29.6675 | 29.833 | 30.6109 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 85% | 32.6918 | 21.2905 | 24.4245 | 28.6885 | 29.0308 | 29.2715 | 29.5192 | 30.4747 | 31.0331 | 31.6043 | 31.8641 | 32.0007 | 31.5268 | 31.7743 | 32.7238 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277
80% | 110.5579 | 18.105 | 21.046 | 25.027 | 25.3794 | 25.6151 | 25.9464 | 26.7015 | 27.2943 | 27.8215 | 28.0064 | 28.2177 | 27.9223 | 28.0781 | 28.8103 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 80% | 84.1072 | 20.0381 | 22.9878 | 27.0009 | 27.3231 | 27.5496 | 27.7828 | 28.682 | 29.2076 | 29.7452 | 29.9898 | 30.1183 | 29.6723 | 29.9052 | 30.7988 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784
75% | 244.2972 | 16.9734 | 19.7306 | 23.4628 | 23.7932 | 24.0141 | 24.3248 | 25.0326 | 25.5884 | 26.0827 | 26.256 | 26.4541 | 26.1772 | 26.3232 | 27.0096 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 75% | 202.095 | 18.7857 | 21.5511 | 25.3134 | 25.6154 | 25.8278 | 26.0464 | 26.8894 | 27.3822 | 27.8862 | 28.1154 | 28.2359 | 27.8178 | 28.0361 | 28.8739 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797
70% | 444.0146 | 15.8418 | 18.4153 | 21.8986 | 22.207 | 22.4132 | 22.7031 | 23.3638 | 23.8825 | 24.3438 | 24.5056 | 24.6905 | 24.432 | 24.5683 | 25.209 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 70% | 388.1413 | 17.5333 | 20.1143 | 23.6258 | 23.9077 | 24.1059 | 24.31 | 25.0968 | 25.5567 | 26.0271 | 26.2411 | 26.3535 | 25.9633 | 26.167 | 26.949 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811
65% | 770.3386 | 14.7103 | 17.0999 | 20.3344 | 20.6207 | 20.8122 | 21.0815 | 21.6949 | 22.1767 | 22.605 | 22.7552 | 22.9269 | 22.6869 | 22.8135 | 23.4083 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 65% | 669.8855 | 16.2809 | 18.6776 | 21.9383 | 22.2001 | 22.3841 | 22.5735 | 23.3041 | 23.7312 | 24.168 | 24.3667 | 24.4711 | 24.1088 | 24.298 | 25.0241 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824
60% | 1209.3009 | 13.5787 | 15.7845 | 18.7703 | 19.0345 | 19.2113 | 19.4598 | 20.0261 | 20.4708 | 20.8661 | 21.0048 | 21.1633 | 20.9417 | 21.0586 | 21.6077 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 60% | 1104.687 | 15.0286 | 17.2408 | 20.2507 | 20.4924 | 20.6622 | 20.8371 | 21.5115 | 21.9057 | 22.3089 | 22.4923 | 22.5887 | 22.2542 | 22.4289 | 23.0991 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838
55% | 1757.6322 | 12.4472 | 14.4691 | 17.2061 | 17.4483 | 17.6104 | 17.8382 | 18.3573 | 18.7649 | 19.1273 | 19.2544 | 19.3997 | 19.1966 | 19.3037 | 19.8071 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 55% | 1631.62 | 13.7762 | 15.8041 | 18.5631 | 18.7847 | 18.9404 | 19.1007 | 19.7189 | 20.0803 | 20.4498 | 20.618 | 20.7063 | 20.3997 | 20.5598 | 21.1742 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851
50% | 2378.4799 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 50% | 2253.9537 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
45% | 3003.7856 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 45% | 2892.3362 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
40% | 3548.2533 | 9.0525 | 10.523 | 12.5135 | 12.6897 | 12.8075 | 12.9732 | 13.3507 | 13.6472 | 13.9108 | 14.0032 | 14.1089 | 13.9612 | 14.0391 | 14.4051 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 40% | 3473.3593 | 10.019 | 11.4939 | 13.5005 | 13.6616 | 13.7748 | 13.8914 | 14.341 | 14.6038 | 14.8726 | 14.9949 | 15.0592 | 14.8362 | 14.9526 | 15.3994 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892
35% | 3927.7759 | 7.9209 | 9.2076 | 10.9493 | 11.1035 | 11.2066 | 11.3516 | 11.6819 | 11.9413 | 12.1719 | 12.2528 | 12.3453 | 12.216 | 12.2842 | 12.6045 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 35% | 3882.8989 | 8.7667 | 10.0572 | 11.8129 | 11.9539 | 12.053 | 12.155 | 12.5484 | 12.7783 | 13.0135 | 13.1205 | 13.1768 | 12.9816 | 13.0835 | 13.4745 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905
30% | 4135.8149 | 6.7894 | 7.8923 | 9.3851 | 9.5173 | 9.6057 | 9.7299 | 10.0131 | 10.2354 | 10.4331 | 10.5024 | 10.5816 | 10.4709 | 10.5293 | 10.8038 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 30% | 4127.1961 | 7.5143 | 8.6204 | 10.1253 | 10.2462 | 10.3311 | 10.4186 | 10.7558 | 10.9529 | 11.1545 | 11.2462 | 11.2944 | 11.1271 | 11.2144 | 11.5496 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919
25% | 4252.0195 | 5.6578 | 6.5769 | 7.8209 | 7.9311 | 8.0047 | 8.1083 | 8.3442 | 8.5295 | 8.6942 | 8.752 | 8.818 | 8.7257 | 8.7744 | 9.0032 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 25% | 4245.1839 | 6.2619 | 7.1837 | 8.4378 | 8.5385 | 8.6093 | 8.6821 | 8.9631 | 9.1274 | 9.2954 | 9.3718 | 9.412 | 9.2726 | 9.3454 | 9.6246 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932
20% | 4325.4275 | 4.5262 | 5.2615 | 6.2568 | 6.3448 | 6.4038 | 6.4866 | 6.6754 | 6.8236 | 6.9554 | 7.0016 | 7.0544 | 6.9806 | 7.0195 | 7.2026 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 20% | 4322.1583 | 5.0095 | 5.7469 | 6.7502 | 6.8308 | 6.8874 | 6.9457 | 7.1705 | 7.3019 | 7.4363 | 7.4974 | 7.5296 | 7.4181 | 7.4763 | 7.6997 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946
15% | 4360.497 | 3.3947 | 3.9461 | 4.6926 | 4.7586 | 4.8028 | 4.865 | 5.0065 | 5.1177 | 5.2165 | 5.2512 | 5.2908 | 5.2354 | 5.2646 | 5.4019 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 15% | 4354.2558 | 3.7571 | 4.3102 | 5.0627 | 5.1231 | 5.1656 | 5.2093 | 5.3779 | 5.4764 | 5.5772 | 5.6231 | 5.6472 | 5.5636 | 5.6072 | 5.7748 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959
10% | 4373.8709 | 2.2631 | 2.6308 | 3.1284 | 3.1724 | 3.2019 | 3.2433 | 3.3377 | 3.4118 | 3.4777 | 3.5008 | 3.5272 | 3.4903 | 3.5098 | 3.6013 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 10% | 4366.1437 | 2.5048 | 2.8735 | 3.3751 | 3.4154 | 3.4437 | 3.4729 | 3.5853 | 3.651 | 3.7182 | 3.7487 | 3.7648 | 3.709 | 3.7381 | 3.8499 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973
5% | 4381.8952 | 1.1316 | 1.3154 | 1.5642 | 1.5862 | 1.6009 | 1.6217 | 1.6688 | 1.7059 | 1.7388 | 1.7504 | 1.7636 | 1.7451 | 1.7549 | 1.8006 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 5% | 4374.4653 | 1.2524 | 1.4367 | 1.6876 | 1.7077 | 1.7219 | 1.7364 | 1.7926 | 1.8255 | 1.8591 | 1.8744 | 1.8824 | 1.8545 | 1.8691 | 1.9249 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986
9.992e-14% | 4391.7028 | 2.2613e-14 | 2.6286e-14 | 3.1259e-14 | 3.1699e-14 | 3.1993e-14 | 3.2407e-14 | 3.335e-14 | 3.4091e-14 | 3.4749e-14 | 3.498e-14 | 3.5244e-14 | 3.4875e-14 | 3.507e-14 | 3.5984e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 9.992e-14% | 4375.9513 | 2.5028e-14 | 2.8712e-14 | 3.3724e-14 | 3.4127e-14 | 3.4409e-14 | 3.4701e-14 | 3.5824e-14 | 3.648e-14 | 3.7152e-14 | 3.7457e-14 | 3.7618e-14 | 3.7061e-14 | 3.7352e-14 | 3.8468e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 100% | 0 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
99% | 0.37816 | 25.6004 | 28.4203 | 33.1682 | 33.1325 | 33.1003 | 33.615 | 34.3705 | 34.8883 | 34.259 | 34.3215 | 34.6215 | 35.8093 | 34.6838 | 34.6177 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 99% | 1.1345 | 27.8174 | 31.2882 | 36.0278 | 35.9641 | 36.0059 | 36.1355 | 36.5757 | 36.8706 | 37.1125 | 37.1481 | 37.3662 | 37.4435 | 37.4433 | 37.3934 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828
98% | 0.37816 | 25.3418 | 28.1332 | 32.8331 | 32.7978 | 32.766 | 33.2754 | 34.0234 | 34.5359 | 33.9129 | 33.9749 | 34.2718 | 35.4476 | 34.3335 | 34.268 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 98% | 1.8908 | 27.5364 | 30.9722 | 35.6639 | 35.6008 | 35.6422 | 35.7705 | 36.2063 | 36.4982 | 36.7376 | 36.7729 | 36.9888 | 37.0653 | 37.0651 | 37.0157 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052
97% | 0.75633 | 25.0832 | 27.8462 | 32.4981 | 32.4631 | 32.4316 | 32.9359 | 33.6762 | 34.1835 | 33.5669 | 33.6282 | 33.9221 | 35.0859 | 33.9831 | 33.9184 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 97% | 2.269 | 27.2555 | 30.6561 | 35.3 | 35.2376 | 35.2785 | 35.4055 | 35.8368 | 36.1258 | 36.3627 | 36.3976 | 36.6114 | 36.6871 | 36.6869 | 36.638 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276
95% | 0.75633 | 24.566 | 27.272 | 31.828 | 31.7938 | 31.763 | 32.2568 | 32.9818 | 33.4787 | 32.8748 | 32.9348 | 33.2226 | 34.3625 | 33.2825 | 33.219 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 95% | 4.1598 | 26.6935 | 30.0241 | 34.5721 | 34.511 | 34.5511 | 34.6754 | 35.0979 | 35.3809 | 35.613 | 35.6472 | 35.8565 | 35.9307 | 35.9305 | 35.8826 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724
90% | 3.7816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 90% | 15.5047 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
85% | 13.6139 | 21.9801 | 24.4013 | 28.4777 | 28.4471 | 28.4195 | 28.8613 | 29.5101 | 29.9546 | 29.4143 | 29.468 | 29.7255 | 30.7454 | 29.779 | 29.7223 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 85% | 31.3876 | 23.8836 | 26.8636 | 30.9329 | 30.8783 | 30.9141 | 31.0254 | 31.4034 | 31.6566 | 31.8643 | 31.8948 | 32.0821 | 32.1485 | 32.1483 | 32.1054 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963
80% | 35.1693 | 20.6872 | 22.9659 | 26.8026 | 26.7737 | 26.7478 | 27.1636 | 27.7742 | 28.1926 | 27.684 | 27.7346 | 27.977 | 28.9368 | 28.0273 | 27.9739 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 80% | 57.8591 | 22.4787 | 25.2834 | 29.1134 | 29.0619 | 29.0957 | 29.2004 | 29.5561 | 29.7944 | 29.9899 | 30.0187 | 30.1949 | 30.2574 | 30.2572 | 30.2169 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083
75% | 80.549 | 19.3942 | 21.5305 | 25.1274 | 25.1004 | 25.076 | 25.4659 | 26.0383 | 26.4305 | 25.9538 | 26.0012 | 26.2284 | 27.1283 | 26.2756 | 26.2255 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 75% | 121.3907 | 21.0738 | 23.7032 | 27.2938 | 27.2455 | 27.2772 | 27.3753 | 27.7089 | 27.9323 | 28.1155 | 28.1425 | 28.3078 | 28.3663 | 28.3662 | 28.3283 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203
70% | 192.1075 | 18.1013 | 20.0952 | 23.4522 | 23.427 | 23.4043 | 23.7682 | 24.3024 | 24.6685 | 24.2235 | 24.2678 | 24.4798 | 25.3197 | 24.5239 | 24.4772 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 70% | 273.4128 | 19.6689 | 22.123 | 25.4742 | 25.4292 | 25.4587 | 25.5503 | 25.8616 | 26.0701 | 26.2411 | 26.2663 | 26.4206 | 26.4752 | 26.4751 | 26.4398 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323
65% | 403.1231 | 16.8083 | 18.6598 | 21.7771 | 21.7537 | 21.7325 | 22.0704 | 22.5665 | 22.9065 | 22.4933 | 22.5343 | 22.7313 | 23.5112 | 22.7722 | 22.7288 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 65% | 529.43 | 18.264 | 20.5428 | 23.6546 | 23.6128 | 23.6402 | 23.7253 | 24.0144 | 24.208 | 24.3668 | 24.3902 | 24.5334 | 24.5841 | 24.584 | 24.5512 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443
60% | 739.3112 | 15.5154 | 17.2244 | 20.1019 | 20.0803 | 20.0608 | 20.3727 | 20.8306 | 21.1444 | 20.763 | 20.8009 | 20.9827 | 21.7026 | 21.0205 | 20.9804 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 60% | 918.9392 | 16.859 | 18.9626 | 21.835 | 21.7964 | 21.8218 | 21.9003 | 22.1671 | 22.3458 | 22.4924 | 22.514 | 22.6462 | 22.6931 | 22.6929 | 22.6627 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562
55% | 1204.8314 | 14.2224 | 15.7891 | 18.4268 | 18.4069 | 18.3891 | 18.675 | 19.0947 | 19.3824 | 19.0328 | 19.0675 | 19.2342 | 19.8941 | 19.2688 | 19.2321 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 55% | 1454.0417 | 15.4541 | 17.3823 | 20.0154 | 19.9801 | 20.0033 | 20.0753 | 20.3198 | 20.4837 | 20.618 | 20.6378 | 20.759 | 20.802 | 20.8019 | 20.7741 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682
50% | 1783.0446 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 50% | 2105.2406 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
45% | 2370.3337 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 45% | 2758.3303 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
40% | 2864.2163 | 10.3436 | 11.483 | 13.4013 | 13.3869 | 13.3739 | 13.5818 | 13.8871 | 14.0963 | 13.842 | 13.8673 | 13.9885 | 14.4684 | 14.0137 | 13.987 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 40% | 3348.2666 | 11.2394 | 12.6417 | 14.5567 | 14.531 | 14.5478 | 14.6002 | 14.7781 | 14.8972 | 14.9949 | 15.0093 | 15.0975 | 15.1287 | 15.1286 | 15.1084 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042
35% | 3297.9707 | 9.0506 | 10.0476 | 11.7261 | 11.7135 | 11.7021 | 11.8841 | 12.1512 | 12.3343 | 12.1118 | 12.1339 | 12.2399 | 12.6599 | 12.262 | 12.2386 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 35% | 3816.434 | 9.8344 | 11.0615 | 12.7371 | 12.7146 | 12.7294 | 12.7752 | 12.9308 | 13.0351 | 13.1206 | 13.1332 | 13.2103 | 13.2376 | 13.2375 | 13.2199 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161
30% | 3579.7031 | 7.7577 | 8.6122 | 10.051 | 10.0401 | 10.0304 | 10.1864 | 10.4153 | 10.5722 | 10.3815 | 10.4005 | 10.4914 | 10.8513 | 10.5102 | 10.4902 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 30% | 4067.1569 | 8.4295 | 9.4813 | 10.9175 | 10.8982 | 10.9109 | 10.9501 | 11.0836 | 11.1729 | 11.2462 | 11.257 | 11.3231 | 11.3465 | 11.3465 | 11.3313 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281
25% | 3796.3913 | 6.4647 | 7.1768 | 8.3758 | 8.3668 | 8.3587 | 8.4886 | 8.6794 | 8.8102 | 8.6513 | 8.6671 | 8.7428 | 9.0428 | 8.7585 | 8.7418 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 25% | 4236.9526 | 7.0246 | 7.9011 | 9.0979 | 9.0818 | 9.0924 | 9.1251 | 9.2363 | 9.3108 | 9.3718 | 9.3808 | 9.4359 | 9.4554 | 9.4554 | 9.4428 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401
20% | 3975.6411 | 5.1718 | 5.7415 | 6.7006 | 6.6934 | 6.6869 | 6.7909 | 6.9435 | 7.0481 | 6.921 | 6.9336 | 6.9942 | 7.2342 | 7.0068 | 6.9935 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 20% | 4332.6282 | 5.6197 | 6.3209 | 7.2783 | 7.2655 | 7.2739 | 7.3001 | 7.389 | 7.4486 | 7.4975 | 7.5047 | 7.5487 | 7.5644 | 7.5643 | 7.5542 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521
15% | 4117.4527 | 3.8788 | 4.3061 | 5.0255 | 5.0201 | 5.0152 | 5.0932 | 5.2077 | 5.2861 | 5.1908 | 5.2002 | 5.2457 | 5.4257 | 5.2551 | 5.2451 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 15% | 4361.7469 | 4.2148 | 4.7406 | 5.4588 | 5.4491 | 5.4554 | 5.4751 | 5.5418 | 5.5865 | 5.6231 | 5.6285 | 5.6616 | 5.6733 | 5.6732 | 5.6657 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641
10% | 4224.8514 | 2.5859 | 2.8707 | 3.3503 | 3.3467 | 3.3435 | 3.3955 | 3.4718 | 3.5241 | 3.4605 | 3.4668 | 3.4971 | 3.6171 | 3.5034 | 3.4967 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 10% | 4375.7389 | 2.8098 | 3.1604 | 3.6392 | 3.6327 | 3.637 | 3.65 | 3.6945 | 3.7243 | 3.7487 | 3.7523 | 3.7744 | 3.7822 | 3.7822 | 3.7771 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776
5% | 4310.3165 | 1.2929 | 1.4354 | 1.6752 | 1.6734 | 1.6717 | 1.6977 | 1.7359 | 1.762 | 1.7303 | 1.7334 | 1.7486 | 1.8086 | 1.7517 | 1.7484 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 5% | 4378.0079 | 1.4049 | 1.5802 | 1.8196 | 1.8164 | 1.8185 | 1.825 | 1.8473 | 1.8622 | 1.8744 | 1.8762 | 1.8872 | 1.8911 | 1.8911 | 1.8886 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888
9.992e-14% | 4382.5459 | 2.5838e-14 | 2.8684e-14 | 3.3476e-14 | 3.344e-14 | 3.3408e-14 | 3.3927e-14 | 3.469e-14 | 3.5213e-14 | 3.4577e-14 | 3.4641e-14 | 3.4943e-14 | 3.6142e-14 | 3.5006e-14 | 3.4939e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 9.992e-14% | 4379.1424 | 2.8076e-14 | 3.1579e-14 | 3.6363e-14 | 3.6298e-14 | 3.6341e-14 | 3.6471e-14 | 3.6916e-14 | 3.7213e-14 | 3.7457e-14 | 3.7493e-14 | 3.7714e-14 | 3.7792e-14 | 3.7791e-14 | 3.7741e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 100% | 0 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
99% | 0.2972 | 22.4049 | 26.0444 | 30.9709 | 31.407 | 31.6987 | 32.1087 | 33.0431 | 33.7767 | 34.4291 | 34.658 | 34.9194 | 34.5539 | 34.7466 | 35.6527 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 99% | 0.2972 | 24.7971 | 28.4474 | 33.4137 | 33.8124 | 34.0926 | 34.3812 | 35.494 | 36.1445 | 36.8097 | 37.1123 | 37.2714 | 36.7195 | 37.0077 | 38.1136 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932
98% | 0.8916 | 22.1786 | 25.7814 | 30.6581 | 31.0897 | 31.3785 | 31.7844 | 32.7093 | 33.4356 | 34.0814 | 34.3079 | 34.5667 | 34.2049 | 34.3957 | 35.2926 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 98% | 0.8916 | 24.5466 | 28.16 | 33.0761 | 33.4708 | 33.7483 | 34.0339 | 35.1355 | 35.7794 | 36.4379 | 36.7375 | 36.8949 | 36.3486 | 36.6338 | 37.7286 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135
97% | 1.7832 | 21.9523 | 25.5183 | 30.3452 | 30.7725 | 31.0583 | 31.46 | 32.3755 | 33.0944 | 33.7336 | 33.9578 | 34.214 | 33.8558 | 34.0447 | 34.9324 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 97% | 2.0804 | 24.2962 | 27.8727 | 32.7386 | 33.1293 | 33.4039 | 33.6866 | 34.777 | 35.4143 | 36.0661 | 36.3626 | 36.5184 | 35.9777 | 36.26 | 37.3436 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338
95% | 4.458 | 21.4996 | 24.9921 | 29.7196 | 30.138 | 30.4179 | 30.8114 | 31.708 | 32.412 | 33.038 | 33.2576 | 33.5085 | 33.1578 | 33.3427 | 34.2122 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 95% | 4.1608 | 23.7952 | 27.298 | 32.0636 | 32.4462 | 32.7152 | 32.9921 | 34.0599 | 34.6841 | 35.3225 | 35.6129 | 35.7655 | 35.2359 | 35.5124 | 36.5736 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743
90% | 15.1571 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 90% | 11.5907 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
85% | 39.5274 | 19.2365 | 22.3614 | 26.5912 | 26.9656 | 27.216 | 27.5681 | 28.3703 | 29.0002 | 29.5604 | 29.7568 | 29.9813 | 29.6675 | 29.833 | 30.6109 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 85% | 32.6918 | 21.2905 | 24.4245 | 28.6885 | 29.0308 | 29.2715 | 29.5192 | 30.4747 | 31.0331 | 31.6043 | 31.8641 | 32.0007 | 31.5268 | 31.7743 | 32.7238 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277
80% | 110.5579 | 18.105 | 21.046 | 25.027 | 25.3794 | 25.6151 | 25.9464 | 26.7015 | 27.2943 | 27.8215 | 28.0064 | 28.2177 | 27.9223 | 28.0781 | 28.8103 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 80% | 84.1072 | 20.0381 | 22.9878 | 27.0009 | 27.3231 | 27.5496 | 27.7828 | 28.682 | 29.2076 | 29.7452 | 29.9898 | 30.1183 | 29.6723 | 29.9052 | 30.7988 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784
75% | 244.2972 | 16.9734 | 19.7306 | 23.4628 | 23.7932 | 24.0141 | 24.3248 | 25.0326 | 25.5884 | 26.0827 | 26.256 | 26.4541 | 26.1772 | 26.3232 | 27.0096 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 75% | 202.095 | 18.7857 | 21.5511 | 25.3134 | 25.6154 | 25.8278 | 26.0464 | 26.8894 | 27.3822 | 27.8862 | 28.1154 | 28.2359 | 27.8178 | 28.0361 | 28.8739 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797
70% | 444.0146 | 15.8418 | 18.4153 | 21.8986 | 22.207 | 22.4132 | 22.7031 | 23.3638 | 23.8825 | 24.3438 | 24.5056 | 24.6905 | 24.432 | 24.5683 | 25.209 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 70% | 388.1413 | 17.5333 | 20.1143 | 23.6258 | 23.9077 | 24.1059 | 24.31 | 25.0968 | 25.5567 | 26.0271 | 26.2411 | 26.3535 | 25.9633 | 26.167 | 26.949 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811
65% | 770.3386 | 14.7103 | 17.0999 | 20.3344 | 20.6207 | 20.8122 | 21.0815 | 21.6949 | 22.1767 | 22.605 | 22.7552 | 22.9269 | 22.6869 | 22.8135 | 23.4083 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 65% | 669.8855 | 16.2809 | 18.6776 | 21.9383 | 22.2001 | 22.3841 | 22.5735 | 23.3041 | 23.7312 | 24.168 | 24.3667 | 24.4711 | 24.1088 | 24.298 | 25.0241 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824
60% | 1209.3009 | 13.5787 | 15.7845 | 18.7703 | 19.0345 | 19.2113 | 19.4598 | 20.0261 | 20.4708 | 20.8661 | 21.0048 | 21.1633 | 20.9417 | 21.0586 | 21.6077 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 60% | 1104.687 | 15.0286 | 17.2408 | 20.2507 | 20.4924 | 20.6622 | 20.8371 | 21.5115 | 21.9057 | 22.3089 | 22.4923 | 22.5887 | 22.2542 | 22.4289 | 23.0991 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838
55% | 1757.6322 | 12.4472 | 14.4691 | 17.2061 | 17.4483 | 17.6104 | 17.8382 | 18.3573 | 18.7649 | 19.1273 | 19.2544 | 19.3997 | 19.1966 | 19.3037 | 19.8071 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 55% | 1631.62 | 13.7762 | 15.8041 | 18.5631 | 18.7847 | 18.9404 | 19.1007 | 19.7189 | 20.0803 | 20.4498 | 20.618 | 20.7063 | 20.3997 | 20.5598 | 21.1742 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851
50% | 2378.4799 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 50% | 2253.9537 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
45% | 3003.7856 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 45% | 2892.3362 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
40% | 3548.2533 | 9.0525 | 10.523 | 12.5135 | 12.6897 | 12.8075 | 12.9732 | 13.3507 | 13.6472 | 13.9108 | 14.0032 | 14.1089 | 13.9612 | 14.0391 | 14.4051 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 40% | 3473.3593 | 10.019 | 11.4939 | 13.5005 | 13.6616 | 13.7748 | 13.8914 | 14.341 | 14.6038 | 14.8726 | 14.9949 | 15.0592 | 14.8362 | 14.9526 | 15.3994 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892
35% | 3927.7759 | 7.9209 | 9.2076 | 10.9493 | 11.1035 | 11.2066 | 11.3516 | 11.6819 | 11.9413 | 12.1719 | 12.2528 | 12.3453 | 12.216 | 12.2842 | 12.6045 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 35% | 3882.8989 | 8.7667 | 10.0572 | 11.8129 | 11.9539 | 12.053 | 12.155 | 12.5484 | 12.7783 | 13.0135 | 13.1205 | 13.1768 | 12.9816 | 13.0835 | 13.4745 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905
30% | 4135.8149 | 6.7894 | 7.8923 | 9.3851 | 9.5173 | 9.6057 | 9.7299 | 10.0131 | 10.2354 | 10.4331 | 10.5024 | 10.5816 | 10.4709 | 10.5293 | 10.8038 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 30% | 4127.1961 | 7.5143 | 8.6204 | 10.1253 | 10.2462 | 10.3311 | 10.4186 | 10.7558 | 10.9529 | 11.1545 | 11.2462 | 11.2944 | 11.1271 | 11.2144 | 11.5496 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919
25% | 4252.0195 | 5.6578 | 6.5769 | 7.8209 | 7.9311 | 8.0047 | 8.1083 | 8.3442 | 8.5295 | 8.6942 | 8.752 | 8.818 | 8.7257 | 8.7744 | 9.0032 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 25% | 4245.1839 | 6.2619 | 7.1837 | 8.4378 | 8.5385 | 8.6093 | 8.6821 | 8.9631 | 9.1274 | 9.2954 | 9.3718 | 9.412 | 9.2726 | 9.3454 | 9.6246 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932
20% | 4325.4275 | 4.5262 | 5.2615 | 6.2568 | 6.3448 | 6.4038 | 6.4866 | 6.6754 | 6.8236 | 6.9554 | 7.0016 | 7.0544 | 6.9806 | 7.0195 | 7.2026 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 20% | 4322.1583 | 5.0095 | 5.7469 | 6.7502 | 6.8308 | 6.8874 | 6.9457 | 7.1705 | 7.3019 | 7.4363 | 7.4974 | 7.5296 | 7.4181 | 7.4763 | 7.6997 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946
15% | 4360.497 | 3.3947 | 3.9461 | 4.6926 | 4.7586 | 4.8028 | 4.865 | 5.0065 | 5.1177 | 5.2165 | 5.2512 | 5.2908 | 5.2354 | 5.2646 | 5.4019 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 15% | 4354.2558 | 3.7571 | 4.3102 | 5.0627 | 5.1231 | 5.1656 | 5.2093 | 5.3779 | 5.4764 | 5.5772 | 5.6231 | 5.6472 | 5.5636 | 5.6072 | 5.7748 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959
10% | 4373.8709 | 2.2631 | 2.6308 | 3.1284 | 3.1724 | 3.2019 | 3.2433 | 3.3377 | 3.4118 | 3.4777 | 3.5008 | 3.5272 | 3.4903 | 3.5098 | 3.6013 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 10% | 4366.1437 | 2.5048 | 2.8735 | 3.3751 | 3.4154 | 3.4437 | 3.4729 | 3.5853 | 3.651 | 3.7182 | 3.7487 | 3.7648 | 3.709 | 3.7381 | 3.8499 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973
5% | 4381.8952 | 1.1316 | 1.3154 | 1.5642 | 1.5862 | 1.6009 | 1.6217 | 1.6688 | 1.7059 | 1.7388 | 1.7504 | 1.7636 | 1.7451 | 1.7549 | 1.8006 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 5% | 4374.4653 | 1.2524 | 1.4367 | 1.6876 | 1.7077 | 1.7219 | 1.7364 | 1.7926 | 1.8255 | 1.8591 | 1.8744 | 1.8824 | 1.8545 | 1.8691 | 1.9249 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986
9.992e-14% | 4391.7028 | 2.2613e-14 | 2.6286e-14 | 3.1259e-14 | 3.1699e-14 | 3.1993e-14 | 3.2407e-14 | 3.335e-14 | 3.4091e-14 | 3.4749e-14 | 3.498e-14 | 3.5244e-14 | 3.4875e-14 | 3.507e-14 | 3.5984e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 9.992e-14% | 4375.9513 | 2.5028e-14 | 2.8712e-14 | 3.3724e-14 | 3.4127e-14 | 3.4409e-14 | 3.4701e-14 | 3.5824e-14 | 3.648e-14 | 3.7152e-14 | 3.7457e-14 | 3.7618e-14 | 3.7061e-14 | 3.7352e-14 | 3.8468e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 100% | 0 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
99% | 0.37816 | 25.6004 | 28.4203 | 33.1682 | 33.1325 | 33.1003 | 33.615 | 34.3705 | 34.8883 | 34.259 | 34.3215 | 34.6215 | 35.8093 | 34.6838 | 34.6177 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 99% | 1.1345 | 27.8174 | 31.2882 | 36.0278 | 35.9641 | 36.0059 | 36.1355 | 36.5757 | 36.8706 | 37.1125 | 37.1481 | 37.3662 | 37.4435 | 37.4433 | 37.3934 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828
98% | 0.37816 | 25.3418 | 28.1332 | 32.8331 | 32.7978 | 32.766 | 33.2754 | 34.0234 | 34.5359 | 33.9129 | 33.9749 | 34.2718 | 35.4476 | 34.3335 | 34.268 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 98% | 1.8908 | 27.5364 | 30.9722 | 35.6639 | 35.6008 | 35.6422 | 35.7705 | 36.2063 | 36.4982 | 36.7376 | 36.7729 | 36.9888 | 37.0653 | 37.0651 | 37.0157 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052
97% | 0.75633 | 25.0832 | 27.8462 | 32.4981 | 32.4631 | 32.4316 | 32.9359 | 33.6762 | 34.1835 | 33.5669 | 33.6282 | 33.9221 | 35.0859 | 33.9831 | 33.9184 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 97% | 2.269 | 27.2555 | 30.6561 | 35.3 | 35.2376 | 35.2785 | 35.4055 | 35.8368 | 36.1258 | 36.3627 | 36.3976 | 36.6114 | 36.6871 | 36.6869 | 36.638 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276
95% | 0.75633 | 24.566 | 27.272 | 31.828 | 31.7938 | 31.763 | 32.2568 | 32.9818 | 33.4787 | 32.8748 | 32.9348 | 33.2226 | 34.3625 | 33.2825 | 33.219 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 95% | 4.1598 | 26.6935 | 30.0241 | 34.5721 | 34.511 | 34.5511 | 34.6754 | 35.0979 | 35.3809 | 35.613 | 35.6472 | 35.8565 | 35.9307 | 35.9305 | 35.8826 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724
90% | 3.7816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 90% | 15.5047 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
85% | 13.6139 | 21.9801 | 24.4013 | 28.4777 | 28.4471 | 28.4195 | 28.8613 | 29.5101 | 29.9546 | 29.4143 | 29.468 | 29.7255 | 30.7454 | 29.779 | 29.7223 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 85% | 31.3876 | 23.8836 | 26.8636 | 30.9329 | 30.8783 | 30.9141 | 31.0254 | 31.4034 | 31.6566 | 31.8643 | 31.8948 | 32.0821 | 32.1485 | 32.1483 | 32.1054 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963
80% | 35.1693 | 20.6872 | 22.9659 | 26.8026 | 26.7737 | 26.7478 | 27.1636 | 27.7742 | 28.1926 | 27.684 | 27.7346 | 27.977 | 28.9368 | 28.0273 | 27.9739 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 80% | 57.8591 | 22.4787 | 25.2834 | 29.1134 | 29.0619 | 29.0957 | 29.2004 | 29.5561 | 29.7944 | 29.9899 | 30.0187 | 30.1949 | 30.2574 | 30.2572 | 30.2169 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083
75% | 80.549 | 19.3942 | 21.5305 | 25.1274 | 25.1004 | 25.076 | 25.4659 | 26.0383 | 26.4305 | 25.9538 | 26.0012 | 26.2284 | 27.1283 | 26.2756 | 26.2255 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 75% | 121.3907 | 21.0738 | 23.7032 | 27.2938 | 27.2455 | 27.2772 | 27.3753 | 27.7089 | 27.9323 | 28.1155 | 28.1425 | 28.3078 | 28.3663 | 28.3662 | 28.3283 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203
70% | 192.1075 | 18.1013 | 20.0952 | 23.4522 | 23.427 | 23.4043 | 23.7682 | 24.3024 | 24.6685 | 24.2235 | 24.2678 | 24.4798 | 25.3197 | 24.5239 | 24.4772 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 70% | 273.4128 | 19.6689 | 22.123 | 25.4742 | 25.4292 | 25.4587 | 25.5503 | 25.8616 | 26.0701 | 26.2411 | 26.2663 | 26.4206 | 26.4752 | 26.4751 | 26.4398 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323
65% | 403.1231 | 16.8083 | 18.6598 | 21.7771 | 21.7537 | 21.7325 | 22.0704 | 22.5665 | 22.9065 | 22.4933 | 22.5343 | 22.7313 | 23.5112 | 22.7722 | 22.7288 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 65% | 529.43 | 18.264 | 20.5428 | 23.6546 | 23.6128 | 23.6402 | 23.7253 | 24.0144 | 24.208 | 24.3668 | 24.3902 | 24.5334 | 24.5841 | 24.584 | 24.5512 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443
60% | 739.3112 | 15.5154 | 17.2244 | 20.1019 | 20.0803 | 20.0608 | 20.3727 | 20.8306 | 21.1444 | 20.763 | 20.8009 | 20.9827 | 21.7026 | 21.0205 | 20.9804 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 60% | 918.9392 | 16.859 | 18.9626 | 21.835 | 21.7964 | 21.8218 | 21.9003 | 22.1671 | 22.3458 | 22.4924 | 22.514 | 22.6462 | 22.6931 | 22.6929 | 22.6627 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562
55% | 1204.8314 | 14.2224 | 15.7891 | 18.4268 | 18.4069 | 18.3891 | 18.675 | 19.0947 | 19.3824 | 19.0328 | 19.0675 | 19.2342 | 19.8941 | 19.2688 | 19.2321 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 55% | 1454.0417 | 15.4541 | 17.3823 | 20.0154 | 19.9801 | 20.0033 | 20.0753 | 20.3198 | 20.4837 | 20.618 | 20.6378 | 20.759 | 20.802 | 20.8019 | 20.7741 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682
50% | 1783.0446 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 50% | 2105.2406 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
45% | 2370.3337 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 45% | 2758.3303 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
40% | 2864.2163 | 10.3436 | 11.483 | 13.4013 | 13.3869 | 13.3739 | 13.5818 | 13.8871 | 14.0963 | 13.842 | 13.8673 | 13.9885 | 14.4684 | 14.0137 | 13.987 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 40% | 3348.2666 | 11.2394 | 12.6417 | 14.5567 | 14.531 | 14.5478 | 14.6002 | 14.7781 | 14.8972 | 14.9949 | 15.0093 | 15.0975 | 15.1287 | 15.1286 | 15.1084 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042
35% | 3297.9707 | 9.0506 | 10.0476 | 11.7261 | 11.7135 | 11.7021 | 11.8841 | 12.1512 | 12.3343 | 12.1118 | 12.1339 | 12.2399 | 12.6599 | 12.262 | 12.2386 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 35% | 3816.434 | 9.8344 | 11.0615 | 12.7371 | 12.7146 | 12.7294 | 12.7752 | 12.9308 | 13.0351 | 13.1206 | 13.1332 | 13.2103 | 13.2376 | 13.2375 | 13.2199 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161
30% | 3579.7031 | 7.7577 | 8.6122 | 10.051 | 10.0401 | 10.0304 | 10.1864 | 10.4153 | 10.5722 | 10.3815 | 10.4005 | 10.4914 | 10.8513 | 10.5102 | 10.4902 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 30% | 4067.1569 | 8.4295 | 9.4813 | 10.9175 | 10.8982 | 10.9109 | 10.9501 | 11.0836 | 11.1729 | 11.2462 | 11.257 | 11.3231 | 11.3465 | 11.3465 | 11.3313 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281
25% | 3796.3913 | 6.4647 | 7.1768 | 8.3758 | 8.3668 | 8.3587 | 8.4886 | 8.6794 | 8.8102 | 8.6513 | 8.6671 | 8.7428 | 9.0428 | 8.7585 | 8.7418 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 25% | 4236.9526 | 7.0246 | 7.9011 | 9.0979 | 9.0818 | 9.0924 | 9.1251 | 9.2363 | 9.3108 | 9.3718 | 9.3808 | 9.4359 | 9.4554 | 9.4554 | 9.4428 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401
20% | 3975.6411 | 5.1718 | 5.7415 | 6.7006 | 6.6934 | 6.6869 | 6.7909 | 6.9435 | 7.0481 | 6.921 | 6.9336 | 6.9942 | 7.2342 | 7.0068 | 6.9935 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 20% | 4332.6282 | 5.6197 | 6.3209 | 7.2783 | 7.2655 | 7.2739 | 7.3001 | 7.389 | 7.4486 | 7.4975 | 7.5047 | 7.5487 | 7.5644 | 7.5643 | 7.5542 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521
15% | 4117.4527 | 3.8788 | 4.3061 | 5.0255 | 5.0201 | 5.0152 | 5.0932 | 5.2077 | 5.2861 | 5.1908 | 5.2002 | 5.2457 | 5.4257 | 5.2551 | 5.2451 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 15% | 4361.7469 | 4.2148 | 4.7406 | 5.4588 | 5.4491 | 5.4554 | 5.4751 | 5.5418 | 5.5865 | 5.6231 | 5.6285 | 5.6616 | 5.6733 | 5.6732 | 5.6657 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641
10% | 4224.8514 | 2.5859 | 2.8707 | 3.3503 | 3.3467 | 3.3435 | 3.3955 | 3.4718 | 3.5241 | 3.4605 | 3.4668 | 3.4971 | 3.6171 | 3.5034 | 3.4967 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 10% | 4375.7389 | 2.8098 | 3.1604 | 3.6392 | 3.6327 | 3.637 | 3.65 | 3.6945 | 3.7243 | 3.7487 | 3.7523 | 3.7744 | 3.7822 | 3.7822 | 3.7771 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776
5% | 4310.3165 | 1.2929 | 1.4354 | 1.6752 | 1.6734 | 1.6717 | 1.6977 | 1.7359 | 1.762 | 1.7303 | 1.7334 | 1.7486 | 1.8086 | 1.7517 | 1.7484 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 5% | 4378.0079 | 1.4049 | 1.5802 | 1.8196 | 1.8164 | 1.8185 | 1.825 | 1.8473 | 1.8622 | 1.8744 | 1.8762 | 1.8872 | 1.8911 | 1.8911 | 1.8886 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888
9.992e-14% | 4382.5459 | 2.5838e-14 | 2.8684e-14 | 3.3476e-14 | 3.344e-14 | 3.3408e-14 | 3.3927e-14 | 3.469e-14 | 3.5213e-14 | 3.4577e-14 | 3.4641e-14 | 3.4943e-14 | 3.6142e-14 | 3.5006e-14 | 3.4939e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 9.992e-14% | 4379.1424 | 2.8076e-14 | 3.1579e-14 | 3.6363e-14 | 3.6298e-14 | 3.6341e-14 | 3.6471e-14 | 3.6916e-14 | 3.7213e-14 | 3.7457e-14 | 3.7493e-14 | 3.7714e-14 | 3.7792e-14 | 3.7791e-14 | 3.7741e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 100% | 0 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
99% | 0.2972 | 22.4049 | 26.0444 | 30.9709 | 31.407 | 31.6987 | 32.1087 | 33.0431 | 33.7767 | 34.4291 | 34.658 | 34.9194 | 34.5539 | 34.7466 | 35.6527 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 99% | 0.2972 | 24.7971 | 28.4474 | 33.4137 | 33.8124 | 34.0926 | 34.3812 | 35.494 | 36.1445 | 36.8097 | 37.1123 | 37.2714 | 36.7195 | 37.0077 | 38.1136 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932
98% | 0.8916 | 22.1786 | 25.7814 | 30.6581 | 31.0897 | 31.3785 | 31.7844 | 32.7093 | 33.4356 | 34.0814 | 34.3079 | 34.5667 | 34.2049 | 34.3957 | 35.2926 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 98% | 0.8916 | 24.5466 | 28.16 | 33.0761 | 33.4708 | 33.7483 | 34.0339 | 35.1355 | 35.7794 | 36.4379 | 36.7375 | 36.8949 | 36.3486 | 36.6338 | 37.7286 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135
97% | 1.7832 | 21.9523 | 25.5183 | 30.3452 | 30.7725 | 31.0583 | 31.46 | 32.3755 | 33.0944 | 33.7336 | 33.9578 | 34.214 | 33.8558 | 34.0447 | 34.9324 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 97% | 2.0804 | 24.2962 | 27.8727 | 32.7386 | 33.1293 | 33.4039 | 33.6866 | 34.777 | 35.4143 | 36.0661 | 36.3626 | 36.5184 | 35.9777 | 36.26 | 37.3436 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338
95% | 4.458 | 21.4996 | 24.9921 | 29.7196 | 30.138 | 30.4179 | 30.8114 | 31.708 | 32.412 | 33.038 | 33.2576 | 33.5085 | 33.1578 | 33.3427 | 34.2122 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 95% | 4.1608 | 23.7952 | 27.298 | 32.0636 | 32.4462 | 32.7152 | 32.9921 | 34.0599 | 34.6841 | 35.3225 | 35.6129 | 35.7655 | 35.2359 | 35.5124 | 36.5736 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743
90% | 15.1571 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 90% | 11.5907 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
85% | 39.5274 | 19.2365 | 22.3614 | 26.5912 | 26.9656 | 27.216 | 27.5681 | 28.3703 | 29.0002 | 29.5604 | 29.7568 | 29.9813 | 29.6675 | 29.833 | 30.6109 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 85% | 32.6918 | 21.2905 | 24.4245 | 28.6885 | 29.0308 | 29.2715 | 29.5192 | 30.4747 | 31.0331 | 31.6043 | 31.8641 | 32.0007 | 31.5268 | 31.7743 | 32.7238 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277
80% | 110.5579 | 18.105 | 21.046 | 25.027 | 25.3794 | 25.6151 | 25.9464 | 26.7015 | 27.2943 | 27.8215 | 28.0064 | 28.2177 | 27.9223 | 28.0781 | 28.8103 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 80% | 84.1072 | 20.0381 | 22.9878 | 27.0009 | 27.3231 | 27.5496 | 27.7828 | 28.682 | 29.2076 | 29.7452 | 29.9898 | 30.1183 | 29.6723 | 29.9052 | 30.7988 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784
75% | 244.2972 | 16.9734 | 19.7306 | 23.4628 | 23.7932 | 24.0141 | 24.3248 | 25.0326 | 25.5884 | 26.0827 | 26.256 | 26.4541 | 26.1772 | 26.3232 | 27.0096 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 75% | 202.095 | 18.7857 | 21.5511 | 25.3134 | 25.6154 | 25.8278 | 26.0464 | 26.8894 | 27.3822 | 27.8862 | 28.1154 | 28.2359 | 27.8178 | 28.0361 | 28.8739 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797
70% | 444.0146 | 15.8418 | 18.4153 | 21.8986 | 22.207 | 22.4132 | 22.7031 | 23.3638 | 23.8825 | 24.3438 | 24.5056 | 24.6905 | 24.432 | 24.5683 | 25.209 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 70% | 388.1413 | 17.5333 | 20.1143 | 23.6258 | 23.9077 | 24.1059 | 24.31 | 25.0968 | 25.5567 | 26.0271 | 26.2411 | 26.3535 | 25.9633 | 26.167 | 26.949 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811
65% | 770.3386 | 14.7103 | 17.0999 | 20.3344 | 20.6207 | 20.8122 | 21.0815 | 21.6949 | 22.1767 | 22.605 | 22.7552 | 22.9269 | 22.6869 | 22.8135 | 23.4083 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 65% | 669.8855 | 16.2809 | 18.6776 | 21.9383 | 22.2001 | 22.3841 | 22.5735 | 23.3041 | 23.7312 | 24.168 | 24.3667 | 24.4711 | 24.1088 | 24.298 | 25.0241 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824
60% | 1209.3009 | 13.5787 | 15.7845 | 18.7703 | 19.0345 | 19.2113 | 19.4598 | 20.0261 | 20.4708 | 20.8661 | 21.0048 | 21.1633 | 20.9417 | 21.0586 | 21.6077 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 60% | 1104.687 | 15.0286 | 17.2408 | 20.2507 | 20.4924 | 20.6622 | 20.8371 | 21.5115 | 21.9057 | 22.3089 | 22.4923 | 22.5887 | 22.2542 | 22.4289 | 23.0991 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838
55% | 1757.6322 | 12.4472 | 14.4691 | 17.2061 | 17.4483 | 17.6104 | 17.8382 | 18.3573 | 18.7649 | 19.1273 | 19.2544 | 19.3997 | 19.1966 | 19.3037 | 19.8071 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 55% | 1631.62 | 13.7762 | 15.8041 | 18.5631 | 18.7847 | 18.9404 | 19.1007 | 19.7189 | 20.0803 | 20.4498 | 20.618 | 20.7063 | 20.3997 | 20.5598 | 21.1742 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851
50% | 2378.4799 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 50% | 2253.9537 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
45% | 3003.7856 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 45% | 2892.3362 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
40% | 3548.2533 | 9.0525 | 10.523 | 12.5135 | 12.6897 | 12.8075 | 12.9732 | 13.3507 | 13.6472 | 13.9108 | 14.0032 | 14.1089 | 13.9612 | 14.0391 | 14.4051 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 40% | 3473.3593 | 10.019 | 11.4939 | 13.5005 | 13.6616 | 13.7748 | 13.8914 | 14.341 | 14.6038 | 14.8726 | 14.9949 | 15.0592 | 14.8362 | 14.9526 | 15.3994 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892
35% | 3927.7759 | 7.9209 | 9.2076 | 10.9493 | 11.1035 | 11.2066 | 11.3516 | 11.6819 | 11.9413 | 12.1719 | 12.2528 | 12.3453 | 12.216 | 12.2842 | 12.6045 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 35% | 3882.8989 | 8.7667 | 10.0572 | 11.8129 | 11.9539 | 12.053 | 12.155 | 12.5484 | 12.7783 | 13.0135 | 13.1205 | 13.1768 | 12.9816 | 13.0835 | 13.4745 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905
30% | 4135.8149 | 6.7894 | 7.8923 | 9.3851 | 9.5173 | 9.6057 | 9.7299 | 10.0131 | 10.2354 | 10.4331 | 10.5024 | 10.5816 | 10.4709 | 10.5293 | 10.8038 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 30% | 4127.1961 | 7.5143 | 8.6204 | 10.1253 | 10.2462 | 10.3311 | 10.4186 | 10.7558 | 10.9529 | 11.1545 | 11.2462 | 11.2944 | 11.1271 | 11.2144 | 11.5496 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919
25% | 4252.0195 | 5.6578 | 6.5769 | 7.8209 | 7.9311 | 8.0047 | 8.1083 | 8.3442 | 8.5295 | 8.6942 | 8.752 | 8.818 | 8.7257 | 8.7744 | 9.0032 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 25% | 4245.1839 | 6.2619 | 7.1837 | 8.4378 | 8.5385 | 8.6093 | 8.6821 | 8.9631 | 9.1274 | 9.2954 | 9.3718 | 9.412 | 9.2726 | 9.3454 | 9.6246 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932
20% | 4325.4275 | 4.5262 | 5.2615 | 6.2568 | 6.3448 | 6.4038 | 6.4866 | 6.6754 | 6.8236 | 6.9554 | 7.0016 | 7.0544 | 6.9806 | 7.0195 | 7.2026 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 20% | 4322.1583 | 5.0095 | 5.7469 | 6.7502 | 6.8308 | 6.8874 | 6.9457 | 7.1705 | 7.3019 | 7.4363 | 7.4974 | 7.5296 | 7.4181 | 7.4763 | 7.6997 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946
15% | 4360.497 | 3.3947 | 3.9461 | 4.6926 | 4.7586 | 4.8028 | 4.865 | 5.0065 | 5.1177 | 5.2165 | 5.2512 | 5.2908 | 5.2354 | 5.2646 | 5.4019 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 15% | 4354.2558 | 3.7571 | 4.3102 | 5.0627 | 5.1231 | 5.1656 | 5.2093 | 5.3779 | 5.4764 | 5.5772 | 5.6231 | 5.6472 | 5.5636 | 5.6072 | 5.7748 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959
10% | 4373.8709 | 2.2631 | 2.6308 | 3.1284 | 3.1724 | 3.2019 | 3.2433 | 3.3377 | 3.4118 | 3.4777 | 3.5008 | 3.5272 | 3.4903 | 3.5098 | 3.6013 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 10% | 4366.1437 | 2.5048 | 2.8735 | 3.3751 | 3.4154 | 3.4437 | 3.4729 | 3.5853 | 3.651 | 3.7182 | 3.7487 | 3.7648 | 3.709 | 3.7381 | 3.8499 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973
5% | 4381.8952 | 1.1316 | 1.3154 | 1.5642 | 1.5862 | 1.6009 | 1.6217 | 1.6688 | 1.7059 | 1.7388 | 1.7504 | 1.7636 | 1.7451 | 1.7549 | 1.8006 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 5% | 4374.4653 | 1.2524 | 1.4367 | 1.6876 | 1.7077 | 1.7219 | 1.7364 | 1.7926 | 1.8255 | 1.8591 | 1.8744 | 1.8824 | 1.8545 | 1.8691 | 1.9249 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986
9.992e-14% | 4391.7028 | 2.2613e-14 | 2.6286e-14 | 3.1259e-14 | 3.1699e-14 | 3.1993e-14 | 3.2407e-14 | 3.335e-14 | 3.4091e-14 | 3.4749e-14 | 3.498e-14 | 3.5244e-14 | 3.4875e-14 | 3.507e-14 | 3.5984e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 9.992e-14% | 4375.9513 | 2.5028e-14 | 2.8712e-14 | 3.3724e-14 | 3.4127e-14 | 3.4409e-14 | 3.4701e-14 | 3.5824e-14 | 3.648e-14 | 3.7152e-14 | 3.7457e-14 | 3.7618e-14 | 3.7061e-14 | 3.7352e-14 | 3.8468e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 100% | 0 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
99% | 0.37816 | 25.6004 | 28.4203 | 33.1682 | 33.1325 | 33.1003 | 33.615 | 34.3705 | 34.8883 | 34.259 | 34.3215 | 34.6215 | 35.8093 | 34.6838 | 34.6177 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 99% | 1.1345 | 27.8174 | 31.2882 | 36.0278 | 35.9641 | 36.0059 | 36.1355 | 36.5757 | 36.8706 | 37.1125 | 37.1481 | 37.3662 | 37.4435 | 37.4433 | 37.3934 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828
98% | 0.37816 | 25.3418 | 28.1332 | 32.8331 | 32.7978 | 32.766 | 33.2754 | 34.0234 | 34.5359 | 33.9129 | 33.9749 | 34.2718 | 35.4476 | 34.3335 | 34.268 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 98% | 1.8908 | 27.5364 | 30.9722 | 35.6639 | 35.6008 | 35.6422 | 35.7705 | 36.2063 | 36.4982 | 36.7376 | 36.7729 | 36.9888 | 37.0653 | 37.0651 | 37.0157 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052
97% | 0.75633 | 25.0832 | 27.8462 | 32.4981 | 32.4631 | 32.4316 | 32.9359 | 33.6762 | 34.1835 | 33.5669 | 33.6282 | 33.9221 | 35.0859 | 33.9831 | 33.9184 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 97% | 2.269 | 27.2555 | 30.6561 | 35.3 | 35.2376 | 35.2785 | 35.4055 | 35.8368 | 36.1258 | 36.3627 | 36.3976 | 36.6114 | 36.6871 | 36.6869 | 36.638 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276
95% | 0.75633 | 24.566 | 27.272 | 31.828 | 31.7938 | 31.763 | 32.2568 | 32.9818 | 33.4787 | 32.8748 | 32.9348 | 33.2226 | 34.3625 | 33.2825 | 33.219 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 95% | 4.1598 | 26.6935 | 30.0241 | 34.5721 | 34.511 | 34.5511 | 34.6754 | 35.0979 | 35.3809 | 35.613 | 35.6472 | 35.8565 | 35.9307 | 35.9305 | 35.8826 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724
90% | 3.7816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 90% | 15.5047 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
85% | 13.6139 | 21.9801 | 24.4013 | 28.4777 | 28.4471 | 28.4195 | 28.8613 | 29.5101 | 29.9546 | 29.4143 | 29.468 | 29.7255 | 30.7454 | 29.779 | 29.7223 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 85% | 31.3876 | 23.8836 | 26.8636 | 30.9329 | 30.8783 | 30.9141 | 31.0254 | 31.4034 | 31.6566 | 31.8643 | 31.8948 | 32.0821 | 32.1485 | 32.1483 | 32.1054 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963
80% | 35.1693 | 20.6872 | 22.9659 | 26.8026 | 26.7737 | 26.7478 | 27.1636 | 27.7742 | 28.1926 | 27.684 | 27.7346 | 27.977 | 28.9368 | 28.0273 | 27.9739 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 80% | 57.8591 | 22.4787 | 25.2834 | 29.1134 | 29.0619 | 29.0957 | 29.2004 | 29.5561 | 29.7944 | 29.9899 | 30.0187 | 30.1949 | 30.2574 | 30.2572 | 30.2169 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083
75% | 80.549 | 19.3942 | 21.5305 | 25.1274 | 25.1004 | 25.076 | 25.4659 | 26.0383 | 26.4305 | 25.9538 | 26.0012 | 26.2284 | 27.1283 | 26.2756 | 26.2255 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 75% | 121.3907 | 21.0738 | 23.7032 | 27.2938 | 27.2455 | 27.2772 | 27.3753 | 27.7089 | 27.9323 | 28.1155 | 28.1425 | 28.3078 | 28.3663 | 28.3662 | 28.3283 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203
70% | 192.1075 | 18.1013 | 20.0952 | 23.4522 | 23.427 | 23.4043 | 23.7682 | 24.3024 | 24.6685 | 24.2235 | 24.2678 | 24.4798 | 25.3197 | 24.5239 | 24.4772 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 70% | 273.4128 | 19.6689 | 22.123 | 25.4742 | 25.4292 | 25.4587 | 25.5503 | 25.8616 | 26.0701 | 26.2411 | 26.2663 | 26.4206 | 26.4752 | 26.4751 | 26.4398 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323
65% | 403.1231 | 16.8083 | 18.6598 | 21.7771 | 21.7537 | 21.7325 | 22.0704 | 22.5665 | 22.9065 | 22.4933 | 22.5343 | 22.7313 | 23.5112 | 22.7722 | 22.7288 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 65% | 529.43 | 18.264 | 20.5428 | 23.6546 | 23.6128 | 23.6402 | 23.7253 | 24.0144 | 24.208 | 24.3668 | 24.3902 | 24.5334 | 24.5841 | 24.584 | 24.5512 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443
60% | 739.3112 | 15.5154 | 17.2244 | 20.1019 | 20.0803 | 20.0608 | 20.3727 | 20.8306 | 21.1444 | 20.763 | 20.8009 | 20.9827 | 21.7026 | 21.0205 | 20.9804 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 60% | 918.9392 | 16.859 | 18.9626 | 21.835 | 21.7964 | 21.8218 | 21.9003 | 22.1671 | 22.3458 | 22.4924 | 22.514 | 22.6462 | 22.6931 | 22.6929 | 22.6627 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562
55% | 1204.8314 | 14.2224 | 15.7891 | 18.4268 | 18.4069 | 18.3891 | 18.675 | 19.0947 | 19.3824 | 19.0328 | 19.0675 | 19.2342 | 19.8941 | 19.2688 | 19.2321 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 55% | 1454.0417 | 15.4541 | 17.3823 | 20.0154 | 19.9801 | 20.0033 | 20.0753 | 20.3198 | 20.4837 | 20.618 | 20.6378 | 20.759 | 20.802 | 20.8019 | 20.7741 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682
50% | 1783.0446 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 50% | 2105.2406 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
45% | 2370.3337 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 45% | 2758.3303 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
40% | 2864.2163 | 10.3436 | 11.483 | 13.4013 | 13.3869 | 13.3739 | 13.5818 | 13.8871 | 14.0963 | 13.842 | 13.8673 | 13.9885 | 14.4684 | 14.0137 | 13.987 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 40% | 3348.2666 | 11.2394 | 12.6417 | 14.5567 | 14.531 | 14.5478 | 14.6002 | 14.7781 | 14.8972 | 14.9949 | 15.0093 | 15.0975 | 15.1287 | 15.1286 | 15.1084 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042
35% | 3297.9707 | 9.0506 | 10.0476 | 11.7261 | 11.7135 | 11.7021 | 11.8841 | 12.1512 | 12.3343 | 12.1118 | 12.1339 | 12.2399 | 12.6599 | 12.262 | 12.2386 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 35% | 3816.434 | 9.8344 | 11.0615 | 12.7371 | 12.7146 | 12.7294 | 12.7752 | 12.9308 | 13.0351 | 13.1206 | 13.1332 | 13.2103 | 13.2376 | 13.2375 | 13.2199 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161
30% | 3579.7031 | 7.7577 | 8.6122 | 10.051 | 10.0401 | 10.0304 | 10.1864 | 10.4153 | 10.5722 | 10.3815 | 10.4005 | 10.4914 | 10.8513 | 10.5102 | 10.4902 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 30% | 4067.1569 | 8.4295 | 9.4813 | 10.9175 | 10.8982 | 10.9109 | 10.9501 | 11.0836 | 11.1729 | 11.2462 | 11.257 | 11.3231 | 11.3465 | 11.3465 | 11.3313 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281
25% | 3796.3913 | 6.4647 | 7.1768 | 8.3758 | 8.3668 | 8.3587 | 8.4886 | 8.6794 | 8.8102 | 8.6513 | 8.6671 | 8.7428 | 9.0428 | 8.7585 | 8.7418 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 25% | 4236.9526 | 7.0246 | 7.9011 | 9.0979 | 9.0818 | 9.0924 | 9.1251 | 9.2363 | 9.3108 | 9.3718 | 9.3808 | 9.4359 | 9.4554 | 9.4554 | 9.4428 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401
20% | 3975.6411 | 5.1718 | 5.7415 | 6.7006 | 6.6934 | 6.6869 | 6.7909 | 6.9435 | 7.0481 | 6.921 | 6.9336 | 6.9942 | 7.2342 | 7.0068 | 6.9935 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 20% | 4332.6282 | 5.6197 | 6.3209 | 7.2783 | 7.2655 | 7.2739 | 7.3001 | 7.389 | 7.4486 | 7.4975 | 7.5047 | 7.5487 | 7.5644 | 7.5643 | 7.5542 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521
15% | 4117.4527 | 3.8788 | 4.3061 | 5.0255 | 5.0201 | 5.0152 | 5.0932 | 5.2077 | 5.2861 | 5.1908 | 5.2002 | 5.2457 | 5.4257 | 5.2551 | 5.2451 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 15% | 4361.7469 | 4.2148 | 4.7406 | 5.4588 | 5.4491 | 5.4554 | 5.4751 | 5.5418 | 5.5865 | 5.6231 | 5.6285 | 5.6616 | 5.6733 | 5.6732 | 5.6657 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641
10% | 4224.8514 | 2.5859 | 2.8707 | 3.3503 | 3.3467 | 3.3435 | 3.3955 | 3.4718 | 3.5241 | 3.4605 | 3.4668 | 3.4971 | 3.6171 | 3.5034 | 3.4967 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 10% | 4375.7389 | 2.8098 | 3.1604 | 3.6392 | 3.6327 | 3.637 | 3.65 | 3.6945 | 3.7243 | 3.7487 | 3.7523 | 3.7744 | 3.7822 | 3.7822 | 3.7771 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776
5% | 4310.3165 | 1.2929 | 1.4354 | 1.6752 | 1.6734 | 1.6717 | 1.6977 | 1.7359 | 1.762 | 1.7303 | 1.7334 | 1.7486 | 1.8086 | 1.7517 | 1.7484 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 5% | 4378.0079 | 1.4049 | 1.5802 | 1.8196 | 1.8164 | 1.8185 | 1.825 | 1.8473 | 1.8622 | 1.8744 | 1.8762 | 1.8872 | 1.8911 | 1.8911 | 1.8886 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888
9.992e-14% | 4382.5459 | 2.5838e-14 | 2.8684e-14 | 3.3476e-14 | 3.344e-14 | 3.3408e-14 | 3.3927e-14 | 3.469e-14 | 3.5213e-14 | 3.4577e-14 | 3.4641e-14 | 3.4943e-14 | 3.6142e-14 | 3.5006e-14 | 3.4939e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 9.992e-14% | 4379.1424 | 2.8076e-14 | 3.1579e-14 | 3.6363e-14 | 3.6298e-14 | 3.6341e-14 | 3.6471e-14 | 3.6916e-14 | 3.7213e-14 | 3.7457e-14 | 3.7493e-14 | 3.7714e-14 | 3.7792e-14 | 3.7791e-14 | 3.7741e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 100% | 0 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
99% | 0.2972 | 22.4049 | 26.0444 | 30.9709 | 31.407 | 31.6987 | 32.1087 | 33.0431 | 33.7767 | 34.4291 | 34.658 | 34.9194 | 34.5539 | 34.7466 | 35.6527 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 99% | 0.2972 | 24.7971 | 28.4474 | 33.4137 | 33.8124 | 34.0926 | 34.3812 | 35.494 | 36.1445 | 36.8097 | 37.1123 | 37.2714 | 36.7195 | 37.0077 | 38.1136 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932
98% | 0.8916 | 22.1786 | 25.7814 | 30.6581 | 31.0897 | 31.3785 | 31.7844 | 32.7093 | 33.4356 | 34.0814 | 34.3079 | 34.5667 | 34.2049 | 34.3957 | 35.2926 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 98% | 0.8916 | 24.5466 | 28.16 | 33.0761 | 33.4708 | 33.7483 | 34.0339 | 35.1355 | 35.7794 | 36.4379 | 36.7375 | 36.8949 | 36.3486 | 36.6338 | 37.7286 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135
97% | 1.7832 | 21.9523 | 25.5183 | 30.3452 | 30.7725 | 31.0583 | 31.46 | 32.3755 | 33.0944 | 33.7336 | 33.9578 | 34.214 | 33.8558 | 34.0447 | 34.9324 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 97% | 2.0804 | 24.2962 | 27.8727 | 32.7386 | 33.1293 | 33.4039 | 33.6866 | 34.777 | 35.4143 | 36.0661 | 36.3626 | 36.5184 | 35.9777 | 36.26 | 37.3436 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338
95% | 4.458 | 21.4996 | 24.9921 | 29.7196 | 30.138 | 30.4179 | 30.8114 | 31.708 | 32.412 | 33.038 | 33.2576 | 33.5085 | 33.1578 | 33.3427 | 34.2122 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 95% | 4.1608 | 23.7952 | 27.298 | 32.0636 | 32.4462 | 32.7152 | 32.9921 | 34.0599 | 34.6841 | 35.3225 | 35.6129 | 35.7655 | 35.2359 | 35.5124 | 36.5736 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743
90% | 15.1571 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 90% | 11.5907 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
85% | 39.5274 | 19.2365 | 22.3614 | 26.5912 | 26.9656 | 27.216 | 27.5681 | 28.3703 | 29.0002 | 29.5604 | 29.7568 | 29.9813 | 29.6675 | 29.833 | 30.6109 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 85% | 32.6918 | 21.2905 | 24.4245 | 28.6885 | 29.0308 | 29.2715 | 29.5192 | 30.4747 | 31.0331 | 31.6043 | 31.8641 | 32.0007 | 31.5268 | 31.7743 | 32.7238 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277
80% | 110.5579 | 18.105 | 21.046 | 25.027 | 25.3794 | 25.6151 | 25.9464 | 26.7015 | 27.2943 | 27.8215 | 28.0064 | 28.2177 | 27.9223 | 28.0781 | 28.8103 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 80% | 84.1072 | 20.0381 | 22.9878 | 27.0009 | 27.3231 | 27.5496 | 27.7828 | 28.682 | 29.2076 | 29.7452 | 29.9898 | 30.1183 | 29.6723 | 29.9052 | 30.7988 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784
75% | 244.2972 | 16.9734 | 19.7306 | 23.4628 | 23.7932 | 24.0141 | 24.3248 | 25.0326 | 25.5884 | 26.0827 | 26.256 | 26.4541 | 26.1772 | 26.3232 | 27.0096 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 75% | 202.095 | 18.7857 | 21.5511 | 25.3134 | 25.6154 | 25.8278 | 26.0464 | 26.8894 | 27.3822 | 27.8862 | 28.1154 | 28.2359 | 27.8178 | 28.0361 | 28.8739 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797
70% | 444.0146 | 15.8418 | 18.4153 | 21.8986 | 22.207 | 22.4132 | 22.7031 | 23.3638 | 23.8825 | 24.3438 | 24.5056 | 24.6905 | 24.432 | 24.5683 | 25.209 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 70% | 388.1413 | 17.5333 | 20.1143 | 23.6258 | 23.9077 | 24.1059 | 24.31 | 25.0968 | 25.5567 | 26.0271 | 26.2411 | 26.3535 | 25.9633 | 26.167 | 26.949 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811
65% | 770.3386 | 14.7103 | 17.0999 | 20.3344 | 20.6207 | 20.8122 | 21.0815 | 21.6949 | 22.1767 | 22.605 | 22.7552 | 22.9269 | 22.6869 | 22.8135 | 23.4083 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 65% | 669.8855 | 16.2809 | 18.6776 | 21.9383 | 22.2001 | 22.3841 | 22.5735 | 23.3041 | 23.7312 | 24.168 | 24.3667 | 24.4711 | 24.1088 | 24.298 | 25.0241 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824
60% | 1209.3009 | 13.5787 | 15.7845 | 18.7703 | 19.0345 | 19.2113 | 19.4598 | 20.0261 | 20.4708 | 20.8661 | 21.0048 | 21.1633 | 20.9417 | 21.0586 | 21.6077 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 60% | 1104.687 | 15.0286 | 17.2408 | 20.2507 | 20.4924 | 20.6622 | 20.8371 | 21.5115 | 21.9057 | 22.3089 | 22.4923 | 22.5887 | 22.2542 | 22.4289 | 23.0991 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838
55% | 1757.6322 | 12.4472 | 14.4691 | 17.2061 | 17.4483 | 17.6104 | 17.8382 | 18.3573 | 18.7649 | 19.1273 | 19.2544 | 19.3997 | 19.1966 | 19.3037 | 19.8071 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 55% | 1631.62 | 13.7762 | 15.8041 | 18.5631 | 18.7847 | 18.9404 | 19.1007 | 19.7189 | 20.0803 | 20.4498 | 20.618 | 20.7063 | 20.3997 | 20.5598 | 21.1742 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851
50% | 2378.4799 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 50% | 2253.9537 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
45% | 3003.7856 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 45% | 2892.3362 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
40% | 3548.2533 | 9.0525 | 10.523 | 12.5135 | 12.6897 | 12.8075 | 12.9732 | 13.3507 | 13.6472 | 13.9108 | 14.0032 | 14.1089 | 13.9612 | 14.0391 | 14.4051 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 40% | 3473.3593 | 10.019 | 11.4939 | 13.5005 | 13.6616 | 13.7748 | 13.8914 | 14.341 | 14.6038 | 14.8726 | 14.9949 | 15.0592 | 14.8362 | 14.9526 | 15.3994 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892
35% | 3927.7759 | 7.9209 | 9.2076 | 10.9493 | 11.1035 | 11.2066 | 11.3516 | 11.6819 | 11.9413 | 12.1719 | 12.2528 | 12.3453 | 12.216 | 12.2842 | 12.6045 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 35% | 3882.8989 | 8.7667 | 10.0572 | 11.8129 | 11.9539 | 12.053 | 12.155 | 12.5484 | 12.7783 | 13.0135 | 13.1205 | 13.1768 | 12.9816 | 13.0835 | 13.4745 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905
30% | 4135.8149 | 6.7894 | 7.8923 | 9.3851 | 9.5173 | 9.6057 | 9.7299 | 10.0131 | 10.2354 | 10.4331 | 10.5024 | 10.5816 | 10.4709 | 10.5293 | 10.8038 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 30% | 4127.1961 | 7.5143 | 8.6204 | 10.1253 | 10.2462 | 10.3311 | 10.4186 | 10.7558 | 10.9529 | 11.1545 | 11.2462 | 11.2944 | 11.1271 | 11.2144 | 11.5496 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919
25% | 4252.0195 | 5.6578 | 6.5769 | 7.8209 | 7.9311 | 8.0047 | 8.1083 | 8.3442 | 8.5295 | 8.6942 | 8.752 | 8.818 | 8.7257 | 8.7744 | 9.0032 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 25% | 4245.1839 | 6.2619 | 7.1837 | 8.4378 | 8.5385 | 8.6093 | 8.6821 | 8.9631 | 9.1274 | 9.2954 | 9.3718 | 9.412 | 9.2726 | 9.3454 | 9.6246 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932
20% | 4325.4275 | 4.5262 | 5.2615 | 6.2568 | 6.3448 | 6.4038 | 6.4866 | 6.6754 | 6.8236 | 6.9554 | 7.0016 | 7.0544 | 6.9806 | 7.0195 | 7.2026 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 20% | 4322.1583 | 5.0095 | 5.7469 | 6.7502 | 6.8308 | 6.8874 | 6.9457 | 7.1705 | 7.3019 | 7.4363 | 7.4974 | 7.5296 | 7.4181 | 7.4763 | 7.6997 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946
15% | 4360.497 | 3.3947 | 3.9461 | 4.6926 | 4.7586 | 4.8028 | 4.865 | 5.0065 | 5.1177 | 5.2165 | 5.2512 | 5.2908 | 5.2354 | 5.2646 | 5.4019 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 15% | 4354.2558 | 3.7571 | 4.3102 | 5.0627 | 5.1231 | 5.1656 | 5.2093 | 5.3779 | 5.4764 | 5.5772 | 5.6231 | 5.6472 | 5.5636 | 5.6072 | 5.7748 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959
10% | 4373.8709 | 2.2631 | 2.6308 | 3.1284 | 3.1724 | 3.2019 | 3.2433 | 3.3377 | 3.4118 | 3.4777 | 3.5008 | 3.5272 | 3.4903 | 3.5098 | 3.6013 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 10% | 4366.1437 | 2.5048 | 2.8735 | 3.3751 | 3.4154 | 3.4437 | 3.4729 | 3.5853 | 3.651 | 3.7182 | 3.7487 | 3.7648 | 3.709 | 3.7381 | 3.8499 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973
5% | 4381.8952 | 1.1316 | 1.3154 | 1.5642 | 1.5862 | 1.6009 | 1.6217 | 1.6688 | 1.7059 | 1.7388 | 1.7504 | 1.7636 | 1.7451 | 1.7549 | 1.8006 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 5% | 4374.4653 | 1.2524 | 1.4367 | 1.6876 | 1.7077 | 1.7219 | 1.7364 | 1.7926 | 1.8255 | 1.8591 | 1.8744 | 1.8824 | 1.8545 | 1.8691 | 1.9249 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986
9.992e-14% | 4391.7028 | 2.2613e-14 | 2.6286e-14 | 3.1259e-14 | 3.1699e-14 | 3.1993e-14 | 3.2407e-14 | 3.335e-14 | 3.4091e-14 | 3.4749e-14 | 3.498e-14 | 3.5244e-14 | 3.4875e-14 | 3.507e-14 | 3.5984e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 9.992e-14% | 4375.9513 | 2.5028e-14 | 2.8712e-14 | 3.3724e-14 | 3.4127e-14 | 3.4409e-14 | 3.4701e-14 | 3.5824e-14 | 3.648e-14 | 3.7152e-14 | 3.7457e-14 | 3.7618e-14 | 3.7061e-14 | 3.7352e-14 | 3.8468e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 100% | 0 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
99% | 0.37816 | 25.6004 | 28.4203 | 33.1682 | 33.1325 | 33.1003 | 33.615 | 34.3705 | 34.8883 | 34.259 | 34.3215 | 34.6215 | 35.8093 | 34.6838 | 34.6177 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 99% | 1.1345 | 27.8174 | 31.2882 | 36.0278 | 35.9641 | 36.0059 | 36.1355 | 36.5757 | 36.8706 | 37.1125 | 37.1481 | 37.3662 | 37.4435 | 37.4433 | 37.3934 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828
98% | 0.37816 | 25.3418 | 28.1332 | 32.8331 | 32.7978 | 32.766 | 33.2754 | 34.0234 | 34.5359 | 33.9129 | 33.9749 | 34.2718 | 35.4476 | 34.3335 | 34.268 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 98% | 1.8908 | 27.5364 | 30.9722 | 35.6639 | 35.6008 | 35.6422 | 35.7705 | 36.2063 | 36.4982 | 36.7376 | 36.7729 | 36.9888 | 37.0653 | 37.0651 | 37.0157 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052
97% | 0.75633 | 25.0832 | 27.8462 | 32.4981 | 32.4631 | 32.4316 | 32.9359 | 33.6762 | 34.1835 | 33.5669 | 33.6282 | 33.9221 | 35.0859 | 33.9831 | 33.9184 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 97% | 2.269 | 27.2555 | 30.6561 | 35.3 | 35.2376 | 35.2785 | 35.4055 | 35.8368 | 36.1258 | 36.3627 | 36.3976 | 36.6114 | 36.6871 | 36.6869 | 36.638 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276
95% | 0.75633 | 24.566 | 27.272 | 31.828 | 31.7938 | 31.763 | 32.2568 | 32.9818 | 33.4787 | 32.8748 | 32.9348 | 33.2226 | 34.3625 | 33.2825 | 33.219 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 95% | 4.1598 | 26.6935 | 30.0241 | 34.5721 | 34.511 | 34.5511 | 34.6754 | 35.0979 | 35.3809 | 35.613 | 35.6472 | 35.8565 | 35.9307 | 35.9305 | 35.8826 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724
90% | 3.7816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 90% | 15.5047 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
85% | 13.6139 | 21.9801 | 24.4013 | 28.4777 | 28.4471 | 28.4195 | 28.8613 | 29.5101 | 29.9546 | 29.4143 | 29.468 | 29.7255 | 30.7454 | 29.779 | 29.7223 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 85% | 31.3876 | 23.8836 | 26.8636 | 30.9329 | 30.8783 | 30.9141 | 31.0254 | 31.4034 | 31.6566 | 31.8643 | 31.8948 | 32.0821 | 32.1485 | 32.1483 | 32.1054 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963
80% | 35.1693 | 20.6872 | 22.9659 | 26.8026 | 26.7737 | 26.7478 | 27.1636 | 27.7742 | 28.1926 | 27.684 | 27.7346 | 27.977 | 28.9368 | 28.0273 | 27.9739 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 80% | 57.8591 | 22.4787 | 25.2834 | 29.1134 | 29.0619 | 29.0957 | 29.2004 | 29.5561 | 29.7944 | 29.9899 | 30.0187 | 30.1949 | 30.2574 | 30.2572 | 30.2169 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083
75% | 80.549 | 19.3942 | 21.5305 | 25.1274 | 25.1004 | 25.076 | 25.4659 | 26.0383 | 26.4305 | 25.9538 | 26.0012 | 26.2284 | 27.1283 | 26.2756 | 26.2255 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 75% | 121.3907 | 21.0738 | 23.7032 | 27.2938 | 27.2455 | 27.2772 | 27.3753 | 27.7089 | 27.9323 | 28.1155 | 28.1425 | 28.3078 | 28.3663 | 28.3662 | 28.3283 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203
70% | 192.1075 | 18.1013 | 20.0952 | 23.4522 | 23.427 | 23.4043 | 23.7682 | 24.3024 | 24.6685 | 24.2235 | 24.2678 | 24.4798 | 25.3197 | 24.5239 | 24.4772 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 70% | 273.4128 | 19.6689 | 22.123 | 25.4742 | 25.4292 | 25.4587 | 25.5503 | 25.8616 | 26.0701 | 26.2411 | 26.2663 | 26.4206 | 26.4752 | 26.4751 | 26.4398 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323
65% | 403.1231 | 16.8083 | 18.6598 | 21.7771 | 21.7537 | 21.7325 | 22.0704 | 22.5665 | 22.9065 | 22.4933 | 22.5343 | 22.7313 | 23.5112 | 22.7722 | 22.7288 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 65% | 529.43 | 18.264 | 20.5428 | 23.6546 | 23.6128 | 23.6402 | 23.7253 | 24.0144 | 24.208 | 24.3668 | 24.3902 | 24.5334 | 24.5841 | 24.584 | 24.5512 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443
60% | 739.3112 | 15.5154 | 17.2244 | 20.1019 | 20.0803 | 20.0608 | 20.3727 | 20.8306 | 21.1444 | 20.763 | 20.8009 | 20.9827 | 21.7026 | 21.0205 | 20.9804 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 60% | 918.9392 | 16.859 | 18.9626 | 21.835 | 21.7964 | 21.8218 | 21.9003 | 22.1671 | 22.3458 | 22.4924 | 22.514 | 22.6462 | 22.6931 | 22.6929 | 22.6627 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562
55% | 1204.8314 | 14.2224 | 15.7891 | 18.4268 | 18.4069 | 18.3891 | 18.675 | 19.0947 | 19.3824 | 19.0328 | 19.0675 | 19.2342 | 19.8941 | 19.2688 | 19.2321 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 55% | 1454.0417 | 15.4541 | 17.3823 | 20.0154 | 19.9801 | 20.0033 | 20.0753 | 20.3198 | 20.4837 | 20.618 | 20.6378 | 20.759 | 20.802 | 20.8019 | 20.7741 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682
50% | 1783.0446 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 50% | 2105.2406 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
45% | 2370.3337 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 45% | 2758.3303 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
40% | 2864.2163 | 10.3436 | 11.483 | 13.4013 | 13.3869 | 13.3739 | 13.5818 | 13.8871 | 14.0963 | 13.842 | 13.8673 | 13.9885 | 14.4684 | 14.0137 | 13.987 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 40% | 3348.2666 | 11.2394 | 12.6417 | 14.5567 | 14.531 | 14.5478 | 14.6002 | 14.7781 | 14.8972 | 14.9949 | 15.0093 | 15.0975 | 15.1287 | 15.1286 | 15.1084 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042
35% | 3297.9707 | 9.0506 | 10.0476 | 11.7261 | 11.7135 | 11.7021 | 11.8841 | 12.1512 | 12.3343 | 12.1118 | 12.1339 | 12.2399 | 12.6599 | 12.262 | 12.2386 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 35% | 3816.434 | 9.8344 | 11.0615 | 12.7371 | 12.7146 | 12.7294 | 12.7752 | 12.9308 | 13.0351 | 13.1206 | 13.1332 | 13.2103 | 13.2376 | 13.2375 | 13.2199 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161
30% | 3579.7031 | 7.7577 | 8.6122 | 10.051 | 10.0401 | 10.0304 | 10.1864 | 10.4153 | 10.5722 | 10.3815 | 10.4005 | 10.4914 | 10.8513 | 10.5102 | 10.4902 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 30% | 4067.1569 | 8.4295 | 9.4813 | 10.9175 | 10.8982 | 10.9109 | 10.9501 | 11.0836 | 11.1729 | 11.2462 | 11.257 | 11.3231 | 11.3465 | 11.3465 | 11.3313 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281
25% | 3796.3913 | 6.4647 | 7.1768 | 8.3758 | 8.3668 | 8.3587 | 8.4886 | 8.6794 | 8.8102 | 8.6513 | 8.6671 | 8.7428 | 9.0428 | 8.7585 | 8.7418 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 25% | 4236.9526 | 7.0246 | 7.9011 | 9.0979 | 9.0818 | 9.0924 | 9.1251 | 9.2363 | 9.3108 | 9.3718 | 9.3808 | 9.4359 | 9.4554 | 9.4554 | 9.4428 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401
20% | 3975.6411 | 5.1718 | 5.7415 | 6.7006 | 6.6934 | 6.6869 | 6.7909 | 6.9435 | 7.0481 | 6.921 | 6.9336 | 6.9942 | 7.2342 | 7.0068 | 6.9935 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 20% | 4332.6282 | 5.6197 | 6.3209 | 7.2783 | 7.2655 | 7.2739 | 7.3001 | 7.389 | 7.4486 | 7.4975 | 7.5047 | 7.5487 | 7.5644 | 7.5643 | 7.5542 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521
15% | 4117.4527 | 3.8788 | 4.3061 | 5.0255 | 5.0201 | 5.0152 | 5.0932 | 5.2077 | 5.2861 | 5.1908 | 5.2002 | 5.2457 | 5.4257 | 5.2551 | 5.2451 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 15% | 4361.7469 | 4.2148 | 4.7406 | 5.4588 | 5.4491 | 5.4554 | 5.4751 | 5.5418 | 5.5865 | 5.6231 | 5.6285 | 5.6616 | 5.6733 | 5.6732 | 5.6657 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641
10% | 4224.8514 | 2.5859 | 2.8707 | 3.3503 | 3.3467 | 3.3435 | 3.3955 | 3.4718 | 3.5241 | 3.4605 | 3.4668 | 3.4971 | 3.6171 | 3.5034 | 3.4967 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 10% | 4375.7389 | 2.8098 | 3.1604 | 3.6392 | 3.6327 | 3.637 | 3.65 | 3.6945 | 3.7243 | 3.7487 | 3.7523 | 3.7744 | 3.7822 | 3.7822 | 3.7771 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776
5% | 4310.3165 | 1.2929 | 1.4354 | 1.6752 | 1.6734 | 1.6717 | 1.6977 | 1.7359 | 1.762 | 1.7303 | 1.7334 | 1.7486 | 1.8086 | 1.7517 | 1.7484 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 5% | 4378.0079 | 1.4049 | 1.5802 | 1.8196 | 1.8164 | 1.8185 | 1.825 | 1.8473 | 1.8622 | 1.8744 | 1.8762 | 1.8872 | 1.8911 | 1.8911 | 1.8886 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888
9.992e-14% | 4382.5459 | 2.5838e-14 | 2.8684e-14 | 3.3476e-14 | 3.344e-14 | 3.3408e-14 | 3.3927e-14 | 3.469e-14 | 3.5213e-14 | 3.4577e-14 | 3.4641e-14 | 3.4943e-14 | 3.6142e-14 | 3.5006e-14 | 3.4939e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 9.992e-14% | 4379.1424 | 2.8076e-14 | 3.1579e-14 | 3.6363e-14 | 3.6298e-14 | 3.6341e-14 | 3.6471e-14 | 3.6916e-14 | 3.7213e-14 | 3.7457e-14 | 3.7493e-14 | 3.7714e-14 | 3.7792e-14 | 3.7791e-14 | 3.7741e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 100% | 0 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
99% | 0.2972 | 22.4049 | 26.0444 | 30.9709 | 31.407 | 31.6987 | 32.1087 | 33.0431 | 33.7767 | 34.4291 | 34.658 | 34.9194 | 34.5539 | 34.7466 | 35.6527 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 99% | 0.2972 | 24.7971 | 28.4474 | 33.4137 | 33.8124 | 34.0926 | 34.3812 | 35.494 | 36.1445 | 36.8097 | 37.1123 | 37.2714 | 36.7195 | 37.0077 | 38.1136 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932
98% | 0.8916 | 22.1786 | 25.7814 | 30.6581 | 31.0897 | 31.3785 | 31.7844 | 32.7093 | 33.4356 | 34.0814 | 34.3079 | 34.5667 | 34.2049 | 34.3957 | 35.2926 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 98% | 0.8916 | 24.5466 | 28.16 | 33.0761 | 33.4708 | 33.7483 | 34.0339 | 35.1355 | 35.7794 | 36.4379 | 36.7375 | 36.8949 | 36.3486 | 36.6338 | 37.7286 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135
97% | 1.7832 | 21.9523 | 25.5183 | 30.3452 | 30.7725 | 31.0583 | 31.46 | 32.3755 | 33.0944 | 33.7336 | 33.9578 | 34.214 | 33.8558 | 34.0447 | 34.9324 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 97% | 2.0804 | 24.2962 | 27.8727 | 32.7386 | 33.1293 | 33.4039 | 33.6866 | 34.777 | 35.4143 | 36.0661 | 36.3626 | 36.5184 | 35.9777 | 36.26 | 37.3436 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338
95% | 4.458 | 21.4996 | 24.9921 | 29.7196 | 30.138 | 30.4179 | 30.8114 | 31.708 | 32.412 | 33.038 | 33.2576 | 33.5085 | 33.1578 | 33.3427 | 34.2122 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 95% | 4.1608 | 23.7952 | 27.298 | 32.0636 | 32.4462 | 32.7152 | 32.9921 | 34.0599 | 34.6841 | 35.3225 | 35.6129 | 35.7655 | 35.2359 | 35.5124 | 36.5736 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743
90% | 15.1571 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 90% | 11.5907 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
85% | 39.5274 | 19.2365 | 22.3614 | 26.5912 | 26.9656 | 27.216 | 27.5681 | 28.3703 | 29.0002 | 29.5604 | 29.7568 | 29.9813 | 29.6675 | 29.833 | 30.6109 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 85% | 32.6918 | 21.2905 | 24.4245 | 28.6885 | 29.0308 | 29.2715 | 29.5192 | 30.4747 | 31.0331 | 31.6043 | 31.8641 | 32.0007 | 31.5268 | 31.7743 | 32.7238 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277
80% | 110.5579 | 18.105 | 21.046 | 25.027 | 25.3794 | 25.6151 | 25.9464 | 26.7015 | 27.2943 | 27.8215 | 28.0064 | 28.2177 | 27.9223 | 28.0781 | 28.8103 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 80% | 84.1072 | 20.0381 | 22.9878 | 27.0009 | 27.3231 | 27.5496 | 27.7828 | 28.682 | 29.2076 | 29.7452 | 29.9898 | 30.1183 | 29.6723 | 29.9052 | 30.7988 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784
75% | 244.2972 | 16.9734 | 19.7306 | 23.4628 | 23.7932 | 24.0141 | 24.3248 | 25.0326 | 25.5884 | 26.0827 | 26.256 | 26.4541 | 26.1772 | 26.3232 | 27.0096 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 75% | 202.095 | 18.7857 | 21.5511 | 25.3134 | 25.6154 | 25.8278 | 26.0464 | 26.8894 | 27.3822 | 27.8862 | 28.1154 | 28.2359 | 27.8178 | 28.0361 | 28.8739 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797
70% | 444.0146 | 15.8418 | 18.4153 | 21.8986 | 22.207 | 22.4132 | 22.7031 | 23.3638 | 23.8825 | 24.3438 | 24.5056 | 24.6905 | 24.432 | 24.5683 | 25.209 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 70% | 388.1413 | 17.5333 | 20.1143 | 23.6258 | 23.9077 | 24.1059 | 24.31 | 25.0968 | 25.5567 | 26.0271 | 26.2411 | 26.3535 | 25.9633 | 26.167 | 26.949 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811
65% | 770.3386 | 14.7103 | 17.0999 | 20.3344 | 20.6207 | 20.8122 | 21.0815 | 21.6949 | 22.1767 | 22.605 | 22.7552 | 22.9269 | 22.6869 | 22.8135 | 23.4083 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 65% | 669.8855 | 16.2809 | 18.6776 | 21.9383 | 22.2001 | 22.3841 | 22.5735 | 23.3041 | 23.7312 | 24.168 | 24.3667 | 24.4711 | 24.1088 | 24.298 | 25.0241 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824
60% | 1209.3009 | 13.5787 | 15.7845 | 18.7703 | 19.0345 | 19.2113 | 19.4598 | 20.0261 | 20.4708 | 20.8661 | 21.0048 | 21.1633 | 20.9417 | 21.0586 | 21.6077 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 60% | 1104.687 | 15.0286 | 17.2408 | 20.2507 | 20.4924 | 20.6622 | 20.8371 | 21.5115 | 21.9057 | 22.3089 | 22.4923 | 22.5887 | 22.2542 | 22.4289 | 23.0991 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838
55% | 1757.6322 | 12.4472 | 14.4691 | 17.2061 | 17.4483 | 17.6104 | 17.8382 | 18.3573 | 18.7649 | 19.1273 | 19.2544 | 19.3997 | 19.1966 | 19.3037 | 19.8071 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 55% | 1631.62 | 13.7762 | 15.8041 | 18.5631 | 18.7847 | 18.9404 | 19.1007 | 19.7189 | 20.0803 | 20.4498 | 20.618 | 20.7063 | 20.3997 | 20.5598 | 21.1742 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851
50% | 2378.4799 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 50% | 2253.9537 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
45% | 3003.7856 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 45% | 2892.3362 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
40% | 3548.2533 | 9.0525 | 10.523 | 12.5135 | 12.6897 | 12.8075 | 12.9732 | 13.3507 | 13.6472 | 13.9108 | 14.0032 | 14.1089 | 13.9612 | 14.0391 | 14.4051 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 40% | 3473.3593 | 10.019 | 11.4939 | 13.5005 | 13.6616 | 13.7748 | 13.8914 | 14.341 | 14.6038 | 14.8726 | 14.9949 | 15.0592 | 14.8362 | 14.9526 | 15.3994 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892
35% | 3927.7759 | 7.9209 | 9.2076 | 10.9493 | 11.1035 | 11.2066 | 11.3516 | 11.6819 | 11.9413 | 12.1719 | 12.2528 | 12.3453 | 12.216 | 12.2842 | 12.6045 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 35% | 3882.8989 | 8.7667 | 10.0572 | 11.8129 | 11.9539 | 12.053 | 12.155 | 12.5484 | 12.7783 | 13.0135 | 13.1205 | 13.1768 | 12.9816 | 13.0835 | 13.4745 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905
30% | 4135.8149 | 6.7894 | 7.8923 | 9.3851 | 9.5173 | 9.6057 | 9.7299 | 10.0131 | 10.2354 | 10.4331 | 10.5024 | 10.5816 | 10.4709 | 10.5293 | 10.8038 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 30% | 4127.1961 | 7.5143 | 8.6204 | 10.1253 | 10.2462 | 10.3311 | 10.4186 | 10.7558 | 10.9529 | 11.1545 | 11.2462 | 11.2944 | 11.1271 | 11.2144 | 11.5496 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919
25% | 4252.0195 | 5.6578 | 6.5769 | 7.8209 | 7.9311 | 8.0047 | 8.1083 | 8.3442 | 8.5295 | 8.6942 | 8.752 | 8.818 | 8.7257 | 8.7744 | 9.0032 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 25% | 4245.1839 | 6.2619 | 7.1837 | 8.4378 | 8.5385 | 8.6093 | 8.6821 | 8.9631 | 9.1274 | 9.2954 | 9.3718 | 9.412 | 9.2726 | 9.3454 | 9.6246 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932
20% | 4325.4275 | 4.5262 | 5.2615 | 6.2568 | 6.3448 | 6.4038 | 6.4866 | 6.6754 | 6.8236 | 6.9554 | 7.0016 | 7.0544 | 6.9806 | 7.0195 | 7.2026 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 20% | 4322.1583 | 5.0095 | 5.7469 | 6.7502 | 6.8308 | 6.8874 | 6.9457 | 7.1705 | 7.3019 | 7.4363 | 7.4974 | 7.5296 | 7.4181 | 7.4763 | 7.6997 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946
15% | 4360.497 | 3.3947 | 3.9461 | 4.6926 | 4.7586 | 4.8028 | 4.865 | 5.0065 | 5.1177 | 5.2165 | 5.2512 | 5.2908 | 5.2354 | 5.2646 | 5.4019 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 15% | 4354.2558 | 3.7571 | 4.3102 | 5.0627 | 5.1231 | 5.1656 | 5.2093 | 5.3779 | 5.4764 | 5.5772 | 5.6231 | 5.6472 | 5.5636 | 5.6072 | 5.7748 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959
10% | 4373.8709 | 2.2631 | 2.6308 | 3.1284 | 3.1724 | 3.2019 | 3.2433 | 3.3377 | 3.4118 | 3.4777 | 3.5008 | 3.5272 | 3.4903 | 3.5098 | 3.6013 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 10% | 4366.1437 | 2.5048 | 2.8735 | 3.3751 | 3.4154 | 3.4437 | 3.4729 | 3.5853 | 3.651 | 3.7182 | 3.7487 | 3.7648 | 3.709 | 3.7381 | 3.8499 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973
5% | 4381.8952 | 1.1316 | 1.3154 | 1.5642 | 1.5862 | 1.6009 | 1.6217 | 1.6688 | 1.7059 | 1.7388 | 1.7504 | 1.7636 | 1.7451 | 1.7549 | 1.8006 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 5% | 4374.4653 | 1.2524 | 1.4367 | 1.6876 | 1.7077 | 1.7219 | 1.7364 | 1.7926 | 1.8255 | 1.8591 | 1.8744 | 1.8824 | 1.8545 | 1.8691 | 1.9249 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986
9.992e-14% | 4391.7028 | 2.2613e-14 | 2.6286e-14 | 3.1259e-14 | 3.1699e-14 | 3.1993e-14 | 3.2407e-14 | 3.335e-14 | 3.4091e-14 | 3.4749e-14 | 3.498e-14 | 3.5244e-14 | 3.4875e-14 | 3.507e-14 | 3.5984e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 9.992e-14% | 4375.9513 | 2.5028e-14 | 2.8712e-14 | 3.3724e-14 | 3.4127e-14 | 3.4409e-14 | 3.4701e-14 | 3.5824e-14 | 3.648e-14 | 3.7152e-14 | 3.7457e-14 | 3.7618e-14 | 3.7061e-14 | 3.7352e-14 | 3.8468e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 100% | 0 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
99% | 0.37816 | 25.6004 | 28.4203 | 33.1682 | 33.1325 | 33.1003 | 33.615 | 34.3705 | 34.8883 | 34.259 | 34.3215 | 34.6215 | 35.8093 | 34.6838 | 34.6177 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 99% | 1.1345 | 27.8174 | 31.2882 | 36.0278 | 35.9641 | 36.0059 | 36.1355 | 36.5757 | 36.8706 | 37.1125 | 37.1481 | 37.3662 | 37.4435 | 37.4433 | 37.3934 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828
98% | 0.37816 | 25.3418 | 28.1332 | 32.8331 | 32.7978 | 32.766 | 33.2754 | 34.0234 | 34.5359 | 33.9129 | 33.9749 | 34.2718 | 35.4476 | 34.3335 | 34.268 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 98% | 1.8908 | 27.5364 | 30.9722 | 35.6639 | 35.6008 | 35.6422 | 35.7705 | 36.2063 | 36.4982 | 36.7376 | 36.7729 | 36.9888 | 37.0653 | 37.0651 | 37.0157 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052
97% | 0.75633 | 25.0832 | 27.8462 | 32.4981 | 32.4631 | 32.4316 | 32.9359 | 33.6762 | 34.1835 | 33.5669 | 33.6282 | 33.9221 | 35.0859 | 33.9831 | 33.9184 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 97% | 2.269 | 27.2555 | 30.6561 | 35.3 | 35.2376 | 35.2785 | 35.4055 | 35.8368 | 36.1258 | 36.3627 | 36.3976 | 36.6114 | 36.6871 | 36.6869 | 36.638 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276
95% | 0.75633 | 24.566 | 27.272 | 31.828 | 31.7938 | 31.763 | 32.2568 | 32.9818 | 33.4787 | 32.8748 | 32.9348 | 33.2226 | 34.3625 | 33.2825 | 33.219 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 95% | 4.1598 | 26.6935 | 30.0241 | 34.5721 | 34.511 | 34.5511 | 34.6754 | 35.0979 | 35.3809 | 35.613 | 35.6472 | 35.8565 | 35.9307 | 35.9305 | 35.8826 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724
90% | 3.7816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 90% | 15.5047 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
85% | 13.6139 | 21.9801 | 24.4013 | 28.4777 | 28.4471 | 28.4195 | 28.8613 | 29.5101 | 29.9546 | 29.4143 | 29.468 | 29.7255 | 30.7454 | 29.779 | 29.7223 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 85% | 31.3876 | 23.8836 | 26.8636 | 30.9329 | 30.8783 | 30.9141 | 31.0254 | 31.4034 | 31.6566 | 31.8643 | 31.8948 | 32.0821 | 32.1485 | 32.1483 | 32.1054 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963
80% | 35.1693 | 20.6872 | 22.9659 | 26.8026 | 26.7737 | 26.7478 | 27.1636 | 27.7742 | 28.1926 | 27.684 | 27.7346 | 27.977 | 28.9368 | 28.0273 | 27.9739 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 80% | 57.8591 | 22.4787 | 25.2834 | 29.1134 | 29.0619 | 29.0957 | 29.2004 | 29.5561 | 29.7944 | 29.9899 | 30.0187 | 30.1949 | 30.2574 | 30.2572 | 30.2169 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083
75% | 80.549 | 19.3942 | 21.5305 | 25.1274 | 25.1004 | 25.076 | 25.4659 | 26.0383 | 26.4305 | 25.9538 | 26.0012 | 26.2284 | 27.1283 | 26.2756 | 26.2255 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 75% | 121.3907 | 21.0738 | 23.7032 | 27.2938 | 27.2455 | 27.2772 | 27.3753 | 27.7089 | 27.9323 | 28.1155 | 28.1425 | 28.3078 | 28.3663 | 28.3662 | 28.3283 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203
70% | 192.1075 | 18.1013 | 20.0952 | 23.4522 | 23.427 | 23.4043 | 23.7682 | 24.3024 | 24.6685 | 24.2235 | 24.2678 | 24.4798 | 25.3197 | 24.5239 | 24.4772 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 70% | 273.4128 | 19.6689 | 22.123 | 25.4742 | 25.4292 | 25.4587 | 25.5503 | 25.8616 | 26.0701 | 26.2411 | 26.2663 | 26.4206 | 26.4752 | 26.4751 | 26.4398 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323
65% | 403.1231 | 16.8083 | 18.6598 | 21.7771 | 21.7537 | 21.7325 | 22.0704 | 22.5665 | 22.9065 | 22.4933 | 22.5343 | 22.7313 | 23.5112 | 22.7722 | 22.7288 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 65% | 529.43 | 18.264 | 20.5428 | 23.6546 | 23.6128 | 23.6402 | 23.7253 | 24.0144 | 24.208 | 24.3668 | 24.3902 | 24.5334 | 24.5841 | 24.584 | 24.5512 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443
60% | 739.3112 | 15.5154 | 17.2244 | 20.1019 | 20.0803 | 20.0608 | 20.3727 | 20.8306 | 21.1444 | 20.763 | 20.8009 | 20.9827 | 21.7026 | 21.0205 | 20.9804 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 60% | 918.9392 | 16.859 | 18.9626 | 21.835 | 21.7964 | 21.8218 | 21.9003 | 22.1671 | 22.3458 | 22.4924 | 22.514 | 22.6462 | 22.6931 | 22.6929 | 22.6627 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562
55% | 1204.8314 | 14.2224 | 15.7891 | 18.4268 | 18.4069 | 18.3891 | 18.675 | 19.0947 | 19.3824 | 19.0328 | 19.0675 | 19.2342 | 19.8941 | 19.2688 | 19.2321 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 55% | 1454.0417 | 15.4541 | 17.3823 | 20.0154 | 19.9801 | 20.0033 | 20.0753 | 20.3198 | 20.4837 | 20.618 | 20.6378 | 20.759 | 20.802 | 20.8019 | 20.7741 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682
50% | 1783.0446 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 50% | 2105.2406 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
45% | 2370.3337 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 45% | 2758.3303 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
40% | 2864.2163 | 10.3436 | 11.483 | 13.4013 | 13.3869 | 13.3739 | 13.5818 | 13.8871 | 14.0963 | 13.842 | 13.8673 | 13.9885 | 14.4684 | 14.0137 | 13.987 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 40% | 3348.2666 | 11.2394 | 12.6417 | 14.5567 | 14.531 | 14.5478 | 14.6002 | 14.7781 | 14.8972 | 14.9949 | 15.0093 | 15.0975 | 15.1287 | 15.1286 | 15.1084 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042
35% | 3297.9707 | 9.0506 | 10.0476 | 11.7261 | 11.7135 | 11.7021 | 11.8841 | 12.1512 | 12.3343 | 12.1118 | 12.1339 | 12.2399 | 12.6599 | 12.262 | 12.2386 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 35% | 3816.434 | 9.8344 | 11.0615 | 12.7371 | 12.7146 | 12.7294 | 12.7752 | 12.9308 | 13.0351 | 13.1206 | 13.1332 | 13.2103 | 13.2376 | 13.2375 | 13.2199 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161
30% | 3579.7031 | 7.7577 | 8.6122 | 10.051 | 10.0401 | 10.0304 | 10.1864 | 10.4153 | 10.5722 | 10.3815 | 10.4005 | 10.4914 | 10.8513 | 10.5102 | 10.4902 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 30% | 4067.1569 | 8.4295 | 9.4813 | 10.9175 | 10.8982 | 10.9109 | 10.9501 | 11.0836 | 11.1729 | 11.2462 | 11.257 | 11.3231 | 11.3465 | 11.3465 | 11.3313 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281
25% | 3796.3913 | 6.4647 | 7.1768 | 8.3758 | 8.3668 | 8.3587 | 8.4886 | 8.6794 | 8.8102 | 8.6513 | 8.6671 | 8.7428 | 9.0428 | 8.7585 | 8.7418 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 25% | 4236.9526 | 7.0246 | 7.9011 | 9.0979 | 9.0818 | 9.0924 | 9.1251 | 9.2363 | 9.3108 | 9.3718 | 9.3808 | 9.4359 | 9.4554 | 9.4554 | 9.4428 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401
20% | 3975.6411 | 5.1718 | 5.7415 | 6.7006 | 6.6934 | 6.6869 | 6.7909 | 6.9435 | 7.0481 | 6.921 | 6.9336 | 6.9942 | 7.2342 | 7.0068 | 6.9935 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 20% | 4332.6282 | 5.6197 | 6.3209 | 7.2783 | 7.2655 | 7.2739 | 7.3001 | 7.389 | 7.4486 | 7.4975 | 7.5047 | 7.5487 | 7.5644 | 7.5643 | 7.5542 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521
15% | 4117.4527 | 3.8788 | 4.3061 | 5.0255 | 5.0201 | 5.0152 | 5.0932 | 5.2077 | 5.2861 | 5.1908 | 5.2002 | 5.2457 | 5.4257 | 5.2551 | 5.2451 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 15% | 4361.7469 | 4.2148 | 4.7406 | 5.4588 | 5.4491 | 5.4554 | 5.4751 | 5.5418 | 5.5865 | 5.6231 | 5.6285 | 5.6616 | 5.6733 | 5.6732 | 5.6657 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641
10% | 4224.8514 | 2.5859 | 2.8707 | 3.3503 | 3.3467 | 3.3435 | 3.3955 | 3.4718 | 3.5241 | 3.4605 | 3.4668 | 3.4971 | 3.6171 | 3.5034 | 3.4967 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 10% | 4375.7389 | 2.8098 | 3.1604 | 3.6392 | 3.6327 | 3.637 | 3.65 | 3.6945 | 3.7243 | 3.7487 | 3.7523 | 3.7744 | 3.7822 | 3.7822 | 3.7771 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776
5% | 4310.3165 | 1.2929 | 1.4354 | 1.6752 | 1.6734 | 1.6717 | 1.6977 | 1.7359 | 1.762 | 1.7303 | 1.7334 | 1.7486 | 1.8086 | 1.7517 | 1.7484 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 5% | 4378.0079 | 1.4049 | 1.5802 | 1.8196 | 1.8164 | 1.8185 | 1.825 | 1.8473 | 1.8622 | 1.8744 | 1.8762 | 1.8872 | 1.8911 | 1.8911 | 1.8886 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888
9.992e-14% | 4382.5459 | 2.5838e-14 | 2.8684e-14 | 3.3476e-14 | 3.344e-14 | 3.3408e-14 | 3.3927e-14 | 3.469e-14 | 3.5213e-14 | 3.4577e-14 | 3.4641e-14 | 3.4943e-14 | 3.6142e-14 | 3.5006e-14 | 3.4939e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 9.992e-14% | 4379.1424 | 2.8076e-14 | 3.1579e-14 | 3.6363e-14 | 3.6298e-14 | 3.6341e-14 | 3.6471e-14 | 3.6916e-14 | 3.7213e-14 | 3.7457e-14 | 3.7493e-14 | 3.7714e-14 | 3.7792e-14 | 3.7791e-14 | 3.7741e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 100% | 0 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
99% | 0.2972 | 22.4049 | 26.0444 | 30.9709 | 31.407 | 31.6987 | 32.1087 | 33.0431 | 33.7767 | 34.4291 | 34.658 | 34.9194 | 34.5539 | 34.7466 | 35.6527 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 99% | 0.2972 | 24.7971 | 28.4474 | 33.4137 | 33.8124 | 34.0926 | 34.3812 | 35.494 | 36.1445 | 36.8097 | 37.1123 | 37.2714 | 36.7195 | 37.0077 | 38.1136 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932
98% | 0.8916 | 22.1786 | 25.7814 | 30.6581 | 31.0897 | 31.3785 | 31.7844 | 32.7093 | 33.4356 | 34.0814 | 34.3079 | 34.5667 | 34.2049 | 34.3957 | 35.2926 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 98% | 0.8916 | 24.5466 | 28.16 | 33.0761 | 33.4708 | 33.7483 | 34.0339 | 35.1355 | 35.7794 | 36.4379 | 36.7375 | 36.8949 | 36.3486 | 36.6338 | 37.7286 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135
97% | 1.7832 | 21.9523 | 25.5183 | 30.3452 | 30.7725 | 31.0583 | 31.46 | 32.3755 | 33.0944 | 33.7336 | 33.9578 | 34.214 | 33.8558 | 34.0447 | 34.9324 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 97% | 2.0804 | 24.2962 | 27.8727 | 32.7386 | 33.1293 | 33.4039 | 33.6866 | 34.777 | 35.4143 | 36.0661 | 36.3626 | 36.5184 | 35.9777 | 36.26 | 37.3436 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338
95% | 4.458 | 21.4996 | 24.9921 | 29.7196 | 30.138 | 30.4179 | 30.8114 | 31.708 | 32.412 | 33.038 | 33.2576 | 33.5085 | 33.1578 | 33.3427 | 34.2122 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 95% | 4.1608 | 23.7952 | 27.298 | 32.0636 | 32.4462 | 32.7152 | 32.9921 | 34.0599 | 34.6841 | 35.3225 | 35.6129 | 35.7655 | 35.2359 | 35.5124 | 36.5736 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743
90% | 15.1571 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 90% | 11.5907 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
85% | 39.5274 | 19.2365 | 22.3614 | 26.5912 | 26.9656 | 27.216 | 27.5681 | 28.3703 | 29.0002 | 29.5604 | 29.7568 | 29.9813 | 29.6675 | 29.833 | 30.6109 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 85% | 32.6918 | 21.2905 | 24.4245 | 28.6885 | 29.0308 | 29.2715 | 29.5192 | 30.4747 | 31.0331 | 31.6043 | 31.8641 | 32.0007 | 31.5268 | 31.7743 | 32.7238 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277
80% | 110.5579 | 18.105 | 21.046 | 25.027 | 25.3794 | 25.6151 | 25.9464 | 26.7015 | 27.2943 | 27.8215 | 28.0064 | 28.2177 | 27.9223 | 28.0781 | 28.8103 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 80% | 84.1072 | 20.0381 | 22.9878 | 27.0009 | 27.3231 | 27.5496 | 27.7828 | 28.682 | 29.2076 | 29.7452 | 29.9898 | 30.1183 | 29.6723 | 29.9052 | 30.7988 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784
75% | 244.2972 | 16.9734 | 19.7306 | 23.4628 | 23.7932 | 24.0141 | 24.3248 | 25.0326 | 25.5884 | 26.0827 | 26.256 | 26.4541 | 26.1772 | 26.3232 | 27.0096 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 75% | 202.095 | 18.7857 | 21.5511 | 25.3134 | 25.6154 | 25.8278 | 26.0464 | 26.8894 | 27.3822 | 27.8862 | 28.1154 | 28.2359 | 27.8178 | 28.0361 | 28.8739 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797
70% | 444.0146 | 15.8418 | 18.4153 | 21.8986 | 22.207 | 22.4132 | 22.7031 | 23.3638 | 23.8825 | 24.3438 | 24.5056 | 24.6905 | 24.432 | 24.5683 | 25.209 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 70% | 388.1413 | 17.5333 | 20.1143 | 23.6258 | 23.9077 | 24.1059 | 24.31 | 25.0968 | 25.5567 | 26.0271 | 26.2411 | 26.3535 | 25.9633 | 26.167 | 26.949 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811
65% | 770.3386 | 14.7103 | 17.0999 | 20.3344 | 20.6207 | 20.8122 | 21.0815 | 21.6949 | 22.1767 | 22.605 | 22.7552 | 22.9269 | 22.6869 | 22.8135 | 23.4083 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 65% | 669.8855 | 16.2809 | 18.6776 | 21.9383 | 22.2001 | 22.3841 | 22.5735 | 23.3041 | 23.7312 | 24.168 | 24.3667 | 24.4711 | 24.1088 | 24.298 | 25.0241 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824
60% | 1209.3009 | 13.5787 | 15.7845 | 18.7703 | 19.0345 | 19.2113 | 19.4598 | 20.0261 | 20.4708 | 20.8661 | 21.0048 | 21.1633 | 20.9417 | 21.0586 | 21.6077 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 60% | 1104.687 | 15.0286 | 17.2408 | 20.2507 | 20.4924 | 20.6622 | 20.8371 | 21.5115 | 21.9057 | 22.3089 | 22.4923 | 22.5887 | 22.2542 | 22.4289 | 23.0991 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838
55% | 1757.6322 | 12.4472 | 14.4691 | 17.2061 | 17.4483 | 17.6104 | 17.8382 | 18.3573 | 18.7649 | 19.1273 | 19.2544 | 19.3997 | 19.1966 | 19.3037 | 19.8071 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 55% | 1631.62 | 13.7762 | 15.8041 | 18.5631 | 18.7847 | 18.9404 | 19.1007 | 19.7189 | 20.0803 | 20.4498 | 20.618 | 20.7063 | 20.3997 | 20.5598 | 21.1742 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851
50% | 2378.4799 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 50% | 2253.9537 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
45% | 3003.7856 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 45% | 2892.3362 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
40% | 3548.2533 | 9.0525 | 10.523 | 12.5135 | 12.6897 | 12.8075 | 12.9732 | 13.3507 | 13.6472 | 13.9108 | 14.0032 | 14.1089 | 13.9612 | 14.0391 | 14.4051 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 40% | 3473.3593 | 10.019 | 11.4939 | 13.5005 | 13.6616 | 13.7748 | 13.8914 | 14.341 | 14.6038 | 14.8726 | 14.9949 | 15.0592 | 14.8362 | 14.9526 | 15.3994 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892
35% | 3927.7759 | 7.9209 | 9.2076 | 10.9493 | 11.1035 | 11.2066 | 11.3516 | 11.6819 | 11.9413 | 12.1719 | 12.2528 | 12.3453 | 12.216 | 12.2842 | 12.6045 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 35% | 3882.8989 | 8.7667 | 10.0572 | 11.8129 | 11.9539 | 12.053 | 12.155 | 12.5484 | 12.7783 | 13.0135 | 13.1205 | 13.1768 | 12.9816 | 13.0835 | 13.4745 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905
30% | 4135.8149 | 6.7894 | 7.8923 | 9.3851 | 9.5173 | 9.6057 | 9.7299 | 10.0131 | 10.2354 | 10.4331 | 10.5024 | 10.5816 | 10.4709 | 10.5293 | 10.8038 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 30% | 4127.1961 | 7.5143 | 8.6204 | 10.1253 | 10.2462 | 10.3311 | 10.4186 | 10.7558 | 10.9529 | 11.1545 | 11.2462 | 11.2944 | 11.1271 | 11.2144 | 11.5496 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919
25% | 4252.0195 | 5.6578 | 6.5769 | 7.8209 | 7.9311 | 8.0047 | 8.1083 | 8.3442 | 8.5295 | 8.6942 | 8.752 | 8.818 | 8.7257 | 8.7744 | 9.0032 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 25% | 4245.1839 | 6.2619 | 7.1837 | 8.4378 | 8.5385 | 8.6093 | 8.6821 | 8.9631 | 9.1274 | 9.2954 | 9.3718 | 9.412 | 9.2726 | 9.3454 | 9.6246 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932
20% | 4325.4275 | 4.5262 | 5.2615 | 6.2568 | 6.3448 | 6.4038 | 6.4866 | 6.6754 | 6.8236 | 6.9554 | 7.0016 | 7.0544 | 6.9806 | 7.0195 | 7.2026 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 20% | 4322.1583 | 5.0095 | 5.7469 | 6.7502 | 6.8308 | 6.8874 | 6.9457 | 7.1705 | 7.3019 | 7.4363 | 7.4974 | 7.5296 | 7.4181 | 7.4763 | 7.6997 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946
15% | 4360.497 | 3.3947 | 3.9461 | 4.6926 | 4.7586 | 4.8028 | 4.865 | 5.0065 | 5.1177 | 5.2165 | 5.2512 | 5.2908 | 5.2354 | 5.2646 | 5.4019 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 15% | 4354.2558 | 3.7571 | 4.3102 | 5.0627 | 5.1231 | 5.1656 | 5.2093 | 5.3779 | 5.4764 | 5.5772 | 5.6231 | 5.6472 | 5.5636 | 5.6072 | 5.7748 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959
10% | 4373.8709 | 2.2631 | 2.6308 | 3.1284 | 3.1724 | 3.2019 | 3.2433 | 3.3377 | 3.4118 | 3.4777 | 3.5008 | 3.5272 | 3.4903 | 3.5098 | 3.6013 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 10% | 4366.1437 | 2.5048 | 2.8735 | 3.3751 | 3.4154 | 3.4437 | 3.4729 | 3.5853 | 3.651 | 3.7182 | 3.7487 | 3.7648 | 3.709 | 3.7381 | 3.8499 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973
5% | 4381.8952 | 1.1316 | 1.3154 | 1.5642 | 1.5862 | 1.6009 | 1.6217 | 1.6688 | 1.7059 | 1.7388 | 1.7504 | 1.7636 | 1.7451 | 1.7549 | 1.8006 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 5% | 4374.4653 | 1.2524 | 1.4367 | 1.6876 | 1.7077 | 1.7219 | 1.7364 | 1.7926 | 1.8255 | 1.8591 | 1.8744 | 1.8824 | 1.8545 | 1.8691 | 1.9249 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986
9.992e-14% | 4391.7028 | 2.2613e-14 | 2.6286e-14 | 3.1259e-14 | 3.1699e-14 | 3.1993e-14 | 3.2407e-14 | 3.335e-14 | 3.4091e-14 | 3.4749e-14 | 3.498e-14 | 3.5244e-14 | 3.4875e-14 | 3.507e-14 | 3.5984e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 9.992e-14% | 4375.9513 | 2.5028e-14 | 2.8712e-14 | 3.3724e-14 | 3.4127e-14 | 3.4409e-14 | 3.4701e-14 | 3.5824e-14 | 3.648e-14 | 3.7152e-14 | 3.7457e-14 | 3.7618e-14 | 3.7061e-14 | 3.7352e-14 | 3.8468e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 100% | 0 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
99% | 0.37816 | 25.6004 | 28.4203 | 33.1682 | 33.1325 | 33.1003 | 33.615 | 34.3705 | 34.8883 | 34.259 | 34.3215 | 34.6215 | 35.8093 | 34.6838 | 34.6177 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 99% | 1.1345 | 27.8174 | 31.2882 | 36.0278 | 35.9641 | 36.0059 | 36.1355 | 36.5757 | 36.8706 | 37.1125 | 37.1481 | 37.3662 | 37.4435 | 37.4433 | 37.3934 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828
98% | 0.37816 | 25.3418 | 28.1332 | 32.8331 | 32.7978 | 32.766 | 33.2754 | 34.0234 | 34.5359 | 33.9129 | 33.9749 | 34.2718 | 35.4476 | 34.3335 | 34.268 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 98% | 1.8908 | 27.5364 | 30.9722 | 35.6639 | 35.6008 | 35.6422 | 35.7705 | 36.2063 | 36.4982 | 36.7376 | 36.7729 | 36.9888 | 37.0653 | 37.0651 | 37.0157 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052
97% | 0.75633 | 25.0832 | 27.8462 | 32.4981 | 32.4631 | 32.4316 | 32.9359 | 33.6762 | 34.1835 | 33.5669 | 33.6282 | 33.9221 | 35.0859 | 33.9831 | 33.9184 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 97% | 2.269 | 27.2555 | 30.6561 | 35.3 | 35.2376 | 35.2785 | 35.4055 | 35.8368 | 36.1258 | 36.3627 | 36.3976 | 36.6114 | 36.6871 | 36.6869 | 36.638 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276
95% | 0.75633 | 24.566 | 27.272 | 31.828 | 31.7938 | 31.763 | 32.2568 | 32.9818 | 33.4787 | 32.8748 | 32.9348 | 33.2226 | 34.3625 | 33.2825 | 33.219 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 95% | 4.1598 | 26.6935 | 30.0241 | 34.5721 | 34.511 | 34.5511 | 34.6754 | 35.0979 | 35.3809 | 35.613 | 35.6472 | 35.8565 | 35.9307 | 35.9305 | 35.8826 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724
90% | 3.7816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 90% | 15.5047 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
85% | 13.6139 | 21.9801 | 24.4013 | 28.4777 | 28.4471 | 28.4195 | 28.8613 | 29.5101 | 29.9546 | 29.4143 | 29.468 | 29.7255 | 30.7454 | 29.779 | 29.7223 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 85% | 31.3876 | 23.8836 | 26.8636 | 30.9329 | 30.8783 | 30.9141 | 31.0254 | 31.4034 | 31.6566 | 31.8643 | 31.8948 | 32.0821 | 32.1485 | 32.1483 | 32.1054 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963
80% | 35.1693 | 20.6872 | 22.9659 | 26.8026 | 26.7737 | 26.7478 | 27.1636 | 27.7742 | 28.1926 | 27.684 | 27.7346 | 27.977 | 28.9368 | 28.0273 | 27.9739 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 80% | 57.8591 | 22.4787 | 25.2834 | 29.1134 | 29.0619 | 29.0957 | 29.2004 | 29.5561 | 29.7944 | 29.9899 | 30.0187 | 30.1949 | 30.2574 | 30.2572 | 30.2169 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083
75% | 80.549 | 19.3942 | 21.5305 | 25.1274 | 25.1004 | 25.076 | 25.4659 | 26.0383 | 26.4305 | 25.9538 | 26.0012 | 26.2284 | 27.1283 | 26.2756 | 26.2255 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 75% | 121.3907 | 21.0738 | 23.7032 | 27.2938 | 27.2455 | 27.2772 | 27.3753 | 27.7089 | 27.9323 | 28.1155 | 28.1425 | 28.3078 | 28.3663 | 28.3662 | 28.3283 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203
70% | 192.1075 | 18.1013 | 20.0952 | 23.4522 | 23.427 | 23.4043 | 23.7682 | 24.3024 | 24.6685 | 24.2235 | 24.2678 | 24.4798 | 25.3197 | 24.5239 | 24.4772 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 70% | 273.4128 | 19.6689 | 22.123 | 25.4742 | 25.4292 | 25.4587 | 25.5503 | 25.8616 | 26.0701 | 26.2411 | 26.2663 | 26.4206 | 26.4752 | 26.4751 | 26.4398 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323
65% | 403.1231 | 16.8083 | 18.6598 | 21.7771 | 21.7537 | 21.7325 | 22.0704 | 22.5665 | 22.9065 | 22.4933 | 22.5343 | 22.7313 | 23.5112 | 22.7722 | 22.7288 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 65% | 529.43 | 18.264 | 20.5428 | 23.6546 | 23.6128 | 23.6402 | 23.7253 | 24.0144 | 24.208 | 24.3668 | 24.3902 | 24.5334 | 24.5841 | 24.584 | 24.5512 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443
60% | 739.3112 | 15.5154 | 17.2244 | 20.1019 | 20.0803 | 20.0608 | 20.3727 | 20.8306 | 21.1444 | 20.763 | 20.8009 | 20.9827 | 21.7026 | 21.0205 | 20.9804 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 60% | 918.9392 | 16.859 | 18.9626 | 21.835 | 21.7964 | 21.8218 | 21.9003 | 22.1671 | 22.3458 | 22.4924 | 22.514 | 22.6462 | 22.6931 | 22.6929 | 22.6627 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562
55% | 1204.8314 | 14.2224 | 15.7891 | 18.4268 | 18.4069 | 18.3891 | 18.675 | 19.0947 | 19.3824 | 19.0328 | 19.0675 | 19.2342 | 19.8941 | 19.2688 | 19.2321 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 55% | 1454.0417 | 15.4541 | 17.3823 | 20.0154 | 19.9801 | 20.0033 | 20.0753 | 20.3198 | 20.4837 | 20.618 | 20.6378 | 20.759 | 20.802 | 20.8019 | 20.7741 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682
50% | 1783.0446 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 50% | 2105.2406 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
45% | 2370.3337 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 45% | 2758.3303 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
40% | 2864.2163 | 10.3436 | 11.483 | 13.4013 | 13.3869 | 13.3739 | 13.5818 | 13.8871 | 14.0963 | 13.842 | 13.8673 | 13.9885 | 14.4684 | 14.0137 | 13.987 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 40% | 3348.2666 | 11.2394 | 12.6417 | 14.5567 | 14.531 | 14.5478 | 14.6002 | 14.7781 | 14.8972 | 14.9949 | 15.0093 | 15.0975 | 15.1287 | 15.1286 | 15.1084 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042
35% | 3297.9707 | 9.0506 | 10.0476 | 11.7261 | 11.7135 | 11.7021 | 11.8841 | 12.1512 | 12.3343 | 12.1118 | 12.1339 | 12.2399 | 12.6599 | 12.262 | 12.2386 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 35% | 3816.434 | 9.8344 | 11.0615 | 12.7371 | 12.7146 | 12.7294 | 12.7752 | 12.9308 | 13.0351 | 13.1206 | 13.1332 | 13.2103 | 13.2376 | 13.2375 | 13.2199 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161
30% | 3579.7031 | 7.7577 | 8.6122 | 10.051 | 10.0401 | 10.0304 | 10.1864 | 10.4153 | 10.5722 | 10.3815 | 10.4005 | 10.4914 | 10.8513 | 10.5102 | 10.4902 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 30% | 4067.1569 | 8.4295 | 9.4813 | 10.9175 | 10.8982 | 10.9109 | 10.9501 | 11.0836 | 11.1729 | 11.2462 | 11.257 | 11.3231 | 11.3465 | 11.3465 | 11.3313 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281
25% | 3796.3913 | 6.4647 | 7.1768 | 8.3758 | 8.3668 | 8.3587 | 8.4886 | 8.6794 | 8.8102 | 8.6513 | 8.6671 | 8.7428 | 9.0428 | 8.7585 | 8.7418 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 25% | 4236.9526 | 7.0246 | 7.9011 | 9.0979 | 9.0818 | 9.0924 | 9.1251 | 9.2363 | 9.3108 | 9.3718 | 9.3808 | 9.4359 | 9.4554 | 9.4554 | 9.4428 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401
20% | 3975.6411 | 5.1718 | 5.7415 | 6.7006 | 6.6934 | 6.6869 | 6.7909 | 6.9435 | 7.0481 | 6.921 | 6.9336 | 6.9942 | 7.2342 | 7.0068 | 6.9935 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 20% | 4332.6282 | 5.6197 | 6.3209 | 7.2783 | 7.2655 | 7.2739 | 7.3001 | 7.389 | 7.4486 | 7.4975 | 7.5047 | 7.5487 | 7.5644 | 7.5643 | 7.5542 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521
15% | 4117.4527 | 3.8788 | 4.3061 | 5.0255 | 5.0201 | 5.0152 | 5.0932 | 5.2077 | 5.2861 | 5.1908 | 5.2002 | 5.2457 | 5.4257 | 5.2551 | 5.2451 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 15% | 4361.7469 | 4.2148 | 4.7406 | 5.4588 | 5.4491 | 5.4554 | 5.4751 | 5.5418 | 5.5865 | 5.6231 | 5.6285 | 5.6616 | 5.6733 | 5.6732 | 5.6657 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641
10% | 4224.8514 | 2.5859 | 2.8707 | 3.3503 | 3.3467 | 3.3435 | 3.3955 | 3.4718 | 3.5241 | 3.4605 | 3.4668 | 3.4971 | 3.6171 | 3.5034 | 3.4967 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 10% | 4375.7389 | 2.8098 | 3.1604 | 3.6392 | 3.6327 | 3.637 | 3.65 | 3.6945 | 3.7243 | 3.7487 | 3.7523 | 3.7744 | 3.7822 | 3.7822 | 3.7771 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776
5% | 4310.3165 | 1.2929 | 1.4354 | 1.6752 | 1.6734 | 1.6717 | 1.6977 | 1.7359 | 1.762 | 1.7303 | 1.7334 | 1.7486 | 1.8086 | 1.7517 | 1.7484 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 5% | 4378.0079 | 1.4049 | 1.5802 | 1.8196 | 1.8164 | 1.8185 | 1.825 | 1.8473 | 1.8622 | 1.8744 | 1.8762 | 1.8872 | 1.8911 | 1.8911 | 1.8886 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888
9.992e-14% | 4382.5459 | 2.5838e-14 | 2.8684e-14 | 3.3476e-14 | 3.344e-14 | 3.3408e-14 | 3.3927e-14 | 3.469e-14 | 3.5213e-14 | 3.4577e-14 | 3.4641e-14 | 3.4943e-14 | 3.6142e-14 | 3.5006e-14 | 3.4939e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 9.992e-14% | 4379.1424 | 2.8076e-14 | 3.1579e-14 | 3.6363e-14 | 3.6298e-14 | 3.6341e-14 | 3.6471e-14 | 3.6916e-14 | 3.7213e-14 | 3.7457e-14 | 3.7493e-14 | 3.7714e-14 | 3.7792e-14 | 3.7791e-14 | 3.7741e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 22.6312 | 26.3075 | 31.2838 | 31.7242 | 32.0188 | 32.433 | 33.3768 | 34.1179 | 34.7769 | 35.008 | 35.2722 | 34.9029 | 35.0976 | 36.0128 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 35.608 | 100% | 0 | 25.0476 | 28.7347 | 33.7512 | 34.1539 | 34.437 | 34.7285 | 35.8525 | 36.5096 | 37.1815 | 37.4872 | 37.6479 | 37.0904 | 37.3815 | 38.4985 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973 | 37.973
99% | 0.2972 | 22.4049 | 26.0444 | 30.9709 | 31.407 | 31.6987 | 32.1087 | 33.0431 | 33.7767 | 34.4291 | 34.658 | 34.9194 | 34.5539 | 34.7466 | 35.6527 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 35.2519 | 99% | 0.2972 | 24.7971 | 28.4474 | 33.4137 | 33.8124 | 34.0926 | 34.3812 | 35.494 | 36.1445 | 36.8097 | 37.1123 | 37.2714 | 36.7195 | 37.0077 | 38.1136 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932 | 37.5932
98% | 0.8916 | 22.1786 | 25.7814 | 30.6581 | 31.0897 | 31.3785 | 31.7844 | 32.7093 | 33.4356 | 34.0814 | 34.3079 | 34.5667 | 34.2049 | 34.3957 | 35.2926 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 34.8959 | 98% | 0.8916 | 24.5466 | 28.16 | 33.0761 | 33.4708 | 33.7483 | 34.0339 | 35.1355 | 35.7794 | 36.4379 | 36.7375 | 36.8949 | 36.3486 | 36.6338 | 37.7286 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135 | 37.2135
97% | 1.7832 | 21.9523 | 25.5183 | 30.3452 | 30.7725 | 31.0583 | 31.46 | 32.3755 | 33.0944 | 33.7336 | 33.9578 | 34.214 | 33.8558 | 34.0447 | 34.9324 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 34.5398 | 97% | 2.0804 | 24.2962 | 27.8727 | 32.7386 | 33.1293 | 33.4039 | 33.6866 | 34.777 | 35.4143 | 36.0661 | 36.3626 | 36.5184 | 35.9777 | 36.26 | 37.3436 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338 | 36.8338
95% | 4.458 | 21.4996 | 24.9921 | 29.7196 | 30.138 | 30.4179 | 30.8114 | 31.708 | 32.412 | 33.038 | 33.2576 | 33.5085 | 33.1578 | 33.3427 | 34.2122 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 33.8276 | 95% | 4.1608 | 23.7952 | 27.298 | 32.0636 | 32.4462 | 32.7152 | 32.9921 | 34.0599 | 34.6841 | 35.3225 | 35.6129 | 35.7655 | 35.2359 | 35.5124 | 36.5736 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743 | 36.0743
90% | 15.1571 | 20.3681 | 23.6768 | 28.1554 | 28.5518 | 28.817 | 29.1897 | 30.0392 | 30.7061 | 31.2992 | 31.5072 | 31.7449 | 31.4126 | 31.5879 | 32.4115 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 32.0472 | 90% | 11.5907 | 22.5428 | 25.8613 | 30.376 | 30.7385 | 30.9933 | 31.2557 | 32.2673 | 32.8586 | 33.4634 | 33.7385 | 33.8831 | 33.3814 | 33.6433 | 34.6487 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757 | 34.1757
85% | 39.5274 | 19.2365 | 22.3614 | 26.5912 | 26.9656 | 27.216 | 27.5681 | 28.3703 | 29.0002 | 29.5604 | 29.7568 | 29.9813 | 29.6675 | 29.833 | 30.6109 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 30.2668 | 85% | 32.6918 | 21.2905 | 24.4245 | 28.6885 | 29.0308 | 29.2715 | 29.5192 | 30.4747 | 31.0331 | 31.6043 | 31.8641 | 32.0007 | 31.5268 | 31.7743 | 32.7238 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277 | 32.277
80% | 110.5579 | 18.105 | 21.046 | 25.027 | 25.3794 | 25.6151 | 25.9464 | 26.7015 | 27.2943 | 27.8215 | 28.0064 | 28.2177 | 27.9223 | 28.0781 | 28.8103 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 28.4864 | 80% | 84.1072 | 20.0381 | 22.9878 | 27.0009 | 27.3231 | 27.5496 | 27.7828 | 28.682 | 29.2076 | 29.7452 | 29.9898 | 30.1183 | 29.6723 | 29.9052 | 30.7988 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784 | 30.3784
75% | 244.2972 | 16.9734 | 19.7306 | 23.4628 | 23.7932 | 24.0141 | 24.3248 | 25.0326 | 25.5884 | 26.0827 | 26.256 | 26.4541 | 26.1772 | 26.3232 | 27.0096 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 75% | 202.095 | 18.7857 | 21.5511 | 25.3134 | 25.6154 | 25.8278 | 26.0464 | 26.8894 | 27.3822 | 27.8862 | 28.1154 | 28.2359 | 27.8178 | 28.0361 | 28.8739 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797 | 28.4797
70% | 444.0146 | 15.8418 | 18.4153 | 21.8986 | 22.207 | 22.4132 | 22.7031 | 23.3638 | 23.8825 | 24.3438 | 24.5056 | 24.6905 | 24.432 | 24.5683 | 25.209 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 24.9256 | 70% | 388.1413 | 17.5333 | 20.1143 | 23.6258 | 23.9077 | 24.1059 | 24.31 | 25.0968 | 25.5567 | 26.0271 | 26.2411 | 26.3535 | 25.9633 | 26.167 | 26.949 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811 | 26.5811
65% | 770.3386 | 14.7103 | 17.0999 | 20.3344 | 20.6207 | 20.8122 | 21.0815 | 21.6949 | 22.1767 | 22.605 | 22.7552 | 22.9269 | 22.6869 | 22.8135 | 23.4083 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 23.1452 | 65% | 669.8855 | 16.2809 | 18.6776 | 21.9383 | 22.2001 | 22.3841 | 22.5735 | 23.3041 | 23.7312 | 24.168 | 24.3667 | 24.4711 | 24.1088 | 24.298 | 25.0241 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824 | 24.6824
60% | 1209.3009 | 13.5787 | 15.7845 | 18.7703 | 19.0345 | 19.2113 | 19.4598 | 20.0261 | 20.4708 | 20.8661 | 21.0048 | 21.1633 | 20.9417 | 21.0586 | 21.6077 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 21.3648 | 60% | 1104.687 | 15.0286 | 17.2408 | 20.2507 | 20.4924 | 20.6622 | 20.8371 | 21.5115 | 21.9057 | 22.3089 | 22.4923 | 22.5887 | 22.2542 | 22.4289 | 23.0991 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838 | 22.7838
55% | 1757.6322 | 12.4472 | 14.4691 | 17.2061 | 17.4483 | 17.6104 | 17.8382 | 18.3573 | 18.7649 | 19.1273 | 19.2544 | 19.3997 | 19.1966 | 19.3037 | 19.8071 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 19.5844 | 55% | 1631.62 | 13.7762 | 15.8041 | 18.5631 | 18.7847 | 18.9404 | 19.1007 | 19.7189 | 20.0803 | 20.4498 | 20.618 | 20.7063 | 20.3997 | 20.5598 | 21.1742 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851 | 20.8851
50% | 2378.4799 | 11.3156 | 13.1538 | 15.6419 | 15.8621 | 16.0094 | 16.2165 | 16.6884 | 17.059 | 17.3884 | 17.504 | 17.6361 | 17.4515 | 17.5488 | 18.0064 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 17.804 | 50% | 2253.9537 | 12.5238 | 14.3674 | 16.8756 | 17.077 | 17.2185 | 17.3643 | 17.9263 | 18.2548 | 18.5908 | 18.7436 | 18.8239 | 18.5452 | 18.6907 | 19.2493 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865 | 18.9865
45% | 3003.7856 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 45% | 2892.3362 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
40% | 3548.2533 | 9.0525 | 10.523 | 12.5135 | 12.6897 | 12.8075 | 12.9732 | 13.3507 | 13.6472 | 13.9108 | 14.0032 | 14.1089 | 13.9612 | 14.0391 | 14.4051 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 14.2432 | 40% | 3473.3593 | 10.019 | 11.4939 | 13.5005 | 13.6616 | 13.7748 | 13.8914 | 14.341 | 14.6038 | 14.8726 | 14.9949 | 15.0592 | 14.8362 | 14.9526 | 15.3994 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892 | 15.1892
35% | 3927.7759 | 7.9209 | 9.2076 | 10.9493 | 11.1035 | 11.2066 | 11.3516 | 11.6819 | 11.9413 | 12.1719 | 12.2528 | 12.3453 | 12.216 | 12.2842 | 12.6045 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 12.4628 | 35% | 3882.8989 | 8.7667 | 10.0572 | 11.8129 | 11.9539 | 12.053 | 12.155 | 12.5484 | 12.7783 | 13.0135 | 13.1205 | 13.1768 | 12.9816 | 13.0835 | 13.4745 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905 | 13.2905
30% | 4135.8149 | 6.7894 | 7.8923 | 9.3851 | 9.5173 | 9.6057 | 9.7299 | 10.0131 | 10.2354 | 10.4331 | 10.5024 | 10.5816 | 10.4709 | 10.5293 | 10.8038 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 10.6824 | 30% | 4127.1961 | 7.5143 | 8.6204 | 10.1253 | 10.2462 | 10.3311 | 10.4186 | 10.7558 | 10.9529 | 11.1545 | 11.2462 | 11.2944 | 11.1271 | 11.2144 | 11.5496 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919 | 11.3919
25% | 4252.0195 | 5.6578 | 6.5769 | 7.8209 | 7.9311 | 8.0047 | 8.1083 | 8.3442 | 8.5295 | 8.6942 | 8.752 | 8.818 | 8.7257 | 8.7744 | 9.0032 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 8.902 | 25% | 4245.1839 | 6.2619 | 7.1837 | 8.4378 | 8.5385 | 8.6093 | 8.6821 | 8.9631 | 9.1274 | 9.2954 | 9.3718 | 9.412 | 9.2726 | 9.3454 | 9.6246 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932 | 9.4932
20% | 4325.4275 | 4.5262 | 5.2615 | 6.2568 | 6.3448 | 6.4038 | 6.4866 | 6.6754 | 6.8236 | 6.9554 | 7.0016 | 7.0544 | 6.9806 | 7.0195 | 7.2026 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 7.1216 | 20% | 4322.1583 | 5.0095 | 5.7469 | 6.7502 | 6.8308 | 6.8874 | 6.9457 | 7.1705 | 7.3019 | 7.4363 | 7.4974 | 7.5296 | 7.4181 | 7.4763 | 7.6997 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946 | 7.5946
15% | 4360.497 | 3.3947 | 3.9461 | 4.6926 | 4.7586 | 4.8028 | 4.865 | 5.0065 | 5.1177 | 5.2165 | 5.2512 | 5.2908 | 5.2354 | 5.2646 | 5.4019 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 5.3412 | 15% | 4354.2558 | 3.7571 | 4.3102 | 5.0627 | 5.1231 | 5.1656 | 5.2093 | 5.3779 | 5.4764 | 5.5772 | 5.6231 | 5.6472 | 5.5636 | 5.6072 | 5.7748 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959 | 5.6959
10% | 4373.8709 | 2.2631 | 2.6308 | 3.1284 | 3.1724 | 3.2019 | 3.2433 | 3.3377 | 3.4118 | 3.4777 | 3.5008 | 3.5272 | 3.4903 | 3.5098 | 3.6013 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 3.5608 | 10% | 4366.1437 | 2.5048 | 2.8735 | 3.3751 | 3.4154 | 3.4437 | 3.4729 | 3.5853 | 3.651 | 3.7182 | 3.7487 | 3.7648 | 3.709 | 3.7381 | 3.8499 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973 | 3.7973
5% | 4381.8952 | 1.1316 | 1.3154 | 1.5642 | 1.5862 | 1.6009 | 1.6217 | 1.6688 | 1.7059 | 1.7388 | 1.7504 | 1.7636 | 1.7451 | 1.7549 | 1.8006 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 1.7804 | 5% | 4374.4653 | 1.2524 | 1.4367 | 1.6876 | 1.7077 | 1.7219 | 1.7364 | 1.7926 | 1.8255 | 1.8591 | 1.8744 | 1.8824 | 1.8545 | 1.8691 | 1.9249 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986 | 1.8986
9.992e-14% | 4391.7028 | 2.2613e-14 | 2.6286e-14 | 3.1259e-14 | 3.1699e-14 | 3.1993e-14 | 3.2407e-14 | 3.335e-14 | 3.4091e-14 | 3.4749e-14 | 3.498e-14 | 3.5244e-14 | 3.4875e-14 | 3.507e-14 | 3.5984e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 3.558e-14 | 9.992e-14% | 4375.9513 | 2.5028e-14 | 2.8712e-14 | 3.3724e-14 | 3.4127e-14 | 3.4409e-14 | 3.4701e-14 | 3.5824e-14 | 3.648e-14 | 3.7152e-14 | 3.7457e-14 | 3.7618e-14 | 3.7061e-14 | 3.7352e-14 | 3.8468e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14 | 3.7943e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 25.859 | 28.7074 | 33.5032 | 33.4672 | 33.4347 | 33.9545 | 34.7177 | 35.2407 | 34.605 | 34.6682 | 34.9712 | 36.171 | 35.0342 | 34.9674 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 34.8957 | 100% | 0 | 28.0984 | 31.6043 | 36.3917 | 36.3274 | 36.3696 | 36.5005 | 36.9452 | 37.243 | 37.4874 | 37.5233 | 37.7437 | 37.8218 | 37.8216 | 37.7711 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604 | 37.7604
99% | 0.37816 | 25.6004 | 28.4203 | 33.1682 | 33.1325 | 33.1003 | 33.615 | 34.3705 | 34.8883 | 34.259 | 34.3215 | 34.6215 | 35.8093 | 34.6838 | 34.6177 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 34.5468 | 99% | 1.1345 | 27.8174 | 31.2882 | 36.0278 | 35.9641 | 36.0059 | 36.1355 | 36.5757 | 36.8706 | 37.1125 | 37.1481 | 37.3662 | 37.4435 | 37.4433 | 37.3934 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828 | 37.3828
98% | 0.37816 | 25.3418 | 28.1332 | 32.8331 | 32.7978 | 32.766 | 33.2754 | 34.0234 | 34.5359 | 33.9129 | 33.9749 | 34.2718 | 35.4476 | 34.3335 | 34.268 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 34.1978 | 98% | 1.8908 | 27.5364 | 30.9722 | 35.6639 | 35.6008 | 35.6422 | 35.7705 | 36.2063 | 36.4982 | 36.7376 | 36.7729 | 36.9888 | 37.0653 | 37.0651 | 37.0157 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052 | 37.0052
97% | 0.75633 | 25.0832 | 27.8462 | 32.4981 | 32.4631 | 32.4316 | 32.9359 | 33.6762 | 34.1835 | 33.5669 | 33.6282 | 33.9221 | 35.0859 | 33.9831 | 33.9184 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 33.8488 | 97% | 2.269 | 27.2555 | 30.6561 | 35.3 | 35.2376 | 35.2785 | 35.4055 | 35.8368 | 36.1258 | 36.3627 | 36.3976 | 36.6114 | 36.6871 | 36.6869 | 36.638 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276 | 36.6276
95% | 0.75633 | 24.566 | 27.272 | 31.828 | 31.7938 | 31.763 | 32.2568 | 32.9818 | 33.4787 | 32.8748 | 32.9348 | 33.2226 | 34.3625 | 33.2825 | 33.219 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 33.1509 | 95% | 4.1598 | 26.6935 | 30.0241 | 34.5721 | 34.511 | 34.5511 | 34.6754 | 35.0979 | 35.3809 | 35.613 | 35.6472 | 35.8565 | 35.9307 | 35.9305 | 35.8826 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724 | 35.8724
90% | 3.7816 | 23.2731 | 25.8366 | 30.1529 | 30.1204 | 30.0912 | 30.5591 | 31.2459 | 31.7167 | 31.1445 | 31.2014 | 31.4741 | 32.5539 | 31.5307 | 31.4706 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 31.4061 | 90% | 15.5047 | 25.2886 | 28.4438 | 32.7525 | 32.6947 | 32.7326 | 32.8504 | 33.2507 | 33.5187 | 33.7386 | 33.771 | 33.9693 | 34.0396 | 34.0394 | 33.994 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844 | 33.9844
85% | 13.6139 | 21.9801 | 24.4013 | 28.4777 | 28.4471 | 28.4195 | 28.8613 | 29.5101 | 29.9546 | 29.4143 | 29.468 | 29.7255 | 30.7454 | 29.779 | 29.7223 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 29.6614 | 85% | 31.3876 | 23.8836 | 26.8636 | 30.9329 | 30.8783 | 30.9141 | 31.0254 | 31.4034 | 31.6566 | 31.8643 | 31.8948 | 32.0821 | 32.1485 | 32.1483 | 32.1054 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963 | 32.0963
80% | 35.1693 | 20.6872 | 22.9659 | 26.8026 | 26.7737 | 26.7478 | 27.1636 | 27.7742 | 28.1926 | 27.684 | 27.7346 | 27.977 | 28.9368 | 28.0273 | 27.9739 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 27.9166 | 80% | 57.8591 | 22.4787 | 25.2834 | 29.1134 | 29.0619 | 29.0957 | 29.2004 | 29.5561 | 29.7944 | 29.9899 | 30.0187 | 30.1949 | 30.2574 | 30.2572 | 30.2169 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083 | 30.2083
75% | 80.549 | 19.3942 | 21.5305 | 25.1274 | 25.1004 | 25.076 | 25.4659 | 26.0383 | 26.4305 | 25.9538 | 26.0012 | 26.2284 | 27.1283 | 26.2756 | 26.2255 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 26.1718 | 75% | 121.3907 | 21.0738 | 23.7032 | 27.2938 | 27.2455 | 27.2772 | 27.3753 | 27.7089 | 27.9323 | 28.1155 | 28.1425 | 28.3078 | 28.3663 | 28.3662 | 28.3283 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203 | 28.3203
70% | 192.1075 | 18.1013 | 20.0952 | 23.4522 | 23.427 | 23.4043 | 23.7682 | 24.3024 | 24.6685 | 24.2235 | 24.2678 | 24.4798 | 25.3197 | 24.5239 | 24.4772 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 24.427 | 70% | 273.4128 | 19.6689 | 22.123 | 25.4742 | 25.4292 | 25.4587 | 25.5503 | 25.8616 | 26.0701 | 26.2411 | 26.2663 | 26.4206 | 26.4752 | 26.4751 | 26.4398 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323 | 26.4323
65% | 403.1231 | 16.8083 | 18.6598 | 21.7771 | 21.7537 | 21.7325 | 22.0704 | 22.5665 | 22.9065 | 22.4933 | 22.5343 | 22.7313 | 23.5112 | 22.7722 | 22.7288 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 22.6822 | 65% | 529.43 | 18.264 | 20.5428 | 23.6546 | 23.6128 | 23.6402 | 23.7253 | 24.0144 | 24.208 | 24.3668 | 24.3902 | 24.5334 | 24.5841 | 24.584 | 24.5512 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443 | 24.5443
60% | 739.3112 | 15.5154 | 17.2244 | 20.1019 | 20.0803 | 20.0608 | 20.3727 | 20.8306 | 21.1444 | 20.763 | 20.8009 | 20.9827 | 21.7026 | 21.0205 | 20.9804 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 20.9374 | 60% | 918.9392 | 16.859 | 18.9626 | 21.835 | 21.7964 | 21.8218 | 21.9003 | 22.1671 | 22.3458 | 22.4924 | 22.514 | 22.6462 | 22.6931 | 22.6929 | 22.6627 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562 | 22.6562
55% | 1204.8314 | 14.2224 | 15.7891 | 18.4268 | 18.4069 | 18.3891 | 18.675 | 19.0947 | 19.3824 | 19.0328 | 19.0675 | 19.2342 | 19.8941 | 19.2688 | 19.2321 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 19.1926 | 55% | 1454.0417 | 15.4541 | 17.3823 | 20.0154 | 19.9801 | 20.0033 | 20.0753 | 20.3198 | 20.4837 | 20.618 | 20.6378 | 20.759 | 20.802 | 20.8019 | 20.7741 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682 | 20.7682
50% | 1783.0446 | 12.9295 | 14.3537 | 16.7516 | 16.7336 | 16.7173 | 16.9773 | 17.3589 | 17.6204 | 17.3025 | 17.3341 | 17.4856 | 18.0855 | 17.5171 | 17.4837 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 17.4479 | 50% | 2105.2406 | 14.0492 | 15.8021 | 18.1959 | 18.1637 | 18.1848 | 18.2502 | 18.4726 | 18.6215 | 18.7437 | 18.7617 | 18.8718 | 18.9109 | 18.9108 | 18.8856 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802 | 18.8802
45% | 2370.3337 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 45% | 2758.3303 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
40% | 2864.2163 | 10.3436 | 11.483 | 13.4013 | 13.3869 | 13.3739 | 13.5818 | 13.8871 | 14.0963 | 13.842 | 13.8673 | 13.9885 | 14.4684 | 14.0137 | 13.987 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 13.9583 | 40% | 3348.2666 | 11.2394 | 12.6417 | 14.5567 | 14.531 | 14.5478 | 14.6002 | 14.7781 | 14.8972 | 14.9949 | 15.0093 | 15.0975 | 15.1287 | 15.1286 | 15.1084 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042 | 15.1042
35% | 3297.9707 | 9.0506 | 10.0476 | 11.7261 | 11.7135 | 11.7021 | 11.8841 | 12.1512 | 12.3343 | 12.1118 | 12.1339 | 12.2399 | 12.6599 | 12.262 | 12.2386 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 12.2135 | 35% | 3816.434 | 9.8344 | 11.0615 | 12.7371 | 12.7146 | 12.7294 | 12.7752 | 12.9308 | 13.0351 | 13.1206 | 13.1332 | 13.2103 | 13.2376 | 13.2375 | 13.2199 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161 | 13.2161
30% | 3579.7031 | 7.7577 | 8.6122 | 10.051 | 10.0401 | 10.0304 | 10.1864 | 10.4153 | 10.5722 | 10.3815 | 10.4005 | 10.4914 | 10.8513 | 10.5102 | 10.4902 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 10.4687 | 30% | 4067.1569 | 8.4295 | 9.4813 | 10.9175 | 10.8982 | 10.9109 | 10.9501 | 11.0836 | 11.1729 | 11.2462 | 11.257 | 11.3231 | 11.3465 | 11.3465 | 11.3313 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281 | 11.3281
25% | 3796.3913 | 6.4647 | 7.1768 | 8.3758 | 8.3668 | 8.3587 | 8.4886 | 8.6794 | 8.8102 | 8.6513 | 8.6671 | 8.7428 | 9.0428 | 8.7585 | 8.7418 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 8.7239 | 25% | 4236.9526 | 7.0246 | 7.9011 | 9.0979 | 9.0818 | 9.0924 | 9.1251 | 9.2363 | 9.3108 | 9.3718 | 9.3808 | 9.4359 | 9.4554 | 9.4554 | 9.4428 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401 | 9.4401
20% | 3975.6411 | 5.1718 | 5.7415 | 6.7006 | 6.6934 | 6.6869 | 6.7909 | 6.9435 | 7.0481 | 6.921 | 6.9336 | 6.9942 | 7.2342 | 7.0068 | 6.9935 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 6.9791 | 20% | 4332.6282 | 5.6197 | 6.3209 | 7.2783 | 7.2655 | 7.2739 | 7.3001 | 7.389 | 7.4486 | 7.4975 | 7.5047 | 7.5487 | 7.5644 | 7.5643 | 7.5542 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521 | 7.5521
15% | 4117.4527 | 3.8788 | 4.3061 | 5.0255 | 5.0201 | 5.0152 | 5.0932 | 5.2077 | 5.2861 | 5.1908 | 5.2002 | 5.2457 | 5.4257 | 5.2551 | 5.2451 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 5.2344 | 15% | 4361.7469 | 4.2148 | 4.7406 | 5.4588 | 5.4491 | 5.4554 | 5.4751 | 5.5418 | 5.5865 | 5.6231 | 5.6285 | 5.6616 | 5.6733 | 5.6732 | 5.6657 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641 | 5.6641
10% | 4224.8514 | 2.5859 | 2.8707 | 3.3503 | 3.3467 | 3.3435 | 3.3955 | 3.4718 | 3.5241 | 3.4605 | 3.4668 | 3.4971 | 3.6171 | 3.5034 | 3.4967 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 3.4896 | 10% | 4375.7389 | 2.8098 | 3.1604 | 3.6392 | 3.6327 | 3.637 | 3.65 | 3.6945 | 3.7243 | 3.7487 | 3.7523 | 3.7744 | 3.7822 | 3.7822 | 3.7771 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776 | 3.776
5% | 4310.3165 | 1.2929 | 1.4354 | 1.6752 | 1.6734 | 1.6717 | 1.6977 | 1.7359 | 1.762 | 1.7303 | 1.7334 | 1.7486 | 1.8086 | 1.7517 | 1.7484 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 1.7448 | 5% | 4378.0079 | 1.4049 | 1.5802 | 1.8196 | 1.8164 | 1.8185 | 1.825 | 1.8473 | 1.8622 | 1.8744 | 1.8762 | 1.8872 | 1.8911 | 1.8911 | 1.8886 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888 | 1.888
9.992e-14% | 4382.5459 | 2.5838e-14 | 2.8684e-14 | 3.3476e-14 | 3.344e-14 | 3.3408e-14 | 3.3927e-14 | 3.469e-14 | 3.5213e-14 | 3.4577e-14 | 3.4641e-14 | 3.4943e-14 | 3.6142e-14 | 3.5006e-14 | 3.4939e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 3.4868e-14 | 9.992e-14% | 4379.1424 | 2.8076e-14 | 3.1579e-14 | 3.6363e-14 | 3.6298e-14 | 3.6341e-14 | 3.6471e-14 | 3.6916e-14 | 3.7213e-14 | 3.7457e-14 | 3.7493e-14 | 3.7714e-14 | 3.7792e-14 | 3.7791e-14 | 3.7741e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14 | 3.773e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 34378474.2948 | 37.17% | 18.2965
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 31576189.3656 | 34.14% | 11.7393
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 10621047.2058 | 11.48% | 3.8453
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 15925855.934 | 17.22% | 3.8307
|  | 92501566.8003 |  | 37.7119 | KW/h
|  |  |  | 37711.8651 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 1 Winter POE50 W E @ R (MWh) N 1 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60940.1589 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 1 Summer POE50 W E @ R (MWh) N 1 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 18282.0477 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 2 Winter POE50 W E @ R (MWh) N 1 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 2 Summer POE50 W E @ R (MWh) N 1 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 3 Winter POE50 W E @ R (MWh) N 1 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 3 Summer POE50 W E @ R (MWh) N 1 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 4 Winter POE50 W E @ R (MWh) N 1 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 4 Summer POE50 W E @ R (MWh) N 1 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 6.6923; FY26: 7.7795; FY27: 9.251 |  | 7.4069 | 8.4972 | 9.9806
98% | FY25: 13.2501; FY26: 15.4026; FY27: 18.316 |  | 14.6649 | 16.8236 | 19.7607
97% | FY25: 19.6734; FY26: 22.8693; FY27: 27.1951 |  | 29.032 | 33.3057 | 39.1201
95% | FY25: 58.1123; FY26: 67.5523; FY27: 80.3303 |  | 50.0244 | 57.3883 | 67.4069
90% | FY25: 223.9745; FY26: 260.3579; FY27: 309.6063 |  | 172.145 | 197.4857 | 231.9622
85% | FY25: 482.5876; FY26: 560.9813; FY27: 667.0946 |  | 462.4652 | 530.5426 | 623.1632
80% | FY25: 1326.1911; FY26: 1541.6235; FY27: 1833.2317 |  | 1062.4602 | 1218.8602 | 1431.6454
75% | FY25: 2345.6784; FY26: 2726.721; FY27: 3242.4981 |  | 2290.3656 | 2627.5202 | 3086.2252
70% | FY25: 3276.8875; FY26: 3809.1999; FY27: 4529.735 |  | 3378.508 | 3875.8432 | 4552.4768
65% | FY25: 4984.945; FY26: 5794.7219; FY27: 6890.8315 |  | 4763.4841 | 5464.6955 | 6418.7064
60% | FY25: 6208.9015; FY26: 7217.5034; FY27: 8582.7415 |  | 6806.7054 | 7808.6904 | 9171.9091
55% | FY25: 7135.4024; FY26: 8294.5093; FY27: 9863.4701 |  | 7589.081 | 8706.2361 | 10226.1458
50% | FY25: 7376.5281; FY26: 8574.8045; FY27: 10196.785 |  | 8183.6791 | 9388.3623 | 11027.3556
45% | FY25: 6721.9241; FY26: 7813.8637; FY27: 9291.9072 |  | 7595.2224 | 8713.2815 | 10234.4212
40% | FY25: 5236.8322; FY26: 6087.5268; FY27: 7239.0223 |  | 6185.1224 | 7095.607 | 8334.3376
35% | FY25: 3220.8939; FY26: 3744.1104; FY27: 4452.3335 |  | 3846.7423 | 4413.0042 | 5183.4138
30% | FY25: 1530.1558; FY26: 1778.7212; FY27: 2115.178 |  | 1988.6932 | 2281.4399 | 2679.7272
25% | FY25: 723.2088; FY26: 840.6901; FY27: 999.7121 |  | 812.7104 | 932.3459 | 1095.1122
20% | FY25: 373.7952; FY26: 434.5162; FY27: 516.7078 |  | 433.8053 | 497.6639 | 584.5446
15% | FY25: 138.8911; FY26: 161.4532; FY27: 191.9931 |  | 140.6936 | 161.4045 | 189.582
10% | FY25: 37.8335; FY26: 43.9794; FY27: 52.2984 |  | 37.2205 | 42.6996 | 50.154
5% | FY25: 13.6201; FY26: 15.8326; FY27: 18.8274 |  | 15.6326 | 17.9338 | 21.0647
9.992e-14% | FY25: 5.5489; FY26: 6.4503; FY27: 7.6704 |  | 0.93051 | 1.0675 | 1.2538
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) N 1 | 35662.8389 | 41456.0709 | 49297.7584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 16592.4382 | 19034.9376 | 22358.0023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 9.73; FY26: 10.8018; FY27: 12.6064 |  | 31.7181 | 35.6755 | 41.0797
98% | FY25: 0; FY26: 0; FY27: 0 |  | 20.9329 | 23.5447 | 27.1112
97% | FY25: 9.5345; FY26: 10.5847; FY27: 12.353 |  | 10.3602 | 11.6528 | 13.418
95% | FY25: 0; FY26: 0; FY27: 0 |  | 51.0039 | 57.3677 | 66.0578
90% | FY25: 72.3641; FY26: 80.3352; FY27: 93.7559 |  | 294.8663 | 331.657 | 381.8967
85% | FY25: 222.4708; FY26: 246.9765; FY27: 288.236 |  | 390.4987 | 439.2215 | 505.7551
80% | FY25: 459.8544; FY26: 510.5085; FY27: 595.7932 |  | 613.6408 | 690.2052 | 794.7579
75% | FY25: 909.441; FY26: 1009.6182; FY27: 1178.2832 |  | 1383.481 | 1556.0989 | 1791.8179
70% | FY25: 2091.4698; FY26: 2321.8503; FY27: 2709.7347 |  | 3096.8935 | 3483.2952 | 4010.9472
65% | FY25: 3683.2359; FY26: 4088.9535; FY27: 4772.0471 |  | 4855.7313 | 5461.5845 | 6288.9093
60% | FY25: 5433.4208; FY26: 6031.9257; FY27: 7039.6088 |  | 6840.3677 | 7693.8455 | 8859.3148
55% | FY25: 6921.7748; FY26: 7684.2255; FY27: 8967.939 |  | 8645.4279 | 9724.1243 | 11197.1417
50% | FY25: 7849.7957; FY26: 8714.4702; FY27: 10170.2947 |  | 9606.2671 | 10804.8481 | 12441.5744
45% | FY25: 7213.676; FY26: 8008.2803; FY27: 9346.1299 |  | 8716.6209 | 9804.2 | 11289.3474
40% | FY25: 5427.7979; FY26: 6025.6834; FY27: 7032.3237 |  | 7044.9147 | 7923.9138 | 9124.2341
35% | FY25: 4206.1645; FY26: 4669.484; FY27: 5449.5599 |  | 4933.0341 | 5548.5324 | 6389.0282
30% | FY25: 2367.7247; FY26: 2628.5354; FY27: 3067.654 |  | 2289.5973 | 2575.272 | 2965.3761
25% | FY25: 1540.9157; FY26: 1710.6514; FY27: 1996.4299 |  | 1312.0224 | 1475.7244 | 1699.2682
20% | FY25: 1042.9234; FY26: 1157.804; FY27: 1351.2248 |  | 604.8745 | 680.3451 | 783.4043
15% | FY25: 641.7426; FY26: 712.4322; FY27: 831.4499 |  | 143.1828 | 161.0479 | 185.4435
10% | FY25: 347.1522; FY26: 385.3919; FY27: 449.7748 |  | 49.1444 | 55.2762 | 63.6494
5% | FY25: 165.753; FY26: 184.0111; FY27: 214.7516 |  | 4.7816 | 5.3782 | 6.1929
9.992e-14% | FY25: 46.6944; FY26: 51.8379; FY27: 60.4979 |  | 0.79694 | 0.89637 | 1.0322
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) N 1 | 35109.8999 | 38977.3426 | 45488.8306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 18099.2272 | 20357.481 | 23441.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 6 Winter POE50 W E @ R (MWh) N 1 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 6 Summer POE50 W E @ R (MWh) N 1 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 7 Winter POE50 W E @ R (MWh) N 1 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 7 Summer POE50 W E @ R (MWh) N 1 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 8 Winter POE50 W E @ R (MWh) N 1 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 8 Summer POE50 W E @ R (MWh) N 1 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 1 Winter POE50 W E @ R (MWh) N 2 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 1 Summer POE50 W E @ R (MWh) N 2 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 2 Winter POE50 W E @ R (MWh) N 2 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 2 Summer POE50 W E @ R (MWh) N 2 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 3 Winter POE50 W E @ R (MWh) N 2 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 3 Summer POE50 W E @ R (MWh) N 2 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 4 Winter POE50 W E @ R (MWh) N 2 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 4 Summer POE50 W E @ R (MWh) N 2 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 5 Winter POE50 W E @ R (MWh) N 2 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 5 Summer POE50 W E @ R (MWh) N 2 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 6 Winter POE50 W E @ R (MWh) N 2 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 6 Summer POE50 W E @ R (MWh) N 2 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 7 Winter POE50 W E @ R (MWh) N 2 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 7 Summer POE50 W E @ R (MWh) N 2 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.6923 | 7.7795 | 9.251 | 9.3813 | 9.4684 | 9.5909 | 9.8699 | 10.0891 | 10.284 | 10.3523 | 10.4304 | 10.3212 | 10.3788 | 10.6494 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 | 10.5297 |  | 7.4069 | 8.4972 | 9.9806 | 10.0997 | 10.1835 | 10.2697 | 10.602 | 10.7963 | 10.995 | 11.0854 | 11.1329 | 10.9681 | 11.0542 | 11.3845 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291 | 11.2291
98% | 13.2501 | 15.4026 | 18.316 | 18.5739 | 18.7464 | 18.9889 | 19.5415 | 19.9754 | 20.3612 | 20.4966 | 20.6512 | 20.435 | 20.549 | 21.0848 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 | 20.8478 |  | 14.6649 | 16.8236 | 19.7607 | 19.9965 | 20.1622 | 20.3329 | 20.991 | 21.3757 | 21.7691 | 21.9481 | 22.0421 | 21.7157 | 21.8861 | 22.5402 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325 | 22.2325
97% | 19.6734 | 22.8693 | 27.1951 | 27.5781 | 27.8342 | 28.1942 | 29.0147 | 29.6589 | 30.2317 | 30.4327 | 30.6623 | 30.3413 | 30.5106 | 31.3062 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 | 30.9543 |  | 29.032 | 33.3057 | 39.1201 | 39.5869 | 39.9151 | 40.2529 | 41.5557 | 42.3173 | 43.0962 | 43.4505 | 43.6367 | 42.9905 | 43.3279 | 44.6227 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135 | 44.0135
95% | 58.1123 | 67.5523 | 80.3303 | 81.4613 | 82.2178 | 83.2814 | 85.7049 | 87.6079 | 89.2999 | 89.8935 | 90.5717 | 89.6235 | 90.1235 | 92.4736 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 | 91.4341 |  | 50.0244 | 57.3883 | 67.4069 | 68.2113 | 68.7767 | 69.3589 | 71.6037 | 72.916 | 74.258 | 74.8685 | 75.1894 | 74.076 | 74.6573 | 76.8883 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386 | 75.8386
90% | 223.9745 | 260.3579 | 309.6063 | 313.9655 | 316.8812 | 320.9802 | 330.3209 | 337.6553 | 344.1768 | 346.4645 | 349.0783 | 345.4241 | 347.3511 | 356.4086 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 | 352.4024 |  | 172.145 | 197.4857 | 231.9622 | 234.7302 | 236.6758 | 238.6791 | 246.4043 | 250.9198 | 255.5382 | 257.639 | 258.7432 | 254.9117 | 256.9123 | 264.5896 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774 | 260.9774
85% | 482.5876 | 560.9813 | 667.0946 | 676.4873 | 682.7696 | 691.6015 | 711.7275 | 727.5305 | 741.5822 | 746.5114 | 752.1432 | 744.2696 | 748.4216 | 767.9375 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 | 759.3054 |  | 462.4652 | 530.5426 | 623.1632 | 630.5996 | 635.8264 | 641.2083 | 661.9617 | 674.0928 | 686.4999 | 692.1437 | 695.11 | 684.8169 | 690.1913 | 710.8163 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123 | 701.1123
80% | 1326.1911 | 1541.6235 | 1833.2317 | 1859.0437 | 1876.308 | 1900.5788 | 1955.8867 | 1999.3147 | 2037.9299 | 2051.4758 | 2066.9523 | 2045.315 | 2056.7251 | 2110.3564 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 | 2086.6347 |  | 1062.4602 | 1218.8602 | 1431.6454 | 1448.7296 | 1460.7376 | 1473.1018 | 1520.7805 | 1548.6502 | 1577.1541 | 1590.1201 | 1596.9349 | 1573.2876 | 1585.6347 | 1633.0183 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244 | 1610.7244
75% | 2345.6784 | 2726.721 | 3242.4981 | 3288.1526 | 3318.6886 | 3361.617 | 3459.442 | 3536.2547 | 3604.5547 | 3628.5137 | 3655.8875 | 3617.6169 | 3637.7983 | 3732.6578 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 | 3690.7003 |  | 2290.3656 | 2627.5202 | 3086.2252 | 3123.054 | 3148.94 | 3175.5936 | 3278.3755 | 3338.4547 | 3399.9011 | 3427.8521 | 3442.543 | 3391.5661 | 3418.1829 | 3520.3287 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694 | 3472.2694
70% | 3276.8875 | 3809.1999 | 4529.735 | 4593.5139 | 4636.1722 | 4696.1429 | 4832.8033 | 4940.1098 | 5035.5241 | 5068.9946 | 5107.2355 | 5053.772 | 5081.9651 | 5214.4828 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 | 5155.8687 |  | 3378.508 | 3875.8432 | 4552.4768 | 4606.8028 | 4644.9871 | 4684.3037 | 4835.9168 | 4924.5394 | 5015.1787 | 5056.4091 | 5078.0796 | 5002.8837 | 5042.1462 | 5192.8209 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288 | 5121.9288
65% | 4984.945 | 5794.7219 | 6890.8315 | 6987.8547 | 7052.7485 | 7143.9784 | 7351.8723 | 7515.1115 | 7660.26 | 7711.1768 | 7769.3506 | 7688.0195 | 7730.9081 | 7932.4998 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 | 7843.3335 |  | 4763.4841 | 5464.6955 | 6418.7064 | 6495.3027 | 6549.1401 | 6604.5741 | 6818.3391 | 6943.2913 | 7071.0871 | 7129.2193 | 7159.7734 | 7053.7519 | 7109.1095 | 7321.5513 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598 | 7221.598
60% | 6208.9015 | 7217.5034 | 8582.7415 | 8703.5868 | 8784.414 | 8898.0437 | 9156.9819 | 9360.3013 | 9541.0882 | 9604.5067 | 9676.9639 | 9575.6635 | 9629.0826 | 9880.1712 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 | 9769.1119 |  | 6806.7054 | 7808.6904 | 9171.9091 | 9281.3602 | 9358.2903 | 9437.5018 | 9742.9579 | 9921.5065 | 10104.1182 | 10187.1853 | 10230.8451 | 10079.3474 | 10158.4497 | 10462.0152 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884 | 10319.1884
55% | 7135.4024 | 8294.5093 | 9863.4701 | 10002.3482 | 10095.2365 | 10225.8222 | 10523.3995 | 10757.0586 | 10964.8227 | 11037.7045 | 11120.9739 | 11004.5573 | 11065.9477 | 11354.5042 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 | 11226.8723 |  | 7589.081 | 8706.2361 | 10226.1458 | 10348.1774 | 10433.95 | 10522.2662 | 10862.832 | 11061.9033 | 11265.5047 | 11358.1197 | 11406.7979 | 11237.8868 | 11326.0812 | 11664.5391 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956 | 11505.2956
50% | 7376.5281 | 8574.8045 | 10196.785 | 10340.3561 | 10436.3834 | 10571.382 | 10879.0152 | 11120.5703 | 11335.3554 | 11410.7001 | 11496.7834 | 11376.4328 | 11439.8977 | 11738.2053 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 | 11606.2605 |  | 8183.6791 | 9388.3623 | 11027.3556 | 11158.9483 | 11251.4411 | 11346.6768 | 11713.9257 | 11928.594 | 12148.1475 | 12248.0188 | 12300.5108 | 12118.3656 | 12213.47 | 12578.4458 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257 | 12406.7257
45% | 6721.9241 | 7813.8637 | 9291.9072 | 9422.7376 | 9510.2433 | 9633.2619 | 9913.5953 | 10133.7145 | 10329.4392 | 10398.0977 | 10476.5419 | 10366.8713 | 10424.7043 | 10696.5396 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 | 10576.3037 |  | 7595.2224 | 8713.2815 | 10234.4212 | 10356.5516 | 10442.3935 | 10530.7813 | 10871.6227 | 11070.855 | 11274.6212 | 11367.3112 | 11416.0287 | 11246.9809 | 11335.2467 | 11673.9785 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061 | 11514.6061
40% | 5236.8322 | 6087.5268 | 7239.0223 | 7340.9481 | 7409.1209 | 7504.9607 | 7723.3593 | 7894.847 | 8047.3298 | 8100.8194 | 8161.9326 | 8076.4919 | 8121.5477 | 8333.3257 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 | 8239.6539 |  | 6185.1224 | 7095.607 | 8334.3376 | 8433.7938 | 8503.6987 | 8575.6766 | 8853.2387 | 9015.4824 | 9181.4181 | 9256.8996 | 9296.5724 | 9158.9094 | 9230.7881 | 9506.6322 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483 | 9376.8483
35% | 3220.8939 | 3744.1104 | 4452.3335 | 4515.0225 | 4556.9519 | 4615.8978 | 4750.2231 | 4855.6959 | 4949.4799 | 4982.3785 | 5019.966 | 4967.4159 | 4995.1273 | 5125.3806 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 | 5067.7681 |  | 3846.7423 | 4413.0042 | 5183.4138 | 5245.2691 | 5288.7453 | 5333.5109 | 5506.1364 | 5607.0414 | 5710.2426 | 5757.1872 | 5781.8611 | 5696.2436 | 5740.9475 | 5912.5045 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874 | 5831.7874
30% | 1530.1558 | 1778.7212 | 2115.178 | 2144.9598 | 2164.8793 | 2192.8828 | 2256.697 | 2306.8041 | 2351.3582 | 2366.9874 | 2384.8442 | 2359.8792 | 2373.044 | 2434.9237 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 | 2407.5536 |  | 1988.6932 | 2281.4399 | 2679.7272 | 2711.7051 | 2734.1816 | 2757.3245 | 2846.5687 | 2898.7346 | 2952.0877 | 2976.3571 | 2989.1131 | 2944.8505 | 2967.9615 | 3056.6533 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241 | 3014.9241
25% | 723.2088 | 840.6901 | 999.7121 | 1013.7881 | 1023.2028 | 1036.4383 | 1066.5993 | 1090.2818 | 1111.3398 | 1118.7267 | 1127.1665 | 1115.3671 | 1121.5893 | 1150.8359 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 | 1137.8998 |  | 812.7104 | 932.3459 | 1095.1122 | 1108.1805 | 1117.3658 | 1126.8235 | 1163.2945 | 1184.613 | 1206.4165 | 1216.3346 | 1221.5475 | 1203.4589 | 1212.9036 | 1249.1489 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956 | 1232.0956
20% | 373.7952 | 434.5162 | 516.7078 | 523.983 | 528.8491 | 535.6899 | 551.2788 | 563.5193 | 574.4032 | 578.2212 | 582.5834 | 576.4848 | 579.7008 | 594.8171 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 | 588.131 |  | 433.8053 | 497.6639 | 584.5446 | 591.5202 | 596.4231 | 601.4714 | 620.9388 | 632.318 | 643.9562 | 649.2503 | 652.0328 | 642.3775 | 647.4189 | 666.7658 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631 | 657.6631
15% | 138.8911 | 161.4532 | 191.9931 | 194.6963 | 196.5044 | 199.0463 | 204.8386 | 209.3868 | 213.431 | 214.8496 | 216.4705 | 214.2044 | 215.3994 | 221.0162 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 | 218.5318 |  | 140.6936 | 161.4045 | 189.582 | 191.8444 | 193.4345 | 195.0718 | 201.3855 | 205.0761 | 208.8507 | 210.5677 | 211.4701 | 208.3387 | 209.9737 | 216.2484 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961 | 213.2961
10% | 37.8335 | 43.9794 | 52.2984 | 53.0347 | 53.5272 | 54.2196 | 55.7975 | 57.0364 | 58.138 | 58.5244 | 58.9659 | 58.3487 | 58.6742 | 60.2042 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 | 59.5274 |  | 37.2205 | 42.6996 | 50.154 | 50.7525 | 51.1732 | 51.6063 | 53.2766 | 54.2529 | 55.2515 | 55.7057 | 55.9445 | 55.116 | 55.5486 | 57.2086 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276 | 56.4276
5% | 13.6201 | 15.8326 | 18.8274 | 19.0925 | 19.2698 | 19.5191 | 20.0871 | 20.5331 | 20.9297 | 21.0688 | 21.2277 | 21.0055 | 21.1227 | 21.6735 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 | 21.4299 |  | 15.6326 | 17.9338 | 21.0647 | 21.316 | 21.4927 | 21.6746 | 22.3762 | 22.7862 | 23.2056 | 23.3964 | 23.4967 | 23.1487 | 23.3304 | 24.0276 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996 | 23.6996
9.992e-14% | 5.5489 | 6.4503 | 7.6704 | 7.7784 | 7.8507 | 7.9522 | 8.1836 | 8.3653 | 8.5269 | 8.5836 | 8.6483 | 8.5578 | 8.6055 | 8.8299 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 | 8.7307 |  | 0.93051 | 1.0675 | 1.2538 | 1.2688 | 1.2793 | 1.2902 | 1.3319 | 1.3563 | 1.3813 | 1.3926 | 1.3986 | 1.3779 | 1.3887 | 1.4302 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107 | 1.4107
E @ R (MWh) | 50946.9127 | 59222.9584 | 70425.3691 | 71416.9611 | 72080.1856 | 73012.5699 | 75137.2775 | 76805.6081 | 78289.0482 | 78809.4258 | 79403.9708 | 78572.7541 | 79011.0826 | 81071.3814 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | 80160.0876 | E @ R (MWh) | 55308.1272 | 63449.7919 | 74526.6742 | 75416.0234 | 76041.1214 | 76684.7574 | 79166.7518 | 80617.5543 | 82101.3726 | 82776.3372 | 83131.0964 | 81900.0966 | 82542.845 | 85009.477 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333 | 83848.9333
Option 8 Winter POE50 W E @ R (MWh) N 2 | 35662.8389 | 41456.0709 | 49297.7584 | 49991.8728 | 50456.1299 | 51108.7989 | 52596.0943 | 53763.9257 | 54802.3337 | 55166.598 | 55582.7796 | 55000.9279 | 55307.7578 | 56749.967 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | 56112.0613 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 16592.4382 | 19034.9376 | 22358.0023 | 22624.807 | 22812.3364 | 23005.4272 | 23750.0256 | 24185.2663 | 24630.4118 | 24832.9012 | 24939.3289 | 24570.029 | 24762.8535 | 25502.8431 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68 | 25154.68
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 9.73 | 10.8018 | 12.6064 | 12.5928 | 12.5806 | 12.7762 | 13.0634 | 13.2602 | 13.0209 | 13.0447 | 13.1587 | 13.6102 | 13.1824 | 13.1573 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 | 13.1303 |  | 31.7181 | 35.6755 | 41.0797 | 41.0071 | 41.0547 | 41.2025 | 41.7045 | 42.0407 | 42.3165 | 42.3571 | 42.6058 | 42.694 | 42.6937 | 42.6368 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247 | 42.6247
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20.9329 | 23.5447 | 27.1112 | 27.0633 | 27.0947 | 27.1923 | 27.5235 | 27.7455 | 27.9275 | 27.9543 | 28.1184 | 28.1766 | 28.1764 | 28.1389 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309 | 28.1309
97% | 9.5345 | 10.5847 | 12.353 | 12.3397 | 12.3277 | 12.5194 | 12.8008 | 12.9936 | 12.7592 | 12.7825 | 12.8942 | 13.3366 | 12.9175 | 12.8928 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 | 12.8664 |  | 10.3602 | 11.6528 | 13.418 | 13.3943 | 13.4098 | 13.4581 | 13.6221 | 13.7319 | 13.822 | 13.8352 | 13.9165 | 13.9453 | 13.9452 | 13.9266 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226 | 13.9226
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 51.0039 | 57.3677 | 66.0578 | 65.9411 | 66.0177 | 66.2552 | 67.0625 | 67.6031 | 68.0466 | 68.1119 | 68.5119 | 68.6536 | 68.6533 | 68.5617 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422 | 68.5422
90% | 72.3641 | 80.3352 | 93.7559 | 93.655 | 93.5642 | 95.0188 | 97.1546 | 98.6182 | 96.8392 | 97.0161 | 97.864 | 101.2215 | 98.0402 | 97.8533 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 | 97.6527 |  | 294.8663 | 331.657 | 381.8967 | 381.2218 | 381.6646 | 383.038 | 387.7048 | 390.8307 | 393.3945 | 393.772 | 396.0843 | 396.9038 | 396.9017 | 396.3723 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598 | 396.2598
85% | 222.4708 | 246.9765 | 288.236 | 287.926 | 287.6466 | 292.1187 | 298.6848 | 303.1843 | 297.715 | 298.2589 | 300.8656 | 311.1878 | 301.4072 | 300.8327 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 | 300.2161 |  | 390.4987 | 439.2215 | 505.7551 | 504.8613 | 505.4477 | 507.2666 | 513.4469 | 517.5866 | 520.9819 | 521.4819 | 524.5441 | 525.6293 | 525.6266 | 524.9255 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765 | 524.7765
80% | 459.8544 | 510.5085 | 595.7932 | 595.1524 | 594.575 | 603.8191 | 617.3913 | 626.692 | 615.3868 | 616.511 | 621.899 | 643.2355 | 623.0187 | 621.831 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 | 620.5566 |  | 613.6408 | 690.2052 | 794.7579 | 793.3535 | 794.275 | 797.1332 | 806.8452 | 813.3504 | 818.6859 | 819.4715 | 824.2835 | 825.9889 | 825.9846 | 824.8829 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488 | 824.6488
75% | 909.441 | 1009.6182 | 1178.2832 | 1177.016 | 1175.8739 | 1194.1557 | 1220.9972 | 1239.3909 | 1217.0329 | 1219.2562 | 1229.912 | 1272.1085 | 1232.1262 | 1229.7775 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 | 1227.257 |  | 1383.481 | 1556.0989 | 1791.8179 | 1788.6516 | 1790.729 | 1797.1731 | 1819.0691 | 1833.7354 | 1845.7645 | 1847.5359 | 1858.3847 | 1862.2295 | 1862.2198 | 1859.736 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081 | 1859.2081
70% | 2091.4698 | 2321.8503 | 2709.7347 | 2706.8204 | 2704.1939 | 2746.2372 | 2807.9654 | 2850.266 | 2798.8485 | 2803.9616 | 2828.4669 | 2925.5077 | 2833.5591 | 2828.1576 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 | 2822.3612 |  | 3096.8935 | 3483.2952 | 4010.9472 | 4003.8596 | 4008.5097 | 4022.9347 | 4071.9485 | 4104.7786 | 4131.7056 | 4135.6707 | 4159.9557 | 4168.5622 | 4168.5404 | 4162.9806 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988 | 4161.7988
65% | 3683.2359 | 4088.9535 | 4772.0471 | 4766.9148 | 4762.2893 | 4836.3308 | 4945.0388 | 5019.5333 | 4928.9833 | 4937.9877 | 4981.1435 | 5152.0396 | 4990.1112 | 4980.5988 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 | 4970.3908 |  | 4855.7313 | 5461.5845 | 6288.9093 | 6277.7963 | 6285.0874 | 6307.7048 | 6384.5554 | 6436.0308 | 6478.2507 | 6484.4677 | 6522.545 | 6536.0395 | 6536.0054 | 6527.2879 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435 | 6525.435
60% | 5433.4208 | 6031.9257 | 7039.6088 | 7032.0378 | 7025.2144 | 7134.4386 | 7294.802 | 7404.6946 | 7271.1173 | 7284.4005 | 7348.0629 | 7600.1646 | 7361.2918 | 7347.2593 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 | 7332.2007 |  | 6840.3677 | 7693.8455 | 8859.3148 | 8843.6597 | 8853.9308 | 8885.7924 | 8994.0533 | 9066.5678 | 9126.0439 | 9134.8019 | 9188.4421 | 9207.4521 | 9207.404 | 9195.1235 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133 | 9192.5133
55% | 6921.7748 | 7684.2255 | 8967.939 | 8958.2942 | 8949.6016 | 9088.7451 | 9293.0361 | 9433.0312 | 9262.8637 | 9279.7854 | 9360.8865 | 9682.0455 | 9377.7393 | 9359.8629 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 | 9340.6794 |  | 8645.4279 | 9724.1243 | 11197.1417 | 11177.3555 | 11190.337 | 11230.6063 | 11367.4355 | 11459.0854 | 11534.2563 | 11545.3253 | 11613.1203 | 11637.1468 | 11637.086 | 11621.5648 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658 | 11618.2658
50% | 7849.7957 | 8714.4702 | 10170.2947 | 10159.3567 | 10149.4987 | 10307.2975 | 10538.9785 | 10697.743 | 10504.7607 | 10523.9512 | 10615.9258 | 10980.1434 | 10635.038 | 10614.7648 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 | 10593.0094 |  | 9606.2671 | 10804.8481 | 12441.5744 | 12419.5892 | 12434.0134 | 12478.7582 | 12630.7944 | 12732.6301 | 12816.1553 | 12828.4546 | 12903.7842 | 12930.4809 | 12930.4134 | 12913.1672 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016 | 12909.5016
45% | 7213.676 | 8008.2803 | 9346.1299 | 9336.0783 | 9327.0192 | 9472.0305 | 9684.9369 | 9830.8357 | 9653.492 | 9671.1273 | 9755.6486 | 10090.3513 | 9773.212 | 9754.5818 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 | 9734.5893 |  | 8716.6209 | 9804.2 | 11289.3474 | 11269.3983 | 11282.4866 | 11323.0876 | 11461.0435 | 11553.4482 | 11629.238 | 11640.3982 | 11708.7515 | 11732.9758 | 11732.9145 | 11717.2655 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393 | 11713.9393
40% | 5427.7979 | 6025.6834 | 7032.3237 | 7024.7606 | 7017.9442 | 7127.0553 | 7287.2528 | 7397.0317 | 7263.5927 | 7276.8621 | 7340.4586 | 7592.2994 | 7353.6738 | 7339.6558 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 | 7324.6129 |  | 7044.9147 | 7923.9138 | 9124.2341 | 9108.1109 | 9118.6891 | 9151.5034 | 9263.0017 | 9337.6846 | 9398.9392 | 9407.9591 | 9463.2033 | 9482.7818 | 9482.7322 | 9470.0845 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962 | 9467.3962
35% | 4206.1645 | 4669.484 | 5449.5599 | 5443.699 | 5438.4168 | 5522.9703 | 5647.1122 | 5732.1831 | 5628.7772 | 5639.0601 | 5688.3429 | 5883.502 | 5698.5838 | 5687.7209 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 | 5676.0636 |  | 4933.0341 | 5548.5324 | 6389.0282 | 6377.7383 | 6385.1454 | 6408.1229 | 6486.1969 | 6538.4918 | 6581.3839 | 6587.6998 | 6626.3833 | 6640.0927 | 6640.058 | 6631.2017 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193 | 6629.3193
30% | 2367.7247 | 2628.5354 | 3067.654 | 3064.3549 | 3061.3814 | 3108.9781 | 3178.8597 | 3226.7477 | 3168.5386 | 3174.327 | 3202.0692 | 3311.9278 | 3207.834 | 3201.7191 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 | 3195.157 |  | 2289.5973 | 2575.272 | 2965.3761 | 2960.136 | 2963.574 | 2974.2386 | 3010.4755 | 3034.7475 | 3054.6552 | 3057.5867 | 3075.5411 | 3081.9041 | 3081.888 | 3077.7775 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038 | 3076.9038
25% | 1540.9157 | 1710.6514 | 1996.4299 | 1994.2828 | 1992.3476 | 2023.3236 | 2068.8026 | 2099.9681 | 2062.0856 | 2065.8527 | 2083.9073 | 2155.4033 | 2087.659 | 2083.6794 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 | 2079.4088 |  | 1312.0224 | 1475.7244 | 1699.2682 | 1696.2654 | 1698.2355 | 1704.3467 | 1725.1118 | 1739.0205 | 1750.4284 | 1752.1082 | 1762.3967 | 1766.043 | 1766.0337 | 1763.6783 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776 | 1763.1776
20% | 1042.9234 | 1157.804 | 1351.2248 | 1349.7716 | 1348.4619 | 1369.427 | 1400.2081 | 1421.3016 | 1395.6619 | 1398.2116 | 1410.4313 | 1458.8213 | 1412.9706 | 1410.2771 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 | 1407.3867 |  | 604.8745 | 680.3451 | 783.4043 | 782.0199 | 782.9282 | 785.7456 | 795.3188 | 801.7311 | 806.9904 | 807.7648 | 812.5081 | 814.1891 | 814.1848 | 813.0989 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681 | 812.8681
15% | 641.7426 | 712.4322 | 831.4499 | 830.5557 | 829.7497 | 842.6502 | 861.5908 | 874.5702 | 858.7934 | 860.3623 | 867.8814 | 897.6572 | 869.4439 | 867.7865 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 | 866.008 |  | 143.1828 | 161.0479 | 185.4435 | 185.1158 | 185.3308 | 185.9978 | 188.2639 | 189.7817 | 191.0267 | 191.21 | 192.3328 | 192.7307 | 192.7297 | 192.4727 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418 | 192.418
10% | 347.1522 | 385.3919 | 449.7748 | 449.2911 | 448.8551 | 455.8336 | 466.0796 | 473.1008 | 464.5663 | 465.415 | 469.4825 | 485.5898 | 470.3278 | 469.4312 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 | 468.4691 |  | 49.1444 | 55.2762 | 63.6494 | 63.537 | 63.6108 | 63.8397 | 64.6175 | 65.1384 | 65.5658 | 65.6287 | 66.0141 | 66.1506 | 66.1503 | 66.0621 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433 | 66.0433
5% | 165.753 | 184.0111 | 214.7516 | 214.5207 | 214.3125 | 217.6445 | 222.5366 | 225.889 | 221.8141 | 222.2193 | 224.1614 | 231.852 | 224.5649 | 224.1369 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 | 223.6775 |  | 4.7816 | 5.3782 | 6.1929 | 6.182 | 6.1892 | 6.2114 | 6.2871 | 6.3378 | 6.3794 | 6.3855 | 6.423 | 6.4363 | 6.4362 | 6.4277 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258 | 6.4258
9.992e-14% | 46.6944 | 51.8379 | 60.4979 | 60.4328 | 60.3742 | 61.3128 | 62.691 | 63.6354 | 62.4874 | 62.6016 | 63.1487 | 65.3153 | 63.2624 | 63.1418 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 | 63.0124 |  | 0.79694 | 0.89637 | 1.0322 | 1.0303 | 1.0315 | 1.0352 | 1.0479 | 1.0563 | 1.0632 | 1.0642 | 1.0705 | 1.0727 | 1.0727 | 1.0713 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071 | 1.071
E @ R (MWh) | 50156.9998 | 55681.918 | 64984.0437 | 64914.1547 | 64851.1662 | 65859.4363 | 67339.7831 | 68354.2239 | 67121.1456 | 67243.7649 | 67831.4451 | 70158.6473 | 67953.5642 | 67824.0272 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | 67685.0187 | E @ R (MWh) | 60330.7573 | 67858.2701 | 78137.4903 | 77999.4156 | 78090.0047 | 78371.0178 | 79325.8589 | 79965.4234 | 80489.9911 | 80567.2348 | 81040.3317 | 81207.9964 | 81207.5723 | 81099.2603 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386 | 81076.2386
Option 8 Summer POE50 W E @ R (MWh) N 2 | 35109.8999 | 38977.3426 | 45488.8306 | 45439.9083 | 45395.8163 | 46101.6054 | 47137.8482 | 47847.9567 | 46984.8019 | 47070.6354 | 47482.0115 | 49111.0531 | 47567.495 | 47476.8191 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | 47379.5131 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 18099.2272 | 20357.481 | 23441.2471 | 23399.8247 | 23427.0014 | 23511.3053 | 23797.7577 | 23989.627 | 24146.9973 | 24170.1704 | 24312.0995 | 24362.3989 | 24362.2717 | 24329.7781 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716 | 24322.8716

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-LLG-TRNFMR-9000007796 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 2 Pof | bar: FY25 to FY54
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
N-1 Risk |  | 0.07365% | 0.07365% | 0.08139% | 0.08959% | 0.09827% | 0.1074% | 0.1171% | 0.1272% | 0.1379% | 0.1491% | 0.1608% | 0.1731% | 0.1858% | 0.1992% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213%
N-2 Risk | bar: FY25 to FY54
N Risk |  | 99.93% | 99.93% | 99.92% | 99.91% | 99.9% | 99.89% | 99.88% | 99.87% | 99.86% | 99.85% | 99.84% | 99.83% | 99.81% | 99.8% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 95.7866 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 1 | 95.7866 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Cost of EUE ($) - Option 1 | 3612289.7659 | 4090292.8113 | 5298881.0232 | 5865658.9267 | 6460415.7205 | 7144193.8456 | 7975434.384 | 8811850.7018 | 9588936.2834 | 10410734.4207 | 11308769.3264 | 12245280.0099 | 13045403.5215 | 14153978.2765 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554
Hours at Risk pA. (Hrs) (N) | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 2 | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Cost of EUE ($) - Option 2 | 3605536.4645 | 4090292.8113 | 5298881.0232 | 5865658.9267 | 6460415.7205 | 7144193.8456 | 7975434.384 | 8811850.7018 | 9588936.2834 | 10410734.4207 | 11308769.3264 | 12245280.0099 | 13045403.5215 | 14153978.2765 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 3 | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Cost of EUE ($) - Option 3 | 3605536.4645 | 4090292.8113 | 5298881.0232 | 5865658.9267 | 6460415.7205 | 7144193.8456 | 7975434.384 | 8811850.7018 | 9588936.2834 | 10410734.4207 | 11308769.3264 | 12245280.0099 | 13045403.5215 | 14153978.2765 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 4 | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Cost of EUE ($) - Option 4 | 3605536.4645 | 4090292.8113 | 5298881.0232 | 5865658.9267 | 6460415.7205 | 7144193.8456 | 7975434.384 | 8811850.7018 | 9588936.2834 | 10410734.4207 | 11308769.3264 | 12245280.0099 | 13045403.5215 | 14153978.2765 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 95.6075 | 108.4617 | 140.5097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 5 | 95.6075 | 108.4617 | 140.5097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of EUE ($) - Option 5 | 3605536.4645 | 4090292.8113 | 5298881.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 6 | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Cost of EUE ($) - Option 6 | 3605536.4645 | 4090292.8113 | 5298881.0232 | 5865658.9267 | 6460415.7205 | 7144193.8456 | 7975434.384 | 8811850.7018 | 9588936.2834 | 10410734.4207 | 11308769.3264 | 12245280.0099 | 13045403.5215 | 14153978.2765 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 7 | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Cost of EUE ($) - Option 7 | 3605536.4645 | 4090292.8113 | 5298881.0232 | 5865658.9267 | 6460415.7205 | 7144193.8456 | 7975434.384 | 8811850.7018 | 9588936.2834 | 10410734.4207 | 11308769.3264 | 12245280.0099 | 13045403.5215 | 14153978.2765 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 8 | 95.6075 | 108.4617 | 140.5097 | 155.5388 | 171.3099 | 189.4415 | 211.4834 | 233.6626 | 254.2684 | 276.0599 | 299.873 | 324.7063 | 345.9231 | 375.319 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122 | 398.8122
Cost of EUE ($) - Option 8 | 3605536.4645 | 4090292.8113 | 5298881.0232 | 5865658.9267 | 6460415.7205 | 7144193.8456 | 7975434.384 | 8811850.7018 | 9588936.2834 | 10410734.4207 | 11308769.3264 | 12245280.0099 | 13045403.5215 | 14153978.2765 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554 | 15039950.4554