## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 34378474.2948 | 37.17% | 18.2965
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 31576189.3656 | 34.14% | 11.7393
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 10621047.2058 | 11.48% | 3.8453
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 15925855.934 | 17.22% | 3.8307
[5 empty] | 92501566.8003 |  | 37.7119
Customer No. and Vol per Feeder | [6 empty] | 37711.8651 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 31576189.3656 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 173.0319 | E@R MWh | 173.0319
RESIDENTL | 34378474.2948 | [14 empty] | cost of EUE ($) | 6525355.4051 | cost of EUE ($M) | 6.5254
FARM | 15925855.934
INDUSTRIAL | 10621047.2058
Forecast (FCT)
Forecast | 2031
Summer POE50 | 28.4054
Summer POE10 | 30.2279
Winter POE50 | 27.3083
Winter POE10 | 29.3339
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 0 |  | Summer POE50 | 28.4054 |  |  | 100% | 0 | 28.4054 | 100% |  | 0% |  | 0%
|  |  | Summer POE10 | 30.2279 |  |  | 99% | 0.37816 | 28.1214 | 99% |  | 0% | 10.6882 | 0% | 10.6882
Embedded Generation |  |  | Winter POE50 | 27.3083 |  |  | 98% | 0.37816 | 27.8373 | 98% |  | 0% | 0 | 0% | 0
|  |  | Winter POE10 | 29.3339 |  |  | 97% | 0.75633 | 27.5532 | 97% |  | 0% | 10.4734 | 0% | 10.4734
Year | 2031 | [5 empty] | 95% | 0.75633 | 26.9851 | 95% |  | 0% | 0 | 0% | 0
Capacity | 0 | [5 empty] | 90% | 3.7816 | 25.5649 | 90% |  | 0% | 79.4901 | 0% | 79.4901
[7 empty] | 85% | 13.6139 | 24.1446 | 85% |  | 0% | 244.3785 | 0% | 244.3785
Demand Mangement | [6 empty] | 80% | 35.1693 | 22.7243 | 80% |  | 0% | 505.1384 | 0% | 505.1384
[7 empty] | 75% | 80.549 | 21.3041 | 75% |  | 0% | 998.9977 | 0% | 998.9977
Year | 2031 | [5 empty] | 70% | 192.1075 | 19.8838 | 70% |  | 0% | 2297.4262 | 0% | 2297.4262
Capacity | 0 | [5 empty] | 65% | 403.1231 | 18.4635 | 65% |  | 0% | 4045.9408 | 0% | 4045.9408
[7 empty] | 60% | 739.3112 | 17.0432 | 60% |  | 0% | 5968.4743 | 0% | 5968.4743
LDC | [6 empty] | 55% | 1204.8314 | 15.623 | 55% |  | 0% | 7603.3932 | 0% | 7603.3932
[7 empty] | 50% | 1783.0446 | 14.2027 | 50% |  | 0% | 8622.8006 | 0% | 8622.8006
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2370.3337 | 12.7824 | 45% |  | 0% | 7924.0392 | 0% | 7924.0392
100% | 0% | 0 |  |  |  |  | 40% | 2864.2163 | 11.3622 | 40% |  | 0% | 5962.2977 | 0% | 5962.2977
99% | 0.00861% | 0.37816 |  |  |  |  | 35% | 3297.9707 | 9.9419 | 35% |  | 0% | 4620.3645 | 0% | 4620.3645
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3579.7031 | 8.5216 | 30% |  | 0% | 2600.8852 | 0% | 2600.8852
97% | 0.01722% | 0.75633 |  |  |  |  | 25% | 3796.3913 | 7.1014 | 25% |  | 0% | 1692.6566 | 0% | 1692.6566
95% | 0.01722% | 0.75633 |  |  |  |  | 20% | 3975.6411 | 5.6811 | 20% |  | 0% | 1145.6248 | 0% | 1145.6248
90% | 0.0861% | 3.7816 |  |  |  |  | 15% | 4117.4527 | 4.2608 | 15% |  | 0% | 704.9379 | 0% | 704.9379
85% | 0.31% | 13.6139 |  |  |  |  | 10% | 4224.8514 | 2.8405 | 10% |  | 0% | 381.3378 | 0% | 381.3378
80% | 0.8008% | 35.1693 |  |  |  |  | 5% | 4310.3165 | 1.4203 | 5% |  | 0% | 182.0754 | 0% | 182.0754
75% | 1.834% | 80.549 |  |  |  |  | 9.992e-14% | 4382.5459 | 2.8383e-14 | 9.992e-14% |  | 0% | 51.2926 | 0% | 51.2926
70% | 4.374% | 192.1075 | [7 empty] | Total E@R | 0 | Total E@R | 55096.1862 | Total E@R | 55096.1862
65% | 9.179% | 403.1231 | [7 empty] | Total WE@R | 0 | Total WE@R | 60.061 | Total WE@R | 0
60% | 16.83% | 739.3112 |  |  |  |  | MD Weighted LDC
55% | 27.43% | 1204.8314
50% | 40.6% | 1783.0446 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 53.97% | 2370.3337 |  |  |  |  | 100% | 0 | 30.2279 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 65.21% | 2864.2163 |  |  |  |  | 99% | 1.1345 | 29.9256
35% | 75.09% | 3297.9707 |  |  |  |  | 98% | 1.8908 | 29.6233 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 81.51% | 3579.7031 |  |  |  |  | 97% | 2.269 | 29.321 | 100% |  | 0% |  | 0%
25% | 86.44% | 3796.3913 |  |  |  |  | 95% | 4.1598 | 28.7165 | 99% |  | 0% | 34.1218 | 0% | 34.1218
20% | 90.52% | 3975.6411 |  |  |  |  | 90% | 15.5047 | 27.2051 | 98% |  | 0% | 22.5193 | 0% | 22.5193
15% | 93.75% | 4117.4527 |  |  |  |  | 85% | 31.3876 | 25.6937 | 97% |  | 0% | 11.1453 | 0% | 11.1453
10% | 96.19% | 4224.8514 |  |  |  |  | 80% | 57.8591 | 24.1823 | 95% |  | 0% | 54.8693 | 0% | 54.8693
5% | 98.14% | 4310.3165 |  |  |  |  | 75% | 121.3907 | 22.6709 | 90% |  | 0% | 317.213 | 0% | 317.213
9.992e-14% | 99.78% | 4382.5459 |  |  |  |  | 70% | 273.4128 | 21.1595 | 85% |  | 0% | 420.0929 | 0% | 420.0929
[7 empty] | 65% | 529.43 | 19.6481 | 80% |  | 0% | 660.146 | 0% | 660.146
[7 empty] | 60% | 918.9392 | 18.1367 | 75% |  | 0% | 1488.3293 | 0% | 1488.3293
[7 empty] | 55% | 1454.0417 | 16.6253 | 70% |  | 0% | 3331.5942 | 0% | 3331.5942
LDC | [6 empty] | 50% | 2105.2406 | 15.1139 | 65% |  | 0% | 5223.7271 | 0% | 5223.7271
[7 empty] | 45% | 2758.3303 | 13.6025 | 60% |  | 0% | 7358.7709 | 0% | 7358.7709
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 3348.2666 | 12.0911 | 55% |  | 0% | 9300.6291 | 0% | 9300.6291
100% | 0% | 0 |  |  |  |  | 35% | 3816.434 | 10.5798 | 50% |  | 0% | 10334.2863 | 0% | 10334.2863
99% | 0.02583% | 1.1345 |  |  |  |  | 30% | 4067.1569 | 9.0684 | 45% |  | 0% | 9377.2174 | 0% | 9377.2174
98% | 0.04305% | 1.8908 |  |  |  |  | 25% | 4236.9526 | 7.557 | 40% |  | 0% | 7578.8196 | 0% | 7578.8196
97% | 0.05166% | 2.269 |  |  |  |  | 20% | 4332.6282 | 6.0456 | 35% |  | 0% | 5306.8884 | 0% | 5306.8884
95% | 0.09471% | 4.1598 |  |  |  |  | 15% | 4361.7469 | 4.5342 | 30% |  | 0% | 2463.1164 | 0% | 2463.1164
90% | 0.353% | 15.5047 |  |  |  |  | 10% | 4375.7389 | 3.0228 | 25% |  | 0% | 1411.4551 | 0% | 1411.4551
85% | 0.7147% | 31.3876 |  |  |  |  | 5% | 4378.0079 | 1.5114 | 20% |  | 0% | 650.7154 | 0% | 650.7154
80% | 1.317% | 57.8591 |  |  |  |  | 9.992e-14% | 4379.1424 | 3.0204e-14 | 15% |  | 0% | 154.0341 | 0% | 154.0341
75% | 2.764% | 121.3907 | [7 empty] | 10% |  | 0% | 52.8688 | 0% | 52.8688
70% | 6.225% | 273.4128 | [7 empty] | 5% |  | 0% | 5.144 | 0% | 5.144
65% | 12.05% | 529.43 | [7 empty] | 9.992e-14% |  | 0% | 0.85733 | 0% | 0.85733
60% | 20.92% | 918.9392 | [7 empty] | Total E@R | 0 | Total E@R | 64902.9755 | Total E@R | 64902.9755
55% | 33.11% | 1454.0417 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 30.3221 | Total WE@R | 0
50% | 47.93% | 2105.2406
45% | 62.8% | 2758.3303 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 76.24% | 3348.2666 |  |  |  |  | 100% | 0 | 27.3083
35% | 86.9% | 3816.434 |  |  |  |  | 99% | 0.2972 | 27.0352 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 92.6% | 4067.1569 |  |  |  |  | 98% | 0.8916 | 26.7622
25% | 96.47% | 4236.9526 |  |  |  |  | 97% | 1.7832 | 26.4891 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 98.65% | 4332.6282 |  |  |  |  | 95% | 4.458 | 25.9429 | 100% |  | 0% |  | 0%
15% | 99.31% | 4361.7469 |  |  |  |  | 90% | 15.1571 | 24.5775 | 99% |  | 0% | 8.0754 | 0% | 8.0754
10% | 99.63% | 4375.7389 |  |  |  |  | 85% | 39.5274 | 23.2121 | 98% |  | 0% | 15.9885 | 0% | 15.9885
5% | 99.68% | 4378.0079 |  |  |  |  | 80% | 110.5579 | 21.8467 | 97% |  | 0% | 23.7393 | 0% | 23.7393
9.992e-14% | 99.71% | 4379.1424 |  |  |  |  | 75% | 244.2972 | 20.4812 | 95% |  | 0% | 70.1222 | 0% | 70.1222
[7 empty] | 70% | 444.0146 | 19.1158 | 90% |  | 0% | 270.2626 | 0% | 270.2626
[7 empty] | 65% | 770.3386 | 17.7504 | 85% |  | 0% | 582.3225 | 0% | 582.3225
[7 empty] | 60% | 1209.3009 | 16.385 | 80% |  | 0% | 1600.2709 | 0% | 1600.2709
LDC | [6 empty] | 55% | 1757.6322 | 15.0196 | 75% |  | 0% | 2830.4526 | 0% | 2830.4526
[7 empty] | 50% | 2378.4799 | 13.6542 | 70% |  | 0% | 3954.1118 | 0% | 3954.1118
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 3003.7856 | 12.2887 | 65% |  | 0% | 6015.1682 | 0% | 6015.1682
100% | 0% | 0 |  |  |  |  | 40% | 3548.2533 | 10.9233 | 60% |  | 0% | 7492.0761 | 0% | 7492.0761
99% | 0.006767% | 0.2972 |  |  |  |  | 35% | 3927.7759 | 9.5579 | 55% |  | 0% | 8610.0541 | 0% | 8610.0541
98% | 0.0203% | 0.8916 |  |  |  |  | 30% | 4135.8149 | 8.1925 | 50% |  | 0% | 8901.0125 | 0% | 8901.0125
97% | 0.0406% | 1.7832 |  |  |  |  | 25% | 4252.0195 | 6.8271 | 45% |  | 0% | 8111.1234 | 0% | 8111.1234
95% | 0.1015% | 4.458 |  |  |  |  | 20% | 4325.4275 | 5.4617 | 40% |  | 0% | 6319.1122 | 0% | 6319.1122
90% | 0.3451% | 15.1571 |  |  |  |  | 15% | 4360.497 | 4.0962 | 35% |  | 0% | 3886.5462 | 0% | 3886.5462
85% | 0.9% | 39.5274 |  |  |  |  | 10% | 4373.8709 | 2.7308 | 30% |  | 0% | 1846.3884 | 0% | 1846.3884
80% | 2.517% | 110.5579 |  |  |  |  | 5% | 4381.8952 | 1.3654 | 25% |  | 0% | 872.6722 | 0% | 872.6722
75% | 5.562% | 244.2972 |  |  |  |  | 9.992e-14% | 4391.7028 | 2.7286e-14 | 20% |  | 0% | 451.0463 | 0% | 451.0463
70% | 10.11% | 444.0146 | [7 empty] | 15% |  | 0% | 167.5953 | 0% | 167.5953
65% | 17.54% | 770.3386 | [7 empty] | 10% |  | 0% | 45.6525 | 0% | 45.6525
60% | 27.53% | 1209.3009 | [7 empty] | 5% |  | 0% | 16.4349 | 0% | 16.4349
55% | 40.02% | 1757.6322 | [7 empty] | 9.992e-14% |  | 0% | 6.6957 | 0% | 6.6957
50% | 54.15% | 2378.4799 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 61475.9543 | Total E@R | 61475.9543
45% | 68.39% | 3003.7856 | [7 empty] | Total WE@R | 0 | Total WE@R | 56.9381 | Total WE@R | 0
40% | 80.79% | 3548.2533 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 89.43% | 3927.7759 |  |  |  |  | 100% | 0 | 29.3339 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 94.17% | 4135.8149 |  |  |  |  | 99% | 0.2972 | 29.0405
25% | 96.81% | 4252.0195 |  |  |  |  | 98% | 0.8916 | 28.7472 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 98.48% | 4325.4275 |  |  |  |  | 97% | 2.0804 | 28.4539 | 100% |  | 100% |  | 100%
15% | 99.28% | 4360.497 |  |  |  |  | 95% | 4.1608 | 27.8672 | 99% |  | 99% | 8.6744 | 99% | 8.6744
10% | 99.59% | 4373.8709 |  |  |  |  | 90% | 11.5907 | 26.4005 | 98% |  | 98% | 17.1744 | 98% | 17.1744
5% | 99.77% | 4381.8952 |  |  |  |  | 85% | 32.6918 | 24.9338 | 97% |  | 97% | 34.0002 | 97% | 34.0002
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 84.1072 | 23.4671 | 95% |  | 95% | 58.5849 | 95% | 58.5849
[7 empty] | 75% | 202.095 | 22.0004 | 90% |  | 90% | 201.6035 | 90% | 201.6035
[7 empty] | 70% | 388.1413 | 20.5337 | 85% |  | 85% | 541.6051 | 85% | 541.6051
[7 empty] | 65% | 669.8855 | 19.067 | 80% |  | 80% | 1244.275 | 80% | 1244.275
LDC | [6 empty] | 60% | 1104.687 | 17.6003 | 75% |  | 75% | 2682.3072 | 75% | 2682.3072
[7 empty] | 55% | 1631.62 | 16.1336 | 70% |  | 70% | 3956.6592 | 70% | 3956.6592
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 2253.9537 | 14.6669 | 65% |  | 65% | 5578.641 | 65% | 5578.641
100% | 0% | 0 |  |  |  |  | 45% | 2892.3362 | 13.2002 | 60% |  | 60% | 7971.511 | 60% | 7971.511
99% | 0.006767% | 0.2972 |  |  |  |  | 40% | 3473.3593 | 11.7336 | 55% |  | 55% | 8887.7717 | 55% | 8887.7717
98% | 0.0203% | 0.8916 |  |  |  |  | 35% | 3882.8989 | 10.2669 | 50% |  | 50% | 9584.121 | 50% | 9584.121
97% | 0.04737% | 2.0804 |  |  |  |  | 30% | 4127.1961 | 8.8002 | 45% |  | 45% | 8894.964 | 45% | 8894.964
95% | 0.09474% | 4.1608 |  |  |  |  | 25% | 4245.1839 | 7.3335 | 40% |  | 40% | 7243.559 | 40% | 7243.559
90% | 0.2639% | 11.5907 |  |  |  |  | 20% | 4322.1583 | 5.8668 | 35% |  | 35% | 4505.0207 | 35% | 4505.0207
85% | 0.7443% | 32.6918 |  |  |  |  | 15% | 4354.2558 | 4.4001 | 30% |  | 30% | 2329.0107 | 30% | 2329.0107
80% | 1.915% | 84.1072 |  |  |  |  | 10% | 4366.1437 | 2.9334 | 25% |  | 25% | 951.7864 | 25% | 951.7864
75% | 4.601% | 202.095 |  |  |  |  | 5% | 4374.4653 | 1.4667 | 20% |  | 20% | 508.0408 | 20% | 508.0408
70% | 8.837% | 388.1413 |  |  |  |  | 9.992e-14% | 4375.9513 | 2.931e-14 | 15% |  | 15% | 164.77 | 15% | 164.77
65% | 15.25% | 669.8855 | [7 empty] | 10% |  | 10% | 43.5899 | 10% | 43.5899
60% | 25.15% | 1104.687 | [7 empty] | 5% |  | 5% | 18.3078 | 5% | 18.3078
55% | 37.15% | 1631.62 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 1.0897 | 9.992e-14% | 1.0897
50% | 51.32% | 2253.9537 | [7 empty] | Total E@R | 0 | Total E@R | 64772.797 | Total E@R | 64772.797
45% | 65.85% | 2892.3362 | [7 empty] | Total WE@R | 0 | Total WE@R | 25.7107 | Total WE@R | 0
40% | 79.08% | 3473.3593
35% | 88.41% | 3882.8989
30% | 93.97% | 4127.1961
25% | 96.66% | 4245.1839
20% | 98.41% | 4322.1583
15% | 99.14% | 4354.2558
10% | 99.41% | 4366.1437
5% | 99.6% | 4374.4653
9.992e-14% | 99.63% | 4375.9513
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 47.4 |  |  | Year | 2031
SCR (N-1) | 0 |  |  | SCR (N) | 47.4
SCR (N-2) | 0 |  |  | SCR (N-1) | 0
WCR (N) | 48.3 |  |  | SCR (N-2) | 0
WCR (N-1) | 0 |  |  | WCR (N) | 48.3
WCR (N-2) | 0 |  |  | WCR (N-1) | 0
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 0.99
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 2.9555 | 3.3466 | 4.3354 | 4.7992 | 5.2858 | 5.8452 | 6.5254 | 7.2097 | 7.8455 | 8.5179 | 9.2526 | 10.0189 | 10.6735 | 11.5805 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054
Total EUE (MWh) | 78.3708 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Residual Values
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 2.95 | 3.3466 | 4.3354 | 4.7992 | 5.2858 | 5.8452 | 6.5254 | 7.2097 | 7.8455 | 8.5179 | 9.2526 | 10.0189 | 10.6735 | 11.5805 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054
Total EUE (MWh) | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 2.95 | 3.3466 | 4.3354 | 4.7992 | 5.2858 | 5.8452 | 6.5254 | 7.2097 | 7.8455 | 8.5179 | 9.2526 | 10.0189 | 10.6735 | 11.5805 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054
Total EUE (MWh) | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 2.95 | 3.3466 | 4.3354 | 4.7992 | 5.2858 | 5.8452 | 6.5254 | 7.2097 | 7.8455 | 8.5179 | 9.2526 | 10.0189 | 10.6735 | 11.5805 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054
Total EUE (MWh) | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 2.95 | 3.3466 | 4.3354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) | 78.2243 | 88.7414 | 114.9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 2.95 | 3.3466 | 4.3354 | 4.7992 | 5.2858 | 5.8452 | 6.5254 | 7.2097 | 7.8455 | 8.5179 | 9.2526 | 10.0189 | 10.6735 | 11.5805 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054
Total EUE (MWh) | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 2.95 | 3.3466 | 4.3354 | 4.7992 | 5.2858 | 5.8452 | 6.5254 | 7.2097 | 7.8455 | 8.5179 | 9.2526 | 10.0189 | 10.6735 | 11.5805 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054
Total EUE (MWh) | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 2.95 | 3.3466 | 4.3354 | 4.7992 | 5.2858 | 5.8452 | 6.5254 | 7.2097 | 7.8455 | 8.5179 | 9.2526 | 10.0189 | 10.6735 | 11.5805 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054 | 12.3054
Total EUE (MWh) | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009

## Key Model Assumption & Inputs
Select ZSS & Region | LLG | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Low | 90% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1B New PHS ZSS + Three new feeders | 1B New PHS ZSS + Three new feeders
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N |  |  |  | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Added Capacity (MVA) Option 5 N-1 |  |  |  | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | LLG
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 23.5081 | 26.0976 | 30.4575 | 30.4247 | 30.3952 | 30.8677 | 31.5616 | 32.037 | 31.4591 | 31.5166 | 31.792 | 32.8827 | 31.8492 | 31.7885 | 31.7234
Summer POE10 | 10 |  |  | 25.544 | 28.7312 | 33.0834 | 33.0249 | 33.0633 | 33.1822 | 33.5865 | 33.8573 | 34.0794 | 34.1121 | 34.3124 | 34.3834 | 34.3832 | 34.3374 | 34.3276
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 20.5738 | 23.9159 | 28.4398 | 28.8402 | 29.108 | 29.4846 | 30.3426 | 31.0163 | 31.6154 | 31.8255 | 32.0656 | 31.7299 | 31.9069 | 32.7389 | 32.3709
Winter POE10 | 10 |  |  | 22.7705 | 26.1225 | 30.6829 | 31.049 | 31.3064 | 31.5714 | 32.5932 | 33.1905 | 33.8014 | 34.0793 | 34.2253 | 33.7185 | 33.9832 | 34.9987 | 34.5209
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | LLG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | PowerFactor | 0.99

## Load Duration Curves
Station
LLG
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0.02583% | 1.1345 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.04305% | 1.8908 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.04737% | 2.0804 | 0.05166% | 2.269 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.09474% | 4.1608 | 0.09471% | 4.1598 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.2639% | 11.5907 | 0.353% | 15.5047 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 0.7443% | 32.6918 | 0.7147% | 31.3876 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 1.915% | 84.1072 | 1.317% | 57.8591 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 4.601% | 202.095 | 2.764% | 121.3907 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 8.837% | 388.1413 | 6.225% | 273.4128 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 15.25% | 669.8855 | 12.05% | 529.43 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 25.15% | 1104.687 | 20.92% | 918.9392 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 37.15% | 1631.62 | 33.11% | 1454.0417 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 51.32% | 2253.9537 | 47.93% | 2105.2406 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 65.85% | 2892.3362 | 62.8% | 2758.3303 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 79.08% | 3473.3593 | 76.24% | 3348.2666 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 88.41% | 3882.8989 | 86.9% | 3816.434 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 93.97% | 4127.1961 | 92.6% | 4067.1569 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 96.66% | 4245.1839 | 96.47% | 4236.9526 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 98.41% | 4322.1583 | 98.65% | 4332.6282 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.14% | 4354.2558 | 99.31% | 4361.7469 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.41% | 4366.1437 | 99.63% | 4375.7389 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.6% | 4374.4653 | 99.68% | 4378.0079 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.63% | 4375.9513 | 99.71% | 4379.1424 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.006767% | 0.2972 | 0.00861% | 0.37816 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.0203% | 0.8916 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.0406% | 1.7832 | 0.01722% | 0.75633 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.1015% | 4.458 | 0.01722% | 0.75633 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.3451% | 15.1571 | 0.0861% | 3.7816 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 0.9% | 39.5274 | 0.31% | 13.6139 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 2.517% | 110.5579 | 0.8008% | 35.1693 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 5.562% | 244.2972 | 1.834% | 80.549 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 10.11% | 444.0146 | 4.374% | 192.1075 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 17.54% | 770.3386 | 9.179% | 403.1231 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 27.53% | 1209.3009 | 16.83% | 739.3112 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 40.02% | 1757.6322 | 27.43% | 1204.8314 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 54.15% | 2378.4799 | 40.6% | 1783.0446 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 68.39% | 3003.7856 | 53.97% | 2370.3337 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 80.79% | 3548.2533 | 65.21% | 2864.2163 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 89.43% | 3927.7759 | 75.09% | 3297.9707 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 94.17% | 4135.8149 | 81.51% | 3579.7031 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 96.81% | 4252.0195 | 86.44% | 3796.3913 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 98.48% | 4325.4275 | 90.52% | 3975.6411 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.28% | 4360.497 | 93.75% | 4117.4527 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.59% | 4373.8709 | 96.19% | 4224.8514 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.77% | 4381.8952 | 98.14% | 4310.3165 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.78% | 4382.5459 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 1 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 2 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 3 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 48.3 | 48.3 | 48.3 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 5 | 47.4 | 47.4 | 47.4 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8 | 94.8
Capacity Added (MVA) | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 6 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 7 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
SCR N Rating (MVA) - Option 8 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
SCR N-1 Rating (MVA) - Option 5 | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Capacity Added (MVA) | 0 | 0 | 0 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-1 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338
Maximum Demand (MVA) - P10 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551
Maximum Demand (MVA) - P10 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
Option 2 - 1B New PHS ZSS + Three new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 100% | 0 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
99% | 0.2972 | 18.3313 | 21.3091 | 25.3398 | 25.6966 | 25.9353 | 26.2707 | 27.0352 | 27.6355 | 28.1693 | 28.3565 | 28.5704 | 28.2714 | 28.4291 | 29.1704 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 99% | 0.2972 | 20.2885 | 23.2751 | 27.3384 | 27.6647 | 27.894 | 28.1301 | 29.0405 | 29.5727 | 30.117 | 30.3646 | 30.4948 | 30.0432 | 30.279 | 31.1838 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581
98% | 0.8916 | 18.1461 | 21.0938 | 25.0839 | 25.4371 | 25.6733 | 26.0054 | 26.7622 | 27.3564 | 27.8847 | 28.0701 | 28.2819 | 27.9858 | 28.1419 | 28.8757 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 98% | 0.8916 | 20.0836 | 23.04 | 27.0623 | 27.3852 | 27.6122 | 27.8459 | 28.7472 | 29.274 | 29.8128 | 30.0579 | 30.1868 | 29.7397 | 29.9731 | 30.8688 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474
97% | 1.7832 | 17.9609 | 20.8786 | 24.8279 | 25.1775 | 25.4113 | 25.74 | 26.4891 | 27.0772 | 27.6002 | 27.7837 | 27.9933 | 27.7002 | 27.8548 | 28.5811 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 97% | 2.0804 | 19.8787 | 22.8049 | 26.7861 | 27.1058 | 27.3305 | 27.5618 | 28.4539 | 28.9753 | 29.5086 | 29.7512 | 29.8787 | 29.4363 | 29.6673 | 30.5538 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367
95% | 4.458 | 17.5906 | 20.4481 | 24.316 | 24.6584 | 24.8874 | 25.2093 | 25.9429 | 26.5189 | 27.0311 | 27.2108 | 27.4161 | 27.1291 | 27.2804 | 27.9918 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 95% | 4.1608 | 19.4688 | 22.3347 | 26.2339 | 26.5469 | 26.767 | 26.9935 | 27.8672 | 28.3779 | 28.9002 | 29.1378 | 29.2627 | 28.8293 | 29.0556 | 29.9239 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154
90% | 15.1571 | 16.6648 | 19.3719 | 23.0362 | 23.3606 | 23.5775 | 23.8825 | 24.5775 | 25.1232 | 25.6084 | 25.7787 | 25.9731 | 25.7012 | 25.8446 | 26.5185 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 90% | 11.5907 | 18.4441 | 21.1592 | 24.8531 | 25.1497 | 25.3582 | 25.5728 | 26.4005 | 26.8843 | 27.3791 | 27.6042 | 27.7225 | 27.312 | 27.5264 | 28.3489 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619
85% | 39.5274 | 15.739 | 18.2957 | 21.7564 | 22.0628 | 22.2676 | 22.5557 | 23.2121 | 23.7275 | 24.1857 | 24.3465 | 24.5302 | 24.2734 | 24.4088 | 25.0453 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 85% | 32.6918 | 17.4195 | 19.9837 | 23.4724 | 23.7525 | 23.9494 | 24.1521 | 24.9338 | 25.3907 | 25.8581 | 26.0707 | 26.1824 | 25.7947 | 25.9971 | 26.774 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085
80% | 110.5579 | 14.8131 | 17.2195 | 20.4766 | 20.765 | 20.9578 | 21.2289 | 21.8467 | 22.3317 | 22.7631 | 22.9144 | 23.0872 | 22.8455 | 22.973 | 23.572 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 80% | 84.1072 | 16.3948 | 18.8082 | 22.0917 | 22.3553 | 22.5406 | 22.7314 | 23.4671 | 23.8972 | 24.337 | 24.5371 | 24.6422 | 24.2773 | 24.4679 | 25.199 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855
75% | 244.2972 | 13.8873 | 16.1432 | 19.1968 | 19.4671 | 19.6479 | 19.9021 | 20.4812 | 20.936 | 21.3404 | 21.4822 | 21.6443 | 21.4177 | 21.5372 | 22.0988 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 75% | 202.095 | 15.3701 | 17.6327 | 20.7109 | 20.9581 | 21.1318 | 21.3107 | 22.0004 | 22.4036 | 22.8159 | 23.0035 | 23.1021 | 22.76 | 22.9386 | 23.6241 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016
70% | 444.0146 | 12.9615 | 15.067 | 17.9171 | 18.1693 | 18.3381 | 18.5753 | 19.1158 | 19.5403 | 19.9177 | 20.0501 | 20.2013 | 19.9899 | 20.1014 | 20.6255 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 70% | 388.1413 | 14.3454 | 16.4572 | 19.3302 | 19.5609 | 19.723 | 19.89 | 20.5337 | 20.91 | 21.2949 | 21.47 | 21.562 | 21.2427 | 21.4094 | 22.0492 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482
65% | 770.3386 | 12.0357 | 13.9908 | 16.6373 | 16.8715 | 17.0282 | 17.2485 | 17.7504 | 18.1445 | 18.495 | 18.6179 | 18.7584 | 18.562 | 18.6656 | 19.1523 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 65% | 669.8855 | 13.3208 | 15.2817 | 17.9495 | 18.1637 | 18.3142 | 18.4692 | 19.067 | 19.4164 | 19.7738 | 19.9364 | 20.0218 | 19.7253 | 19.8801 | 20.4742 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947
60% | 1209.3009 | 11.1099 | 12.9146 | 15.3575 | 15.5737 | 15.7183 | 15.9217 | 16.385 | 16.7488 | 17.0723 | 17.1858 | 17.3154 | 17.1342 | 17.2297 | 17.679 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 60% | 1104.687 | 12.2961 | 14.1061 | 16.5688 | 16.7665 | 16.9054 | 17.0485 | 17.6003 | 17.9229 | 18.2528 | 18.4028 | 18.4817 | 18.208 | 18.3509 | 18.8993 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413
55% | 1757.6322 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 55% | 1631.62 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
50% | 2378.4799 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 50% | 2253.9537 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
45% | 3003.7856 | 8.3324 | 9.6859 | 11.5181 | 11.6803 | 11.7888 | 11.9412 | 12.2887 | 12.5616 | 12.8042 | 12.8893 | 12.9866 | 12.8506 | 12.9223 | 13.2593 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 45% | 2892.3362 | 9.2221 | 10.5796 | 12.4266 | 12.5749 | 12.6791 | 12.7864 | 13.2002 | 13.4422 | 13.6896 | 13.8021 | 13.8613 | 13.656 | 13.7632 | 14.1745 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981
40% | 3548.2533 | 7.4066 | 8.6097 | 10.2383 | 10.3825 | 10.4789 | 10.6144 | 10.9233 | 11.1659 | 11.3815 | 11.4572 | 11.5436 | 11.4228 | 11.4865 | 11.786 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 40% | 3473.3593 | 8.1974 | 9.4041 | 11.0458 | 11.1776 | 11.2703 | 11.3657 | 11.7336 | 11.9486 | 12.1685 | 12.2685 | 12.3211 | 12.1387 | 12.2339 | 12.5995 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275
35% | 3927.7759 | 6.4808 | 7.5335 | 8.9585 | 9.0847 | 9.169 | 9.2876 | 9.5579 | 9.7701 | 9.9588 | 10.025 | 10.1007 | 9.9949 | 10.0507 | 10.3128 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 35% | 3882.8989 | 7.1727 | 8.2286 | 9.6651 | 9.7804 | 9.8615 | 9.945 | 10.2669 | 10.455 | 10.6474 | 10.735 | 10.781 | 10.6213 | 10.7047 | 11.0246 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741
30% | 4135.8149 | 5.5549 | 6.4573 | 7.6787 | 7.7869 | 7.8592 | 7.9608 | 8.1925 | 8.3744 | 8.5361 | 8.5929 | 8.6577 | 8.5671 | 8.6149 | 8.8395 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 30% | 4127.1961 | 6.148 | 7.0531 | 8.2844 | 8.3832 | 8.4527 | 8.5243 | 8.8002 | 8.9614 | 9.1264 | 9.2014 | 9.2408 | 9.104 | 9.1755 | 9.4496 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206
25% | 4252.0195 | 4.6291 | 5.3811 | 6.3989 | 6.489 | 6.5493 | 6.634 | 6.8271 | 6.9787 | 7.1135 | 7.1607 | 7.2148 | 7.1392 | 7.1791 | 7.3663 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 25% | 4245.1839 | 5.1234 | 5.8776 | 6.9036 | 6.986 | 7.0439 | 7.1036 | 7.3335 | 7.4679 | 7.6053 | 7.6678 | 7.7007 | 7.5867 | 7.6462 | 7.8747 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672
20% | 4325.4275 | 3.7033 | 4.3049 | 5.1192 | 5.1912 | 5.2394 | 5.3072 | 5.4617 | 5.5829 | 5.6908 | 5.7286 | 5.7718 | 5.7114 | 5.7432 | 5.893 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 20% | 4322.1583 | 4.0987 | 4.702 | 5.5229 | 5.5888 | 5.6351 | 5.6828 | 5.8668 | 5.9743 | 6.0843 | 6.1343 | 6.1606 | 6.0693 | 6.117 | 6.2998 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138
15% | 4360.497 | 2.7775 | 3.2286 | 3.8394 | 3.8934 | 3.9296 | 3.9804 | 4.0962 | 4.1872 | 4.2681 | 4.2964 | 4.3289 | 4.2835 | 4.3074 | 4.4198 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 15% | 4354.2558 | 3.074 | 3.5265 | 4.1422 | 4.1916 | 4.2264 | 4.2621 | 4.4001 | 4.4807 | 4.5632 | 4.6007 | 4.6204 | 4.552 | 4.5877 | 4.7248 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603
10% | 4373.8709 | 1.8516 | 2.1524 | 2.5596 | 2.5956 | 2.6197 | 2.6536 | 2.7308 | 2.7915 | 2.8454 | 2.8643 | 2.8859 | 2.8557 | 2.8716 | 2.9465 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 10% | 4366.1437 | 2.0493 | 2.351 | 2.7615 | 2.7944 | 2.8176 | 2.8414 | 2.9334 | 2.9871 | 3.0421 | 3.0671 | 3.0803 | 3.0347 | 3.0585 | 3.1499 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069
5% | 4381.8952 | 0.92582 | 1.0762 | 1.2798 | 1.2978 | 1.3099 | 1.3268 | 1.3654 | 1.3957 | 1.4227 | 1.4321 | 1.443 | 1.4278 | 1.4358 | 1.4733 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 5% | 4374.4653 | 1.0247 | 1.1755 | 1.3807 | 1.3972 | 1.4088 | 1.4207 | 1.4667 | 1.4936 | 1.5211 | 1.5336 | 1.5401 | 1.5173 | 1.5292 | 1.5749 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534
9.992e-14% | 4391.7028 | 1.8502e-14 | 2.1507e-14 | 2.5575e-14 | 2.5935e-14 | 2.6176e-14 | 2.6515e-14 | 2.7286e-14 | 2.7892e-14 | 2.8431e-14 | 2.862e-14 | 2.8836e-14 | 2.8534e-14 | 2.8693e-14 | 2.9441e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 9.992e-14% | 4375.9513 | 2.0477e-14 | 2.3491e-14 | 2.7593e-14 | 2.7922e-14 | 2.8153e-14 | 2.8392e-14 | 2.931e-14 | 2.9848e-14 | 3.0397e-14 | 3.0647e-14 | 3.0778e-14 | 3.0322e-14 | 3.056e-14 | 3.1474e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 100% | 0 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
99% | 0.37816 | 20.9458 | 23.253 | 27.1376 | 27.1084 | 27.0821 | 27.5032 | 28.1214 | 28.545 | 28.0301 | 28.0813 | 28.3267 | 29.2985 | 28.3777 | 28.3236 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 99% | 1.1345 | 22.7597 | 25.5995 | 29.4773 | 29.4252 | 29.4594 | 29.5654 | 29.9256 | 30.1669 | 30.3648 | 30.3939 | 30.5724 | 30.6356 | 30.6355 | 30.5946 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859
98% | 0.37816 | 20.7342 | 23.0181 | 26.8635 | 26.8346 | 26.8085 | 27.2253 | 27.8373 | 28.2567 | 27.7469 | 27.7976 | 28.0405 | 29.0026 | 28.091 | 28.0375 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 98% | 1.8908 | 22.5298 | 25.3409 | 29.1795 | 29.128 | 29.1618 | 29.2667 | 29.6233 | 29.8621 | 30.058 | 30.0869 | 30.2636 | 30.3262 | 30.326 | 30.2856 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277
97% | 0.75633 | 20.5226 | 22.7832 | 26.5894 | 26.5608 | 26.535 | 26.9475 | 27.5532 | 27.9683 | 27.4638 | 27.514 | 27.7544 | 28.7066 | 27.8044 | 27.7514 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 97% | 2.269 | 22.2999 | 25.0823 | 28.8818 | 28.8307 | 28.8642 | 28.9681 | 29.321 | 29.5574 | 29.7513 | 29.7799 | 29.9547 | 30.0167 | 30.0166 | 29.9765 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968
95% | 0.75633 | 20.0995 | 22.3135 | 26.0411 | 26.0131 | 25.9879 | 26.3919 | 26.9851 | 27.3917 | 26.8975 | 26.9467 | 27.1822 | 28.1147 | 27.2311 | 27.1792 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 95% | 4.1598 | 21.8401 | 24.5651 | 28.2863 | 28.2363 | 28.2691 | 28.3708 | 28.7165 | 28.948 | 29.1379 | 29.1659 | 29.3371 | 29.3978 | 29.3977 | 29.3585 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501
90% | 3.7816 | 19.0416 | 21.1391 | 24.6705 | 24.644 | 24.6201 | 25.0029 | 25.5649 | 25.95 | 25.4819 | 25.5284 | 25.7515 | 26.635 | 25.7979 | 25.7487 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 90% | 15.5047 | 20.6906 | 23.2722 | 26.7975 | 26.7502 | 26.7812 | 26.8776 | 27.2051 | 27.4244 | 27.6043 | 27.6308 | 27.7931 | 27.8506 | 27.8504 | 27.8133 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054
85% | 13.6139 | 17.9837 | 19.9647 | 23.2999 | 23.2749 | 23.2523 | 23.6138 | 24.1446 | 24.5083 | 24.0662 | 24.1102 | 24.3209 | 25.1553 | 24.3647 | 24.3182 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 85% | 31.3876 | 19.5412 | 21.9793 | 25.3088 | 25.2641 | 25.2934 | 25.3844 | 25.6937 | 25.9008 | 26.0708 | 26.0958 | 26.249 | 26.3033 | 26.3032 | 26.2681 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606
80% | 35.1693 | 16.9259 | 18.7903 | 21.9294 | 21.9058 | 21.8845 | 22.2248 | 22.7243 | 23.0667 | 22.6505 | 22.6919 | 22.8902 | 23.6756 | 22.9315 | 22.8877 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 80% | 57.8591 | 18.3917 | 20.6864 | 23.82 | 23.7779 | 23.8055 | 23.8912 | 24.1823 | 24.3773 | 24.5372 | 24.5607 | 24.7049 | 24.7561 | 24.7559 | 24.7229 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159
75% | 80.549 | 15.868 | 17.6159 | 20.5588 | 20.5367 | 20.5167 | 20.8357 | 21.3041 | 21.625 | 21.2349 | 21.2737 | 21.4596 | 22.1959 | 21.4982 | 21.4573 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 75% | 121.3907 | 17.2422 | 19.3935 | 22.3313 | 22.2918 | 22.3177 | 22.398 | 22.6709 | 22.8537 | 23.0036 | 23.0257 | 23.1609 | 23.2088 | 23.2087 | 23.1777 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712
70% | 192.1075 | 14.8101 | 16.4415 | 19.1882 | 19.1676 | 19.149 | 19.4467 | 19.8838 | 20.1833 | 19.8192 | 19.8554 | 20.029 | 20.7161 | 20.065 | 20.0268 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 70% | 273.4128 | 16.0927 | 18.1006 | 20.8425 | 20.8057 | 20.8299 | 20.9048 | 21.1595 | 21.3301 | 21.47 | 21.4906 | 21.6168 | 21.6616 | 21.6614 | 21.6325 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264
65% | 403.1231 | 13.7523 | 15.2671 | 17.8176 | 17.7984 | 17.7812 | 18.0576 | 18.4635 | 18.7417 | 18.4036 | 18.4372 | 18.5983 | 19.2364 | 18.6318 | 18.5963 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 65% | 529.43 | 14.9432 | 16.8077 | 19.3538 | 19.3196 | 19.342 | 19.4116 | 19.6481 | 19.8065 | 19.9365 | 19.9556 | 20.0728 | 20.1143 | 20.1142 | 20.0874 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817
60% | 739.3112 | 12.6944 | 14.0927 | 16.447 | 16.4293 | 16.4134 | 16.6686 | 17.0432 | 17.3 | 16.9879 | 17.0189 | 17.1677 | 17.7567 | 17.1986 | 17.1658 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 60% | 918.9392 | 13.7938 | 15.5148 | 17.865 | 17.8334 | 17.8542 | 17.9184 | 18.1367 | 18.2829 | 18.4029 | 18.4205 | 18.5287 | 18.567 | 18.5669 | 18.5422 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369
55% | 1204.8314 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 55% | 1454.0417 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
50% | 1783.0446 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 50% | 2105.2406 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
45% | 2370.3337 | 9.5208 | 10.5695 | 12.3353 | 12.322 | 12.31 | 12.5014 | 12.7824 | 12.975 | 12.7409 | 12.7642 | 12.8758 | 13.3175 | 12.8989 | 12.8744 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 45% | 2758.3303 | 10.3453 | 11.6361 | 13.3988 | 13.3751 | 13.3906 | 13.4388 | 13.6025 | 13.7122 | 13.8022 | 13.8154 | 13.8965 | 13.9253 | 13.9252 | 13.9066 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027
40% | 2864.2163 | 8.4629 | 9.3951 | 10.9647 | 10.9529 | 10.9423 | 11.1124 | 11.3622 | 11.5333 | 11.3253 | 11.346 | 11.4451 | 11.8378 | 11.4657 | 11.4439 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 40% | 3348.2666 | 9.1958 | 10.3432 | 11.91 | 11.889 | 11.9028 | 11.9456 | 12.0911 | 12.1886 | 12.2686 | 12.2804 | 12.3525 | 12.378 | 12.378 | 12.3615 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579
35% | 3297.9707 | 7.4051 | 8.2208 | 9.5941 | 9.5838 | 9.5745 | 9.7233 | 9.9419 | 10.0917 | 9.9096 | 9.9277 | 10.0145 | 10.3581 | 10.0325 | 10.0134 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 35% | 3816.434 | 8.0464 | 9.0503 | 10.4213 | 10.4028 | 10.4149 | 10.4524 | 10.5798 | 10.6651 | 10.735 | 10.7453 | 10.8084 | 10.8308 | 10.8307 | 10.8163 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132
30% | 3579.7031 | 6.3472 | 7.0464 | 8.2235 | 8.2147 | 8.2067 | 8.3343 | 8.5216 | 8.65 | 8.494 | 8.5095 | 8.5838 | 8.8783 | 8.5993 | 8.5829 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 30% | 4067.1569 | 6.8969 | 7.7574 | 8.9325 | 8.9167 | 8.9271 | 8.9592 | 9.0684 | 9.1415 | 9.2014 | 9.2103 | 9.2644 | 9.2835 | 9.2835 | 9.2711 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685
25% | 3796.3913 | 5.2893 | 5.872 | 6.8529 | 6.8456 | 6.8389 | 6.9452 | 7.1014 | 7.2083 | 7.0783 | 7.0912 | 7.1532 | 7.3986 | 7.1661 | 7.1524 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 25% | 4236.9526 | 5.7474 | 6.4645 | 7.4438 | 7.4306 | 7.4392 | 7.466 | 7.557 | 7.6179 | 7.6679 | 7.6752 | 7.7203 | 7.7363 | 7.7362 | 7.7259 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237
20% | 3975.6411 | 4.2315 | 4.6976 | 5.4823 | 5.4764 | 5.4711 | 5.5562 | 5.6811 | 5.7667 | 5.6626 | 5.673 | 5.7226 | 5.9189 | 5.7329 | 5.7219 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 20% | 4332.6282 | 4.5979 | 5.1716 | 5.955 | 5.9445 | 5.9514 | 5.9728 | 6.0456 | 6.0943 | 6.1343 | 6.1402 | 6.1762 | 6.189 | 6.189 | 6.1807 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179
15% | 4117.4527 | 3.1736 | 3.5232 | 4.1118 | 4.1073 | 4.1033 | 4.1671 | 4.2608 | 4.325 | 4.247 | 4.2547 | 4.2919 | 4.4392 | 4.2996 | 4.2915 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 15% | 4361.7469 | 3.4484 | 3.8787 | 4.4663 | 4.4584 | 4.4635 | 4.4796 | 4.5342 | 4.5707 | 4.6007 | 4.6051 | 4.6322 | 4.6418 | 4.6417 | 4.6355 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342
10% | 4224.8514 | 2.1157 | 2.3488 | 2.7412 | 2.7382 | 2.7356 | 2.7781 | 2.8405 | 2.8833 | 2.8313 | 2.8365 | 2.8613 | 2.9594 | 2.8664 | 2.861 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 10% | 4375.7389 | 2.299 | 2.5858 | 2.9775 | 2.9722 | 2.9757 | 2.9864 | 3.0228 | 3.0472 | 3.0671 | 3.0701 | 3.0881 | 3.0945 | 3.0945 | 3.0904 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895
5% | 4310.3165 | 1.0579 | 1.1744 | 1.3706 | 1.3691 | 1.3678 | 1.389 | 1.4203 | 1.4417 | 1.4157 | 1.4182 | 1.4306 | 1.4797 | 1.4332 | 1.4305 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 5% | 4378.0079 | 1.1495 | 1.2929 | 1.4888 | 1.4861 | 1.4878 | 1.4932 | 1.5114 | 1.5236 | 1.5336 | 1.535 | 1.5441 | 1.5473 | 1.5472 | 1.5452 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447
9.992e-14% | 4382.5459 | 2.114e-14 | 2.3469e-14 | 2.739e-14 | 2.736e-14 | 2.7334e-14 | 2.7759e-14 | 2.8383e-14 | 2.881e-14 | 2.8291e-14 | 2.8342e-14 | 2.859e-14 | 2.9571e-14 | 2.8641e-14 | 2.8587e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 9.992e-14% | 4379.1424 | 2.2971e-14 | 2.5837e-14 | 2.9751e-14 | 2.9699e-14 | 2.9733e-14 | 2.984e-14 | 3.0204e-14 | 3.0447e-14 | 3.0647e-14 | 3.0676e-14 | 3.0857e-14 | 3.092e-14 | 3.092e-14 | 3.0879e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 100% | 0 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
99% | 0.2972 | 18.3313 | 21.3091 | 25.3398 | 25.6966 | 25.9353 | 26.2707 | 27.0352 | 27.6355 | 28.1693 | 28.3565 | 28.5704 | 28.2714 | 28.4291 | 29.1704 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 99% | 0.2972 | 20.2885 | 23.2751 | 27.3384 | 27.6647 | 27.894 | 28.1301 | 29.0405 | 29.5727 | 30.117 | 30.3646 | 30.4948 | 30.0432 | 30.279 | 31.1838 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581
98% | 0.8916 | 18.1461 | 21.0938 | 25.0839 | 25.4371 | 25.6733 | 26.0054 | 26.7622 | 27.3564 | 27.8847 | 28.0701 | 28.2819 | 27.9858 | 28.1419 | 28.8757 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 98% | 0.8916 | 20.0836 | 23.04 | 27.0623 | 27.3852 | 27.6122 | 27.8459 | 28.7472 | 29.274 | 29.8128 | 30.0579 | 30.1868 | 29.7397 | 29.9731 | 30.8688 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474
97% | 1.7832 | 17.9609 | 20.8786 | 24.8279 | 25.1775 | 25.4113 | 25.74 | 26.4891 | 27.0772 | 27.6002 | 27.7837 | 27.9933 | 27.7002 | 27.8548 | 28.5811 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 97% | 2.0804 | 19.8787 | 22.8049 | 26.7861 | 27.1058 | 27.3305 | 27.5618 | 28.4539 | 28.9753 | 29.5086 | 29.7512 | 29.8787 | 29.4363 | 29.6673 | 30.5538 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367
95% | 4.458 | 17.5906 | 20.4481 | 24.316 | 24.6584 | 24.8874 | 25.2093 | 25.9429 | 26.5189 | 27.0311 | 27.2108 | 27.4161 | 27.1291 | 27.2804 | 27.9918 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 95% | 4.1608 | 19.4688 | 22.3347 | 26.2339 | 26.5469 | 26.767 | 26.9935 | 27.8672 | 28.3779 | 28.9002 | 29.1378 | 29.2627 | 28.8293 | 29.0556 | 29.9239 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154
90% | 15.1571 | 16.6648 | 19.3719 | 23.0362 | 23.3606 | 23.5775 | 23.8825 | 24.5775 | 25.1232 | 25.6084 | 25.7787 | 25.9731 | 25.7012 | 25.8446 | 26.5185 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 90% | 11.5907 | 18.4441 | 21.1592 | 24.8531 | 25.1497 | 25.3582 | 25.5728 | 26.4005 | 26.8843 | 27.3791 | 27.6042 | 27.7225 | 27.312 | 27.5264 | 28.3489 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619
85% | 39.5274 | 15.739 | 18.2957 | 21.7564 | 22.0628 | 22.2676 | 22.5557 | 23.2121 | 23.7275 | 24.1857 | 24.3465 | 24.5302 | 24.2734 | 24.4088 | 25.0453 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 85% | 32.6918 | 17.4195 | 19.9837 | 23.4724 | 23.7525 | 23.9494 | 24.1521 | 24.9338 | 25.3907 | 25.8581 | 26.0707 | 26.1824 | 25.7947 | 25.9971 | 26.774 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085
80% | 110.5579 | 14.8131 | 17.2195 | 20.4766 | 20.765 | 20.9578 | 21.2289 | 21.8467 | 22.3317 | 22.7631 | 22.9144 | 23.0872 | 22.8455 | 22.973 | 23.572 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 80% | 84.1072 | 16.3948 | 18.8082 | 22.0917 | 22.3553 | 22.5406 | 22.7314 | 23.4671 | 23.8972 | 24.337 | 24.5371 | 24.6422 | 24.2773 | 24.4679 | 25.199 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855
75% | 244.2972 | 13.8873 | 16.1432 | 19.1968 | 19.4671 | 19.6479 | 19.9021 | 20.4812 | 20.936 | 21.3404 | 21.4822 | 21.6443 | 21.4177 | 21.5372 | 22.0988 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 75% | 202.095 | 15.3701 | 17.6327 | 20.7109 | 20.9581 | 21.1318 | 21.3107 | 22.0004 | 22.4036 | 22.8159 | 23.0035 | 23.1021 | 22.76 | 22.9386 | 23.6241 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016
70% | 444.0146 | 12.9615 | 15.067 | 17.9171 | 18.1693 | 18.3381 | 18.5753 | 19.1158 | 19.5403 | 19.9177 | 20.0501 | 20.2013 | 19.9899 | 20.1014 | 20.6255 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 70% | 388.1413 | 14.3454 | 16.4572 | 19.3302 | 19.5609 | 19.723 | 19.89 | 20.5337 | 20.91 | 21.2949 | 21.47 | 21.562 | 21.2427 | 21.4094 | 22.0492 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482
65% | 770.3386 | 12.0357 | 13.9908 | 16.6373 | 16.8715 | 17.0282 | 17.2485 | 17.7504 | 18.1445 | 18.495 | 18.6179 | 18.7584 | 18.562 | 18.6656 | 19.1523 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 65% | 669.8855 | 13.3208 | 15.2817 | 17.9495 | 18.1637 | 18.3142 | 18.4692 | 19.067 | 19.4164 | 19.7738 | 19.9364 | 20.0218 | 19.7253 | 19.8801 | 20.4742 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947
60% | 1209.3009 | 11.1099 | 12.9146 | 15.3575 | 15.5737 | 15.7183 | 15.9217 | 16.385 | 16.7488 | 17.0723 | 17.1858 | 17.3154 | 17.1342 | 17.2297 | 17.679 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 60% | 1104.687 | 12.2961 | 14.1061 | 16.5688 | 16.7665 | 16.9054 | 17.0485 | 17.6003 | 17.9229 | 18.2528 | 18.4028 | 18.4817 | 18.208 | 18.3509 | 18.8993 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413
55% | 1757.6322 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 55% | 1631.62 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
50% | 2378.4799 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 50% | 2253.9537 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
45% | 3003.7856 | 8.3324 | 9.6859 | 11.5181 | 11.6803 | 11.7888 | 11.9412 | 12.2887 | 12.5616 | 12.8042 | 12.8893 | 12.9866 | 12.8506 | 12.9223 | 13.2593 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 45% | 2892.3362 | 9.2221 | 10.5796 | 12.4266 | 12.5749 | 12.6791 | 12.7864 | 13.2002 | 13.4422 | 13.6896 | 13.8021 | 13.8613 | 13.656 | 13.7632 | 14.1745 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981
40% | 3548.2533 | 7.4066 | 8.6097 | 10.2383 | 10.3825 | 10.4789 | 10.6144 | 10.9233 | 11.1659 | 11.3815 | 11.4572 | 11.5436 | 11.4228 | 11.4865 | 11.786 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 40% | 3473.3593 | 8.1974 | 9.4041 | 11.0458 | 11.1776 | 11.2703 | 11.3657 | 11.7336 | 11.9486 | 12.1685 | 12.2685 | 12.3211 | 12.1387 | 12.2339 | 12.5995 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275
35% | 3927.7759 | 6.4808 | 7.5335 | 8.9585 | 9.0847 | 9.169 | 9.2876 | 9.5579 | 9.7701 | 9.9588 | 10.025 | 10.1007 | 9.9949 | 10.0507 | 10.3128 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 35% | 3882.8989 | 7.1727 | 8.2286 | 9.6651 | 9.7804 | 9.8615 | 9.945 | 10.2669 | 10.455 | 10.6474 | 10.735 | 10.781 | 10.6213 | 10.7047 | 11.0246 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741
30% | 4135.8149 | 5.5549 | 6.4573 | 7.6787 | 7.7869 | 7.8592 | 7.9608 | 8.1925 | 8.3744 | 8.5361 | 8.5929 | 8.6577 | 8.5671 | 8.6149 | 8.8395 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 30% | 4127.1961 | 6.148 | 7.0531 | 8.2844 | 8.3832 | 8.4527 | 8.5243 | 8.8002 | 8.9614 | 9.1264 | 9.2014 | 9.2408 | 9.104 | 9.1755 | 9.4496 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206
25% | 4252.0195 | 4.6291 | 5.3811 | 6.3989 | 6.489 | 6.5493 | 6.634 | 6.8271 | 6.9787 | 7.1135 | 7.1607 | 7.2148 | 7.1392 | 7.1791 | 7.3663 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 25% | 4245.1839 | 5.1234 | 5.8776 | 6.9036 | 6.986 | 7.0439 | 7.1036 | 7.3335 | 7.4679 | 7.6053 | 7.6678 | 7.7007 | 7.5867 | 7.6462 | 7.8747 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672
20% | 4325.4275 | 3.7033 | 4.3049 | 5.1192 | 5.1912 | 5.2394 | 5.3072 | 5.4617 | 5.5829 | 5.6908 | 5.7286 | 5.7718 | 5.7114 | 5.7432 | 5.893 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 20% | 4322.1583 | 4.0987 | 4.702 | 5.5229 | 5.5888 | 5.6351 | 5.6828 | 5.8668 | 5.9743 | 6.0843 | 6.1343 | 6.1606 | 6.0693 | 6.117 | 6.2998 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138
15% | 4360.497 | 2.7775 | 3.2286 | 3.8394 | 3.8934 | 3.9296 | 3.9804 | 4.0962 | 4.1872 | 4.2681 | 4.2964 | 4.3289 | 4.2835 | 4.3074 | 4.4198 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 15% | 4354.2558 | 3.074 | 3.5265 | 4.1422 | 4.1916 | 4.2264 | 4.2621 | 4.4001 | 4.4807 | 4.5632 | 4.6007 | 4.6204 | 4.552 | 4.5877 | 4.7248 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603
10% | 4373.8709 | 1.8516 | 2.1524 | 2.5596 | 2.5956 | 2.6197 | 2.6536 | 2.7308 | 2.7915 | 2.8454 | 2.8643 | 2.8859 | 2.8557 | 2.8716 | 2.9465 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 10% | 4366.1437 | 2.0493 | 2.351 | 2.7615 | 2.7944 | 2.8176 | 2.8414 | 2.9334 | 2.9871 | 3.0421 | 3.0671 | 3.0803 | 3.0347 | 3.0585 | 3.1499 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069
5% | 4381.8952 | 0.92582 | 1.0762 | 1.2798 | 1.2978 | 1.3099 | 1.3268 | 1.3654 | 1.3957 | 1.4227 | 1.4321 | 1.443 | 1.4278 | 1.4358 | 1.4733 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 5% | 4374.4653 | 1.0247 | 1.1755 | 1.3807 | 1.3972 | 1.4088 | 1.4207 | 1.4667 | 1.4936 | 1.5211 | 1.5336 | 1.5401 | 1.5173 | 1.5292 | 1.5749 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534
9.992e-14% | 4391.7028 | 1.8502e-14 | 2.1507e-14 | 2.5575e-14 | 2.5935e-14 | 2.6176e-14 | 2.6515e-14 | 2.7286e-14 | 2.7892e-14 | 2.8431e-14 | 2.862e-14 | 2.8836e-14 | 2.8534e-14 | 2.8693e-14 | 2.9441e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 9.992e-14% | 4375.9513 | 2.0477e-14 | 2.3491e-14 | 2.7593e-14 | 2.7922e-14 | 2.8153e-14 | 2.8392e-14 | 2.931e-14 | 2.9848e-14 | 3.0397e-14 | 3.0647e-14 | 3.0778e-14 | 3.0322e-14 | 3.056e-14 | 3.1474e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 100% | 0 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
99% | 0.37816 | 20.9458 | 23.253 | 27.1376 | 27.1084 | 27.0821 | 27.5032 | 28.1214 | 28.545 | 28.0301 | 28.0813 | 28.3267 | 29.2985 | 28.3777 | 28.3236 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 99% | 1.1345 | 22.7597 | 25.5995 | 29.4773 | 29.4252 | 29.4594 | 29.5654 | 29.9256 | 30.1669 | 30.3648 | 30.3939 | 30.5724 | 30.6356 | 30.6355 | 30.5946 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859
98% | 0.37816 | 20.7342 | 23.0181 | 26.8635 | 26.8346 | 26.8085 | 27.2253 | 27.8373 | 28.2567 | 27.7469 | 27.7976 | 28.0405 | 29.0026 | 28.091 | 28.0375 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 98% | 1.8908 | 22.5298 | 25.3409 | 29.1795 | 29.128 | 29.1618 | 29.2667 | 29.6233 | 29.8621 | 30.058 | 30.0869 | 30.2636 | 30.3262 | 30.326 | 30.2856 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277
97% | 0.75633 | 20.5226 | 22.7832 | 26.5894 | 26.5608 | 26.535 | 26.9475 | 27.5532 | 27.9683 | 27.4638 | 27.514 | 27.7544 | 28.7066 | 27.8044 | 27.7514 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 97% | 2.269 | 22.2999 | 25.0823 | 28.8818 | 28.8307 | 28.8642 | 28.9681 | 29.321 | 29.5574 | 29.7513 | 29.7799 | 29.9547 | 30.0167 | 30.0166 | 29.9765 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968
95% | 0.75633 | 20.0995 | 22.3135 | 26.0411 | 26.0131 | 25.9879 | 26.3919 | 26.9851 | 27.3917 | 26.8975 | 26.9467 | 27.1822 | 28.1147 | 27.2311 | 27.1792 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 95% | 4.1598 | 21.8401 | 24.5651 | 28.2863 | 28.2363 | 28.2691 | 28.3708 | 28.7165 | 28.948 | 29.1379 | 29.1659 | 29.3371 | 29.3978 | 29.3977 | 29.3585 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501
90% | 3.7816 | 19.0416 | 21.1391 | 24.6705 | 24.644 | 24.6201 | 25.0029 | 25.5649 | 25.95 | 25.4819 | 25.5284 | 25.7515 | 26.635 | 25.7979 | 25.7487 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 90% | 15.5047 | 20.6906 | 23.2722 | 26.7975 | 26.7502 | 26.7812 | 26.8776 | 27.2051 | 27.4244 | 27.6043 | 27.6308 | 27.7931 | 27.8506 | 27.8504 | 27.8133 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054
85% | 13.6139 | 17.9837 | 19.9647 | 23.2999 | 23.2749 | 23.2523 | 23.6138 | 24.1446 | 24.5083 | 24.0662 | 24.1102 | 24.3209 | 25.1553 | 24.3647 | 24.3182 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 85% | 31.3876 | 19.5412 | 21.9793 | 25.3088 | 25.2641 | 25.2934 | 25.3844 | 25.6937 | 25.9008 | 26.0708 | 26.0958 | 26.249 | 26.3033 | 26.3032 | 26.2681 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606
80% | 35.1693 | 16.9259 | 18.7903 | 21.9294 | 21.9058 | 21.8845 | 22.2248 | 22.7243 | 23.0667 | 22.6505 | 22.6919 | 22.8902 | 23.6756 | 22.9315 | 22.8877 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 80% | 57.8591 | 18.3917 | 20.6864 | 23.82 | 23.7779 | 23.8055 | 23.8912 | 24.1823 | 24.3773 | 24.5372 | 24.5607 | 24.7049 | 24.7561 | 24.7559 | 24.7229 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159
75% | 80.549 | 15.868 | 17.6159 | 20.5588 | 20.5367 | 20.5167 | 20.8357 | 21.3041 | 21.625 | 21.2349 | 21.2737 | 21.4596 | 22.1959 | 21.4982 | 21.4573 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 75% | 121.3907 | 17.2422 | 19.3935 | 22.3313 | 22.2918 | 22.3177 | 22.398 | 22.6709 | 22.8537 | 23.0036 | 23.0257 | 23.1609 | 23.2088 | 23.2087 | 23.1777 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712
70% | 192.1075 | 14.8101 | 16.4415 | 19.1882 | 19.1676 | 19.149 | 19.4467 | 19.8838 | 20.1833 | 19.8192 | 19.8554 | 20.029 | 20.7161 | 20.065 | 20.0268 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 70% | 273.4128 | 16.0927 | 18.1006 | 20.8425 | 20.8057 | 20.8299 | 20.9048 | 21.1595 | 21.3301 | 21.47 | 21.4906 | 21.6168 | 21.6616 | 21.6614 | 21.6325 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264
65% | 403.1231 | 13.7523 | 15.2671 | 17.8176 | 17.7984 | 17.7812 | 18.0576 | 18.4635 | 18.7417 | 18.4036 | 18.4372 | 18.5983 | 19.2364 | 18.6318 | 18.5963 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 65% | 529.43 | 14.9432 | 16.8077 | 19.3538 | 19.3196 | 19.342 | 19.4116 | 19.6481 | 19.8065 | 19.9365 | 19.9556 | 20.0728 | 20.1143 | 20.1142 | 20.0874 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817
60% | 739.3112 | 12.6944 | 14.0927 | 16.447 | 16.4293 | 16.4134 | 16.6686 | 17.0432 | 17.3 | 16.9879 | 17.0189 | 17.1677 | 17.7567 | 17.1986 | 17.1658 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 60% | 918.9392 | 13.7938 | 15.5148 | 17.865 | 17.8334 | 17.8542 | 17.9184 | 18.1367 | 18.2829 | 18.4029 | 18.4205 | 18.5287 | 18.567 | 18.5669 | 18.5422 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369
55% | 1204.8314 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 55% | 1454.0417 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
50% | 1783.0446 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 50% | 2105.2406 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
45% | 2370.3337 | 9.5208 | 10.5695 | 12.3353 | 12.322 | 12.31 | 12.5014 | 12.7824 | 12.975 | 12.7409 | 12.7642 | 12.8758 | 13.3175 | 12.8989 | 12.8744 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 45% | 2758.3303 | 10.3453 | 11.6361 | 13.3988 | 13.3751 | 13.3906 | 13.4388 | 13.6025 | 13.7122 | 13.8022 | 13.8154 | 13.8965 | 13.9253 | 13.9252 | 13.9066 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027
40% | 2864.2163 | 8.4629 | 9.3951 | 10.9647 | 10.9529 | 10.9423 | 11.1124 | 11.3622 | 11.5333 | 11.3253 | 11.346 | 11.4451 | 11.8378 | 11.4657 | 11.4439 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 40% | 3348.2666 | 9.1958 | 10.3432 | 11.91 | 11.889 | 11.9028 | 11.9456 | 12.0911 | 12.1886 | 12.2686 | 12.2804 | 12.3525 | 12.378 | 12.378 | 12.3615 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579
35% | 3297.9707 | 7.4051 | 8.2208 | 9.5941 | 9.5838 | 9.5745 | 9.7233 | 9.9419 | 10.0917 | 9.9096 | 9.9277 | 10.0145 | 10.3581 | 10.0325 | 10.0134 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 35% | 3816.434 | 8.0464 | 9.0503 | 10.4213 | 10.4028 | 10.4149 | 10.4524 | 10.5798 | 10.6651 | 10.735 | 10.7453 | 10.8084 | 10.8308 | 10.8307 | 10.8163 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132
30% | 3579.7031 | 6.3472 | 7.0464 | 8.2235 | 8.2147 | 8.2067 | 8.3343 | 8.5216 | 8.65 | 8.494 | 8.5095 | 8.5838 | 8.8783 | 8.5993 | 8.5829 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 30% | 4067.1569 | 6.8969 | 7.7574 | 8.9325 | 8.9167 | 8.9271 | 8.9592 | 9.0684 | 9.1415 | 9.2014 | 9.2103 | 9.2644 | 9.2835 | 9.2835 | 9.2711 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685
25% | 3796.3913 | 5.2893 | 5.872 | 6.8529 | 6.8456 | 6.8389 | 6.9452 | 7.1014 | 7.2083 | 7.0783 | 7.0912 | 7.1532 | 7.3986 | 7.1661 | 7.1524 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 25% | 4236.9526 | 5.7474 | 6.4645 | 7.4438 | 7.4306 | 7.4392 | 7.466 | 7.557 | 7.6179 | 7.6679 | 7.6752 | 7.7203 | 7.7363 | 7.7362 | 7.7259 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237
20% | 3975.6411 | 4.2315 | 4.6976 | 5.4823 | 5.4764 | 5.4711 | 5.5562 | 5.6811 | 5.7667 | 5.6626 | 5.673 | 5.7226 | 5.9189 | 5.7329 | 5.7219 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 20% | 4332.6282 | 4.5979 | 5.1716 | 5.955 | 5.9445 | 5.9514 | 5.9728 | 6.0456 | 6.0943 | 6.1343 | 6.1402 | 6.1762 | 6.189 | 6.189 | 6.1807 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179
15% | 4117.4527 | 3.1736 | 3.5232 | 4.1118 | 4.1073 | 4.1033 | 4.1671 | 4.2608 | 4.325 | 4.247 | 4.2547 | 4.2919 | 4.4392 | 4.2996 | 4.2915 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 15% | 4361.7469 | 3.4484 | 3.8787 | 4.4663 | 4.4584 | 4.4635 | 4.4796 | 4.5342 | 4.5707 | 4.6007 | 4.6051 | 4.6322 | 4.6418 | 4.6417 | 4.6355 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342
10% | 4224.8514 | 2.1157 | 2.3488 | 2.7412 | 2.7382 | 2.7356 | 2.7781 | 2.8405 | 2.8833 | 2.8313 | 2.8365 | 2.8613 | 2.9594 | 2.8664 | 2.861 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 10% | 4375.7389 | 2.299 | 2.5858 | 2.9775 | 2.9722 | 2.9757 | 2.9864 | 3.0228 | 3.0472 | 3.0671 | 3.0701 | 3.0881 | 3.0945 | 3.0945 | 3.0904 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895
5% | 4310.3165 | 1.0579 | 1.1744 | 1.3706 | 1.3691 | 1.3678 | 1.389 | 1.4203 | 1.4417 | 1.4157 | 1.4182 | 1.4306 | 1.4797 | 1.4332 | 1.4305 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 5% | 4378.0079 | 1.1495 | 1.2929 | 1.4888 | 1.4861 | 1.4878 | 1.4932 | 1.5114 | 1.5236 | 1.5336 | 1.535 | 1.5441 | 1.5473 | 1.5472 | 1.5452 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447
9.992e-14% | 4382.5459 | 2.114e-14 | 2.3469e-14 | 2.739e-14 | 2.736e-14 | 2.7334e-14 | 2.7759e-14 | 2.8383e-14 | 2.881e-14 | 2.8291e-14 | 2.8342e-14 | 2.859e-14 | 2.9571e-14 | 2.8641e-14 | 2.8587e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 9.992e-14% | 4379.1424 | 2.2971e-14 | 2.5837e-14 | 2.9751e-14 | 2.9699e-14 | 2.9733e-14 | 2.984e-14 | 3.0204e-14 | 3.0447e-14 | 3.0647e-14 | 3.0676e-14 | 3.0857e-14 | 3.092e-14 | 3.092e-14 | 3.0879e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 100% | 0 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
99% | 0.2972 | 18.3313 | 21.3091 | 25.3398 | 25.6966 | 25.9353 | 26.2707 | 27.0352 | 27.6355 | 28.1693 | 28.3565 | 28.5704 | 28.2714 | 28.4291 | 29.1704 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 99% | 0.2972 | 20.2885 | 23.2751 | 27.3384 | 27.6647 | 27.894 | 28.1301 | 29.0405 | 29.5727 | 30.117 | 30.3646 | 30.4948 | 30.0432 | 30.279 | 31.1838 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581
98% | 0.8916 | 18.1461 | 21.0938 | 25.0839 | 25.4371 | 25.6733 | 26.0054 | 26.7622 | 27.3564 | 27.8847 | 28.0701 | 28.2819 | 27.9858 | 28.1419 | 28.8757 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 98% | 0.8916 | 20.0836 | 23.04 | 27.0623 | 27.3852 | 27.6122 | 27.8459 | 28.7472 | 29.274 | 29.8128 | 30.0579 | 30.1868 | 29.7397 | 29.9731 | 30.8688 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474
97% | 1.7832 | 17.9609 | 20.8786 | 24.8279 | 25.1775 | 25.4113 | 25.74 | 26.4891 | 27.0772 | 27.6002 | 27.7837 | 27.9933 | 27.7002 | 27.8548 | 28.5811 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 97% | 2.0804 | 19.8787 | 22.8049 | 26.7861 | 27.1058 | 27.3305 | 27.5618 | 28.4539 | 28.9753 | 29.5086 | 29.7512 | 29.8787 | 29.4363 | 29.6673 | 30.5538 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367
95% | 4.458 | 17.5906 | 20.4481 | 24.316 | 24.6584 | 24.8874 | 25.2093 | 25.9429 | 26.5189 | 27.0311 | 27.2108 | 27.4161 | 27.1291 | 27.2804 | 27.9918 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 95% | 4.1608 | 19.4688 | 22.3347 | 26.2339 | 26.5469 | 26.767 | 26.9935 | 27.8672 | 28.3779 | 28.9002 | 29.1378 | 29.2627 | 28.8293 | 29.0556 | 29.9239 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154
90% | 15.1571 | 16.6648 | 19.3719 | 23.0362 | 23.3606 | 23.5775 | 23.8825 | 24.5775 | 25.1232 | 25.6084 | 25.7787 | 25.9731 | 25.7012 | 25.8446 | 26.5185 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 90% | 11.5907 | 18.4441 | 21.1592 | 24.8531 | 25.1497 | 25.3582 | 25.5728 | 26.4005 | 26.8843 | 27.3791 | 27.6042 | 27.7225 | 27.312 | 27.5264 | 28.3489 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619
85% | 39.5274 | 15.739 | 18.2957 | 21.7564 | 22.0628 | 22.2676 | 22.5557 | 23.2121 | 23.7275 | 24.1857 | 24.3465 | 24.5302 | 24.2734 | 24.4088 | 25.0453 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 85% | 32.6918 | 17.4195 | 19.9837 | 23.4724 | 23.7525 | 23.9494 | 24.1521 | 24.9338 | 25.3907 | 25.8581 | 26.0707 | 26.1824 | 25.7947 | 25.9971 | 26.774 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085
80% | 110.5579 | 14.8131 | 17.2195 | 20.4766 | 20.765 | 20.9578 | 21.2289 | 21.8467 | 22.3317 | 22.7631 | 22.9144 | 23.0872 | 22.8455 | 22.973 | 23.572 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 80% | 84.1072 | 16.3948 | 18.8082 | 22.0917 | 22.3553 | 22.5406 | 22.7314 | 23.4671 | 23.8972 | 24.337 | 24.5371 | 24.6422 | 24.2773 | 24.4679 | 25.199 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855
75% | 244.2972 | 13.8873 | 16.1432 | 19.1968 | 19.4671 | 19.6479 | 19.9021 | 20.4812 | 20.936 | 21.3404 | 21.4822 | 21.6443 | 21.4177 | 21.5372 | 22.0988 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 75% | 202.095 | 15.3701 | 17.6327 | 20.7109 | 20.9581 | 21.1318 | 21.3107 | 22.0004 | 22.4036 | 22.8159 | 23.0035 | 23.1021 | 22.76 | 22.9386 | 23.6241 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016
70% | 444.0146 | 12.9615 | 15.067 | 17.9171 | 18.1693 | 18.3381 | 18.5753 | 19.1158 | 19.5403 | 19.9177 | 20.0501 | 20.2013 | 19.9899 | 20.1014 | 20.6255 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 70% | 388.1413 | 14.3454 | 16.4572 | 19.3302 | 19.5609 | 19.723 | 19.89 | 20.5337 | 20.91 | 21.2949 | 21.47 | 21.562 | 21.2427 | 21.4094 | 22.0492 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482
65% | 770.3386 | 12.0357 | 13.9908 | 16.6373 | 16.8715 | 17.0282 | 17.2485 | 17.7504 | 18.1445 | 18.495 | 18.6179 | 18.7584 | 18.562 | 18.6656 | 19.1523 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 65% | 669.8855 | 13.3208 | 15.2817 | 17.9495 | 18.1637 | 18.3142 | 18.4692 | 19.067 | 19.4164 | 19.7738 | 19.9364 | 20.0218 | 19.7253 | 19.8801 | 20.4742 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947
60% | 1209.3009 | 11.1099 | 12.9146 | 15.3575 | 15.5737 | 15.7183 | 15.9217 | 16.385 | 16.7488 | 17.0723 | 17.1858 | 17.3154 | 17.1342 | 17.2297 | 17.679 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 60% | 1104.687 | 12.2961 | 14.1061 | 16.5688 | 16.7665 | 16.9054 | 17.0485 | 17.6003 | 17.9229 | 18.2528 | 18.4028 | 18.4817 | 18.208 | 18.3509 | 18.8993 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413
55% | 1757.6322 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 55% | 1631.62 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
50% | 2378.4799 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 50% | 2253.9537 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
45% | 3003.7856 | 8.3324 | 9.6859 | 11.5181 | 11.6803 | 11.7888 | 11.9412 | 12.2887 | 12.5616 | 12.8042 | 12.8893 | 12.9866 | 12.8506 | 12.9223 | 13.2593 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 45% | 2892.3362 | 9.2221 | 10.5796 | 12.4266 | 12.5749 | 12.6791 | 12.7864 | 13.2002 | 13.4422 | 13.6896 | 13.8021 | 13.8613 | 13.656 | 13.7632 | 14.1745 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981
40% | 3548.2533 | 7.4066 | 8.6097 | 10.2383 | 10.3825 | 10.4789 | 10.6144 | 10.9233 | 11.1659 | 11.3815 | 11.4572 | 11.5436 | 11.4228 | 11.4865 | 11.786 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 40% | 3473.3593 | 8.1974 | 9.4041 | 11.0458 | 11.1776 | 11.2703 | 11.3657 | 11.7336 | 11.9486 | 12.1685 | 12.2685 | 12.3211 | 12.1387 | 12.2339 | 12.5995 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275
35% | 3927.7759 | 6.4808 | 7.5335 | 8.9585 | 9.0847 | 9.169 | 9.2876 | 9.5579 | 9.7701 | 9.9588 | 10.025 | 10.1007 | 9.9949 | 10.0507 | 10.3128 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 35% | 3882.8989 | 7.1727 | 8.2286 | 9.6651 | 9.7804 | 9.8615 | 9.945 | 10.2669 | 10.455 | 10.6474 | 10.735 | 10.781 | 10.6213 | 10.7047 | 11.0246 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741
30% | 4135.8149 | 5.5549 | 6.4573 | 7.6787 | 7.7869 | 7.8592 | 7.9608 | 8.1925 | 8.3744 | 8.5361 | 8.5929 | 8.6577 | 8.5671 | 8.6149 | 8.8395 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 30% | 4127.1961 | 6.148 | 7.0531 | 8.2844 | 8.3832 | 8.4527 | 8.5243 | 8.8002 | 8.9614 | 9.1264 | 9.2014 | 9.2408 | 9.104 | 9.1755 | 9.4496 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206
25% | 4252.0195 | 4.6291 | 5.3811 | 6.3989 | 6.489 | 6.5493 | 6.634 | 6.8271 | 6.9787 | 7.1135 | 7.1607 | 7.2148 | 7.1392 | 7.1791 | 7.3663 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 25% | 4245.1839 | 5.1234 | 5.8776 | 6.9036 | 6.986 | 7.0439 | 7.1036 | 7.3335 | 7.4679 | 7.6053 | 7.6678 | 7.7007 | 7.5867 | 7.6462 | 7.8747 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672
20% | 4325.4275 | 3.7033 | 4.3049 | 5.1192 | 5.1912 | 5.2394 | 5.3072 | 5.4617 | 5.5829 | 5.6908 | 5.7286 | 5.7718 | 5.7114 | 5.7432 | 5.893 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 20% | 4322.1583 | 4.0987 | 4.702 | 5.5229 | 5.5888 | 5.6351 | 5.6828 | 5.8668 | 5.9743 | 6.0843 | 6.1343 | 6.1606 | 6.0693 | 6.117 | 6.2998 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138
15% | 4360.497 | 2.7775 | 3.2286 | 3.8394 | 3.8934 | 3.9296 | 3.9804 | 4.0962 | 4.1872 | 4.2681 | 4.2964 | 4.3289 | 4.2835 | 4.3074 | 4.4198 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 15% | 4354.2558 | 3.074 | 3.5265 | 4.1422 | 4.1916 | 4.2264 | 4.2621 | 4.4001 | 4.4807 | 4.5632 | 4.6007 | 4.6204 | 4.552 | 4.5877 | 4.7248 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603
10% | 4373.8709 | 1.8516 | 2.1524 | 2.5596 | 2.5956 | 2.6197 | 2.6536 | 2.7308 | 2.7915 | 2.8454 | 2.8643 | 2.8859 | 2.8557 | 2.8716 | 2.9465 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 10% | 4366.1437 | 2.0493 | 2.351 | 2.7615 | 2.7944 | 2.8176 | 2.8414 | 2.9334 | 2.9871 | 3.0421 | 3.0671 | 3.0803 | 3.0347 | 3.0585 | 3.1499 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069
5% | 4381.8952 | 0.92582 | 1.0762 | 1.2798 | 1.2978 | 1.3099 | 1.3268 | 1.3654 | 1.3957 | 1.4227 | 1.4321 | 1.443 | 1.4278 | 1.4358 | 1.4733 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 5% | 4374.4653 | 1.0247 | 1.1755 | 1.3807 | 1.3972 | 1.4088 | 1.4207 | 1.4667 | 1.4936 | 1.5211 | 1.5336 | 1.5401 | 1.5173 | 1.5292 | 1.5749 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534
9.992e-14% | 4391.7028 | 1.8502e-14 | 2.1507e-14 | 2.5575e-14 | 2.5935e-14 | 2.6176e-14 | 2.6515e-14 | 2.7286e-14 | 2.7892e-14 | 2.8431e-14 | 2.862e-14 | 2.8836e-14 | 2.8534e-14 | 2.8693e-14 | 2.9441e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 9.992e-14% | 4375.9513 | 2.0477e-14 | 2.3491e-14 | 2.7593e-14 | 2.7922e-14 | 2.8153e-14 | 2.8392e-14 | 2.931e-14 | 2.9848e-14 | 3.0397e-14 | 3.0647e-14 | 3.0778e-14 | 3.0322e-14 | 3.056e-14 | 3.1474e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 100% | 0 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
99% | 0.37816 | 20.9458 | 23.253 | 27.1376 | 27.1084 | 27.0821 | 27.5032 | 28.1214 | 28.545 | 28.0301 | 28.0813 | 28.3267 | 29.2985 | 28.3777 | 28.3236 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 99% | 1.1345 | 22.7597 | 25.5995 | 29.4773 | 29.4252 | 29.4594 | 29.5654 | 29.9256 | 30.1669 | 30.3648 | 30.3939 | 30.5724 | 30.6356 | 30.6355 | 30.5946 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859
98% | 0.37816 | 20.7342 | 23.0181 | 26.8635 | 26.8346 | 26.8085 | 27.2253 | 27.8373 | 28.2567 | 27.7469 | 27.7976 | 28.0405 | 29.0026 | 28.091 | 28.0375 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 98% | 1.8908 | 22.5298 | 25.3409 | 29.1795 | 29.128 | 29.1618 | 29.2667 | 29.6233 | 29.8621 | 30.058 | 30.0869 | 30.2636 | 30.3262 | 30.326 | 30.2856 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277
97% | 0.75633 | 20.5226 | 22.7832 | 26.5894 | 26.5608 | 26.535 | 26.9475 | 27.5532 | 27.9683 | 27.4638 | 27.514 | 27.7544 | 28.7066 | 27.8044 | 27.7514 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 97% | 2.269 | 22.2999 | 25.0823 | 28.8818 | 28.8307 | 28.8642 | 28.9681 | 29.321 | 29.5574 | 29.7513 | 29.7799 | 29.9547 | 30.0167 | 30.0166 | 29.9765 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968
95% | 0.75633 | 20.0995 | 22.3135 | 26.0411 | 26.0131 | 25.9879 | 26.3919 | 26.9851 | 27.3917 | 26.8975 | 26.9467 | 27.1822 | 28.1147 | 27.2311 | 27.1792 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 95% | 4.1598 | 21.8401 | 24.5651 | 28.2863 | 28.2363 | 28.2691 | 28.3708 | 28.7165 | 28.948 | 29.1379 | 29.1659 | 29.3371 | 29.3978 | 29.3977 | 29.3585 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501
90% | 3.7816 | 19.0416 | 21.1391 | 24.6705 | 24.644 | 24.6201 | 25.0029 | 25.5649 | 25.95 | 25.4819 | 25.5284 | 25.7515 | 26.635 | 25.7979 | 25.7487 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 90% | 15.5047 | 20.6906 | 23.2722 | 26.7975 | 26.7502 | 26.7812 | 26.8776 | 27.2051 | 27.4244 | 27.6043 | 27.6308 | 27.7931 | 27.8506 | 27.8504 | 27.8133 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054
85% | 13.6139 | 17.9837 | 19.9647 | 23.2999 | 23.2749 | 23.2523 | 23.6138 | 24.1446 | 24.5083 | 24.0662 | 24.1102 | 24.3209 | 25.1553 | 24.3647 | 24.3182 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 85% | 31.3876 | 19.5412 | 21.9793 | 25.3088 | 25.2641 | 25.2934 | 25.3844 | 25.6937 | 25.9008 | 26.0708 | 26.0958 | 26.249 | 26.3033 | 26.3032 | 26.2681 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606
80% | 35.1693 | 16.9259 | 18.7903 | 21.9294 | 21.9058 | 21.8845 | 22.2248 | 22.7243 | 23.0667 | 22.6505 | 22.6919 | 22.8902 | 23.6756 | 22.9315 | 22.8877 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 80% | 57.8591 | 18.3917 | 20.6864 | 23.82 | 23.7779 | 23.8055 | 23.8912 | 24.1823 | 24.3773 | 24.5372 | 24.5607 | 24.7049 | 24.7561 | 24.7559 | 24.7229 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159
75% | 80.549 | 15.868 | 17.6159 | 20.5588 | 20.5367 | 20.5167 | 20.8357 | 21.3041 | 21.625 | 21.2349 | 21.2737 | 21.4596 | 22.1959 | 21.4982 | 21.4573 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 75% | 121.3907 | 17.2422 | 19.3935 | 22.3313 | 22.2918 | 22.3177 | 22.398 | 22.6709 | 22.8537 | 23.0036 | 23.0257 | 23.1609 | 23.2088 | 23.2087 | 23.1777 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712
70% | 192.1075 | 14.8101 | 16.4415 | 19.1882 | 19.1676 | 19.149 | 19.4467 | 19.8838 | 20.1833 | 19.8192 | 19.8554 | 20.029 | 20.7161 | 20.065 | 20.0268 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 70% | 273.4128 | 16.0927 | 18.1006 | 20.8425 | 20.8057 | 20.8299 | 20.9048 | 21.1595 | 21.3301 | 21.47 | 21.4906 | 21.6168 | 21.6616 | 21.6614 | 21.6325 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264
65% | 403.1231 | 13.7523 | 15.2671 | 17.8176 | 17.7984 | 17.7812 | 18.0576 | 18.4635 | 18.7417 | 18.4036 | 18.4372 | 18.5983 | 19.2364 | 18.6318 | 18.5963 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 65% | 529.43 | 14.9432 | 16.8077 | 19.3538 | 19.3196 | 19.342 | 19.4116 | 19.6481 | 19.8065 | 19.9365 | 19.9556 | 20.0728 | 20.1143 | 20.1142 | 20.0874 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817
60% | 739.3112 | 12.6944 | 14.0927 | 16.447 | 16.4293 | 16.4134 | 16.6686 | 17.0432 | 17.3 | 16.9879 | 17.0189 | 17.1677 | 17.7567 | 17.1986 | 17.1658 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 60% | 918.9392 | 13.7938 | 15.5148 | 17.865 | 17.8334 | 17.8542 | 17.9184 | 18.1367 | 18.2829 | 18.4029 | 18.4205 | 18.5287 | 18.567 | 18.5669 | 18.5422 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369
55% | 1204.8314 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 55% | 1454.0417 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
50% | 1783.0446 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 50% | 2105.2406 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
45% | 2370.3337 | 9.5208 | 10.5695 | 12.3353 | 12.322 | 12.31 | 12.5014 | 12.7824 | 12.975 | 12.7409 | 12.7642 | 12.8758 | 13.3175 | 12.8989 | 12.8744 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 45% | 2758.3303 | 10.3453 | 11.6361 | 13.3988 | 13.3751 | 13.3906 | 13.4388 | 13.6025 | 13.7122 | 13.8022 | 13.8154 | 13.8965 | 13.9253 | 13.9252 | 13.9066 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027
40% | 2864.2163 | 8.4629 | 9.3951 | 10.9647 | 10.9529 | 10.9423 | 11.1124 | 11.3622 | 11.5333 | 11.3253 | 11.346 | 11.4451 | 11.8378 | 11.4657 | 11.4439 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 40% | 3348.2666 | 9.1958 | 10.3432 | 11.91 | 11.889 | 11.9028 | 11.9456 | 12.0911 | 12.1886 | 12.2686 | 12.2804 | 12.3525 | 12.378 | 12.378 | 12.3615 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579
35% | 3297.9707 | 7.4051 | 8.2208 | 9.5941 | 9.5838 | 9.5745 | 9.7233 | 9.9419 | 10.0917 | 9.9096 | 9.9277 | 10.0145 | 10.3581 | 10.0325 | 10.0134 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 35% | 3816.434 | 8.0464 | 9.0503 | 10.4213 | 10.4028 | 10.4149 | 10.4524 | 10.5798 | 10.6651 | 10.735 | 10.7453 | 10.8084 | 10.8308 | 10.8307 | 10.8163 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132
30% | 3579.7031 | 6.3472 | 7.0464 | 8.2235 | 8.2147 | 8.2067 | 8.3343 | 8.5216 | 8.65 | 8.494 | 8.5095 | 8.5838 | 8.8783 | 8.5993 | 8.5829 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 30% | 4067.1569 | 6.8969 | 7.7574 | 8.9325 | 8.9167 | 8.9271 | 8.9592 | 9.0684 | 9.1415 | 9.2014 | 9.2103 | 9.2644 | 9.2835 | 9.2835 | 9.2711 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685
25% | 3796.3913 | 5.2893 | 5.872 | 6.8529 | 6.8456 | 6.8389 | 6.9452 | 7.1014 | 7.2083 | 7.0783 | 7.0912 | 7.1532 | 7.3986 | 7.1661 | 7.1524 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 25% | 4236.9526 | 5.7474 | 6.4645 | 7.4438 | 7.4306 | 7.4392 | 7.466 | 7.557 | 7.6179 | 7.6679 | 7.6752 | 7.7203 | 7.7363 | 7.7362 | 7.7259 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237
20% | 3975.6411 | 4.2315 | 4.6976 | 5.4823 | 5.4764 | 5.4711 | 5.5562 | 5.6811 | 5.7667 | 5.6626 | 5.673 | 5.7226 | 5.9189 | 5.7329 | 5.7219 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 20% | 4332.6282 | 4.5979 | 5.1716 | 5.955 | 5.9445 | 5.9514 | 5.9728 | 6.0456 | 6.0943 | 6.1343 | 6.1402 | 6.1762 | 6.189 | 6.189 | 6.1807 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179
15% | 4117.4527 | 3.1736 | 3.5232 | 4.1118 | 4.1073 | 4.1033 | 4.1671 | 4.2608 | 4.325 | 4.247 | 4.2547 | 4.2919 | 4.4392 | 4.2996 | 4.2915 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 15% | 4361.7469 | 3.4484 | 3.8787 | 4.4663 | 4.4584 | 4.4635 | 4.4796 | 4.5342 | 4.5707 | 4.6007 | 4.6051 | 4.6322 | 4.6418 | 4.6417 | 4.6355 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342
10% | 4224.8514 | 2.1157 | 2.3488 | 2.7412 | 2.7382 | 2.7356 | 2.7781 | 2.8405 | 2.8833 | 2.8313 | 2.8365 | 2.8613 | 2.9594 | 2.8664 | 2.861 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 10% | 4375.7389 | 2.299 | 2.5858 | 2.9775 | 2.9722 | 2.9757 | 2.9864 | 3.0228 | 3.0472 | 3.0671 | 3.0701 | 3.0881 | 3.0945 | 3.0945 | 3.0904 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895
5% | 4310.3165 | 1.0579 | 1.1744 | 1.3706 | 1.3691 | 1.3678 | 1.389 | 1.4203 | 1.4417 | 1.4157 | 1.4182 | 1.4306 | 1.4797 | 1.4332 | 1.4305 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 5% | 4378.0079 | 1.1495 | 1.2929 | 1.4888 | 1.4861 | 1.4878 | 1.4932 | 1.5114 | 1.5236 | 1.5336 | 1.535 | 1.5441 | 1.5473 | 1.5472 | 1.5452 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447
9.992e-14% | 4382.5459 | 2.114e-14 | 2.3469e-14 | 2.739e-14 | 2.736e-14 | 2.7334e-14 | 2.7759e-14 | 2.8383e-14 | 2.881e-14 | 2.8291e-14 | 2.8342e-14 | 2.859e-14 | 2.9571e-14 | 2.8641e-14 | 2.8587e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 9.992e-14% | 4379.1424 | 2.2971e-14 | 2.5837e-14 | 2.9751e-14 | 2.9699e-14 | 2.9733e-14 | 2.984e-14 | 3.0204e-14 | 3.0447e-14 | 3.0647e-14 | 3.0676e-14 | 3.0857e-14 | 3.092e-14 | 3.092e-14 | 3.0879e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 100% | 0 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
99% | 0.2972 | 18.3313 | 21.3091 | 25.3398 | 25.6966 | 25.9353 | 26.2707 | 27.0352 | 27.6355 | 28.1693 | 28.3565 | 28.5704 | 28.2714 | 28.4291 | 29.1704 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 99% | 0.2972 | 20.2885 | 23.2751 | 27.3384 | 27.6647 | 27.894 | 28.1301 | 29.0405 | 29.5727 | 30.117 | 30.3646 | 30.4948 | 30.0432 | 30.279 | 31.1838 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581
98% | 0.8916 | 18.1461 | 21.0938 | 25.0839 | 25.4371 | 25.6733 | 26.0054 | 26.7622 | 27.3564 | 27.8847 | 28.0701 | 28.2819 | 27.9858 | 28.1419 | 28.8757 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 98% | 0.8916 | 20.0836 | 23.04 | 27.0623 | 27.3852 | 27.6122 | 27.8459 | 28.7472 | 29.274 | 29.8128 | 30.0579 | 30.1868 | 29.7397 | 29.9731 | 30.8688 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474
97% | 1.7832 | 17.9609 | 20.8786 | 24.8279 | 25.1775 | 25.4113 | 25.74 | 26.4891 | 27.0772 | 27.6002 | 27.7837 | 27.9933 | 27.7002 | 27.8548 | 28.5811 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 97% | 2.0804 | 19.8787 | 22.8049 | 26.7861 | 27.1058 | 27.3305 | 27.5618 | 28.4539 | 28.9753 | 29.5086 | 29.7512 | 29.8787 | 29.4363 | 29.6673 | 30.5538 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367
95% | 4.458 | 17.5906 | 20.4481 | 24.316 | 24.6584 | 24.8874 | 25.2093 | 25.9429 | 26.5189 | 27.0311 | 27.2108 | 27.4161 | 27.1291 | 27.2804 | 27.9918 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 95% | 4.1608 | 19.4688 | 22.3347 | 26.2339 | 26.5469 | 26.767 | 26.9935 | 27.8672 | 28.3779 | 28.9002 | 29.1378 | 29.2627 | 28.8293 | 29.0556 | 29.9239 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154
90% | 15.1571 | 16.6648 | 19.3719 | 23.0362 | 23.3606 | 23.5775 | 23.8825 | 24.5775 | 25.1232 | 25.6084 | 25.7787 | 25.9731 | 25.7012 | 25.8446 | 26.5185 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 90% | 11.5907 | 18.4441 | 21.1592 | 24.8531 | 25.1497 | 25.3582 | 25.5728 | 26.4005 | 26.8843 | 27.3791 | 27.6042 | 27.7225 | 27.312 | 27.5264 | 28.3489 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619
85% | 39.5274 | 15.739 | 18.2957 | 21.7564 | 22.0628 | 22.2676 | 22.5557 | 23.2121 | 23.7275 | 24.1857 | 24.3465 | 24.5302 | 24.2734 | 24.4088 | 25.0453 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 85% | 32.6918 | 17.4195 | 19.9837 | 23.4724 | 23.7525 | 23.9494 | 24.1521 | 24.9338 | 25.3907 | 25.8581 | 26.0707 | 26.1824 | 25.7947 | 25.9971 | 26.774 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085
80% | 110.5579 | 14.8131 | 17.2195 | 20.4766 | 20.765 | 20.9578 | 21.2289 | 21.8467 | 22.3317 | 22.7631 | 22.9144 | 23.0872 | 22.8455 | 22.973 | 23.572 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 80% | 84.1072 | 16.3948 | 18.8082 | 22.0917 | 22.3553 | 22.5406 | 22.7314 | 23.4671 | 23.8972 | 24.337 | 24.5371 | 24.6422 | 24.2773 | 24.4679 | 25.199 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855
75% | 244.2972 | 13.8873 | 16.1432 | 19.1968 | 19.4671 | 19.6479 | 19.9021 | 20.4812 | 20.936 | 21.3404 | 21.4822 | 21.6443 | 21.4177 | 21.5372 | 22.0988 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 75% | 202.095 | 15.3701 | 17.6327 | 20.7109 | 20.9581 | 21.1318 | 21.3107 | 22.0004 | 22.4036 | 22.8159 | 23.0035 | 23.1021 | 22.76 | 22.9386 | 23.6241 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016
70% | 444.0146 | 12.9615 | 15.067 | 17.9171 | 18.1693 | 18.3381 | 18.5753 | 19.1158 | 19.5403 | 19.9177 | 20.0501 | 20.2013 | 19.9899 | 20.1014 | 20.6255 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 70% | 388.1413 | 14.3454 | 16.4572 | 19.3302 | 19.5609 | 19.723 | 19.89 | 20.5337 | 20.91 | 21.2949 | 21.47 | 21.562 | 21.2427 | 21.4094 | 22.0492 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482
65% | 770.3386 | 12.0357 | 13.9908 | 16.6373 | 16.8715 | 17.0282 | 17.2485 | 17.7504 | 18.1445 | 18.495 | 18.6179 | 18.7584 | 18.562 | 18.6656 | 19.1523 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 65% | 669.8855 | 13.3208 | 15.2817 | 17.9495 | 18.1637 | 18.3142 | 18.4692 | 19.067 | 19.4164 | 19.7738 | 19.9364 | 20.0218 | 19.7253 | 19.8801 | 20.4742 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947
60% | 1209.3009 | 11.1099 | 12.9146 | 15.3575 | 15.5737 | 15.7183 | 15.9217 | 16.385 | 16.7488 | 17.0723 | 17.1858 | 17.3154 | 17.1342 | 17.2297 | 17.679 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 60% | 1104.687 | 12.2961 | 14.1061 | 16.5688 | 16.7665 | 16.9054 | 17.0485 | 17.6003 | 17.9229 | 18.2528 | 18.4028 | 18.4817 | 18.208 | 18.3509 | 18.8993 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413
55% | 1757.6322 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 55% | 1631.62 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
50% | 2378.4799 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 50% | 2253.9537 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
45% | 3003.7856 | 8.3324 | 9.6859 | 11.5181 | 11.6803 | 11.7888 | 11.9412 | 12.2887 | 12.5616 | 12.8042 | 12.8893 | 12.9866 | 12.8506 | 12.9223 | 13.2593 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 45% | 2892.3362 | 9.2221 | 10.5796 | 12.4266 | 12.5749 | 12.6791 | 12.7864 | 13.2002 | 13.4422 | 13.6896 | 13.8021 | 13.8613 | 13.656 | 13.7632 | 14.1745 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981
40% | 3548.2533 | 7.4066 | 8.6097 | 10.2383 | 10.3825 | 10.4789 | 10.6144 | 10.9233 | 11.1659 | 11.3815 | 11.4572 | 11.5436 | 11.4228 | 11.4865 | 11.786 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 40% | 3473.3593 | 8.1974 | 9.4041 | 11.0458 | 11.1776 | 11.2703 | 11.3657 | 11.7336 | 11.9486 | 12.1685 | 12.2685 | 12.3211 | 12.1387 | 12.2339 | 12.5995 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275
35% | 3927.7759 | 6.4808 | 7.5335 | 8.9585 | 9.0847 | 9.169 | 9.2876 | 9.5579 | 9.7701 | 9.9588 | 10.025 | 10.1007 | 9.9949 | 10.0507 | 10.3128 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 35% | 3882.8989 | 7.1727 | 8.2286 | 9.6651 | 9.7804 | 9.8615 | 9.945 | 10.2669 | 10.455 | 10.6474 | 10.735 | 10.781 | 10.6213 | 10.7047 | 11.0246 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741
30% | 4135.8149 | 5.5549 | 6.4573 | 7.6787 | 7.7869 | 7.8592 | 7.9608 | 8.1925 | 8.3744 | 8.5361 | 8.5929 | 8.6577 | 8.5671 | 8.6149 | 8.8395 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 30% | 4127.1961 | 6.148 | 7.0531 | 8.2844 | 8.3832 | 8.4527 | 8.5243 | 8.8002 | 8.9614 | 9.1264 | 9.2014 | 9.2408 | 9.104 | 9.1755 | 9.4496 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206
25% | 4252.0195 | 4.6291 | 5.3811 | 6.3989 | 6.489 | 6.5493 | 6.634 | 6.8271 | 6.9787 | 7.1135 | 7.1607 | 7.2148 | 7.1392 | 7.1791 | 7.3663 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 25% | 4245.1839 | 5.1234 | 5.8776 | 6.9036 | 6.986 | 7.0439 | 7.1036 | 7.3335 | 7.4679 | 7.6053 | 7.6678 | 7.7007 | 7.5867 | 7.6462 | 7.8747 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672
20% | 4325.4275 | 3.7033 | 4.3049 | 5.1192 | 5.1912 | 5.2394 | 5.3072 | 5.4617 | 5.5829 | 5.6908 | 5.7286 | 5.7718 | 5.7114 | 5.7432 | 5.893 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 20% | 4322.1583 | 4.0987 | 4.702 | 5.5229 | 5.5888 | 5.6351 | 5.6828 | 5.8668 | 5.9743 | 6.0843 | 6.1343 | 6.1606 | 6.0693 | 6.117 | 6.2998 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138
15% | 4360.497 | 2.7775 | 3.2286 | 3.8394 | 3.8934 | 3.9296 | 3.9804 | 4.0962 | 4.1872 | 4.2681 | 4.2964 | 4.3289 | 4.2835 | 4.3074 | 4.4198 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 15% | 4354.2558 | 3.074 | 3.5265 | 4.1422 | 4.1916 | 4.2264 | 4.2621 | 4.4001 | 4.4807 | 4.5632 | 4.6007 | 4.6204 | 4.552 | 4.5877 | 4.7248 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603
10% | 4373.8709 | 1.8516 | 2.1524 | 2.5596 | 2.5956 | 2.6197 | 2.6536 | 2.7308 | 2.7915 | 2.8454 | 2.8643 | 2.8859 | 2.8557 | 2.8716 | 2.9465 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 10% | 4366.1437 | 2.0493 | 2.351 | 2.7615 | 2.7944 | 2.8176 | 2.8414 | 2.9334 | 2.9871 | 3.0421 | 3.0671 | 3.0803 | 3.0347 | 3.0585 | 3.1499 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069
5% | 4381.8952 | 0.92582 | 1.0762 | 1.2798 | 1.2978 | 1.3099 | 1.3268 | 1.3654 | 1.3957 | 1.4227 | 1.4321 | 1.443 | 1.4278 | 1.4358 | 1.4733 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 5% | 4374.4653 | 1.0247 | 1.1755 | 1.3807 | 1.3972 | 1.4088 | 1.4207 | 1.4667 | 1.4936 | 1.5211 | 1.5336 | 1.5401 | 1.5173 | 1.5292 | 1.5749 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534
9.992e-14% | 4391.7028 | 1.8502e-14 | 2.1507e-14 | 2.5575e-14 | 2.5935e-14 | 2.6176e-14 | 2.6515e-14 | 2.7286e-14 | 2.7892e-14 | 2.8431e-14 | 2.862e-14 | 2.8836e-14 | 2.8534e-14 | 2.8693e-14 | 2.9441e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 9.992e-14% | 4375.9513 | 2.0477e-14 | 2.3491e-14 | 2.7593e-14 | 2.7922e-14 | 2.8153e-14 | 2.8392e-14 | 2.931e-14 | 2.9848e-14 | 3.0397e-14 | 3.0647e-14 | 3.0778e-14 | 3.0322e-14 | 3.056e-14 | 3.1474e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 100% | 0 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
99% | 0.37816 | 20.9458 | 23.253 | 27.1376 | 27.1084 | 27.0821 | 27.5032 | 28.1214 | 28.545 | 28.0301 | 28.0813 | 28.3267 | 29.2985 | 28.3777 | 28.3236 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 99% | 1.1345 | 22.7597 | 25.5995 | 29.4773 | 29.4252 | 29.4594 | 29.5654 | 29.9256 | 30.1669 | 30.3648 | 30.3939 | 30.5724 | 30.6356 | 30.6355 | 30.5946 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859
98% | 0.37816 | 20.7342 | 23.0181 | 26.8635 | 26.8346 | 26.8085 | 27.2253 | 27.8373 | 28.2567 | 27.7469 | 27.7976 | 28.0405 | 29.0026 | 28.091 | 28.0375 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 98% | 1.8908 | 22.5298 | 25.3409 | 29.1795 | 29.128 | 29.1618 | 29.2667 | 29.6233 | 29.8621 | 30.058 | 30.0869 | 30.2636 | 30.3262 | 30.326 | 30.2856 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277
97% | 0.75633 | 20.5226 | 22.7832 | 26.5894 | 26.5608 | 26.535 | 26.9475 | 27.5532 | 27.9683 | 27.4638 | 27.514 | 27.7544 | 28.7066 | 27.8044 | 27.7514 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 97% | 2.269 | 22.2999 | 25.0823 | 28.8818 | 28.8307 | 28.8642 | 28.9681 | 29.321 | 29.5574 | 29.7513 | 29.7799 | 29.9547 | 30.0167 | 30.0166 | 29.9765 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968
95% | 0.75633 | 20.0995 | 22.3135 | 26.0411 | 26.0131 | 25.9879 | 26.3919 | 26.9851 | 27.3917 | 26.8975 | 26.9467 | 27.1822 | 28.1147 | 27.2311 | 27.1792 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 95% | 4.1598 | 21.8401 | 24.5651 | 28.2863 | 28.2363 | 28.2691 | 28.3708 | 28.7165 | 28.948 | 29.1379 | 29.1659 | 29.3371 | 29.3978 | 29.3977 | 29.3585 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501
90% | 3.7816 | 19.0416 | 21.1391 | 24.6705 | 24.644 | 24.6201 | 25.0029 | 25.5649 | 25.95 | 25.4819 | 25.5284 | 25.7515 | 26.635 | 25.7979 | 25.7487 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 90% | 15.5047 | 20.6906 | 23.2722 | 26.7975 | 26.7502 | 26.7812 | 26.8776 | 27.2051 | 27.4244 | 27.6043 | 27.6308 | 27.7931 | 27.8506 | 27.8504 | 27.8133 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054
85% | 13.6139 | 17.9837 | 19.9647 | 23.2999 | 23.2749 | 23.2523 | 23.6138 | 24.1446 | 24.5083 | 24.0662 | 24.1102 | 24.3209 | 25.1553 | 24.3647 | 24.3182 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 85% | 31.3876 | 19.5412 | 21.9793 | 25.3088 | 25.2641 | 25.2934 | 25.3844 | 25.6937 | 25.9008 | 26.0708 | 26.0958 | 26.249 | 26.3033 | 26.3032 | 26.2681 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606
80% | 35.1693 | 16.9259 | 18.7903 | 21.9294 | 21.9058 | 21.8845 | 22.2248 | 22.7243 | 23.0667 | 22.6505 | 22.6919 | 22.8902 | 23.6756 | 22.9315 | 22.8877 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 80% | 57.8591 | 18.3917 | 20.6864 | 23.82 | 23.7779 | 23.8055 | 23.8912 | 24.1823 | 24.3773 | 24.5372 | 24.5607 | 24.7049 | 24.7561 | 24.7559 | 24.7229 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159
75% | 80.549 | 15.868 | 17.6159 | 20.5588 | 20.5367 | 20.5167 | 20.8357 | 21.3041 | 21.625 | 21.2349 | 21.2737 | 21.4596 | 22.1959 | 21.4982 | 21.4573 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 75% | 121.3907 | 17.2422 | 19.3935 | 22.3313 | 22.2918 | 22.3177 | 22.398 | 22.6709 | 22.8537 | 23.0036 | 23.0257 | 23.1609 | 23.2088 | 23.2087 | 23.1777 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712
70% | 192.1075 | 14.8101 | 16.4415 | 19.1882 | 19.1676 | 19.149 | 19.4467 | 19.8838 | 20.1833 | 19.8192 | 19.8554 | 20.029 | 20.7161 | 20.065 | 20.0268 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 70% | 273.4128 | 16.0927 | 18.1006 | 20.8425 | 20.8057 | 20.8299 | 20.9048 | 21.1595 | 21.3301 | 21.47 | 21.4906 | 21.6168 | 21.6616 | 21.6614 | 21.6325 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264
65% | 403.1231 | 13.7523 | 15.2671 | 17.8176 | 17.7984 | 17.7812 | 18.0576 | 18.4635 | 18.7417 | 18.4036 | 18.4372 | 18.5983 | 19.2364 | 18.6318 | 18.5963 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 65% | 529.43 | 14.9432 | 16.8077 | 19.3538 | 19.3196 | 19.342 | 19.4116 | 19.6481 | 19.8065 | 19.9365 | 19.9556 | 20.0728 | 20.1143 | 20.1142 | 20.0874 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817
60% | 739.3112 | 12.6944 | 14.0927 | 16.447 | 16.4293 | 16.4134 | 16.6686 | 17.0432 | 17.3 | 16.9879 | 17.0189 | 17.1677 | 17.7567 | 17.1986 | 17.1658 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 60% | 918.9392 | 13.7938 | 15.5148 | 17.865 | 17.8334 | 17.8542 | 17.9184 | 18.1367 | 18.2829 | 18.4029 | 18.4205 | 18.5287 | 18.567 | 18.5669 | 18.5422 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369
55% | 1204.8314 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 55% | 1454.0417 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
50% | 1783.0446 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 50% | 2105.2406 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
45% | 2370.3337 | 9.5208 | 10.5695 | 12.3353 | 12.322 | 12.31 | 12.5014 | 12.7824 | 12.975 | 12.7409 | 12.7642 | 12.8758 | 13.3175 | 12.8989 | 12.8744 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 45% | 2758.3303 | 10.3453 | 11.6361 | 13.3988 | 13.3751 | 13.3906 | 13.4388 | 13.6025 | 13.7122 | 13.8022 | 13.8154 | 13.8965 | 13.9253 | 13.9252 | 13.9066 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027
40% | 2864.2163 | 8.4629 | 9.3951 | 10.9647 | 10.9529 | 10.9423 | 11.1124 | 11.3622 | 11.5333 | 11.3253 | 11.346 | 11.4451 | 11.8378 | 11.4657 | 11.4439 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 40% | 3348.2666 | 9.1958 | 10.3432 | 11.91 | 11.889 | 11.9028 | 11.9456 | 12.0911 | 12.1886 | 12.2686 | 12.2804 | 12.3525 | 12.378 | 12.378 | 12.3615 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579
35% | 3297.9707 | 7.4051 | 8.2208 | 9.5941 | 9.5838 | 9.5745 | 9.7233 | 9.9419 | 10.0917 | 9.9096 | 9.9277 | 10.0145 | 10.3581 | 10.0325 | 10.0134 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 35% | 3816.434 | 8.0464 | 9.0503 | 10.4213 | 10.4028 | 10.4149 | 10.4524 | 10.5798 | 10.6651 | 10.735 | 10.7453 | 10.8084 | 10.8308 | 10.8307 | 10.8163 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132
30% | 3579.7031 | 6.3472 | 7.0464 | 8.2235 | 8.2147 | 8.2067 | 8.3343 | 8.5216 | 8.65 | 8.494 | 8.5095 | 8.5838 | 8.8783 | 8.5993 | 8.5829 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 30% | 4067.1569 | 6.8969 | 7.7574 | 8.9325 | 8.9167 | 8.9271 | 8.9592 | 9.0684 | 9.1415 | 9.2014 | 9.2103 | 9.2644 | 9.2835 | 9.2835 | 9.2711 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685
25% | 3796.3913 | 5.2893 | 5.872 | 6.8529 | 6.8456 | 6.8389 | 6.9452 | 7.1014 | 7.2083 | 7.0783 | 7.0912 | 7.1532 | 7.3986 | 7.1661 | 7.1524 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 25% | 4236.9526 | 5.7474 | 6.4645 | 7.4438 | 7.4306 | 7.4392 | 7.466 | 7.557 | 7.6179 | 7.6679 | 7.6752 | 7.7203 | 7.7363 | 7.7362 | 7.7259 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237
20% | 3975.6411 | 4.2315 | 4.6976 | 5.4823 | 5.4764 | 5.4711 | 5.5562 | 5.6811 | 5.7667 | 5.6626 | 5.673 | 5.7226 | 5.9189 | 5.7329 | 5.7219 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 20% | 4332.6282 | 4.5979 | 5.1716 | 5.955 | 5.9445 | 5.9514 | 5.9728 | 6.0456 | 6.0943 | 6.1343 | 6.1402 | 6.1762 | 6.189 | 6.189 | 6.1807 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179
15% | 4117.4527 | 3.1736 | 3.5232 | 4.1118 | 4.1073 | 4.1033 | 4.1671 | 4.2608 | 4.325 | 4.247 | 4.2547 | 4.2919 | 4.4392 | 4.2996 | 4.2915 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 15% | 4361.7469 | 3.4484 | 3.8787 | 4.4663 | 4.4584 | 4.4635 | 4.4796 | 4.5342 | 4.5707 | 4.6007 | 4.6051 | 4.6322 | 4.6418 | 4.6417 | 4.6355 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342
10% | 4224.8514 | 2.1157 | 2.3488 | 2.7412 | 2.7382 | 2.7356 | 2.7781 | 2.8405 | 2.8833 | 2.8313 | 2.8365 | 2.8613 | 2.9594 | 2.8664 | 2.861 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 10% | 4375.7389 | 2.299 | 2.5858 | 2.9775 | 2.9722 | 2.9757 | 2.9864 | 3.0228 | 3.0472 | 3.0671 | 3.0701 | 3.0881 | 3.0945 | 3.0945 | 3.0904 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895
5% | 4310.3165 | 1.0579 | 1.1744 | 1.3706 | 1.3691 | 1.3678 | 1.389 | 1.4203 | 1.4417 | 1.4157 | 1.4182 | 1.4306 | 1.4797 | 1.4332 | 1.4305 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 5% | 4378.0079 | 1.1495 | 1.2929 | 1.4888 | 1.4861 | 1.4878 | 1.4932 | 1.5114 | 1.5236 | 1.5336 | 1.535 | 1.5441 | 1.5473 | 1.5472 | 1.5452 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447
9.992e-14% | 4382.5459 | 2.114e-14 | 2.3469e-14 | 2.739e-14 | 2.736e-14 | 2.7334e-14 | 2.7759e-14 | 2.8383e-14 | 2.881e-14 | 2.8291e-14 | 2.8342e-14 | 2.859e-14 | 2.9571e-14 | 2.8641e-14 | 2.8587e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 9.992e-14% | 4379.1424 | 2.2971e-14 | 2.5837e-14 | 2.9751e-14 | 2.9699e-14 | 2.9733e-14 | 2.984e-14 | 3.0204e-14 | 3.0447e-14 | 3.0647e-14 | 3.0676e-14 | 3.0857e-14 | 3.092e-14 | 3.092e-14 | 3.0879e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 100% | 0 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
99% | 0.2972 | 18.3313 | 21.3091 | 25.3398 | 25.6966 | 25.9353 | 26.2707 | 27.0352 | 27.6355 | 28.1693 | 28.3565 | 28.5704 | 28.2714 | 28.4291 | 29.1704 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 99% | 0.2972 | 20.2885 | 23.2751 | 27.3384 | 27.6647 | 27.894 | 28.1301 | 29.0405 | 29.5727 | 30.117 | 30.3646 | 30.4948 | 30.0432 | 30.279 | 31.1838 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581
98% | 0.8916 | 18.1461 | 21.0938 | 25.0839 | 25.4371 | 25.6733 | 26.0054 | 26.7622 | 27.3564 | 27.8847 | 28.0701 | 28.2819 | 27.9858 | 28.1419 | 28.8757 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 98% | 0.8916 | 20.0836 | 23.04 | 27.0623 | 27.3852 | 27.6122 | 27.8459 | 28.7472 | 29.274 | 29.8128 | 30.0579 | 30.1868 | 29.7397 | 29.9731 | 30.8688 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474
97% | 1.7832 | 17.9609 | 20.8786 | 24.8279 | 25.1775 | 25.4113 | 25.74 | 26.4891 | 27.0772 | 27.6002 | 27.7837 | 27.9933 | 27.7002 | 27.8548 | 28.5811 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 97% | 2.0804 | 19.8787 | 22.8049 | 26.7861 | 27.1058 | 27.3305 | 27.5618 | 28.4539 | 28.9753 | 29.5086 | 29.7512 | 29.8787 | 29.4363 | 29.6673 | 30.5538 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367
95% | 4.458 | 17.5906 | 20.4481 | 24.316 | 24.6584 | 24.8874 | 25.2093 | 25.9429 | 26.5189 | 27.0311 | 27.2108 | 27.4161 | 27.1291 | 27.2804 | 27.9918 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 95% | 4.1608 | 19.4688 | 22.3347 | 26.2339 | 26.5469 | 26.767 | 26.9935 | 27.8672 | 28.3779 | 28.9002 | 29.1378 | 29.2627 | 28.8293 | 29.0556 | 29.9239 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154
90% | 15.1571 | 16.6648 | 19.3719 | 23.0362 | 23.3606 | 23.5775 | 23.8825 | 24.5775 | 25.1232 | 25.6084 | 25.7787 | 25.9731 | 25.7012 | 25.8446 | 26.5185 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 90% | 11.5907 | 18.4441 | 21.1592 | 24.8531 | 25.1497 | 25.3582 | 25.5728 | 26.4005 | 26.8843 | 27.3791 | 27.6042 | 27.7225 | 27.312 | 27.5264 | 28.3489 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619
85% | 39.5274 | 15.739 | 18.2957 | 21.7564 | 22.0628 | 22.2676 | 22.5557 | 23.2121 | 23.7275 | 24.1857 | 24.3465 | 24.5302 | 24.2734 | 24.4088 | 25.0453 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 85% | 32.6918 | 17.4195 | 19.9837 | 23.4724 | 23.7525 | 23.9494 | 24.1521 | 24.9338 | 25.3907 | 25.8581 | 26.0707 | 26.1824 | 25.7947 | 25.9971 | 26.774 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085
80% | 110.5579 | 14.8131 | 17.2195 | 20.4766 | 20.765 | 20.9578 | 21.2289 | 21.8467 | 22.3317 | 22.7631 | 22.9144 | 23.0872 | 22.8455 | 22.973 | 23.572 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 80% | 84.1072 | 16.3948 | 18.8082 | 22.0917 | 22.3553 | 22.5406 | 22.7314 | 23.4671 | 23.8972 | 24.337 | 24.5371 | 24.6422 | 24.2773 | 24.4679 | 25.199 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855
75% | 244.2972 | 13.8873 | 16.1432 | 19.1968 | 19.4671 | 19.6479 | 19.9021 | 20.4812 | 20.936 | 21.3404 | 21.4822 | 21.6443 | 21.4177 | 21.5372 | 22.0988 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 75% | 202.095 | 15.3701 | 17.6327 | 20.7109 | 20.9581 | 21.1318 | 21.3107 | 22.0004 | 22.4036 | 22.8159 | 23.0035 | 23.1021 | 22.76 | 22.9386 | 23.6241 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016
70% | 444.0146 | 12.9615 | 15.067 | 17.9171 | 18.1693 | 18.3381 | 18.5753 | 19.1158 | 19.5403 | 19.9177 | 20.0501 | 20.2013 | 19.9899 | 20.1014 | 20.6255 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 70% | 388.1413 | 14.3454 | 16.4572 | 19.3302 | 19.5609 | 19.723 | 19.89 | 20.5337 | 20.91 | 21.2949 | 21.47 | 21.562 | 21.2427 | 21.4094 | 22.0492 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482
65% | 770.3386 | 12.0357 | 13.9908 | 16.6373 | 16.8715 | 17.0282 | 17.2485 | 17.7504 | 18.1445 | 18.495 | 18.6179 | 18.7584 | 18.562 | 18.6656 | 19.1523 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 65% | 669.8855 | 13.3208 | 15.2817 | 17.9495 | 18.1637 | 18.3142 | 18.4692 | 19.067 | 19.4164 | 19.7738 | 19.9364 | 20.0218 | 19.7253 | 19.8801 | 20.4742 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947
60% | 1209.3009 | 11.1099 | 12.9146 | 15.3575 | 15.5737 | 15.7183 | 15.9217 | 16.385 | 16.7488 | 17.0723 | 17.1858 | 17.3154 | 17.1342 | 17.2297 | 17.679 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 60% | 1104.687 | 12.2961 | 14.1061 | 16.5688 | 16.7665 | 16.9054 | 17.0485 | 17.6003 | 17.9229 | 18.2528 | 18.4028 | 18.4817 | 18.208 | 18.3509 | 18.8993 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413
55% | 1757.6322 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 55% | 1631.62 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
50% | 2378.4799 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 50% | 2253.9537 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
45% | 3003.7856 | 8.3324 | 9.6859 | 11.5181 | 11.6803 | 11.7888 | 11.9412 | 12.2887 | 12.5616 | 12.8042 | 12.8893 | 12.9866 | 12.8506 | 12.9223 | 13.2593 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 45% | 2892.3362 | 9.2221 | 10.5796 | 12.4266 | 12.5749 | 12.6791 | 12.7864 | 13.2002 | 13.4422 | 13.6896 | 13.8021 | 13.8613 | 13.656 | 13.7632 | 14.1745 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981
40% | 3548.2533 | 7.4066 | 8.6097 | 10.2383 | 10.3825 | 10.4789 | 10.6144 | 10.9233 | 11.1659 | 11.3815 | 11.4572 | 11.5436 | 11.4228 | 11.4865 | 11.786 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 40% | 3473.3593 | 8.1974 | 9.4041 | 11.0458 | 11.1776 | 11.2703 | 11.3657 | 11.7336 | 11.9486 | 12.1685 | 12.2685 | 12.3211 | 12.1387 | 12.2339 | 12.5995 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275
35% | 3927.7759 | 6.4808 | 7.5335 | 8.9585 | 9.0847 | 9.169 | 9.2876 | 9.5579 | 9.7701 | 9.9588 | 10.025 | 10.1007 | 9.9949 | 10.0507 | 10.3128 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 35% | 3882.8989 | 7.1727 | 8.2286 | 9.6651 | 9.7804 | 9.8615 | 9.945 | 10.2669 | 10.455 | 10.6474 | 10.735 | 10.781 | 10.6213 | 10.7047 | 11.0246 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741
30% | 4135.8149 | 5.5549 | 6.4573 | 7.6787 | 7.7869 | 7.8592 | 7.9608 | 8.1925 | 8.3744 | 8.5361 | 8.5929 | 8.6577 | 8.5671 | 8.6149 | 8.8395 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 30% | 4127.1961 | 6.148 | 7.0531 | 8.2844 | 8.3832 | 8.4527 | 8.5243 | 8.8002 | 8.9614 | 9.1264 | 9.2014 | 9.2408 | 9.104 | 9.1755 | 9.4496 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206
25% | 4252.0195 | 4.6291 | 5.3811 | 6.3989 | 6.489 | 6.5493 | 6.634 | 6.8271 | 6.9787 | 7.1135 | 7.1607 | 7.2148 | 7.1392 | 7.1791 | 7.3663 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 25% | 4245.1839 | 5.1234 | 5.8776 | 6.9036 | 6.986 | 7.0439 | 7.1036 | 7.3335 | 7.4679 | 7.6053 | 7.6678 | 7.7007 | 7.5867 | 7.6462 | 7.8747 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672
20% | 4325.4275 | 3.7033 | 4.3049 | 5.1192 | 5.1912 | 5.2394 | 5.3072 | 5.4617 | 5.5829 | 5.6908 | 5.7286 | 5.7718 | 5.7114 | 5.7432 | 5.893 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 20% | 4322.1583 | 4.0987 | 4.702 | 5.5229 | 5.5888 | 5.6351 | 5.6828 | 5.8668 | 5.9743 | 6.0843 | 6.1343 | 6.1606 | 6.0693 | 6.117 | 6.2998 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138
15% | 4360.497 | 2.7775 | 3.2286 | 3.8394 | 3.8934 | 3.9296 | 3.9804 | 4.0962 | 4.1872 | 4.2681 | 4.2964 | 4.3289 | 4.2835 | 4.3074 | 4.4198 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 15% | 4354.2558 | 3.074 | 3.5265 | 4.1422 | 4.1916 | 4.2264 | 4.2621 | 4.4001 | 4.4807 | 4.5632 | 4.6007 | 4.6204 | 4.552 | 4.5877 | 4.7248 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603
10% | 4373.8709 | 1.8516 | 2.1524 | 2.5596 | 2.5956 | 2.6197 | 2.6536 | 2.7308 | 2.7915 | 2.8454 | 2.8643 | 2.8859 | 2.8557 | 2.8716 | 2.9465 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 10% | 4366.1437 | 2.0493 | 2.351 | 2.7615 | 2.7944 | 2.8176 | 2.8414 | 2.9334 | 2.9871 | 3.0421 | 3.0671 | 3.0803 | 3.0347 | 3.0585 | 3.1499 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069
5% | 4381.8952 | 0.92582 | 1.0762 | 1.2798 | 1.2978 | 1.3099 | 1.3268 | 1.3654 | 1.3957 | 1.4227 | 1.4321 | 1.443 | 1.4278 | 1.4358 | 1.4733 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 5% | 4374.4653 | 1.0247 | 1.1755 | 1.3807 | 1.3972 | 1.4088 | 1.4207 | 1.4667 | 1.4936 | 1.5211 | 1.5336 | 1.5401 | 1.5173 | 1.5292 | 1.5749 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534
9.992e-14% | 4391.7028 | 1.8502e-14 | 2.1507e-14 | 2.5575e-14 | 2.5935e-14 | 2.6176e-14 | 2.6515e-14 | 2.7286e-14 | 2.7892e-14 | 2.8431e-14 | 2.862e-14 | 2.8836e-14 | 2.8534e-14 | 2.8693e-14 | 2.9441e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 9.992e-14% | 4375.9513 | 2.0477e-14 | 2.3491e-14 | 2.7593e-14 | 2.7922e-14 | 2.8153e-14 | 2.8392e-14 | 2.931e-14 | 2.9848e-14 | 3.0397e-14 | 3.0647e-14 | 3.0778e-14 | 3.0322e-14 | 3.056e-14 | 3.1474e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 100% | 0 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
99% | 0.37816 | 20.9458 | 23.253 | 27.1376 | 27.1084 | 27.0821 | 27.5032 | 28.1214 | 28.545 | 28.0301 | 28.0813 | 28.3267 | 29.2985 | 28.3777 | 28.3236 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 99% | 1.1345 | 22.7597 | 25.5995 | 29.4773 | 29.4252 | 29.4594 | 29.5654 | 29.9256 | 30.1669 | 30.3648 | 30.3939 | 30.5724 | 30.6356 | 30.6355 | 30.5946 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859
98% | 0.37816 | 20.7342 | 23.0181 | 26.8635 | 26.8346 | 26.8085 | 27.2253 | 27.8373 | 28.2567 | 27.7469 | 27.7976 | 28.0405 | 29.0026 | 28.091 | 28.0375 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 98% | 1.8908 | 22.5298 | 25.3409 | 29.1795 | 29.128 | 29.1618 | 29.2667 | 29.6233 | 29.8621 | 30.058 | 30.0869 | 30.2636 | 30.3262 | 30.326 | 30.2856 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277
97% | 0.75633 | 20.5226 | 22.7832 | 26.5894 | 26.5608 | 26.535 | 26.9475 | 27.5532 | 27.9683 | 27.4638 | 27.514 | 27.7544 | 28.7066 | 27.8044 | 27.7514 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 97% | 2.269 | 22.2999 | 25.0823 | 28.8818 | 28.8307 | 28.8642 | 28.9681 | 29.321 | 29.5574 | 29.7513 | 29.7799 | 29.9547 | 30.0167 | 30.0166 | 29.9765 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968
95% | 0.75633 | 20.0995 | 22.3135 | 26.0411 | 26.0131 | 25.9879 | 26.3919 | 26.9851 | 27.3917 | 26.8975 | 26.9467 | 27.1822 | 28.1147 | 27.2311 | 27.1792 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 95% | 4.1598 | 21.8401 | 24.5651 | 28.2863 | 28.2363 | 28.2691 | 28.3708 | 28.7165 | 28.948 | 29.1379 | 29.1659 | 29.3371 | 29.3978 | 29.3977 | 29.3585 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501
90% | 3.7816 | 19.0416 | 21.1391 | 24.6705 | 24.644 | 24.6201 | 25.0029 | 25.5649 | 25.95 | 25.4819 | 25.5284 | 25.7515 | 26.635 | 25.7979 | 25.7487 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 90% | 15.5047 | 20.6906 | 23.2722 | 26.7975 | 26.7502 | 26.7812 | 26.8776 | 27.2051 | 27.4244 | 27.6043 | 27.6308 | 27.7931 | 27.8506 | 27.8504 | 27.8133 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054
85% | 13.6139 | 17.9837 | 19.9647 | 23.2999 | 23.2749 | 23.2523 | 23.6138 | 24.1446 | 24.5083 | 24.0662 | 24.1102 | 24.3209 | 25.1553 | 24.3647 | 24.3182 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 85% | 31.3876 | 19.5412 | 21.9793 | 25.3088 | 25.2641 | 25.2934 | 25.3844 | 25.6937 | 25.9008 | 26.0708 | 26.0958 | 26.249 | 26.3033 | 26.3032 | 26.2681 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606
80% | 35.1693 | 16.9259 | 18.7903 | 21.9294 | 21.9058 | 21.8845 | 22.2248 | 22.7243 | 23.0667 | 22.6505 | 22.6919 | 22.8902 | 23.6756 | 22.9315 | 22.8877 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 80% | 57.8591 | 18.3917 | 20.6864 | 23.82 | 23.7779 | 23.8055 | 23.8912 | 24.1823 | 24.3773 | 24.5372 | 24.5607 | 24.7049 | 24.7561 | 24.7559 | 24.7229 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159
75% | 80.549 | 15.868 | 17.6159 | 20.5588 | 20.5367 | 20.5167 | 20.8357 | 21.3041 | 21.625 | 21.2349 | 21.2737 | 21.4596 | 22.1959 | 21.4982 | 21.4573 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 75% | 121.3907 | 17.2422 | 19.3935 | 22.3313 | 22.2918 | 22.3177 | 22.398 | 22.6709 | 22.8537 | 23.0036 | 23.0257 | 23.1609 | 23.2088 | 23.2087 | 23.1777 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712
70% | 192.1075 | 14.8101 | 16.4415 | 19.1882 | 19.1676 | 19.149 | 19.4467 | 19.8838 | 20.1833 | 19.8192 | 19.8554 | 20.029 | 20.7161 | 20.065 | 20.0268 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 70% | 273.4128 | 16.0927 | 18.1006 | 20.8425 | 20.8057 | 20.8299 | 20.9048 | 21.1595 | 21.3301 | 21.47 | 21.4906 | 21.6168 | 21.6616 | 21.6614 | 21.6325 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264
65% | 403.1231 | 13.7523 | 15.2671 | 17.8176 | 17.7984 | 17.7812 | 18.0576 | 18.4635 | 18.7417 | 18.4036 | 18.4372 | 18.5983 | 19.2364 | 18.6318 | 18.5963 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 65% | 529.43 | 14.9432 | 16.8077 | 19.3538 | 19.3196 | 19.342 | 19.4116 | 19.6481 | 19.8065 | 19.9365 | 19.9556 | 20.0728 | 20.1143 | 20.1142 | 20.0874 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817
60% | 739.3112 | 12.6944 | 14.0927 | 16.447 | 16.4293 | 16.4134 | 16.6686 | 17.0432 | 17.3 | 16.9879 | 17.0189 | 17.1677 | 17.7567 | 17.1986 | 17.1658 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 60% | 918.9392 | 13.7938 | 15.5148 | 17.865 | 17.8334 | 17.8542 | 17.9184 | 18.1367 | 18.2829 | 18.4029 | 18.4205 | 18.5287 | 18.567 | 18.5669 | 18.5422 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369
55% | 1204.8314 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 55% | 1454.0417 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
50% | 1783.0446 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 50% | 2105.2406 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
45% | 2370.3337 | 9.5208 | 10.5695 | 12.3353 | 12.322 | 12.31 | 12.5014 | 12.7824 | 12.975 | 12.7409 | 12.7642 | 12.8758 | 13.3175 | 12.8989 | 12.8744 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 45% | 2758.3303 | 10.3453 | 11.6361 | 13.3988 | 13.3751 | 13.3906 | 13.4388 | 13.6025 | 13.7122 | 13.8022 | 13.8154 | 13.8965 | 13.9253 | 13.9252 | 13.9066 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027
40% | 2864.2163 | 8.4629 | 9.3951 | 10.9647 | 10.9529 | 10.9423 | 11.1124 | 11.3622 | 11.5333 | 11.3253 | 11.346 | 11.4451 | 11.8378 | 11.4657 | 11.4439 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 40% | 3348.2666 | 9.1958 | 10.3432 | 11.91 | 11.889 | 11.9028 | 11.9456 | 12.0911 | 12.1886 | 12.2686 | 12.2804 | 12.3525 | 12.378 | 12.378 | 12.3615 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579
35% | 3297.9707 | 7.4051 | 8.2208 | 9.5941 | 9.5838 | 9.5745 | 9.7233 | 9.9419 | 10.0917 | 9.9096 | 9.9277 | 10.0145 | 10.3581 | 10.0325 | 10.0134 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 35% | 3816.434 | 8.0464 | 9.0503 | 10.4213 | 10.4028 | 10.4149 | 10.4524 | 10.5798 | 10.6651 | 10.735 | 10.7453 | 10.8084 | 10.8308 | 10.8307 | 10.8163 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132
30% | 3579.7031 | 6.3472 | 7.0464 | 8.2235 | 8.2147 | 8.2067 | 8.3343 | 8.5216 | 8.65 | 8.494 | 8.5095 | 8.5838 | 8.8783 | 8.5993 | 8.5829 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 30% | 4067.1569 | 6.8969 | 7.7574 | 8.9325 | 8.9167 | 8.9271 | 8.9592 | 9.0684 | 9.1415 | 9.2014 | 9.2103 | 9.2644 | 9.2835 | 9.2835 | 9.2711 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685
25% | 3796.3913 | 5.2893 | 5.872 | 6.8529 | 6.8456 | 6.8389 | 6.9452 | 7.1014 | 7.2083 | 7.0783 | 7.0912 | 7.1532 | 7.3986 | 7.1661 | 7.1524 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 25% | 4236.9526 | 5.7474 | 6.4645 | 7.4438 | 7.4306 | 7.4392 | 7.466 | 7.557 | 7.6179 | 7.6679 | 7.6752 | 7.7203 | 7.7363 | 7.7362 | 7.7259 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237
20% | 3975.6411 | 4.2315 | 4.6976 | 5.4823 | 5.4764 | 5.4711 | 5.5562 | 5.6811 | 5.7667 | 5.6626 | 5.673 | 5.7226 | 5.9189 | 5.7329 | 5.7219 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 20% | 4332.6282 | 4.5979 | 5.1716 | 5.955 | 5.9445 | 5.9514 | 5.9728 | 6.0456 | 6.0943 | 6.1343 | 6.1402 | 6.1762 | 6.189 | 6.189 | 6.1807 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179
15% | 4117.4527 | 3.1736 | 3.5232 | 4.1118 | 4.1073 | 4.1033 | 4.1671 | 4.2608 | 4.325 | 4.247 | 4.2547 | 4.2919 | 4.4392 | 4.2996 | 4.2915 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 15% | 4361.7469 | 3.4484 | 3.8787 | 4.4663 | 4.4584 | 4.4635 | 4.4796 | 4.5342 | 4.5707 | 4.6007 | 4.6051 | 4.6322 | 4.6418 | 4.6417 | 4.6355 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342
10% | 4224.8514 | 2.1157 | 2.3488 | 2.7412 | 2.7382 | 2.7356 | 2.7781 | 2.8405 | 2.8833 | 2.8313 | 2.8365 | 2.8613 | 2.9594 | 2.8664 | 2.861 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 10% | 4375.7389 | 2.299 | 2.5858 | 2.9775 | 2.9722 | 2.9757 | 2.9864 | 3.0228 | 3.0472 | 3.0671 | 3.0701 | 3.0881 | 3.0945 | 3.0945 | 3.0904 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895
5% | 4310.3165 | 1.0579 | 1.1744 | 1.3706 | 1.3691 | 1.3678 | 1.389 | 1.4203 | 1.4417 | 1.4157 | 1.4182 | 1.4306 | 1.4797 | 1.4332 | 1.4305 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 5% | 4378.0079 | 1.1495 | 1.2929 | 1.4888 | 1.4861 | 1.4878 | 1.4932 | 1.5114 | 1.5236 | 1.5336 | 1.535 | 1.5441 | 1.5473 | 1.5472 | 1.5452 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447
9.992e-14% | 4382.5459 | 2.114e-14 | 2.3469e-14 | 2.739e-14 | 2.736e-14 | 2.7334e-14 | 2.7759e-14 | 2.8383e-14 | 2.881e-14 | 2.8291e-14 | 2.8342e-14 | 2.859e-14 | 2.9571e-14 | 2.8641e-14 | 2.8587e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 9.992e-14% | 4379.1424 | 2.2971e-14 | 2.5837e-14 | 2.9751e-14 | 2.9699e-14 | 2.9733e-14 | 2.984e-14 | 3.0204e-14 | 3.0447e-14 | 3.0647e-14 | 3.0676e-14 | 3.0857e-14 | 3.092e-14 | 3.092e-14 | 3.0879e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 100% | 0 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
99% | 0.2972 | 18.3313 | 21.3091 | 25.3398 | 25.6966 | 25.9353 | 26.2707 | 27.0352 | 27.6355 | 28.1693 | 28.3565 | 28.5704 | 28.2714 | 28.4291 | 29.1704 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 99% | 0.2972 | 20.2885 | 23.2751 | 27.3384 | 27.6647 | 27.894 | 28.1301 | 29.0405 | 29.5727 | 30.117 | 30.3646 | 30.4948 | 30.0432 | 30.279 | 31.1838 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581
98% | 0.8916 | 18.1461 | 21.0938 | 25.0839 | 25.4371 | 25.6733 | 26.0054 | 26.7622 | 27.3564 | 27.8847 | 28.0701 | 28.2819 | 27.9858 | 28.1419 | 28.8757 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 98% | 0.8916 | 20.0836 | 23.04 | 27.0623 | 27.3852 | 27.6122 | 27.8459 | 28.7472 | 29.274 | 29.8128 | 30.0579 | 30.1868 | 29.7397 | 29.9731 | 30.8688 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474
97% | 1.7832 | 17.9609 | 20.8786 | 24.8279 | 25.1775 | 25.4113 | 25.74 | 26.4891 | 27.0772 | 27.6002 | 27.7837 | 27.9933 | 27.7002 | 27.8548 | 28.5811 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 97% | 2.0804 | 19.8787 | 22.8049 | 26.7861 | 27.1058 | 27.3305 | 27.5618 | 28.4539 | 28.9753 | 29.5086 | 29.7512 | 29.8787 | 29.4363 | 29.6673 | 30.5538 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367
95% | 4.458 | 17.5906 | 20.4481 | 24.316 | 24.6584 | 24.8874 | 25.2093 | 25.9429 | 26.5189 | 27.0311 | 27.2108 | 27.4161 | 27.1291 | 27.2804 | 27.9918 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 95% | 4.1608 | 19.4688 | 22.3347 | 26.2339 | 26.5469 | 26.767 | 26.9935 | 27.8672 | 28.3779 | 28.9002 | 29.1378 | 29.2627 | 28.8293 | 29.0556 | 29.9239 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154
90% | 15.1571 | 16.6648 | 19.3719 | 23.0362 | 23.3606 | 23.5775 | 23.8825 | 24.5775 | 25.1232 | 25.6084 | 25.7787 | 25.9731 | 25.7012 | 25.8446 | 26.5185 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 90% | 11.5907 | 18.4441 | 21.1592 | 24.8531 | 25.1497 | 25.3582 | 25.5728 | 26.4005 | 26.8843 | 27.3791 | 27.6042 | 27.7225 | 27.312 | 27.5264 | 28.3489 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619
85% | 39.5274 | 15.739 | 18.2957 | 21.7564 | 22.0628 | 22.2676 | 22.5557 | 23.2121 | 23.7275 | 24.1857 | 24.3465 | 24.5302 | 24.2734 | 24.4088 | 25.0453 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 85% | 32.6918 | 17.4195 | 19.9837 | 23.4724 | 23.7525 | 23.9494 | 24.1521 | 24.9338 | 25.3907 | 25.8581 | 26.0707 | 26.1824 | 25.7947 | 25.9971 | 26.774 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085
80% | 110.5579 | 14.8131 | 17.2195 | 20.4766 | 20.765 | 20.9578 | 21.2289 | 21.8467 | 22.3317 | 22.7631 | 22.9144 | 23.0872 | 22.8455 | 22.973 | 23.572 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 80% | 84.1072 | 16.3948 | 18.8082 | 22.0917 | 22.3553 | 22.5406 | 22.7314 | 23.4671 | 23.8972 | 24.337 | 24.5371 | 24.6422 | 24.2773 | 24.4679 | 25.199 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855
75% | 244.2972 | 13.8873 | 16.1432 | 19.1968 | 19.4671 | 19.6479 | 19.9021 | 20.4812 | 20.936 | 21.3404 | 21.4822 | 21.6443 | 21.4177 | 21.5372 | 22.0988 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 75% | 202.095 | 15.3701 | 17.6327 | 20.7109 | 20.9581 | 21.1318 | 21.3107 | 22.0004 | 22.4036 | 22.8159 | 23.0035 | 23.1021 | 22.76 | 22.9386 | 23.6241 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016
70% | 444.0146 | 12.9615 | 15.067 | 17.9171 | 18.1693 | 18.3381 | 18.5753 | 19.1158 | 19.5403 | 19.9177 | 20.0501 | 20.2013 | 19.9899 | 20.1014 | 20.6255 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 70% | 388.1413 | 14.3454 | 16.4572 | 19.3302 | 19.5609 | 19.723 | 19.89 | 20.5337 | 20.91 | 21.2949 | 21.47 | 21.562 | 21.2427 | 21.4094 | 22.0492 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482
65% | 770.3386 | 12.0357 | 13.9908 | 16.6373 | 16.8715 | 17.0282 | 17.2485 | 17.7504 | 18.1445 | 18.495 | 18.6179 | 18.7584 | 18.562 | 18.6656 | 19.1523 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 65% | 669.8855 | 13.3208 | 15.2817 | 17.9495 | 18.1637 | 18.3142 | 18.4692 | 19.067 | 19.4164 | 19.7738 | 19.9364 | 20.0218 | 19.7253 | 19.8801 | 20.4742 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947
60% | 1209.3009 | 11.1099 | 12.9146 | 15.3575 | 15.5737 | 15.7183 | 15.9217 | 16.385 | 16.7488 | 17.0723 | 17.1858 | 17.3154 | 17.1342 | 17.2297 | 17.679 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 60% | 1104.687 | 12.2961 | 14.1061 | 16.5688 | 16.7665 | 16.9054 | 17.0485 | 17.6003 | 17.9229 | 18.2528 | 18.4028 | 18.4817 | 18.208 | 18.3509 | 18.8993 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413
55% | 1757.6322 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 55% | 1631.62 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
50% | 2378.4799 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 50% | 2253.9537 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
45% | 3003.7856 | 8.3324 | 9.6859 | 11.5181 | 11.6803 | 11.7888 | 11.9412 | 12.2887 | 12.5616 | 12.8042 | 12.8893 | 12.9866 | 12.8506 | 12.9223 | 13.2593 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 45% | 2892.3362 | 9.2221 | 10.5796 | 12.4266 | 12.5749 | 12.6791 | 12.7864 | 13.2002 | 13.4422 | 13.6896 | 13.8021 | 13.8613 | 13.656 | 13.7632 | 14.1745 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981
40% | 3548.2533 | 7.4066 | 8.6097 | 10.2383 | 10.3825 | 10.4789 | 10.6144 | 10.9233 | 11.1659 | 11.3815 | 11.4572 | 11.5436 | 11.4228 | 11.4865 | 11.786 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 40% | 3473.3593 | 8.1974 | 9.4041 | 11.0458 | 11.1776 | 11.2703 | 11.3657 | 11.7336 | 11.9486 | 12.1685 | 12.2685 | 12.3211 | 12.1387 | 12.2339 | 12.5995 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275
35% | 3927.7759 | 6.4808 | 7.5335 | 8.9585 | 9.0847 | 9.169 | 9.2876 | 9.5579 | 9.7701 | 9.9588 | 10.025 | 10.1007 | 9.9949 | 10.0507 | 10.3128 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 35% | 3882.8989 | 7.1727 | 8.2286 | 9.6651 | 9.7804 | 9.8615 | 9.945 | 10.2669 | 10.455 | 10.6474 | 10.735 | 10.781 | 10.6213 | 10.7047 | 11.0246 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741
30% | 4135.8149 | 5.5549 | 6.4573 | 7.6787 | 7.7869 | 7.8592 | 7.9608 | 8.1925 | 8.3744 | 8.5361 | 8.5929 | 8.6577 | 8.5671 | 8.6149 | 8.8395 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 30% | 4127.1961 | 6.148 | 7.0531 | 8.2844 | 8.3832 | 8.4527 | 8.5243 | 8.8002 | 8.9614 | 9.1264 | 9.2014 | 9.2408 | 9.104 | 9.1755 | 9.4496 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206
25% | 4252.0195 | 4.6291 | 5.3811 | 6.3989 | 6.489 | 6.5493 | 6.634 | 6.8271 | 6.9787 | 7.1135 | 7.1607 | 7.2148 | 7.1392 | 7.1791 | 7.3663 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 25% | 4245.1839 | 5.1234 | 5.8776 | 6.9036 | 6.986 | 7.0439 | 7.1036 | 7.3335 | 7.4679 | 7.6053 | 7.6678 | 7.7007 | 7.5867 | 7.6462 | 7.8747 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672
20% | 4325.4275 | 3.7033 | 4.3049 | 5.1192 | 5.1912 | 5.2394 | 5.3072 | 5.4617 | 5.5829 | 5.6908 | 5.7286 | 5.7718 | 5.7114 | 5.7432 | 5.893 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 20% | 4322.1583 | 4.0987 | 4.702 | 5.5229 | 5.5888 | 5.6351 | 5.6828 | 5.8668 | 5.9743 | 6.0843 | 6.1343 | 6.1606 | 6.0693 | 6.117 | 6.2998 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138
15% | 4360.497 | 2.7775 | 3.2286 | 3.8394 | 3.8934 | 3.9296 | 3.9804 | 4.0962 | 4.1872 | 4.2681 | 4.2964 | 4.3289 | 4.2835 | 4.3074 | 4.4198 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 15% | 4354.2558 | 3.074 | 3.5265 | 4.1422 | 4.1916 | 4.2264 | 4.2621 | 4.4001 | 4.4807 | 4.5632 | 4.6007 | 4.6204 | 4.552 | 4.5877 | 4.7248 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603
10% | 4373.8709 | 1.8516 | 2.1524 | 2.5596 | 2.5956 | 2.6197 | 2.6536 | 2.7308 | 2.7915 | 2.8454 | 2.8643 | 2.8859 | 2.8557 | 2.8716 | 2.9465 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 10% | 4366.1437 | 2.0493 | 2.351 | 2.7615 | 2.7944 | 2.8176 | 2.8414 | 2.9334 | 2.9871 | 3.0421 | 3.0671 | 3.0803 | 3.0347 | 3.0585 | 3.1499 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069
5% | 4381.8952 | 0.92582 | 1.0762 | 1.2798 | 1.2978 | 1.3099 | 1.3268 | 1.3654 | 1.3957 | 1.4227 | 1.4321 | 1.443 | 1.4278 | 1.4358 | 1.4733 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 5% | 4374.4653 | 1.0247 | 1.1755 | 1.3807 | 1.3972 | 1.4088 | 1.4207 | 1.4667 | 1.4936 | 1.5211 | 1.5336 | 1.5401 | 1.5173 | 1.5292 | 1.5749 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534
9.992e-14% | 4391.7028 | 1.8502e-14 | 2.1507e-14 | 2.5575e-14 | 2.5935e-14 | 2.6176e-14 | 2.6515e-14 | 2.7286e-14 | 2.7892e-14 | 2.8431e-14 | 2.862e-14 | 2.8836e-14 | 2.8534e-14 | 2.8693e-14 | 2.9441e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 9.992e-14% | 4375.9513 | 2.0477e-14 | 2.3491e-14 | 2.7593e-14 | 2.7922e-14 | 2.8153e-14 | 2.8392e-14 | 2.931e-14 | 2.9848e-14 | 3.0397e-14 | 3.0647e-14 | 3.0778e-14 | 3.0322e-14 | 3.056e-14 | 3.1474e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 100% | 0 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
99% | 0.37816 | 20.9458 | 23.253 | 27.1376 | 27.1084 | 27.0821 | 27.5032 | 28.1214 | 28.545 | 28.0301 | 28.0813 | 28.3267 | 29.2985 | 28.3777 | 28.3236 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 99% | 1.1345 | 22.7597 | 25.5995 | 29.4773 | 29.4252 | 29.4594 | 29.5654 | 29.9256 | 30.1669 | 30.3648 | 30.3939 | 30.5724 | 30.6356 | 30.6355 | 30.5946 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859
98% | 0.37816 | 20.7342 | 23.0181 | 26.8635 | 26.8346 | 26.8085 | 27.2253 | 27.8373 | 28.2567 | 27.7469 | 27.7976 | 28.0405 | 29.0026 | 28.091 | 28.0375 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 98% | 1.8908 | 22.5298 | 25.3409 | 29.1795 | 29.128 | 29.1618 | 29.2667 | 29.6233 | 29.8621 | 30.058 | 30.0869 | 30.2636 | 30.3262 | 30.326 | 30.2856 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277
97% | 0.75633 | 20.5226 | 22.7832 | 26.5894 | 26.5608 | 26.535 | 26.9475 | 27.5532 | 27.9683 | 27.4638 | 27.514 | 27.7544 | 28.7066 | 27.8044 | 27.7514 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 97% | 2.269 | 22.2999 | 25.0823 | 28.8818 | 28.8307 | 28.8642 | 28.9681 | 29.321 | 29.5574 | 29.7513 | 29.7799 | 29.9547 | 30.0167 | 30.0166 | 29.9765 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968
95% | 0.75633 | 20.0995 | 22.3135 | 26.0411 | 26.0131 | 25.9879 | 26.3919 | 26.9851 | 27.3917 | 26.8975 | 26.9467 | 27.1822 | 28.1147 | 27.2311 | 27.1792 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 95% | 4.1598 | 21.8401 | 24.5651 | 28.2863 | 28.2363 | 28.2691 | 28.3708 | 28.7165 | 28.948 | 29.1379 | 29.1659 | 29.3371 | 29.3978 | 29.3977 | 29.3585 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501
90% | 3.7816 | 19.0416 | 21.1391 | 24.6705 | 24.644 | 24.6201 | 25.0029 | 25.5649 | 25.95 | 25.4819 | 25.5284 | 25.7515 | 26.635 | 25.7979 | 25.7487 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 90% | 15.5047 | 20.6906 | 23.2722 | 26.7975 | 26.7502 | 26.7812 | 26.8776 | 27.2051 | 27.4244 | 27.6043 | 27.6308 | 27.7931 | 27.8506 | 27.8504 | 27.8133 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054
85% | 13.6139 | 17.9837 | 19.9647 | 23.2999 | 23.2749 | 23.2523 | 23.6138 | 24.1446 | 24.5083 | 24.0662 | 24.1102 | 24.3209 | 25.1553 | 24.3647 | 24.3182 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 85% | 31.3876 | 19.5412 | 21.9793 | 25.3088 | 25.2641 | 25.2934 | 25.3844 | 25.6937 | 25.9008 | 26.0708 | 26.0958 | 26.249 | 26.3033 | 26.3032 | 26.2681 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606
80% | 35.1693 | 16.9259 | 18.7903 | 21.9294 | 21.9058 | 21.8845 | 22.2248 | 22.7243 | 23.0667 | 22.6505 | 22.6919 | 22.8902 | 23.6756 | 22.9315 | 22.8877 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 80% | 57.8591 | 18.3917 | 20.6864 | 23.82 | 23.7779 | 23.8055 | 23.8912 | 24.1823 | 24.3773 | 24.5372 | 24.5607 | 24.7049 | 24.7561 | 24.7559 | 24.7229 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159
75% | 80.549 | 15.868 | 17.6159 | 20.5588 | 20.5367 | 20.5167 | 20.8357 | 21.3041 | 21.625 | 21.2349 | 21.2737 | 21.4596 | 22.1959 | 21.4982 | 21.4573 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 75% | 121.3907 | 17.2422 | 19.3935 | 22.3313 | 22.2918 | 22.3177 | 22.398 | 22.6709 | 22.8537 | 23.0036 | 23.0257 | 23.1609 | 23.2088 | 23.2087 | 23.1777 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712
70% | 192.1075 | 14.8101 | 16.4415 | 19.1882 | 19.1676 | 19.149 | 19.4467 | 19.8838 | 20.1833 | 19.8192 | 19.8554 | 20.029 | 20.7161 | 20.065 | 20.0268 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 70% | 273.4128 | 16.0927 | 18.1006 | 20.8425 | 20.8057 | 20.8299 | 20.9048 | 21.1595 | 21.3301 | 21.47 | 21.4906 | 21.6168 | 21.6616 | 21.6614 | 21.6325 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264
65% | 403.1231 | 13.7523 | 15.2671 | 17.8176 | 17.7984 | 17.7812 | 18.0576 | 18.4635 | 18.7417 | 18.4036 | 18.4372 | 18.5983 | 19.2364 | 18.6318 | 18.5963 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 65% | 529.43 | 14.9432 | 16.8077 | 19.3538 | 19.3196 | 19.342 | 19.4116 | 19.6481 | 19.8065 | 19.9365 | 19.9556 | 20.0728 | 20.1143 | 20.1142 | 20.0874 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817
60% | 739.3112 | 12.6944 | 14.0927 | 16.447 | 16.4293 | 16.4134 | 16.6686 | 17.0432 | 17.3 | 16.9879 | 17.0189 | 17.1677 | 17.7567 | 17.1986 | 17.1658 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 60% | 918.9392 | 13.7938 | 15.5148 | 17.865 | 17.8334 | 17.8542 | 17.9184 | 18.1367 | 18.2829 | 18.4029 | 18.4205 | 18.5287 | 18.567 | 18.5669 | 18.5422 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369
55% | 1204.8314 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 55% | 1454.0417 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
50% | 1783.0446 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 50% | 2105.2406 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
45% | 2370.3337 | 9.5208 | 10.5695 | 12.3353 | 12.322 | 12.31 | 12.5014 | 12.7824 | 12.975 | 12.7409 | 12.7642 | 12.8758 | 13.3175 | 12.8989 | 12.8744 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 45% | 2758.3303 | 10.3453 | 11.6361 | 13.3988 | 13.3751 | 13.3906 | 13.4388 | 13.6025 | 13.7122 | 13.8022 | 13.8154 | 13.8965 | 13.9253 | 13.9252 | 13.9066 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027
40% | 2864.2163 | 8.4629 | 9.3951 | 10.9647 | 10.9529 | 10.9423 | 11.1124 | 11.3622 | 11.5333 | 11.3253 | 11.346 | 11.4451 | 11.8378 | 11.4657 | 11.4439 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 40% | 3348.2666 | 9.1958 | 10.3432 | 11.91 | 11.889 | 11.9028 | 11.9456 | 12.0911 | 12.1886 | 12.2686 | 12.2804 | 12.3525 | 12.378 | 12.378 | 12.3615 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579
35% | 3297.9707 | 7.4051 | 8.2208 | 9.5941 | 9.5838 | 9.5745 | 9.7233 | 9.9419 | 10.0917 | 9.9096 | 9.9277 | 10.0145 | 10.3581 | 10.0325 | 10.0134 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 35% | 3816.434 | 8.0464 | 9.0503 | 10.4213 | 10.4028 | 10.4149 | 10.4524 | 10.5798 | 10.6651 | 10.735 | 10.7453 | 10.8084 | 10.8308 | 10.8307 | 10.8163 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132
30% | 3579.7031 | 6.3472 | 7.0464 | 8.2235 | 8.2147 | 8.2067 | 8.3343 | 8.5216 | 8.65 | 8.494 | 8.5095 | 8.5838 | 8.8783 | 8.5993 | 8.5829 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 30% | 4067.1569 | 6.8969 | 7.7574 | 8.9325 | 8.9167 | 8.9271 | 8.9592 | 9.0684 | 9.1415 | 9.2014 | 9.2103 | 9.2644 | 9.2835 | 9.2835 | 9.2711 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685
25% | 3796.3913 | 5.2893 | 5.872 | 6.8529 | 6.8456 | 6.8389 | 6.9452 | 7.1014 | 7.2083 | 7.0783 | 7.0912 | 7.1532 | 7.3986 | 7.1661 | 7.1524 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 25% | 4236.9526 | 5.7474 | 6.4645 | 7.4438 | 7.4306 | 7.4392 | 7.466 | 7.557 | 7.6179 | 7.6679 | 7.6752 | 7.7203 | 7.7363 | 7.7362 | 7.7259 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237
20% | 3975.6411 | 4.2315 | 4.6976 | 5.4823 | 5.4764 | 5.4711 | 5.5562 | 5.6811 | 5.7667 | 5.6626 | 5.673 | 5.7226 | 5.9189 | 5.7329 | 5.7219 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 20% | 4332.6282 | 4.5979 | 5.1716 | 5.955 | 5.9445 | 5.9514 | 5.9728 | 6.0456 | 6.0943 | 6.1343 | 6.1402 | 6.1762 | 6.189 | 6.189 | 6.1807 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179
15% | 4117.4527 | 3.1736 | 3.5232 | 4.1118 | 4.1073 | 4.1033 | 4.1671 | 4.2608 | 4.325 | 4.247 | 4.2547 | 4.2919 | 4.4392 | 4.2996 | 4.2915 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 15% | 4361.7469 | 3.4484 | 3.8787 | 4.4663 | 4.4584 | 4.4635 | 4.4796 | 4.5342 | 4.5707 | 4.6007 | 4.6051 | 4.6322 | 4.6418 | 4.6417 | 4.6355 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342
10% | 4224.8514 | 2.1157 | 2.3488 | 2.7412 | 2.7382 | 2.7356 | 2.7781 | 2.8405 | 2.8833 | 2.8313 | 2.8365 | 2.8613 | 2.9594 | 2.8664 | 2.861 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 10% | 4375.7389 | 2.299 | 2.5858 | 2.9775 | 2.9722 | 2.9757 | 2.9864 | 3.0228 | 3.0472 | 3.0671 | 3.0701 | 3.0881 | 3.0945 | 3.0945 | 3.0904 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895
5% | 4310.3165 | 1.0579 | 1.1744 | 1.3706 | 1.3691 | 1.3678 | 1.389 | 1.4203 | 1.4417 | 1.4157 | 1.4182 | 1.4306 | 1.4797 | 1.4332 | 1.4305 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 5% | 4378.0079 | 1.1495 | 1.2929 | 1.4888 | 1.4861 | 1.4878 | 1.4932 | 1.5114 | 1.5236 | 1.5336 | 1.535 | 1.5441 | 1.5473 | 1.5472 | 1.5452 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447
9.992e-14% | 4382.5459 | 2.114e-14 | 2.3469e-14 | 2.739e-14 | 2.736e-14 | 2.7334e-14 | 2.7759e-14 | 2.8383e-14 | 2.881e-14 | 2.8291e-14 | 2.8342e-14 | 2.859e-14 | 2.9571e-14 | 2.8641e-14 | 2.8587e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 9.992e-14% | 4379.1424 | 2.2971e-14 | 2.5837e-14 | 2.9751e-14 | 2.9699e-14 | 2.9733e-14 | 2.984e-14 | 3.0204e-14 | 3.0447e-14 | 3.0647e-14 | 3.0676e-14 | 3.0857e-14 | 3.092e-14 | 3.092e-14 | 3.0879e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 100% | 0 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
99% | 0.2972 | 18.3313 | 21.3091 | 25.3398 | 25.6966 | 25.9353 | 26.2707 | 27.0352 | 27.6355 | 28.1693 | 28.3565 | 28.5704 | 28.2714 | 28.4291 | 29.1704 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 99% | 0.2972 | 20.2885 | 23.2751 | 27.3384 | 27.6647 | 27.894 | 28.1301 | 29.0405 | 29.5727 | 30.117 | 30.3646 | 30.4948 | 30.0432 | 30.279 | 31.1838 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581
98% | 0.8916 | 18.1461 | 21.0938 | 25.0839 | 25.4371 | 25.6733 | 26.0054 | 26.7622 | 27.3564 | 27.8847 | 28.0701 | 28.2819 | 27.9858 | 28.1419 | 28.8757 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 98% | 0.8916 | 20.0836 | 23.04 | 27.0623 | 27.3852 | 27.6122 | 27.8459 | 28.7472 | 29.274 | 29.8128 | 30.0579 | 30.1868 | 29.7397 | 29.9731 | 30.8688 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474
97% | 1.7832 | 17.9609 | 20.8786 | 24.8279 | 25.1775 | 25.4113 | 25.74 | 26.4891 | 27.0772 | 27.6002 | 27.7837 | 27.9933 | 27.7002 | 27.8548 | 28.5811 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 97% | 2.0804 | 19.8787 | 22.8049 | 26.7861 | 27.1058 | 27.3305 | 27.5618 | 28.4539 | 28.9753 | 29.5086 | 29.7512 | 29.8787 | 29.4363 | 29.6673 | 30.5538 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367
95% | 4.458 | 17.5906 | 20.4481 | 24.316 | 24.6584 | 24.8874 | 25.2093 | 25.9429 | 26.5189 | 27.0311 | 27.2108 | 27.4161 | 27.1291 | 27.2804 | 27.9918 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 95% | 4.1608 | 19.4688 | 22.3347 | 26.2339 | 26.5469 | 26.767 | 26.9935 | 27.8672 | 28.3779 | 28.9002 | 29.1378 | 29.2627 | 28.8293 | 29.0556 | 29.9239 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154
90% | 15.1571 | 16.6648 | 19.3719 | 23.0362 | 23.3606 | 23.5775 | 23.8825 | 24.5775 | 25.1232 | 25.6084 | 25.7787 | 25.9731 | 25.7012 | 25.8446 | 26.5185 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 90% | 11.5907 | 18.4441 | 21.1592 | 24.8531 | 25.1497 | 25.3582 | 25.5728 | 26.4005 | 26.8843 | 27.3791 | 27.6042 | 27.7225 | 27.312 | 27.5264 | 28.3489 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619
85% | 39.5274 | 15.739 | 18.2957 | 21.7564 | 22.0628 | 22.2676 | 22.5557 | 23.2121 | 23.7275 | 24.1857 | 24.3465 | 24.5302 | 24.2734 | 24.4088 | 25.0453 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 85% | 32.6918 | 17.4195 | 19.9837 | 23.4724 | 23.7525 | 23.9494 | 24.1521 | 24.9338 | 25.3907 | 25.8581 | 26.0707 | 26.1824 | 25.7947 | 25.9971 | 26.774 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085
80% | 110.5579 | 14.8131 | 17.2195 | 20.4766 | 20.765 | 20.9578 | 21.2289 | 21.8467 | 22.3317 | 22.7631 | 22.9144 | 23.0872 | 22.8455 | 22.973 | 23.572 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 80% | 84.1072 | 16.3948 | 18.8082 | 22.0917 | 22.3553 | 22.5406 | 22.7314 | 23.4671 | 23.8972 | 24.337 | 24.5371 | 24.6422 | 24.2773 | 24.4679 | 25.199 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855
75% | 244.2972 | 13.8873 | 16.1432 | 19.1968 | 19.4671 | 19.6479 | 19.9021 | 20.4812 | 20.936 | 21.3404 | 21.4822 | 21.6443 | 21.4177 | 21.5372 | 22.0988 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 75% | 202.095 | 15.3701 | 17.6327 | 20.7109 | 20.9581 | 21.1318 | 21.3107 | 22.0004 | 22.4036 | 22.8159 | 23.0035 | 23.1021 | 22.76 | 22.9386 | 23.6241 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016
70% | 444.0146 | 12.9615 | 15.067 | 17.9171 | 18.1693 | 18.3381 | 18.5753 | 19.1158 | 19.5403 | 19.9177 | 20.0501 | 20.2013 | 19.9899 | 20.1014 | 20.6255 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 70% | 388.1413 | 14.3454 | 16.4572 | 19.3302 | 19.5609 | 19.723 | 19.89 | 20.5337 | 20.91 | 21.2949 | 21.47 | 21.562 | 21.2427 | 21.4094 | 22.0492 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482
65% | 770.3386 | 12.0357 | 13.9908 | 16.6373 | 16.8715 | 17.0282 | 17.2485 | 17.7504 | 18.1445 | 18.495 | 18.6179 | 18.7584 | 18.562 | 18.6656 | 19.1523 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 65% | 669.8855 | 13.3208 | 15.2817 | 17.9495 | 18.1637 | 18.3142 | 18.4692 | 19.067 | 19.4164 | 19.7738 | 19.9364 | 20.0218 | 19.7253 | 19.8801 | 20.4742 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947
60% | 1209.3009 | 11.1099 | 12.9146 | 15.3575 | 15.5737 | 15.7183 | 15.9217 | 16.385 | 16.7488 | 17.0723 | 17.1858 | 17.3154 | 17.1342 | 17.2297 | 17.679 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 60% | 1104.687 | 12.2961 | 14.1061 | 16.5688 | 16.7665 | 16.9054 | 17.0485 | 17.6003 | 17.9229 | 18.2528 | 18.4028 | 18.4817 | 18.208 | 18.3509 | 18.8993 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413
55% | 1757.6322 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 55% | 1631.62 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
50% | 2378.4799 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 50% | 2253.9537 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
45% | 3003.7856 | 8.3324 | 9.6859 | 11.5181 | 11.6803 | 11.7888 | 11.9412 | 12.2887 | 12.5616 | 12.8042 | 12.8893 | 12.9866 | 12.8506 | 12.9223 | 13.2593 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 45% | 2892.3362 | 9.2221 | 10.5796 | 12.4266 | 12.5749 | 12.6791 | 12.7864 | 13.2002 | 13.4422 | 13.6896 | 13.8021 | 13.8613 | 13.656 | 13.7632 | 14.1745 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981
40% | 3548.2533 | 7.4066 | 8.6097 | 10.2383 | 10.3825 | 10.4789 | 10.6144 | 10.9233 | 11.1659 | 11.3815 | 11.4572 | 11.5436 | 11.4228 | 11.4865 | 11.786 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 40% | 3473.3593 | 8.1974 | 9.4041 | 11.0458 | 11.1776 | 11.2703 | 11.3657 | 11.7336 | 11.9486 | 12.1685 | 12.2685 | 12.3211 | 12.1387 | 12.2339 | 12.5995 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275
35% | 3927.7759 | 6.4808 | 7.5335 | 8.9585 | 9.0847 | 9.169 | 9.2876 | 9.5579 | 9.7701 | 9.9588 | 10.025 | 10.1007 | 9.9949 | 10.0507 | 10.3128 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 35% | 3882.8989 | 7.1727 | 8.2286 | 9.6651 | 9.7804 | 9.8615 | 9.945 | 10.2669 | 10.455 | 10.6474 | 10.735 | 10.781 | 10.6213 | 10.7047 | 11.0246 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741
30% | 4135.8149 | 5.5549 | 6.4573 | 7.6787 | 7.7869 | 7.8592 | 7.9608 | 8.1925 | 8.3744 | 8.5361 | 8.5929 | 8.6577 | 8.5671 | 8.6149 | 8.8395 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 30% | 4127.1961 | 6.148 | 7.0531 | 8.2844 | 8.3832 | 8.4527 | 8.5243 | 8.8002 | 8.9614 | 9.1264 | 9.2014 | 9.2408 | 9.104 | 9.1755 | 9.4496 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206
25% | 4252.0195 | 4.6291 | 5.3811 | 6.3989 | 6.489 | 6.5493 | 6.634 | 6.8271 | 6.9787 | 7.1135 | 7.1607 | 7.2148 | 7.1392 | 7.1791 | 7.3663 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 25% | 4245.1839 | 5.1234 | 5.8776 | 6.9036 | 6.986 | 7.0439 | 7.1036 | 7.3335 | 7.4679 | 7.6053 | 7.6678 | 7.7007 | 7.5867 | 7.6462 | 7.8747 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672
20% | 4325.4275 | 3.7033 | 4.3049 | 5.1192 | 5.1912 | 5.2394 | 5.3072 | 5.4617 | 5.5829 | 5.6908 | 5.7286 | 5.7718 | 5.7114 | 5.7432 | 5.893 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 20% | 4322.1583 | 4.0987 | 4.702 | 5.5229 | 5.5888 | 5.6351 | 5.6828 | 5.8668 | 5.9743 | 6.0843 | 6.1343 | 6.1606 | 6.0693 | 6.117 | 6.2998 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138
15% | 4360.497 | 2.7775 | 3.2286 | 3.8394 | 3.8934 | 3.9296 | 3.9804 | 4.0962 | 4.1872 | 4.2681 | 4.2964 | 4.3289 | 4.2835 | 4.3074 | 4.4198 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 15% | 4354.2558 | 3.074 | 3.5265 | 4.1422 | 4.1916 | 4.2264 | 4.2621 | 4.4001 | 4.4807 | 4.5632 | 4.6007 | 4.6204 | 4.552 | 4.5877 | 4.7248 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603
10% | 4373.8709 | 1.8516 | 2.1524 | 2.5596 | 2.5956 | 2.6197 | 2.6536 | 2.7308 | 2.7915 | 2.8454 | 2.8643 | 2.8859 | 2.8557 | 2.8716 | 2.9465 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 10% | 4366.1437 | 2.0493 | 2.351 | 2.7615 | 2.7944 | 2.8176 | 2.8414 | 2.9334 | 2.9871 | 3.0421 | 3.0671 | 3.0803 | 3.0347 | 3.0585 | 3.1499 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069
5% | 4381.8952 | 0.92582 | 1.0762 | 1.2798 | 1.2978 | 1.3099 | 1.3268 | 1.3654 | 1.3957 | 1.4227 | 1.4321 | 1.443 | 1.4278 | 1.4358 | 1.4733 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 5% | 4374.4653 | 1.0247 | 1.1755 | 1.3807 | 1.3972 | 1.4088 | 1.4207 | 1.4667 | 1.4936 | 1.5211 | 1.5336 | 1.5401 | 1.5173 | 1.5292 | 1.5749 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534
9.992e-14% | 4391.7028 | 1.8502e-14 | 2.1507e-14 | 2.5575e-14 | 2.5935e-14 | 2.6176e-14 | 2.6515e-14 | 2.7286e-14 | 2.7892e-14 | 2.8431e-14 | 2.862e-14 | 2.8836e-14 | 2.8534e-14 | 2.8693e-14 | 2.9441e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 9.992e-14% | 4375.9513 | 2.0477e-14 | 2.3491e-14 | 2.7593e-14 | 2.7922e-14 | 2.8153e-14 | 2.8392e-14 | 2.931e-14 | 2.9848e-14 | 3.0397e-14 | 3.0647e-14 | 3.0778e-14 | 3.0322e-14 | 3.056e-14 | 3.1474e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 100% | 0 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
99% | 0.37816 | 20.9458 | 23.253 | 27.1376 | 27.1084 | 27.0821 | 27.5032 | 28.1214 | 28.545 | 28.0301 | 28.0813 | 28.3267 | 29.2985 | 28.3777 | 28.3236 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 99% | 1.1345 | 22.7597 | 25.5995 | 29.4773 | 29.4252 | 29.4594 | 29.5654 | 29.9256 | 30.1669 | 30.3648 | 30.3939 | 30.5724 | 30.6356 | 30.6355 | 30.5946 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859
98% | 0.37816 | 20.7342 | 23.0181 | 26.8635 | 26.8346 | 26.8085 | 27.2253 | 27.8373 | 28.2567 | 27.7469 | 27.7976 | 28.0405 | 29.0026 | 28.091 | 28.0375 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 98% | 1.8908 | 22.5298 | 25.3409 | 29.1795 | 29.128 | 29.1618 | 29.2667 | 29.6233 | 29.8621 | 30.058 | 30.0869 | 30.2636 | 30.3262 | 30.326 | 30.2856 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277
97% | 0.75633 | 20.5226 | 22.7832 | 26.5894 | 26.5608 | 26.535 | 26.9475 | 27.5532 | 27.9683 | 27.4638 | 27.514 | 27.7544 | 28.7066 | 27.8044 | 27.7514 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 97% | 2.269 | 22.2999 | 25.0823 | 28.8818 | 28.8307 | 28.8642 | 28.9681 | 29.321 | 29.5574 | 29.7513 | 29.7799 | 29.9547 | 30.0167 | 30.0166 | 29.9765 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968
95% | 0.75633 | 20.0995 | 22.3135 | 26.0411 | 26.0131 | 25.9879 | 26.3919 | 26.9851 | 27.3917 | 26.8975 | 26.9467 | 27.1822 | 28.1147 | 27.2311 | 27.1792 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 95% | 4.1598 | 21.8401 | 24.5651 | 28.2863 | 28.2363 | 28.2691 | 28.3708 | 28.7165 | 28.948 | 29.1379 | 29.1659 | 29.3371 | 29.3978 | 29.3977 | 29.3585 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501
90% | 3.7816 | 19.0416 | 21.1391 | 24.6705 | 24.644 | 24.6201 | 25.0029 | 25.5649 | 25.95 | 25.4819 | 25.5284 | 25.7515 | 26.635 | 25.7979 | 25.7487 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 90% | 15.5047 | 20.6906 | 23.2722 | 26.7975 | 26.7502 | 26.7812 | 26.8776 | 27.2051 | 27.4244 | 27.6043 | 27.6308 | 27.7931 | 27.8506 | 27.8504 | 27.8133 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054
85% | 13.6139 | 17.9837 | 19.9647 | 23.2999 | 23.2749 | 23.2523 | 23.6138 | 24.1446 | 24.5083 | 24.0662 | 24.1102 | 24.3209 | 25.1553 | 24.3647 | 24.3182 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 85% | 31.3876 | 19.5412 | 21.9793 | 25.3088 | 25.2641 | 25.2934 | 25.3844 | 25.6937 | 25.9008 | 26.0708 | 26.0958 | 26.249 | 26.3033 | 26.3032 | 26.2681 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606
80% | 35.1693 | 16.9259 | 18.7903 | 21.9294 | 21.9058 | 21.8845 | 22.2248 | 22.7243 | 23.0667 | 22.6505 | 22.6919 | 22.8902 | 23.6756 | 22.9315 | 22.8877 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 80% | 57.8591 | 18.3917 | 20.6864 | 23.82 | 23.7779 | 23.8055 | 23.8912 | 24.1823 | 24.3773 | 24.5372 | 24.5607 | 24.7049 | 24.7561 | 24.7559 | 24.7229 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159
75% | 80.549 | 15.868 | 17.6159 | 20.5588 | 20.5367 | 20.5167 | 20.8357 | 21.3041 | 21.625 | 21.2349 | 21.2737 | 21.4596 | 22.1959 | 21.4982 | 21.4573 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 75% | 121.3907 | 17.2422 | 19.3935 | 22.3313 | 22.2918 | 22.3177 | 22.398 | 22.6709 | 22.8537 | 23.0036 | 23.0257 | 23.1609 | 23.2088 | 23.2087 | 23.1777 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712
70% | 192.1075 | 14.8101 | 16.4415 | 19.1882 | 19.1676 | 19.149 | 19.4467 | 19.8838 | 20.1833 | 19.8192 | 19.8554 | 20.029 | 20.7161 | 20.065 | 20.0268 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 70% | 273.4128 | 16.0927 | 18.1006 | 20.8425 | 20.8057 | 20.8299 | 20.9048 | 21.1595 | 21.3301 | 21.47 | 21.4906 | 21.6168 | 21.6616 | 21.6614 | 21.6325 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264
65% | 403.1231 | 13.7523 | 15.2671 | 17.8176 | 17.7984 | 17.7812 | 18.0576 | 18.4635 | 18.7417 | 18.4036 | 18.4372 | 18.5983 | 19.2364 | 18.6318 | 18.5963 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 65% | 529.43 | 14.9432 | 16.8077 | 19.3538 | 19.3196 | 19.342 | 19.4116 | 19.6481 | 19.8065 | 19.9365 | 19.9556 | 20.0728 | 20.1143 | 20.1142 | 20.0874 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817
60% | 739.3112 | 12.6944 | 14.0927 | 16.447 | 16.4293 | 16.4134 | 16.6686 | 17.0432 | 17.3 | 16.9879 | 17.0189 | 17.1677 | 17.7567 | 17.1986 | 17.1658 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 60% | 918.9392 | 13.7938 | 15.5148 | 17.865 | 17.8334 | 17.8542 | 17.9184 | 18.1367 | 18.2829 | 18.4029 | 18.4205 | 18.5287 | 18.567 | 18.5669 | 18.5422 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369
55% | 1204.8314 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 55% | 1454.0417 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
50% | 1783.0446 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 50% | 2105.2406 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
45% | 2370.3337 | 9.5208 | 10.5695 | 12.3353 | 12.322 | 12.31 | 12.5014 | 12.7824 | 12.975 | 12.7409 | 12.7642 | 12.8758 | 13.3175 | 12.8989 | 12.8744 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 45% | 2758.3303 | 10.3453 | 11.6361 | 13.3988 | 13.3751 | 13.3906 | 13.4388 | 13.6025 | 13.7122 | 13.8022 | 13.8154 | 13.8965 | 13.9253 | 13.9252 | 13.9066 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027
40% | 2864.2163 | 8.4629 | 9.3951 | 10.9647 | 10.9529 | 10.9423 | 11.1124 | 11.3622 | 11.5333 | 11.3253 | 11.346 | 11.4451 | 11.8378 | 11.4657 | 11.4439 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 40% | 3348.2666 | 9.1958 | 10.3432 | 11.91 | 11.889 | 11.9028 | 11.9456 | 12.0911 | 12.1886 | 12.2686 | 12.2804 | 12.3525 | 12.378 | 12.378 | 12.3615 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579
35% | 3297.9707 | 7.4051 | 8.2208 | 9.5941 | 9.5838 | 9.5745 | 9.7233 | 9.9419 | 10.0917 | 9.9096 | 9.9277 | 10.0145 | 10.3581 | 10.0325 | 10.0134 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 35% | 3816.434 | 8.0464 | 9.0503 | 10.4213 | 10.4028 | 10.4149 | 10.4524 | 10.5798 | 10.6651 | 10.735 | 10.7453 | 10.8084 | 10.8308 | 10.8307 | 10.8163 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132
30% | 3579.7031 | 6.3472 | 7.0464 | 8.2235 | 8.2147 | 8.2067 | 8.3343 | 8.5216 | 8.65 | 8.494 | 8.5095 | 8.5838 | 8.8783 | 8.5993 | 8.5829 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 30% | 4067.1569 | 6.8969 | 7.7574 | 8.9325 | 8.9167 | 8.9271 | 8.9592 | 9.0684 | 9.1415 | 9.2014 | 9.2103 | 9.2644 | 9.2835 | 9.2835 | 9.2711 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685
25% | 3796.3913 | 5.2893 | 5.872 | 6.8529 | 6.8456 | 6.8389 | 6.9452 | 7.1014 | 7.2083 | 7.0783 | 7.0912 | 7.1532 | 7.3986 | 7.1661 | 7.1524 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 25% | 4236.9526 | 5.7474 | 6.4645 | 7.4438 | 7.4306 | 7.4392 | 7.466 | 7.557 | 7.6179 | 7.6679 | 7.6752 | 7.7203 | 7.7363 | 7.7362 | 7.7259 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237
20% | 3975.6411 | 4.2315 | 4.6976 | 5.4823 | 5.4764 | 5.4711 | 5.5562 | 5.6811 | 5.7667 | 5.6626 | 5.673 | 5.7226 | 5.9189 | 5.7329 | 5.7219 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 20% | 4332.6282 | 4.5979 | 5.1716 | 5.955 | 5.9445 | 5.9514 | 5.9728 | 6.0456 | 6.0943 | 6.1343 | 6.1402 | 6.1762 | 6.189 | 6.189 | 6.1807 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179
15% | 4117.4527 | 3.1736 | 3.5232 | 4.1118 | 4.1073 | 4.1033 | 4.1671 | 4.2608 | 4.325 | 4.247 | 4.2547 | 4.2919 | 4.4392 | 4.2996 | 4.2915 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 15% | 4361.7469 | 3.4484 | 3.8787 | 4.4663 | 4.4584 | 4.4635 | 4.4796 | 4.5342 | 4.5707 | 4.6007 | 4.6051 | 4.6322 | 4.6418 | 4.6417 | 4.6355 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342
10% | 4224.8514 | 2.1157 | 2.3488 | 2.7412 | 2.7382 | 2.7356 | 2.7781 | 2.8405 | 2.8833 | 2.8313 | 2.8365 | 2.8613 | 2.9594 | 2.8664 | 2.861 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 10% | 4375.7389 | 2.299 | 2.5858 | 2.9775 | 2.9722 | 2.9757 | 2.9864 | 3.0228 | 3.0472 | 3.0671 | 3.0701 | 3.0881 | 3.0945 | 3.0945 | 3.0904 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895
5% | 4310.3165 | 1.0579 | 1.1744 | 1.3706 | 1.3691 | 1.3678 | 1.389 | 1.4203 | 1.4417 | 1.4157 | 1.4182 | 1.4306 | 1.4797 | 1.4332 | 1.4305 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 5% | 4378.0079 | 1.1495 | 1.2929 | 1.4888 | 1.4861 | 1.4878 | 1.4932 | 1.5114 | 1.5236 | 1.5336 | 1.535 | 1.5441 | 1.5473 | 1.5472 | 1.5452 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447
9.992e-14% | 4382.5459 | 2.114e-14 | 2.3469e-14 | 2.739e-14 | 2.736e-14 | 2.7334e-14 | 2.7759e-14 | 2.8383e-14 | 2.881e-14 | 2.8291e-14 | 2.8342e-14 | 2.859e-14 | 2.9571e-14 | 2.8641e-14 | 2.8587e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 9.992e-14% | 4379.1424 | 2.2971e-14 | 2.5837e-14 | 2.9751e-14 | 2.9699e-14 | 2.9733e-14 | 2.984e-14 | 3.0204e-14 | 3.0447e-14 | 3.0647e-14 | 3.0676e-14 | 3.0857e-14 | 3.092e-14 | 3.092e-14 | 3.0879e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 18.5164 | 21.5243 | 25.5958 | 25.9562 | 26.1972 | 26.5361 | 27.3083 | 27.9147 | 28.4538 | 28.6429 | 28.859 | 28.5569 | 28.7162 | 29.465 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 29.1338 | 100% | 0 | 20.4935 | 23.5102 | 27.6146 | 27.9441 | 28.1757 | 28.4142 | 29.3339 | 29.8715 | 30.4213 | 30.6714 | 30.8028 | 30.3467 | 30.5848 | 31.4988 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688 | 31.0688
99% | 0.2972 | 18.3313 | 21.3091 | 25.3398 | 25.6966 | 25.9353 | 26.2707 | 27.0352 | 27.6355 | 28.1693 | 28.3565 | 28.5704 | 28.2714 | 28.4291 | 29.1704 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 28.8425 | 99% | 0.2972 | 20.2885 | 23.2751 | 27.3384 | 27.6647 | 27.894 | 28.1301 | 29.0405 | 29.5727 | 30.117 | 30.3646 | 30.4948 | 30.0432 | 30.279 | 31.1838 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581 | 30.7581
98% | 0.8916 | 18.1461 | 21.0938 | 25.0839 | 25.4371 | 25.6733 | 26.0054 | 26.7622 | 27.3564 | 27.8847 | 28.0701 | 28.2819 | 27.9858 | 28.1419 | 28.8757 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 28.5512 | 98% | 0.8916 | 20.0836 | 23.04 | 27.0623 | 27.3852 | 27.6122 | 27.8459 | 28.7472 | 29.274 | 29.8128 | 30.0579 | 30.1868 | 29.7397 | 29.9731 | 30.8688 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474 | 30.4474
97% | 1.7832 | 17.9609 | 20.8786 | 24.8279 | 25.1775 | 25.4113 | 25.74 | 26.4891 | 27.0772 | 27.6002 | 27.7837 | 27.9933 | 27.7002 | 27.8548 | 28.5811 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 28.2598 | 97% | 2.0804 | 19.8787 | 22.8049 | 26.7861 | 27.1058 | 27.3305 | 27.5618 | 28.4539 | 28.9753 | 29.5086 | 29.7512 | 29.8787 | 29.4363 | 29.6673 | 30.5538 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367 | 30.1367
95% | 4.458 | 17.5906 | 20.4481 | 24.316 | 24.6584 | 24.8874 | 25.2093 | 25.9429 | 26.5189 | 27.0311 | 27.2108 | 27.4161 | 27.1291 | 27.2804 | 27.9918 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 27.6771 | 95% | 4.1608 | 19.4688 | 22.3347 | 26.2339 | 26.5469 | 26.767 | 26.9935 | 27.8672 | 28.3779 | 28.9002 | 29.1378 | 29.2627 | 28.8293 | 29.0556 | 29.9239 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154 | 29.5154
90% | 15.1571 | 16.6648 | 19.3719 | 23.0362 | 23.3606 | 23.5775 | 23.8825 | 24.5775 | 25.1232 | 25.6084 | 25.7787 | 25.9731 | 25.7012 | 25.8446 | 26.5185 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 26.2205 | 90% | 11.5907 | 18.4441 | 21.1592 | 24.8531 | 25.1497 | 25.3582 | 25.5728 | 26.4005 | 26.8843 | 27.3791 | 27.6042 | 27.7225 | 27.312 | 27.5264 | 28.3489 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619 | 27.9619
85% | 39.5274 | 15.739 | 18.2957 | 21.7564 | 22.0628 | 22.2676 | 22.5557 | 23.2121 | 23.7275 | 24.1857 | 24.3465 | 24.5302 | 24.2734 | 24.4088 | 25.0453 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 24.7638 | 85% | 32.6918 | 17.4195 | 19.9837 | 23.4724 | 23.7525 | 23.9494 | 24.1521 | 24.9338 | 25.3907 | 25.8581 | 26.0707 | 26.1824 | 25.7947 | 25.9971 | 26.774 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085 | 26.4085
80% | 110.5579 | 14.8131 | 17.2195 | 20.4766 | 20.765 | 20.9578 | 21.2289 | 21.8467 | 22.3317 | 22.7631 | 22.9144 | 23.0872 | 22.8455 | 22.973 | 23.572 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 23.3071 | 80% | 84.1072 | 16.3948 | 18.8082 | 22.0917 | 22.3553 | 22.5406 | 22.7314 | 23.4671 | 23.8972 | 24.337 | 24.5371 | 24.6422 | 24.2773 | 24.4679 | 25.199 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855 | 24.855
75% | 244.2972 | 13.8873 | 16.1432 | 19.1968 | 19.4671 | 19.6479 | 19.9021 | 20.4812 | 20.936 | 21.3404 | 21.4822 | 21.6443 | 21.4177 | 21.5372 | 22.0988 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 21.8504 | 75% | 202.095 | 15.3701 | 17.6327 | 20.7109 | 20.9581 | 21.1318 | 21.3107 | 22.0004 | 22.4036 | 22.8159 | 23.0035 | 23.1021 | 22.76 | 22.9386 | 23.6241 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016 | 23.3016
70% | 444.0146 | 12.9615 | 15.067 | 17.9171 | 18.1693 | 18.3381 | 18.5753 | 19.1158 | 19.5403 | 19.9177 | 20.0501 | 20.2013 | 19.9899 | 20.1014 | 20.6255 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 20.3937 | 70% | 388.1413 | 14.3454 | 16.4572 | 19.3302 | 19.5609 | 19.723 | 19.89 | 20.5337 | 20.91 | 21.2949 | 21.47 | 21.562 | 21.2427 | 21.4094 | 22.0492 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482 | 21.7482
65% | 770.3386 | 12.0357 | 13.9908 | 16.6373 | 16.8715 | 17.0282 | 17.2485 | 17.7504 | 18.1445 | 18.495 | 18.6179 | 18.7584 | 18.562 | 18.6656 | 19.1523 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 18.937 | 65% | 669.8855 | 13.3208 | 15.2817 | 17.9495 | 18.1637 | 18.3142 | 18.4692 | 19.067 | 19.4164 | 19.7738 | 19.9364 | 20.0218 | 19.7253 | 19.8801 | 20.4742 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947 | 20.1947
60% | 1209.3009 | 11.1099 | 12.9146 | 15.3575 | 15.5737 | 15.7183 | 15.9217 | 16.385 | 16.7488 | 17.0723 | 17.1858 | 17.3154 | 17.1342 | 17.2297 | 17.679 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 17.4803 | 60% | 1104.687 | 12.2961 | 14.1061 | 16.5688 | 16.7665 | 16.9054 | 17.0485 | 17.6003 | 17.9229 | 18.2528 | 18.4028 | 18.4817 | 18.208 | 18.3509 | 18.8993 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413 | 18.6413
55% | 1757.6322 | 10.184 | 11.8384 | 14.0777 | 14.2759 | 14.4085 | 14.5949 | 15.0196 | 15.3531 | 15.6496 | 15.7536 | 15.8725 | 15.7063 | 15.7939 | 16.2058 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 16.0236 | 55% | 1631.62 | 11.2714 | 12.9306 | 15.188 | 15.3693 | 15.4967 | 15.6278 | 16.1336 | 16.4293 | 16.7317 | 16.8692 | 16.9415 | 16.6907 | 16.8217 | 17.3243 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878 | 17.0878
50% | 2378.4799 | 9.2582 | 10.7622 | 12.7979 | 12.9781 | 13.0986 | 13.2681 | 13.6542 | 13.9573 | 14.2269 | 14.3215 | 14.4295 | 14.2785 | 14.3581 | 14.7325 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 14.5669 | 50% | 2253.9537 | 10.2467 | 11.7551 | 13.8073 | 13.9721 | 14.0879 | 14.2071 | 14.6669 | 14.9357 | 15.2106 | 15.3357 | 15.4014 | 15.1733 | 15.2924 | 15.7494 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344 | 15.5344
45% | 3003.7856 | 8.3324 | 9.6859 | 11.5181 | 11.6803 | 11.7888 | 11.9412 | 12.2887 | 12.5616 | 12.8042 | 12.8893 | 12.9866 | 12.8506 | 12.9223 | 13.2593 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 13.1102 | 45% | 2892.3362 | 9.2221 | 10.5796 | 12.4266 | 12.5749 | 12.6791 | 12.7864 | 13.2002 | 13.4422 | 13.6896 | 13.8021 | 13.8613 | 13.656 | 13.7632 | 14.1745 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981 | 13.981
40% | 3548.2533 | 7.4066 | 8.6097 | 10.2383 | 10.3825 | 10.4789 | 10.6144 | 10.9233 | 11.1659 | 11.3815 | 11.4572 | 11.5436 | 11.4228 | 11.4865 | 11.786 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 11.6535 | 40% | 3473.3593 | 8.1974 | 9.4041 | 11.0458 | 11.1776 | 11.2703 | 11.3657 | 11.7336 | 11.9486 | 12.1685 | 12.2685 | 12.3211 | 12.1387 | 12.2339 | 12.5995 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275 | 12.4275
35% | 3927.7759 | 6.4808 | 7.5335 | 8.9585 | 9.0847 | 9.169 | 9.2876 | 9.5579 | 9.7701 | 9.9588 | 10.025 | 10.1007 | 9.9949 | 10.0507 | 10.3128 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 10.1968 | 35% | 3882.8989 | 7.1727 | 8.2286 | 9.6651 | 9.7804 | 9.8615 | 9.945 | 10.2669 | 10.455 | 10.6474 | 10.735 | 10.781 | 10.6213 | 10.7047 | 11.0246 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741 | 10.8741
30% | 4135.8149 | 5.5549 | 6.4573 | 7.6787 | 7.7869 | 7.8592 | 7.9608 | 8.1925 | 8.3744 | 8.5361 | 8.5929 | 8.6577 | 8.5671 | 8.6149 | 8.8395 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 8.7402 | 30% | 4127.1961 | 6.148 | 7.0531 | 8.2844 | 8.3832 | 8.4527 | 8.5243 | 8.8002 | 8.9614 | 9.1264 | 9.2014 | 9.2408 | 9.104 | 9.1755 | 9.4496 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206 | 9.3206
25% | 4252.0195 | 4.6291 | 5.3811 | 6.3989 | 6.489 | 6.5493 | 6.634 | 6.8271 | 6.9787 | 7.1135 | 7.1607 | 7.2148 | 7.1392 | 7.1791 | 7.3663 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 7.2835 | 25% | 4245.1839 | 5.1234 | 5.8776 | 6.9036 | 6.986 | 7.0439 | 7.1036 | 7.3335 | 7.4679 | 7.6053 | 7.6678 | 7.7007 | 7.5867 | 7.6462 | 7.8747 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672 | 7.7672
20% | 4325.4275 | 3.7033 | 4.3049 | 5.1192 | 5.1912 | 5.2394 | 5.3072 | 5.4617 | 5.5829 | 5.6908 | 5.7286 | 5.7718 | 5.7114 | 5.7432 | 5.893 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 5.8268 | 20% | 4322.1583 | 4.0987 | 4.702 | 5.5229 | 5.5888 | 5.6351 | 5.6828 | 5.8668 | 5.9743 | 6.0843 | 6.1343 | 6.1606 | 6.0693 | 6.117 | 6.2998 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138 | 6.2138
15% | 4360.497 | 2.7775 | 3.2286 | 3.8394 | 3.8934 | 3.9296 | 3.9804 | 4.0962 | 4.1872 | 4.2681 | 4.2964 | 4.3289 | 4.2835 | 4.3074 | 4.4198 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 4.3701 | 15% | 4354.2558 | 3.074 | 3.5265 | 4.1422 | 4.1916 | 4.2264 | 4.2621 | 4.4001 | 4.4807 | 4.5632 | 4.6007 | 4.6204 | 4.552 | 4.5877 | 4.7248 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603 | 4.6603
10% | 4373.8709 | 1.8516 | 2.1524 | 2.5596 | 2.5956 | 2.6197 | 2.6536 | 2.7308 | 2.7915 | 2.8454 | 2.8643 | 2.8859 | 2.8557 | 2.8716 | 2.9465 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 2.9134 | 10% | 4366.1437 | 2.0493 | 2.351 | 2.7615 | 2.7944 | 2.8176 | 2.8414 | 2.9334 | 2.9871 | 3.0421 | 3.0671 | 3.0803 | 3.0347 | 3.0585 | 3.1499 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069 | 3.1069
5% | 4381.8952 | 0.92582 | 1.0762 | 1.2798 | 1.2978 | 1.3099 | 1.3268 | 1.3654 | 1.3957 | 1.4227 | 1.4321 | 1.443 | 1.4278 | 1.4358 | 1.4733 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 1.4567 | 5% | 4374.4653 | 1.0247 | 1.1755 | 1.3807 | 1.3972 | 1.4088 | 1.4207 | 1.4667 | 1.4936 | 1.5211 | 1.5336 | 1.5401 | 1.5173 | 1.5292 | 1.5749 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534 | 1.5534
9.992e-14% | 4391.7028 | 1.8502e-14 | 2.1507e-14 | 2.5575e-14 | 2.5935e-14 | 2.6176e-14 | 2.6515e-14 | 2.7286e-14 | 2.7892e-14 | 2.8431e-14 | 2.862e-14 | 2.8836e-14 | 2.8534e-14 | 2.8693e-14 | 2.9441e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 2.9111e-14 | 9.992e-14% | 4375.9513 | 2.0477e-14 | 2.3491e-14 | 2.7593e-14 | 2.7922e-14 | 2.8153e-14 | 2.8392e-14 | 2.931e-14 | 2.9848e-14 | 3.0397e-14 | 3.0647e-14 | 3.0778e-14 | 3.0322e-14 | 3.056e-14 | 3.1474e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14 | 3.1044e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 21.1573 | 23.4879 | 27.4117 | 27.3822 | 27.3557 | 27.781 | 28.4054 | 28.8333 | 28.3132 | 28.3649 | 28.6128 | 29.5945 | 28.6643 | 28.6097 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 28.551 | 100% | 0 | 22.9896 | 25.858 | 29.775 | 29.7224 | 29.7569 | 29.864 | 30.2279 | 30.4716 | 30.6715 | 30.7009 | 30.8812 | 30.9451 | 30.9449 | 30.9036 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949 | 30.8949
99% | 0.37816 | 20.9458 | 23.253 | 27.1376 | 27.1084 | 27.0821 | 27.5032 | 28.1214 | 28.545 | 28.0301 | 28.0813 | 28.3267 | 29.2985 | 28.3777 | 28.3236 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 28.2655 | 99% | 1.1345 | 22.7597 | 25.5995 | 29.4773 | 29.4252 | 29.4594 | 29.5654 | 29.9256 | 30.1669 | 30.3648 | 30.3939 | 30.5724 | 30.6356 | 30.6355 | 30.5946 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859 | 30.5859
98% | 0.37816 | 20.7342 | 23.0181 | 26.8635 | 26.8346 | 26.8085 | 27.2253 | 27.8373 | 28.2567 | 27.7469 | 27.7976 | 28.0405 | 29.0026 | 28.091 | 28.0375 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 27.98 | 98% | 1.8908 | 22.5298 | 25.3409 | 29.1795 | 29.128 | 29.1618 | 29.2667 | 29.6233 | 29.8621 | 30.058 | 30.0869 | 30.2636 | 30.3262 | 30.326 | 30.2856 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277 | 30.277
97% | 0.75633 | 20.5226 | 22.7832 | 26.5894 | 26.5608 | 26.535 | 26.9475 | 27.5532 | 27.9683 | 27.4638 | 27.514 | 27.7544 | 28.7066 | 27.8044 | 27.7514 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 27.6945 | 97% | 2.269 | 22.2999 | 25.0823 | 28.8818 | 28.8307 | 28.8642 | 28.9681 | 29.321 | 29.5574 | 29.7513 | 29.7799 | 29.9547 | 30.0167 | 30.0166 | 29.9765 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968 | 29.968
95% | 0.75633 | 20.0995 | 22.3135 | 26.0411 | 26.0131 | 25.9879 | 26.3919 | 26.9851 | 27.3917 | 26.8975 | 26.9467 | 27.1822 | 28.1147 | 27.2311 | 27.1792 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 27.1235 | 95% | 4.1598 | 21.8401 | 24.5651 | 28.2863 | 28.2363 | 28.2691 | 28.3708 | 28.7165 | 28.948 | 29.1379 | 29.1659 | 29.3371 | 29.3978 | 29.3977 | 29.3585 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501 | 29.3501
90% | 3.7816 | 19.0416 | 21.1391 | 24.6705 | 24.644 | 24.6201 | 25.0029 | 25.5649 | 25.95 | 25.4819 | 25.5284 | 25.7515 | 26.635 | 25.7979 | 25.7487 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 25.6959 | 90% | 15.5047 | 20.6906 | 23.2722 | 26.7975 | 26.7502 | 26.7812 | 26.8776 | 27.2051 | 27.4244 | 27.6043 | 27.6308 | 27.7931 | 27.8506 | 27.8504 | 27.8133 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054 | 27.8054
85% | 13.6139 | 17.9837 | 19.9647 | 23.2999 | 23.2749 | 23.2523 | 23.6138 | 24.1446 | 24.5083 | 24.0662 | 24.1102 | 24.3209 | 25.1553 | 24.3647 | 24.3182 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 24.2684 | 85% | 31.3876 | 19.5412 | 21.9793 | 25.3088 | 25.2641 | 25.2934 | 25.3844 | 25.6937 | 25.9008 | 26.0708 | 26.0958 | 26.249 | 26.3033 | 26.3032 | 26.2681 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606 | 26.2606
80% | 35.1693 | 16.9259 | 18.7903 | 21.9294 | 21.9058 | 21.8845 | 22.2248 | 22.7243 | 23.0667 | 22.6505 | 22.6919 | 22.8902 | 23.6756 | 22.9315 | 22.8877 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 22.8408 | 80% | 57.8591 | 18.3917 | 20.6864 | 23.82 | 23.7779 | 23.8055 | 23.8912 | 24.1823 | 24.3773 | 24.5372 | 24.5607 | 24.7049 | 24.7561 | 24.7559 | 24.7229 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159 | 24.7159
75% | 80.549 | 15.868 | 17.6159 | 20.5588 | 20.5367 | 20.5167 | 20.8357 | 21.3041 | 21.625 | 21.2349 | 21.2737 | 21.4596 | 22.1959 | 21.4982 | 21.4573 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 21.4133 | 75% | 121.3907 | 17.2422 | 19.3935 | 22.3313 | 22.2918 | 22.3177 | 22.398 | 22.6709 | 22.8537 | 23.0036 | 23.0257 | 23.1609 | 23.2088 | 23.2087 | 23.1777 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712 | 23.1712
70% | 192.1075 | 14.8101 | 16.4415 | 19.1882 | 19.1676 | 19.149 | 19.4467 | 19.8838 | 20.1833 | 19.8192 | 19.8554 | 20.029 | 20.7161 | 20.065 | 20.0268 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 19.9857 | 70% | 273.4128 | 16.0927 | 18.1006 | 20.8425 | 20.8057 | 20.8299 | 20.9048 | 21.1595 | 21.3301 | 21.47 | 21.4906 | 21.6168 | 21.6616 | 21.6614 | 21.6325 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264 | 21.6264
65% | 403.1231 | 13.7523 | 15.2671 | 17.8176 | 17.7984 | 17.7812 | 18.0576 | 18.4635 | 18.7417 | 18.4036 | 18.4372 | 18.5983 | 19.2364 | 18.6318 | 18.5963 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 18.5582 | 65% | 529.43 | 14.9432 | 16.8077 | 19.3538 | 19.3196 | 19.342 | 19.4116 | 19.6481 | 19.8065 | 19.9365 | 19.9556 | 20.0728 | 20.1143 | 20.1142 | 20.0874 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817 | 20.0817
60% | 739.3112 | 12.6944 | 14.0927 | 16.447 | 16.4293 | 16.4134 | 16.6686 | 17.0432 | 17.3 | 16.9879 | 17.0189 | 17.1677 | 17.7567 | 17.1986 | 17.1658 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 17.1306 | 60% | 918.9392 | 13.7938 | 15.5148 | 17.865 | 17.8334 | 17.8542 | 17.9184 | 18.1367 | 18.2829 | 18.4029 | 18.4205 | 18.5287 | 18.567 | 18.5669 | 18.5422 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369 | 18.5369
55% | 1204.8314 | 11.6365 | 12.9183 | 15.0764 | 15.0602 | 15.0456 | 15.2795 | 15.623 | 15.8583 | 15.5723 | 15.6007 | 15.737 | 16.277 | 15.7654 | 15.7353 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 15.7031 | 55% | 1454.0417 | 12.6443 | 14.2219 | 16.3763 | 16.3473 | 16.3663 | 16.4252 | 16.6253 | 16.7594 | 16.8693 | 16.8855 | 16.9847 | 17.0198 | 17.0197 | 16.997 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922 | 16.9922
50% | 1783.0446 | 10.5787 | 11.7439 | 13.7059 | 13.6911 | 13.6778 | 13.8905 | 14.2027 | 14.4167 | 14.1566 | 14.1825 | 14.3064 | 14.7972 | 14.3322 | 14.3048 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 14.2755 | 50% | 2105.2406 | 11.4948 | 12.929 | 14.8875 | 14.8612 | 14.8785 | 14.932 | 15.1139 | 15.2358 | 15.3357 | 15.3505 | 15.4406 | 15.4725 | 15.4725 | 15.4518 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474 | 15.4474
45% | 2370.3337 | 9.5208 | 10.5695 | 12.3353 | 12.322 | 12.31 | 12.5014 | 12.7824 | 12.975 | 12.7409 | 12.7642 | 12.8758 | 13.3175 | 12.8989 | 12.8744 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 12.848 | 45% | 2758.3303 | 10.3453 | 11.6361 | 13.3988 | 13.3751 | 13.3906 | 13.4388 | 13.6025 | 13.7122 | 13.8022 | 13.8154 | 13.8965 | 13.9253 | 13.9252 | 13.9066 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027 | 13.9027
40% | 2864.2163 | 8.4629 | 9.3951 | 10.9647 | 10.9529 | 10.9423 | 11.1124 | 11.3622 | 11.5333 | 11.3253 | 11.346 | 11.4451 | 11.8378 | 11.4657 | 11.4439 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 11.4204 | 40% | 3348.2666 | 9.1958 | 10.3432 | 11.91 | 11.889 | 11.9028 | 11.9456 | 12.0911 | 12.1886 | 12.2686 | 12.2804 | 12.3525 | 12.378 | 12.378 | 12.3615 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579 | 12.3579
35% | 3297.9707 | 7.4051 | 8.2208 | 9.5941 | 9.5838 | 9.5745 | 9.7233 | 9.9419 | 10.0917 | 9.9096 | 9.9277 | 10.0145 | 10.3581 | 10.0325 | 10.0134 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 9.9929 | 35% | 3816.434 | 8.0464 | 9.0503 | 10.4213 | 10.4028 | 10.4149 | 10.4524 | 10.5798 | 10.6651 | 10.735 | 10.7453 | 10.8084 | 10.8308 | 10.8307 | 10.8163 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132 | 10.8132
30% | 3579.7031 | 6.3472 | 7.0464 | 8.2235 | 8.2147 | 8.2067 | 8.3343 | 8.5216 | 8.65 | 8.494 | 8.5095 | 8.5838 | 8.8783 | 8.5993 | 8.5829 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 8.5653 | 30% | 4067.1569 | 6.8969 | 7.7574 | 8.9325 | 8.9167 | 8.9271 | 8.9592 | 9.0684 | 9.1415 | 9.2014 | 9.2103 | 9.2644 | 9.2835 | 9.2835 | 9.2711 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685 | 9.2685
25% | 3796.3913 | 5.2893 | 5.872 | 6.8529 | 6.8456 | 6.8389 | 6.9452 | 7.1014 | 7.2083 | 7.0783 | 7.0912 | 7.1532 | 7.3986 | 7.1661 | 7.1524 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 7.1378 | 25% | 4236.9526 | 5.7474 | 6.4645 | 7.4438 | 7.4306 | 7.4392 | 7.466 | 7.557 | 7.6179 | 7.6679 | 7.6752 | 7.7203 | 7.7363 | 7.7362 | 7.7259 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237 | 7.7237
20% | 3975.6411 | 4.2315 | 4.6976 | 5.4823 | 5.4764 | 5.4711 | 5.5562 | 5.6811 | 5.7667 | 5.6626 | 5.673 | 5.7226 | 5.9189 | 5.7329 | 5.7219 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 5.7102 | 20% | 4332.6282 | 4.5979 | 5.1716 | 5.955 | 5.9445 | 5.9514 | 5.9728 | 6.0456 | 6.0943 | 6.1343 | 6.1402 | 6.1762 | 6.189 | 6.189 | 6.1807 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179 | 6.179
15% | 4117.4527 | 3.1736 | 3.5232 | 4.1118 | 4.1073 | 4.1033 | 4.1671 | 4.2608 | 4.325 | 4.247 | 4.2547 | 4.2919 | 4.4392 | 4.2996 | 4.2915 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 4.2827 | 15% | 4361.7469 | 3.4484 | 3.8787 | 4.4663 | 4.4584 | 4.4635 | 4.4796 | 4.5342 | 4.5707 | 4.6007 | 4.6051 | 4.6322 | 4.6418 | 4.6417 | 4.6355 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342 | 4.6342
10% | 4224.8514 | 2.1157 | 2.3488 | 2.7412 | 2.7382 | 2.7356 | 2.7781 | 2.8405 | 2.8833 | 2.8313 | 2.8365 | 2.8613 | 2.9594 | 2.8664 | 2.861 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 2.8551 | 10% | 4375.7389 | 2.299 | 2.5858 | 2.9775 | 2.9722 | 2.9757 | 2.9864 | 3.0228 | 3.0472 | 3.0671 | 3.0701 | 3.0881 | 3.0945 | 3.0945 | 3.0904 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895 | 3.0895
5% | 4310.3165 | 1.0579 | 1.1744 | 1.3706 | 1.3691 | 1.3678 | 1.389 | 1.4203 | 1.4417 | 1.4157 | 1.4182 | 1.4306 | 1.4797 | 1.4332 | 1.4305 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 1.4276 | 5% | 4378.0079 | 1.1495 | 1.2929 | 1.4888 | 1.4861 | 1.4878 | 1.4932 | 1.5114 | 1.5236 | 1.5336 | 1.535 | 1.5441 | 1.5473 | 1.5472 | 1.5452 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447 | 1.5447
9.992e-14% | 4382.5459 | 2.114e-14 | 2.3469e-14 | 2.739e-14 | 2.736e-14 | 2.7334e-14 | 2.7759e-14 | 2.8383e-14 | 2.881e-14 | 2.8291e-14 | 2.8342e-14 | 2.859e-14 | 2.9571e-14 | 2.8641e-14 | 2.8587e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 2.8528e-14 | 9.992e-14% | 4379.1424 | 2.2971e-14 | 2.5837e-14 | 2.9751e-14 | 2.9699e-14 | 2.9733e-14 | 2.984e-14 | 3.0204e-14 | 3.0447e-14 | 3.0647e-14 | 3.0676e-14 | 3.0857e-14 | 3.092e-14 | 3.092e-14 | 3.0879e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14 | 3.087e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 34378474.2948 | 37.17% | 18.2965
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 31576189.3656 | 34.14% | 11.7393
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 10621047.2058 | 11.48% | 3.8453
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 15925855.934 | 17.22% | 3.8307
|  | 92501566.8003 |  | 37.7119 | KW/h
|  |  |  | 37711.8651 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 1 Winter POE50 W E @ R (MWh) N 1 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49860.13 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 1 Summer POE50 W E @ R (MWh) N 1 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 14958.039 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 2 Winter POE50 W E @ R (MWh) N 1 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 2 Summer POE50 W E @ R (MWh) N 1 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 3 Winter POE50 W E @ R (MWh) N 1 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 3 Summer POE50 W E @ R (MWh) N 1 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 4 Winter POE50 W E @ R (MWh) N 1 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 4 Summer POE50 W E @ R (MWh) N 1 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 5.4755; FY26: 6.365; FY27: 7.569 |  | 6.0602 | 6.9523 | 8.166
98% | FY25: 10.841; FY26: 12.6021; FY27: 14.9859 |  | 11.9985 | 13.7648 | 16.1678
97% | FY25: 16.0964; FY26: 18.7112; FY27: 22.2506 |  | 23.7535 | 27.2501 | 32.0074
95% | FY25: 47.5464; FY26: 55.2701; FY27: 65.7248 |  | 40.9291 | 46.954 | 55.1511
90% | FY25: 183.2518; FY26: 213.0201; FY27: 253.3142 |  | 140.8459 | 161.5792 | 189.7872
85% | FY25: 394.8444; FY26: 458.9847; FY27: 545.8047 |  | 378.3806 | 434.0803 | 509.8608
80% | FY25: 1085.0654; FY26: 1261.3284; FY27: 1499.9169 |  | 869.2856 | 997.2493 | 1171.3462
75% | FY25: 1919.1914; FY26: 2230.9535; FY27: 2652.953 |  | 1873.9355 | 2149.7893 | 2525.0933
70% | FY25: 2681.0898; FY26: 3116.6181; FY27: 3706.1468 |  | 2764.2338 | 3171.1444 | 3724.7537
65% | FY25: 4078.5914; FY26: 4741.1361; FY27: 5637.9531 |  | 3897.3961 | 4471.1145 | 5251.6688
60% | FY25: 5080.0103; FY26: 5905.23; FY27: 7022.243 |  | 5569.1226 | 6388.9285 | 7504.2893
55% | FY25: 5838.0565; FY26: 6786.4167; FY27: 8070.1119 |  | 6209.2481 | 7123.2841 | 8366.8465
50% | FY25: 6035.3412; FY26: 7015.7491; FY27: 8342.8241 |  | 6695.7374 | 7681.3873 | 9022.3818
45% | FY25: 5499.7561; FY26: 6393.1612; FY27: 7602.4695 |  | 6214.2729 | 7129.0485 | 8373.6173
40% | FY25: 4284.6809; FY26: 4980.7037; FY27: 5922.8365 |  | 5060.5547 | 5805.4966 | 6819.0035
35% | FY25: 2635.2768; FY26: 3063.3631; FY27: 3642.8183 |  | 3147.3346 | 3610.6398 | 4240.975
30% | FY25: 1251.9457; FY26: 1455.3174; FY27: 1730.6002 |  | 1627.1126 | 1866.6327 | 2192.504
25% | FY25: 591.7163; FY26: 687.8374; FY27: 817.9463 |  | 664.9449 | 762.8285 | 896.0009
20% | FY25: 305.8324; FY26: 355.5132; FY27: 422.7609 |  | 354.9316 | 407.1796 | 478.2638
15% | FY25: 113.6381; FY26: 132.098; FY27: 157.0852 |  | 115.113 | 132.0582 | 155.1126
10% | FY25: 30.9547; FY26: 35.9831; FY27: 42.7896 |  | 30.4532 | 34.936 | 41.0351
5% | FY25: 11.1437; FY26: 12.9539; FY27: 15.4042 |  | 12.7903 | 14.6731 | 17.2347
9.992e-14% | FY25: 4.54; FY26: 5.2775; FY27: 6.2758 |  | 0.76133 | 0.8734 | 1.0259
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) N 1 | 29178.6863 | 33918.6034 | 40334.5296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 13575.6312 | 15574.0398 | 18292.9109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 7.9609; FY26: 8.8379; FY27: 10.3143 |  | 25.9511 | 29.1891 | 33.6107
98% | FY25: 0; FY26: 0; FY27: 0 |  | 17.1269 | 19.2638 | 22.1819
97% | FY25: 7.8009; FY26: 8.6602; FY27: 10.107 |  | 8.4765 | 9.5341 | 10.9784
95% | FY25: 0; FY26: 0; FY27: 0 |  | 41.7305 | 46.9372 | 54.0473
90% | FY25: 59.207; FY26: 65.7288; FY27: 76.7093 |  | 241.2543 | 271.3557 | 312.4609
85% | FY25: 182.0215; FY26: 202.0717; FY27: 235.8294 |  | 319.4989 | 359.363 | 413.7996
80% | FY25: 376.2445; FY26: 417.6888; FY27: 487.4672 |  | 502.0697 | 564.7133 | 650.2565
75% | FY25: 744.0881; FY26: 826.0512; FY27: 964.0499 |  | 1131.939 | 1273.1718 | 1466.0328
70% | FY25: 1711.2025; FY26: 1899.6957; FY27: 2217.0556 |  | 2533.8219 | 2849.9688 | 3281.6841
65% | FY25: 3013.5567; FY26: 3345.5074; FY27: 3904.4021 |  | 3972.8711 | 4468.5691 | 5145.4712
60% | FY25: 4445.5261; FY26: 4935.2119; FY27: 5759.6799 |  | 5596.6645 | 6294.9645 | 7248.5303
55% | FY25: 5663.2703; FY26: 6287.0936; FY27: 7337.4046 |  | 7073.5319 | 7956.1017 | 9161.2978
50% | FY25: 6422.5601; FY26: 7130.0211; FY27: 8321.1502 |  | 7859.6731 | 8840.3303 | 10179.4699
45% | FY25: 5902.0985; FY26: 6552.2294; FY27: 7646.8335 |  | 7131.7807 | 8021.6182 | 9236.7388
40% | FY25: 4440.9256; FY26: 4930.1046; FY27: 5753.7194 |  | 5764.0211 | 6483.2022 | 7465.2824
35% | FY25: 3441.4073; FY26: 3820.4869; FY27: 4458.7308 |  | 4036.1188 | 4539.7084 | 5227.3867
30% | FY25: 1937.2293; FY26: 2150.6199; FY27: 2509.8988 |  | 1873.3069 | 2107.0407 | 2426.2168
25% | FY25: 1260.7492; FY26: 1399.6239; FY27: 1633.4426 |  | 1073.4729 | 1207.4109 | 1390.3103
20% | FY25: 853.301; FY26: 947.2942; FY27: 1105.5476 |  | 494.8973 | 556.646 | 640.9671
15% | FY25: 525.0621; FY26: 582.899; FY27: 680.2772 |  | 117.1496 | 131.7664 | 151.7265
10% | FY25: 284.0336; FY26: 315.3206; FY27: 367.9975 |  | 40.209 | 45.226 | 52.0768
5% | FY25: 135.6161; FY26: 150.5545; FY27: 175.7059 |  | 3.9122 | 4.4004 | 5.0669
9.992e-14% | FY25: 38.2045; FY26: 42.4128; FY27: 49.4983 |  | 0.65204 | 0.73339 | 0.84449
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) N 1 | 28726.2817 | 31890.5531 | 37218.1341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 14808.4586 | 16656.1209 | 19179.2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 6 Winter POE50 W E @ R (MWh) N 1 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 6 Summer POE50 W E @ R (MWh) N 1 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 7 Winter POE50 W E @ R (MWh) N 1 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 7 Summer POE50 W E @ R (MWh) N 1 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 8 Winter POE50 W E @ R (MWh) N 1 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 8 Summer POE50 W E @ R (MWh) N 1 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 1 Winter POE50 W E @ R (MWh) N 2 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 1 Summer POE50 W E @ R (MWh) N 2 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 2 Winter POE50 W E @ R (MWh) N 2 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 2 Summer POE50 W E @ R (MWh) N 2 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 3 Winter POE50 W E @ R (MWh) N 2 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 3 Summer POE50 W E @ R (MWh) N 2 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 4 Winter POE50 W E @ R (MWh) N 2 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 4 Summer POE50 W E @ R (MWh) N 2 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 5 Winter POE50 W E @ R (MWh) N 2 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 5 Summer POE50 W E @ R (MWh) N 2 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 6 Winter POE50 W E @ R (MWh) N 2 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 6 Summer POE50 W E @ R (MWh) N 2 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 7 Winter POE50 W E @ R (MWh) N 2 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 7 Summer POE50 W E @ R (MWh) N 2 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 5.4755 | 6.365 | 7.569 | 7.6756 | 7.7469 | 7.8471 | 8.0754 | 8.2547 | 8.4142 | 8.4701 | 8.534 | 8.4446 | 8.4918 | 8.7132 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 | 8.6152 |  | 6.0602 | 6.9523 | 8.166 | 8.2634 | 8.3319 | 8.4024 | 8.6744 | 8.8334 | 8.9959 | 9.0699 | 9.1088 | 8.9739 | 9.0443 | 9.3146 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874 | 9.1874
98% | 10.841 | 12.6021 | 14.9859 | 15.1969 | 15.338 | 15.5364 | 15.9885 | 16.3435 | 16.6592 | 16.7699 | 16.8964 | 16.7195 | 16.8128 | 17.2512 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 | 17.0573 |  | 11.9985 | 13.7648 | 16.1678 | 16.3608 | 16.4964 | 16.636 | 17.1744 | 17.4892 | 17.8111 | 17.9575 | 18.0345 | 17.7674 | 17.9068 | 18.442 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902 | 18.1902
97% | 16.0964 | 18.7112 | 22.2506 | 22.5639 | 22.7734 | 23.068 | 23.7393 | 24.2664 | 24.7351 | 24.8995 | 25.0873 | 24.8247 | 24.9632 | 25.6141 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 | 25.3262 |  | 23.7535 | 27.2501 | 32.0074 | 32.3893 | 32.6578 | 32.9342 | 34.0002 | 34.6232 | 35.2605 | 35.5504 | 35.7027 | 35.1741 | 35.4501 | 36.5095 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011 | 36.011
95% | 47.5464 | 55.2701 | 65.7248 | 66.6502 | 67.2691 | 68.1393 | 70.1222 | 71.6792 | 73.0636 | 73.5492 | 74.1041 | 73.3284 | 73.7374 | 75.6602 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 | 74.8097 |  | 40.9291 | 46.954 | 55.1511 | 55.8093 | 56.2719 | 56.7482 | 58.5849 | 59.6585 | 60.7566 | 61.256 | 61.5186 | 60.6076 | 61.0833 | 62.9086 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498 | 62.0498
90% | 183.2518 | 213.0201 | 253.3142 | 256.8809 | 259.2665 | 262.6202 | 270.2626 | 276.2634 | 281.5992 | 283.471 | 285.6095 | 282.6197 | 284.1963 | 291.607 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 | 288.3292 |  | 140.8459 | 161.5792 | 189.7872 | 192.052 | 193.6439 | 195.2829 | 201.6035 | 205.2981 | 209.0767 | 210.7955 | 211.699 | 208.5641 | 210.2009 | 216.4824 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527 | 213.527
85% | 394.8444 | 458.9847 | 545.8047 | 553.4896 | 558.6297 | 565.8558 | 582.3225 | 595.2523 | 606.7491 | 610.7821 | 615.3899 | 608.9478 | 612.3449 | 628.3125 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 | 621.2499 |  | 378.3806 | 434.0803 | 509.8608 | 515.9451 | 520.2216 | 524.6249 | 541.6051 | 551.5305 | 561.6817 | 566.2994 | 568.7264 | 560.3047 | 564.702 | 581.577 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374 | 573.6374
80% | 1085.0654 | 1261.3284 | 1499.9169 | 1521.0358 | 1535.1611 | 1555.019 | 1600.2709 | 1635.803 | 1667.3972 | 1678.4802 | 1691.1428 | 1673.4396 | 1682.7751 | 1726.6552 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 | 1707.2465 |  | 869.2856 | 997.2493 | 1171.3462 | 1185.3242 | 1195.149 | 1205.2651 | 1244.275 | 1267.0774 | 1290.3988 | 1301.0073 | 1306.5831 | 1287.2353 | 1297.3375 | 1336.1059 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655 | 1317.8655
75% | 1919.1914 | 2230.9535 | 2652.953 | 2690.3067 | 2715.2906 | 2750.4139 | 2830.4526 | 2893.2993 | 2949.1811 | 2968.7839 | 2991.1807 | 2959.8684 | 2976.3804 | 3053.9927 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 | 3019.6639 |  | 1873.9355 | 2149.7893 | 2525.0933 | 2555.226 | 2576.4054 | 2598.2129 | 2682.3072 | 2731.4629 | 2781.7373 | 2804.6062 | 2816.6261 | 2774.9177 | 2796.6951 | 2880.2689 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477 | 2840.9477
70% | 2681.0898 | 3116.6181 | 3706.1468 | 3758.3295 | 3793.2318 | 3842.2987 | 3954.1118 | 4041.908 | 4119.9743 | 4147.3592 | 4178.6473 | 4134.9043 | 4157.9714 | 4266.395 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 | 4218.438 |  | 2764.2338 | 3171.1444 | 3724.7537 | 3769.2023 | 3800.444 | 3832.6121 | 3956.6592 | 4029.1686 | 4103.328 | 4137.062 | 4154.7924 | 4093.2685 | 4125.3923 | 4248.6716 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669 | 4190.669
65% | 4078.5914 | 4741.1361 | 5637.9531 | 5717.3357 | 5770.4306 | 5845.0733 | 6015.1682 | 6148.7276 | 6267.4855 | 6309.1447 | 6356.7414 | 6290.1978 | 6325.2885 | 6490.2271 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 | 6417.2729 |  | 3897.3961 | 4471.1145 | 5251.6688 | 5314.3386 | 5358.3873 | 5403.7424 | 5578.641 | 5680.8747 | 5785.4349 | 5832.9976 | 5857.9964 | 5771.2516 | 5816.5441 | 5990.3602 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802 | 5908.5802
60% | 5080.0103 | 5905.23 | 7022.243 | 7121.1165 | 7187.2478 | 7280.2176 | 7492.0761 | 7658.4284 | 7806.3449 | 7858.2327 | 7917.5159 | 7834.6338 | 7878.3403 | 8083.7765 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 | 7992.9097 |  | 5569.1226 | 6388.9285 | 7504.2893 | 7593.8402 | 7656.783 | 7721.5924 | 7971.511 | 8117.5962 | 8267.0058 | 8334.9698 | 8370.6914 | 8246.7388 | 8311.4588 | 8559.8306 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723 | 8442.9723
55% | 5838.0565 | 6786.4167 | 8070.1119 | 8183.7394 | 8259.739 | 8366.5818 | 8610.0541 | 8801.2297 | 8971.2186 | 9030.8492 | 9098.9787 | 9003.7287 | 9053.9572 | 9290.0489 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 | 9185.6228 |  | 6209.2481 | 7123.2841 | 8366.8465 | 8466.6906 | 8536.8682 | 8609.1269 | 8887.7717 | 9050.6481 | 9217.2312 | 9293.0071 | 9332.8346 | 9194.6346 | 9266.7937 | 9543.7138 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236 | 9413.4236
50% | 6035.3412 | 7015.7491 | 8342.8241 | 8460.2914 | 8538.8592 | 8649.3125 | 8901.0125 | 9098.6485 | 9274.3817 | 9336.0274 | 9406.4592 | 9307.9905 | 9359.9163 | 9603.9862 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 | 9496.0313 |  | 6695.7374 | 7681.3873 | 9022.3818 | 9130.0486 | 9205.7245 | 9283.6447 | 9584.121 | 9759.7587 | 9939.3934 | 10021.1063 | 10064.0543 | 9915.0264 | 9992.8391 | 10291.4556 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574 | 10150.9574
45% | 5499.7561 | 6393.1612 | 7602.4695 | 7709.5126 | 7781.1082 | 7881.7597 | 8111.1234 | 8291.2209 | 8451.3594 | 8507.5345 | 8571.7161 | 8481.9856 | 8529.3035 | 8751.7142 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 | 8653.3394 |  | 6214.2729 | 7129.0485 | 8373.6173 | 8473.5422 | 8543.7765 | 8616.0938 | 8894.964 | 9057.9723 | 9224.6901 | 9300.5273 | 9340.3871 | 9202.0753 | 9274.2928 | 9551.4369 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414 | 9421.0414
40% | 4284.6809 | 4980.7037 | 5922.8365 | 6006.2302 | 6062.008 | 6140.4224 | 6319.1122 | 6459.4203 | 6584.1789 | 6627.9431 | 6677.9449 | 6608.0388 | 6644.9026 | 6818.1756 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 | 6741.535 |  | 5060.5547 | 5805.4966 | 6819.0035 | 6900.3767 | 6957.5716 | 7016.4627 | 7243.559 | 7376.3037 | 7512.0694 | 7573.827 | 7606.2865 | 7493.6531 | 7552.463 | 7778.1536 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668 | 7671.9668
35% | 2635.2768 | 3063.3631 | 3642.8183 | 3694.1093 | 3728.4152 | 3776.6437 | 3886.5462 | 3972.8421 | 4049.5745 | 4076.4915 | 4107.2449 | 4064.2494 | 4086.9224 | 4193.4933 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 | 4146.3557 |  | 3147.3346 | 3610.6398 | 4240.975 | 4291.5838 | 4327.1553 | 4363.7817 | 4505.0207 | 4587.5793 | 4672.0167 | 4710.4259 | 4730.6136 | 4660.563 | 4697.1389 | 4837.5037 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624 | 4771.4624
30% | 1251.9457 | 1455.3174 | 1730.6002 | 1754.9671 | 1771.2649 | 1794.1768 | 1846.3884 | 1887.3852 | 1923.8386 | 1936.6261 | 1951.2361 | 1930.8102 | 1941.5815 | 1992.2103 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 | 1969.8166 |  | 1627.1126 | 1866.6327 | 2192.504 | 2218.6678 | 2237.0576 | 2255.9928 | 2329.0107 | 2371.6919 | 2415.3445 | 2435.2013 | 2445.638 | 2409.4231 | 2428.3322 | 2500.8981 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561 | 2466.7561
25% | 591.7163 | 687.8374 | 817.9463 | 829.463 | 837.166 | 847.995 | 872.6722 | 892.0488 | 909.278 | 915.3218 | 922.2271 | 912.573 | 917.664 | 941.593 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 | 931.0089 |  | 664.9449 | 762.8285 | 896.0009 | 906.6931 | 914.2084 | 921.9465 | 951.7864 | 969.2288 | 987.0681 | 995.1829 | 999.448 | 984.6482 | 992.3757 | 1022.0309 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782 | 1008.0782
20% | 305.8324 | 355.5132 | 422.7609 | 428.7134 | 432.6947 | 438.2918 | 451.0463 | 461.0612 | 469.9663 | 473.0901 | 476.6591 | 471.6694 | 474.3006 | 486.6685 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 | 481.1981 |  | 354.9316 | 407.1796 | 478.2638 | 483.9711 | 487.9825 | 492.113 | 508.0408 | 517.3511 | 526.8733 | 531.2048 | 533.4814 | 525.5816 | 529.7064 | 545.5356 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088 | 538.088
15% | 113.6381 | 132.098 | 157.0852 | 159.297 | 160.7763 | 162.8561 | 167.5953 | 171.3165 | 174.6253 | 175.7861 | 177.1122 | 175.2582 | 176.2359 | 180.8314 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 | 178.7987 |  | 115.113 | 132.0582 | 155.1126 | 156.9636 | 158.2646 | 159.6042 | 164.77 | 167.7895 | 170.8778 | 172.2826 | 173.021 | 170.4589 | 171.7967 | 176.9305 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515 | 174.515
10% | 30.9547 | 35.9831 | 42.7896 | 43.392 | 43.795 | 44.3615 | 45.6525 | 46.6661 | 47.5674 | 47.8836 | 48.2448 | 47.7398 | 48.0061 | 49.2579 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 | 48.7043 |  | 30.4532 | 34.936 | 41.0351 | 41.5248 | 41.8689 | 42.2233 | 43.5899 | 44.3888 | 45.2058 | 45.5774 | 45.7727 | 45.0949 | 45.4489 | 46.807 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168 | 46.168
5% | 11.1437 | 12.9539 | 15.4042 | 15.6211 | 15.7662 | 15.9701 | 16.4349 | 16.7998 | 17.1243 | 17.2381 | 17.3681 | 17.1863 | 17.2822 | 17.7329 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 | 17.5335 |  | 12.7903 | 14.6731 | 17.2347 | 17.4404 | 17.585 | 17.7338 | 18.3078 | 18.6433 | 18.9864 | 19.1425 | 19.2246 | 18.9399 | 19.0885 | 19.6589 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906 | 19.3906
9.992e-14% | 4.54 | 5.2775 | 6.2758 | 6.3642 | 6.4233 | 6.5064 | 6.6957 | 6.8444 | 6.9766 | 7.0229 | 7.0759 | 7.0018 | 7.0409 | 7.2245 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 | 7.1433 |  | 0.76133 | 0.8734 | 1.0259 | 1.0381 | 1.0467 | 1.0556 | 1.0897 | 1.1097 | 1.1301 | 1.1394 | 1.1443 | 1.1274 | 1.1362 | 1.1702 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542 | 1.1542
E @ R (MWh) | 41683.8376 | 48455.1478 | 57620.7565 | 58432.0591 | 58974.6973 | 59737.5572 | 61475.9543 | 62840.9521 | 64054.6758 | 64480.4393 | 64966.8852 | 64286.7988 | 64645.4312 | 66331.1302 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | 65585.5262 | E @ R (MWh) | 45252.1041 | 51913.4661 | 60976.3698 | 61704.0191 | 62215.463 | 62742.0742 | 64772.797 | 65959.8172 | 67173.8503 | 67726.0941 | 68016.3516 | 67009.1699 | 67535.055 | 69553.2084 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727 | 68603.6727
Option 8 Winter POE50 W E @ R (MWh) N 2 | 29178.6863 | 33918.6034 | 40334.5296 | 40902.4414 | 41282.2881 | 41816.29 | 43033.168 | 43988.6664 | 44838.2731 | 45136.3075 | 45476.8196 | 45000.7592 | 45251.8019 | 46431.7912 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | 45909.8684 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 13575.6312 | 15574.0398 | 18292.9109 | 18511.2057 | 18664.6389 | 18822.6223 | 19431.8391 | 19787.9451 | 20152.1551 | 20317.8282 | 20404.9055 | 20102.751 | 20260.5165 | 20865.9625 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018 | 20581.1018
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 7.9609 | 8.8379 | 10.3143 | 10.3032 | 10.2932 | 10.4532 | 10.6882 | 10.8492 | 10.6535 | 10.673 | 10.7662 | 11.1356 | 10.7856 | 10.7651 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 | 10.743 |  | 25.9511 | 29.1891 | 33.6107 | 33.5513 | 33.5902 | 33.7111 | 34.1218 | 34.3969 | 34.6226 | 34.6558 | 34.8593 | 34.9314 | 34.9312 | 34.8847 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748 | 34.8748
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17.1269 | 19.2638 | 22.1819 | 22.1427 | 22.1684 | 22.2482 | 22.5193 | 22.7008 | 22.8497 | 22.8717 | 23.006 | 23.0536 | 23.0535 | 23.0227 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162 | 23.0162
97% | 7.8009 | 8.6602 | 10.107 | 10.0961 | 10.0863 | 10.2431 | 10.4734 | 10.6311 | 10.4394 | 10.4584 | 10.5498 | 10.9118 | 10.5688 | 10.5487 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 | 10.5271 |  | 8.4765 | 9.5341 | 10.9784 | 10.959 | 10.9717 | 11.0112 | 11.1453 | 11.2352 | 11.3089 | 11.3197 | 11.3862 | 11.4098 | 11.4097 | 11.3945 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913 | 11.3913
95% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.7305 | 46.9372 | 54.0473 | 53.9518 | 54.0144 | 54.2088 | 54.8693 | 55.3117 | 55.6745 | 55.7279 | 56.0552 | 56.1711 | 56.1709 | 56.0959 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08 | 56.08
90% | 59.207 | 65.7288 | 76.7093 | 76.6268 | 76.5525 | 77.7427 | 79.4901 | 80.6876 | 79.2321 | 79.3768 | 80.0705 | 82.8176 | 80.2147 | 80.0618 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 | 79.8977 |  | 241.2543 | 271.3557 | 312.4609 | 311.9088 | 312.271 | 313.3948 | 317.213 | 319.7706 | 321.8682 | 322.1771 | 324.069 | 324.7394 | 324.7377 | 324.3046 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126 | 324.2126
85% | 182.0215 | 202.0717 | 235.8294 | 235.5758 | 235.3472 | 239.0062 | 244.3785 | 248.0599 | 243.585 | 244.03 | 246.1627 | 254.6082 | 246.6059 | 246.1358 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 | 245.6313 |  | 319.4989 | 359.363 | 413.7996 | 413.0684 | 413.5481 | 415.0363 | 420.0929 | 423.4799 | 426.2579 | 426.667 | 429.1724 | 430.0603 | 430.0581 | 429.4845 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626 | 429.3626
80% | 376.2445 | 417.6888 | 487.4672 | 486.9429 | 486.4704 | 494.0338 | 505.1384 | 512.748 | 503.4983 | 504.4181 | 508.8265 | 526.2836 | 509.7425 | 508.7708 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 | 507.7281 |  | 502.0697 | 564.7133 | 650.2565 | 649.1074 | 649.8613 | 652.1999 | 660.146 | 665.4685 | 669.8339 | 670.4767 | 674.4138 | 675.8091 | 675.8056 | 674.9042 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126 | 674.7126
75% | 744.0881 | 826.0512 | 964.0499 | 963.0131 | 962.0787 | 977.0365 | 998.9977 | 1014.0471 | 995.7542 | 997.5733 | 1006.2916 | 1040.8161 | 1008.1033 | 1006.1816 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 | 1004.1194 |  | 1131.939 | 1273.1718 | 1466.0328 | 1463.4422 | 1465.1419 | 1470.4143 | 1488.3293 | 1500.3289 | 1510.171 | 1511.6202 | 1520.4966 | 1523.6424 | 1523.6344 | 1521.6022 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703 | 1521.1703
70% | 1711.2025 | 1899.6957 | 2217.0556 | 2214.6713 | 2212.5223 | 2246.9213 | 2297.4262 | 2332.0358 | 2289.967 | 2294.1504 | 2314.2002 | 2393.5972 | 2318.3666 | 2313.9471 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 | 2309.2046 |  | 2533.8219 | 2849.9688 | 3281.6841 | 3275.8851 | 3279.6898 | 3291.492 | 3331.5942 | 3358.4552 | 3380.4864 | 3383.7306 | 3403.6001 | 3410.6418 | 3410.624 | 3406.075 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081 | 3405.1081
65% | 3013.5567 | 3345.5074 | 3904.4021 | 3900.203 | 3896.4185 | 3956.9979 | 4045.9408 | 4106.8909 | 4032.8045 | 4040.1718 | 4075.4811 | 4215.3051 | 4082.8183 | 4075.0354 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 | 4066.6834 |  | 3972.8711 | 4468.5691 | 5145.4712 | 5136.3788 | 5142.3442 | 5160.8494 | 5223.7271 | 5265.8434 | 5300.387 | 5305.4736 | 5336.6277 | 5347.6687 | 5347.6408 | 5340.5083 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922 | 5338.9922
60% | 4445.5261 | 4935.2119 | 5759.6799 | 5753.4855 | 5747.9027 | 5837.2679 | 5968.4743 | 6058.3865 | 5949.096 | 5959.964 | 6012.0514 | 6218.3165 | 6022.8751 | 6011.394 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 | 5999.0733 |  | 5596.6645 | 6294.9645 | 7248.5303 | 7235.7216 | 7244.1252 | 7270.1938 | 7358.7709 | 7418.101 | 7466.7632 | 7473.9288 | 7517.8163 | 7533.3699 | 7533.3306 | 7523.2829 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472 | 7521.1472
55% | 5663.2703 | 6287.0936 | 7337.4046 | 7329.5134 | 7322.4013 | 7436.246 | 7603.3932 | 7717.9346 | 7578.7067 | 7592.5517 | 7658.9072 | 7921.6736 | 7672.6958 | 7658.0696 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 | 7642.374 |  | 7073.5319 | 7956.1017 | 9161.2978 | 9145.1091 | 9155.7303 | 9188.6779 | 9300.6291 | 9375.6154 | 9437.1188 | 9446.1753 | 9501.6439 | 9521.3019 | 9521.2522 | 9508.5531 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538 | 9505.8538
50% | 6422.5601 | 7130.0211 | 8321.1502 | 8312.201 | 8304.1353 | 8433.2434 | 8622.8006 | 8752.6988 | 8594.8042 | 8610.5055 | 8685.7574 | 8983.7537 | 8701.3947 | 8684.8076 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 | 8667.0077 |  | 7859.6731 | 8840.3303 | 10179.4699 | 10161.4821 | 10173.2837 | 10209.8931 | 10334.2863 | 10417.6065 | 10485.9453 | 10496.0083 | 10557.6416 | 10579.4844 | 10579.4291 | 10565.3186 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195 | 10562.3195
45% | 5902.0985 | 6552.2294 | 7646.8335 | 7638.6095 | 7631.1975 | 7749.8432 | 7924.0392 | 8043.411 | 7898.3116 | 7912.7405 | 7981.8943 | 8255.742 | 7996.2644 | 7981.0214 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 | 7964.664 |  | 7131.7807 | 8021.6182 | 9236.7388 | 9220.4168 | 9231.1254 | 9264.3444 | 9377.2174 | 9452.8212 | 9514.8311 | 9523.9622 | 9579.8876 | 9599.7075 | 9599.6573 | 9586.8536 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322 | 9584.1322
40% | 4440.9256 | 4930.1046 | 5753.7194 | 5747.5314 | 5741.9544 | 5831.2271 | 5962.2977 | 6052.1168 | 5942.9395 | 5953.7962 | 6005.8297 | 6211.8814 | 6016.6422 | 6005.1729 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 | 5992.8651 |  | 5764.0211 | 6483.2022 | 7465.2824 | 7452.0907 | 7460.7456 | 7487.5937 | 7578.8196 | 7639.9238 | 7690.0412 | 7697.421 | 7742.6209 | 7758.6396 | 7758.5991 | 7748.2509 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514 | 7746.0514
35% | 3441.4073 | 3820.4869 | 4458.7308 | 4453.9356 | 4449.6138 | 4518.7939 | 4620.3645 | 4689.968 | 4605.3632 | 4613.7764 | 4654.0988 | 4813.7744 | 4662.4777 | 4653.5898 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 | 4644.052 |  | 4036.1188 | 4539.7084 | 5227.3867 | 5218.1495 | 5224.2099 | 5243.0096 | 5306.8884 | 5349.6751 | 5384.7686 | 5389.9362 | 5421.5863 | 5432.8031 | 5432.7747 | 5425.5287 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885 | 5423.9885
30% | 1937.2293 | 2150.6199 | 2509.8988 | 2507.1994 | 2504.7666 | 2543.7093 | 2600.8852 | 2640.0663 | 2592.4407 | 2597.1767 | 2619.8748 | 2709.7591 | 2624.5915 | 2619.5883 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 | 2614.2194 |  | 1873.3069 | 2107.0407 | 2426.2168 | 2421.9295 | 2424.7423 | 2433.468 | 2463.1164 | 2482.9752 | 2499.2634 | 2501.6618 | 2516.3518 | 2521.5579 | 2521.5447 | 2518.1816 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667 | 2517.4667
25% | 1260.7492 | 1399.6239 | 1633.4426 | 1631.6859 | 1630.1026 | 1655.4466 | 1692.6566 | 1718.1557 | 1687.161 | 1690.2431 | 1705.0151 | 1763.5118 | 1708.0847 | 1704.8286 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 | 1701.3345 |  | 1073.4729 | 1207.4109 | 1390.3103 | 1387.8535 | 1389.4654 | 1394.4655 | 1411.4551 | 1422.835 | 1432.1687 | 1433.5431 | 1441.961 | 1444.9442 | 1444.9367 | 1443.0095 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999 | 1442.5999
20% | 853.301 | 947.2942 | 1105.5476 | 1104.3586 | 1103.287 | 1120.4403 | 1145.6248 | 1162.8831 | 1141.9052 | 1143.9913 | 1153.9893 | 1193.581 | 1156.0668 | 1153.8631 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 | 1151.4982 |  | 494.8973 | 556.646 | 640.9671 | 639.8345 | 640.5776 | 642.8828 | 650.7154 | 655.9618 | 660.2648 | 660.8985 | 664.7793 | 666.1547 | 666.1512 | 665.2627 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739 | 665.0739
15% | 525.0621 | 582.899 | 680.2772 | 679.5455 | 678.8861 | 689.4411 | 704.9379 | 715.5575 | 702.6491 | 703.9328 | 710.0848 | 734.4468 | 711.3632 | 710.0072 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 | 708.552 |  | 117.1496 | 131.7664 | 151.7265 | 151.4584 | 151.6343 | 152.18 | 154.0341 | 155.276 | 156.2946 | 156.4446 | 157.3632 | 157.6888 | 157.688 | 157.4776 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329 | 157.4329
10% | 284.0336 | 315.3206 | 367.9975 | 367.6018 | 367.2451 | 372.9548 | 381.3378 | 387.0825 | 380.0997 | 380.7941 | 384.1221 | 397.3008 | 384.8136 | 384.0801 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 | 383.2929 |  | 40.209 | 45.226 | 52.0768 | 51.9848 | 52.0452 | 52.2325 | 52.8688 | 53.2951 | 53.6447 | 53.6962 | 54.0115 | 54.1232 | 54.123 | 54.0508 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354 | 54.0354
5% | 135.6161 | 150.5545 | 175.7059 | 175.5169 | 175.3466 | 178.0728 | 182.0754 | 184.8183 | 181.4842 | 181.8158 | 183.4048 | 189.6971 | 183.735 | 183.3847 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 | 183.0089 |  | 3.9122 | 4.4004 | 5.0669 | 5.058 | 5.0639 | 5.0821 | 5.144 | 5.1855 | 5.2195 | 5.2245 | 5.2552 | 5.266 | 5.266 | 5.259 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575 | 5.2575
9.992e-14% | 38.2045 | 42.4128 | 49.4983 | 49.445 | 49.397 | 50.165 | 51.2926 | 52.0653 | 51.1261 | 51.2195 | 51.6671 | 53.4398 | 51.7601 | 51.6615 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 | 51.5556 |  | 0.65204 | 0.73339 | 0.84449 | 0.843 | 0.84398 | 0.84701 | 0.85733 | 0.86424 | 0.86991 | 0.87075 | 0.87586 | 0.87767 | 0.87767 | 0.8765 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625 | 0.87625
E @ R (MWh) | 41037.5453 | 45557.9329 | 53168.763 | 53111.5811 | 53060.0451 | 53884.9933 | 55096.1862 | 55926.1832 | 54917.301 | 55017.6258 | 55498.455 | 57402.5296 | 55598.3707 | 55492.3859 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | 55378.6516 | E @ R (MWh) | 49361.5287 | 55520.4028 | 63930.6739 | 63817.7036 | 63891.822 | 64121.7419 | 64902.9755 | 65426.2555 | 65855.4473 | 65918.6467 | 66305.7259 | 66442.9061 | 66442.5592 | 66353.9403 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043 | 66335.1043
Option 8 Summer POE50 W E @ R (MWh) N 2 | 28726.2817 | 31890.5531 | 37218.1341 | 37178.1068 | 37142.0316 | 37719.4953 | 38567.3303 | 39148.3282 | 38442.1107 | 38512.3381 | 38848.9185 | 40181.7707 | 38918.8595 | 38844.6701 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | 38765.0561 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 14808.4586 | 16656.1209 | 19179.2022 | 19145.3111 | 19167.5466 | 19236.5226 | 19470.8926 | 19627.8767 | 19756.6342 | 19775.594 | 19891.7178 | 19932.8718 | 19932.7677 | 19906.1821 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313 | 19900.5313

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-LLG-TRNFMR-9000007796 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 2 Pof | bar: FY25 to FY54
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
N-1 Risk |  | 0.07365% | 0.07365% | 0.08139% | 0.08959% | 0.09827% | 0.1074% | 0.1171% | 0.1272% | 0.1379% | 0.1491% | 0.1608% | 0.1731% | 0.1858% | 0.1992% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213% | 0.213%
N-2 Risk | bar: FY25 to FY54
N Risk |  | 99.93% | 99.93% | 99.92% | 99.91% | 99.9% | 99.89% | 99.88% | 99.87% | 99.86% | 99.85% | 99.84% | 99.83% | 99.81% | 99.8% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79% | 99.79%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 78.3708 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 1 | 78.3708 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Cost of EUE ($) - Option 1 | 2955509.8084 | 3346603.2093 | 4335448.1099 | 4799175.4855 | 5285794.6804 | 5845249.51 | 6525355.4051 | 7209696.0287 | 7845493.3227 | 8517873.6169 | 9252629.4489 | 10018865.4627 | 10673511.9721 | 11580527.6808 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089
Hours at Risk pA. (Hrs) (N) | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972 | 0.2972
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 2 | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Cost of EUE ($) - Option 2 | 2949984.38 | 3346603.2093 | 4335448.1099 | 4799175.4855 | 5285794.6804 | 5845249.51 | 6525355.4051 | 7209696.0287 | 7845493.3227 | 8517873.6169 | 9252629.4489 | 10018865.4627 | 10673511.9721 | 11580527.6808 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 3 | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Cost of EUE ($) - Option 3 | 2949984.38 | 3346603.2093 | 4335448.1099 | 4799175.4855 | 5285794.6804 | 5845249.51 | 6525355.4051 | 7209696.0287 | 7845493.3227 | 8517873.6169 | 9252629.4489 | 10018865.4627 | 10673511.9721 | 11580527.6808 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 4 | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Cost of EUE ($) - Option 4 | 2949984.38 | 3346603.2093 | 4335448.1099 | 4799175.4855 | 5285794.6804 | 5845249.51 | 6525355.4051 | 7209696.0287 | 7845493.3227 | 8517873.6169 | 9252629.4489 | 10018865.4627 | 10673511.9721 | 11580527.6808 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 78.2243 | 88.7414 | 114.9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 5 | 78.2243 | 88.7414 | 114.9624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost of EUE ($) - Option 5 | 2949984.38 | 3346603.2093 | 4335448.1099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 6 | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Cost of EUE ($) - Option 6 | 2949984.38 | 3346603.2093 | 4335448.1099 | 4799175.4855 | 5285794.6804 | 5845249.51 | 6525355.4051 | 7209696.0287 | 7845493.3227 | 8517873.6169 | 9252629.4489 | 10018865.4627 | 10673511.9721 | 11580527.6808 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 7 | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Cost of EUE ($) - Option 7 | 2949984.38 | 3346603.2093 | 4335448.1099 | 4799175.4855 | 5285794.6804 | 5845249.51 | 6525355.4051 | 7209696.0287 | 7845493.3227 | 8517873.6169 | 9252629.4489 | 10018865.4627 | 10673511.9721 | 11580527.6808 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total EUE (MWh) - Option 8 | 78.2243 | 88.7414 | 114.9624 | 127.259 | 140.1626 | 154.9976 | 173.0319 | 191.1785 | 208.0378 | 225.8672 | 245.3506 | 265.6688 | 283.028 | 307.0792 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009 | 326.3009
Cost of EUE ($) - Option 8 | 2949984.38 | 3346603.2093 | 4335448.1099 | 4799175.4855 | 5285794.6804 | 5845249.51 | 6525355.4051 | 7209696.0287 | 7845493.3227 | 8517873.6169 | 9252629.4489 | 10018865.4627 | 10673511.9721 | 11580527.6808 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089 | 12305414.0089