## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 105212961.6203 | 61.5% | 30.2784
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 59818974.1027 | 34.97% | 12.0256
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 2268426.58 | 1.326% | 0.44409
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 3766583.5488 | 2.202% | 0.4899
[5 empty] | 171066945.8518 |  | 43.238
Customer No. and Vol per Feeder | [6 empty] | 43237.9539 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 59818974.1027 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 60.6713 | E@R MWh | 60.6713
RESIDENTL | 105212961.6203 | [14 empty] | cost of EUE ($) | 2623301.6632 | cost of EUE ($M) | 2.6233
FARM | 3766583.5488
INDUSTRIAL | 2268426.58
Forecast (FCT)
Forecast | 2031
Summer POE50 | 88.4957
Summer POE10 | 97.6853
Winter POE50 | 85.2911
Winter POE10 | 89.2792
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 3.06 |  | Summer POE50 | 85.4357 |  |  | 100% | 0 | 85.4357 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 94.6253 |  |  | 99% | 0 | 84.5813 | 99% |  | 99% | 0 | 99% | 0
Embedded Generation |  |  | Winter POE50 | 82.2311 |  |  | 98% | 0.37816 | 83.727 | 98% |  | 98% | 14.7311 | 98% | 31.8241
|  |  | Winter POE10 | 86.2192 |  |  | 97% | 0.75633 | 82.8726 | 97% |  | 97% | 14.408 | 97% | 31.501
Year | 2031 | [5 empty] | 95% | 1.8908 | 81.1639 | 95% |  | 95% | 41.77 | 95% | 93.0491
Capacity | 0 | [5 empty] | 90% | 4.538 | 76.8921 | 90% |  | 90% | 89.5478 | 90% | 209.1989
[7 empty] | 85% | 9.0759 | 72.6203 | 85% |  | 85% | 134.1252 | 85% | 339.2415
Demand Mangement | [6 empty] | 80% | 27.606 | 68.3485 | 80% |  | 80% | 468.5217 | 80% | 1306.0799
[7 empty] | 75% | 57.481 | 64.0767 | 75% |  | 75% | 627.7522 | 75% | 1978.1012
Year | 2031 | [5 empty] | 70% | 106.2642 | 59.805 | 70% |  | 70% | 816.6725 | 70% | 3021.6728
Capacity | 0 | [5 empty] | 65% | 201.9397 | 55.5332 | 65% |  | 65% | 1192.9858 | 65% | 5517.5213
[7 empty] | 60% | 402.745 | 51.2614 | 60% |  | 60% | 1646.0591 | 60% | 10722.4557
LDC | [6 empty] | 55% | 655.7369 | 46.9896 | 55% |  | 55% | 993.1218 | 55% | 12428.356
[7 empty] | 50% | 981.7145 | 42.7178 | 50% |  | 50% | 122.1993 | 50% | 14621.3102
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 1622.7029 | 38.446 | 45% |  | 45% |  | 45% | 26012.5564
100% | 0% | 0 |  |  |  |  | 40% | 2442.9413 | 34.1743 | 40% |  | 40% |  | 40% | 29782.9837
99% | 0% | 0 |  |  |  |  | 35% | 3006.7842 | 29.9025 | 35% |  | 35% |  | 35% | 18064.6118
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3276.4154 | 25.6307 | 30% |  | 30% |  | 30% | 7486.7376
97% | 0.01722% | 0.75633 |  |  |  |  | 25% | 3466.632 | 21.3589 | 25% |  | 25% |  | 25% | 4469.1034
95% | 0.04305% | 1.8908 |  |  |  |  | 20% | 3713.9514 | 17.0871 | 20% |  | 20% |  | 20% | 4754.2278
90% | 0.1033% | 4.538 |  |  |  |  | 15% | 4043.3325 | 12.8153 | 15% |  | 15% |  | 15% | 4924.6563
85% | 0.2066% | 9.0759 |  |  |  |  | 10% | 4350.7801 | 8.5436 | 10% |  | 10% |  | 10% | 3283.3734
80% | 0.6286% | 27.606 |  |  |  |  | 5% | 4391.6218 | 4.2718 | 5% |  | 5% |  | 5% | 261.7006
75% | 1.309% | 57.481 |  |  |  |  | 9.992e-14% | 4391.6218 | 8.5367e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
70% | 2.419% | 106.2642 | [7 empty] | Total E@R | 0 | Total E@R | 6161.8944 | Total E@R | 149340.263
65% | 4.598% | 201.9397 | [7 empty] | Total WE@R | 0 | Total WE@R | 13.4343 | Total WE@R | 0.30019
60% | 9.17% | 402.745 |  |  |  |  | MD Weighted LDC
55% | 14.93% | 655.7369
50% | 22.35% | 981.7145 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 36.95% | 1622.7029 |  |  |  |  | 100% | 0 | 94.6253 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 55.62% | 2442.9413 |  |  |  |  | 99% | 0.75633 | 93.679
35% | 68.46% | 3006.7842 |  |  |  |  | 98% | 1.1345 | 92.7328 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 74.6% | 3276.4154 |  |  |  |  | 97% | 1.8908 | 91.7865 | 100% |  | 100% |  | 100%
25% | 78.93% | 3466.632 |  |  |  |  | 95% | 3.4035 | 89.894 | 99% | 0.72015 | 99% | 37.0239 | 99% | 71.21
20% | 84.56% | 3713.9514 |  |  |  |  | 90% | 9.0759 | 85.1628 | 98% | 0.045855 | 98% | 18.1541 | 98% | 35.2471
15% | 92.06% | 4043.3325 |  |  |  |  | 85% | 16.2611 | 80.4315 | 97% |  | 97% | 35.5926 | 97% | 69.7786
10% | 99.06% | 4350.7801 |  |  |  |  | 80% | 24.9588 | 75.7002 | 95% |  | 95% | 69.0381 | 95% | 137.4102
5% | 99.99% | 4391.6218 |  |  |  |  | 75% | 32.9003 | 70.969 | 90% |  | 90% | 240.1063 | 90% | 496.5017
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 41.9762 | 66.2377 | 85% |  | 85% | 270.14 | 85% | 594.9075
[7 empty] | 65% | 67.6914 | 61.5064 | 80% |  | 80% | 285.86 | 80% | 678.9996
[7 empty] | 60% | 98.7009 | 56.7752 | 75% |  | 75% | 223.4295 | 75% | 582.3831
[7 empty] | 55% | 153.5347 | 52.0439 | 70% |  | 70% | 212.4074 | 70% | 622.64
LDC | [6 empty] | 50% | 258.2862 | 47.3126 | 65% |  | 65% | 480.1556 | 65% | 1642.4813
[7 empty] | 45% | 488.9664 | 42.5814 | 60% |  | 60% | 432.2971 | 60% | 1833.9252
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 928.0152 | 37.8501 | 55% |  | 55% | 504.9945 | 55% | 2983.4832
100% | 0% | 0 |  |  |  |  | 35% | 1530.4309 | 33.1189 | 50% |  | 50% | 469.1066 | 50% | 5203.8747
99% | 0.01722% | 0.75633 |  |  |  |  | 30% | 2592.3162 | 28.3876 | 45% |  | 45% | 108.8071 | 45% | 10368.387
98% | 0.02583% | 1.1345 |  |  |  |  | 25% | 3659.4958 | 23.6563 | 40% |  | 40% |  | 40% | 17656.6743
97% | 0.04305% | 1.8908 |  |  |  |  | 20% | 4005.5161 | 18.9251 | 35% |  | 35% |  | 35% | 21376.4114
95% | 0.07749% | 3.4035 |  |  |  |  | 15% | 4281.1979 | 14.1938 | 30% |  | 30% |  | 30% | 32656.3934
90% | 0.2066% | 9.0759 |  |  |  |  | 10% | 4391.6218 | 9.4625 | 25% |  | 25% |  | 25% | 27770.1009
85% | 0.3702% | 16.2611 |  |  |  |  | 5% | 4391.6218 | 4.7313 | 20% |  | 20% |  | 20% | 7367.0118
80% | 0.5683% | 24.9588 |  |  |  |  | 9.992e-14% | 4391.6218 | 9.455e-14 | 15% |  | 15% |  | 15% | 4565.1319
75% | 0.7491% | 32.9003 | [7 empty] | 10% |  | 10% |  | 10% | 1306.1126
70% | 0.9557% | 41.9762 | [7 empty] | 5% |  | 5% |  | 5% | 0
65% | 1.541% | 67.6914 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
60% | 2.247% | 98.7009 | [7 empty] | Total E@R | 0.76601 | Total E@R | 3387.1128 | Total E@R | 138019.0656
55% | 3.496% | 153.5347 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0.30492 | Total WE@R | 3.1649 | Total WE@R | 0.1189
50% | 5.881% | 258.2862
45% | 11.13% | 488.9664 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 21.13% | 928.0152 |  |  |  |  | 100% | 0 | 82.2311
35% | 34.85% | 1530.4309 |  |  |  |  | 99% | 0.8916 | 81.4088 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 59.02% | 2592.3162 |  |  |  |  | 98% | 3.5664 | 80.5865
25% | 83.32% | 3659.4958 |  |  |  |  | 97% | 4.7552 | 79.7641 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 91.2% | 4005.5161 |  |  |  |  | 95% | 7.7272 | 78.1195 | 100% |  | 100% |  | 100%
15% | 97.48% | 4281.1979 |  |  |  |  | 90% | 39.2302 | 74.008 | 99% |  | 99% | 30.1537 | 99% | 72.9503
10% | 99.99% | 4391.6218 |  |  |  |  | 85% | 117.6906 | 69.8964 | 98% |  | 98% | 88.2616 | 98% | 216.6514
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 268.3703 | 65.7849 | 97% |  | 97% | 38.2498 | 97% | 95.3119
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 455.9026 | 61.6733 | 95% |  | 95% | 91.9587 | 95% | 234.614
[7 empty] | 70% | 690.9866 | 57.5618 | 90% |  | 90% | 884.0936 | 90% | 2396.2398
[7 empty] | 65% | 967.6784 | 53.4502 | 85% |  | 85% | 1879.2993 | 85% | 5645.3992
[7 empty] | 60% | 1292.8136 | 49.3386 | 80% |  | 80% | 2989.5813 | 80% | 10222.2049
LDC | [6 empty] | 55% | 1647.0743 | 45.2271 | 75% |  | 75% | 2949.7118 | 75% | 11951.2611
[7 empty] | 50% | 2104.1657 | 41.1155 | 70% |  | 70% | 2731.097 | 70% | 14015.1311
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 2736.0097 | 37.004 | 65% |  | 65% | 2076.8435 | 65% | 15358.0518
100% | 0% | 0 |  |  |  |  | 40% | 3483.7613 | 32.8924 | 60% |  | 60% | 1103.6475 | 60% | 16710.1371
99% | 0.0203% | 0.8916 |  |  |  |  | 35% | 3830.2948 | 28.7809 | 55% |  | 55% | 77.2006 | 55% | 16750.4614
98% | 0.0812% | 3.5664 |  |  |  |  | 30% | 3953.6322 | 24.6693 | 50% |  | 50% |  | 50% | 19733.2361
97% | 0.1083% | 4.7552 |  |  |  |  | 25% | 4060.9208 | 20.5578 | 45% |  | 45% |  | 45% | 24679.6811
95% | 0.1759% | 7.7272 |  |  |  |  | 20% | 4165.2375 | 16.4462 | 40% |  | 40% |  | 40% | 26132.5771
90% | 0.8932% | 39.2302 |  |  |  |  | 15% | 4270.4458 | 12.3347 | 35% |  | 35% |  | 35% | 10685.9341
85% | 2.68% | 117.6906 |  |  |  |  | 10% | 4373.8709 | 8.2231 | 30% |  | 30% |  | 30% | 3296.2044
80% | 6.11% | 268.3703 |  |  |  |  | 5% | 4391.7028 | 4.1116 | 25% |  | 25% |  | 25% | 2426.1775
75% | 10.38% | 455.9026 |  |  |  |  | 9.992e-14% | 4391.7028 | 8.2165e-14 | 20% |  | 20% |  | 20% | 1930.0667
70% | 15.73% | 690.9866 | [7 empty] | 15% |  | 15% |  | 15% | 1513.9934
65% | 22.03% | 967.6784 | [7 empty] | 10% |  | 10% |  | 10% | 1063.0946
60% | 29.44% | 1292.8136 | [7 empty] | 5% |  | 5% |  | 5% | 109.9753
55% | 37.5% | 1647.0743 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
50% | 47.91% | 2104.1657 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 14940.0983 | Total E@R | 185239.3543
45% | 62.3% | 2736.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 27.6746 | Total WE@R | 0.31636
40% | 79.32% | 3483.7613 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 87.21% | 3830.2948 |  |  |  |  | 100% | 0 | 86.2192 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 90.02% | 3953.6322 |  |  |  |  | 99% | 0.8916 | 85.357
25% | 92.46% | 4060.9208 |  |  |  |  | 98% | 3.5664 | 84.4948 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 94.84% | 4165.2375 |  |  |  |  | 97% | 4.7552 | 83.6327 | 100% |  | 100% |  | 100%
15% | 97.23% | 4270.4458 |  |  |  |  | 95% | 7.7272 | 81.9083 | 99% |  | 99% | 33.6917 | 99% | 76.4883
10% | 99.59% | 4373.8709 |  |  |  |  | 90% | 39.2302 | 77.5973 | 98% |  | 98% | 98.769 | 98% | 227.1588
5% | 99.99% | 4391.7028 |  |  |  |  | 85% | 117.6906 | 73.2863 | 97% |  | 97% | 42.8724 | 97% | 99.9345
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 268.3703 | 68.9754 | 95% |  | 95% | 103.3373 | 95% | 245.9926
[7 empty] | 75% | 455.9026 | 64.6644 | 90% |  | 90% | 1000.3096 | 90% | 2512.4557
[7 empty] | 70% | 690.9866 | 60.3535 | 85% |  | 85% | 2153.0972 | 85% | 5919.1971
[7 empty] | 65% | 967.6784 | 56.0425 | 80% |  | 80% | 3485.351 | 80% | 10717.9747
LDC | [6 empty] | 60% | 1292.8136 | 51.7315 | 75% |  | 75% | 3529.3396 | 75% | 12530.8889
[7 empty] | 55% | 1647.0743 | 47.4206 | 70% |  | 70% | 3410.821 | 70% | 14694.8551
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 2104.1657 | 43.1096 | 65% |  | 65% | 2821.6983 | 65% | 16102.9065
100% | 0% | 0 |  |  |  |  | 45% | 2736.0097 | 38.7987 | 60% |  | 60% | 1914.0774 | 60% | 17520.567
99% | 0.0203% | 0.8916 |  |  |  |  | 40% | 3483.7613 | 34.4877 | 55% |  | 55% | 572.1301 | 55% | 17562.847
98% | 0.0812% | 3.5664 |  |  |  |  | 35% | 3830.2948 | 30.1767 | 50% |  | 50% |  | 50% | 20690.2843
97% | 0.1083% | 4.7552 |  |  |  |  | 30% | 3953.6322 | 25.8658 | 45% |  | 45% |  | 45% | 25876.6283
95% | 0.1759% | 7.7272 |  |  |  |  | 25% | 4060.9208 | 21.5548 | 40% |  | 40% |  | 40% | 27399.9888
90% | 0.8932% | 39.2302 |  |  |  |  | 20% | 4165.2375 | 17.2438 | 35% |  | 35% |  | 35% | 11204.1944
85% | 2.68% | 117.6906 |  |  |  |  | 15% | 4270.4458 | 12.9329 | 30% |  | 30% |  | 30% | 3456.068
80% | 6.11% | 268.3703 |  |  |  |  | 10% | 4373.8709 | 8.6219 | 25% |  | 25% |  | 25% | 2543.8454
75% | 10.38% | 455.9026 |  |  |  |  | 5% | 4391.7028 | 4.311 | 20% |  | 20% |  | 20% | 2023.6735
70% | 15.73% | 690.9866 |  |  |  |  | 9.992e-14% | 4391.7028 | 8.615e-14 | 15% |  | 15% |  | 15% | 1587.421
65% | 22.03% | 967.6784 | [7 empty] | 10% |  | 10% |  | 10% | 1114.654
60% | 29.44% | 1292.8136 | [7 empty] | 5% |  | 5% |  | 5% | 115.309
55% | 37.5% | 1647.0743 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0 | 9.992e-14% | 0
50% | 47.91% | 2104.1657 | [7 empty] | Total E@R | 0 | Total E@R | 19165.4946 | Total E@R | 194223.3331
45% | 62.3% | 2736.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 15.215 | Total WE@R | 0.14216
40% | 79.32% | 3483.7613
35% | 87.21% | 3830.2948
30% | 90.02% | 3953.6322
25% | 92.46% | 4060.9208
20% | 94.84% | 4165.2375
15% | 97.23% | 4270.4458
10% | 99.59% | 4373.8709
5% | 99.99% | 4391.7028
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 93.2 |  |  | Year | 2031
SCR (N-1) | 45.2 |  |  | SCR (N) | 93.2
SCR (N-2) | 0 |  |  | SCR (N-1) | 45.2
WCR (N) | 93.2 |  |  | SCR (N-2) | 0
WCR (N-1) | 48 |  |  | WCR (N) | 93.2
WCR (N-2) | 0 |  |  | WCR (N-1) | 48
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.072084 | 0.12257 | 0.45496 | 1.0065 | 1.488 | 2.0019 | 2.6233 | 3.3328 | 4.1934 | 4.8807 | 5.8172 | 7.3061 | 7.7481 | 10.3894 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407
Total EUE (MWh) | 1.6672 | 2.8349 | 10.5223 | 23.2792 | 34.4131 | 46.2985 | 60.6713 | 77.0813 | 96.9845 | 112.8792 | 134.54 | 168.9751 | 179.1971 | 240.2831 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858
Residual Values
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.072084 | 0.12257 | 0.45496 | 1.0065 | 1.488 | 0.47278 | 0.72119 | 1.0067 | 1.3739 | 1.6601 | 2.0516 | 2.707 | 2.7478 | 3.8345 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197 | 5.1197
Total EUE (MWh) | 1.6672 | 2.8349 | 10.5223 | 23.2792 | 34.4131 | 10.9344 | 16.6795 | 23.2831 | 31.7752 | 38.3949 | 47.4496 | 62.6069 | 63.5511 | 88.6839 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.072084 | 0.12257 | 0.45496 | 0.14625 | 0.29101 | 0.040412 | 0.067126 | 0.11327 | 0.19136 | 0.25861 | 0.36065 | 0.57837 | 0.55263 | 0.97862 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154
Total EUE (MWh) | 1.6672 | 2.8349 | 10.5223 | 3.3825 | 6.7305 | 0.93465 | 1.5525 | 2.6197 | 4.4258 | 5.981 | 8.341 | 13.3765 | 12.7811 | 22.6334 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.072084 | 0.12257 | 0.45496 | 0.00088763 | 0.0014027 | 0.0020812 | 0.0030868 | 0.0044382 | 0.00624 | 0.007893 | 0.010271 | 0.014294 | 0.016874 | 0.025283 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069 | 0.042069
Total EUE (MWh) | 1.6672 | 2.8349 | 10.5223 | 0.020529 | 0.032441 | 0.048134 | 0.071391 | 0.10265 | 0.14432 | 0.18255 | 0.23754 | 0.33059 | 0.39026 | 0.58475 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.072084 | 0.12257 | 0.45496 | 0.14625 | 0.29101 | 0.040412 | 0.067126 | 0.11327 | 0.19136 | 0.25861 | 0.36065 | 0.57837 | 0.55263 | 0.97862 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154 | 1.6154
Total EUE (MWh) | 1.6672 | 2.8349 | 10.5223 | 3.3825 | 6.7305 | 0.93465 | 1.5525 | 2.6197 | 4.4258 | 5.981 | 8.341 | 13.3765 | 12.7811 | 22.6334 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.029117 | 0.043551 | 0.19278 | 0.51157 | 0.81343 | 1.1471 | 1.56 | 2.0077 | 2.5505 | 2.984 | 3.5556 | 4.457 | 4.6033 | 6.0753 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999 | 7.6999
Total EUE (MWh) | 0.67341 | 1.0072 | 4.4585 | 11.8314 | 18.8129 | 26.5289 | 36.0783 | 46.4327 | 58.9886 | 69.0143 | 82.2327 | 103.0801 | 106.4647 | 140.5093 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.072084 | 0.12257 | 0.45496 | 1.0065 | 1.488 | 2.0019 | 2.6233 | 3.3328 | 4.1934 | 4.8807 | 5.8172 | 7.3061 | 7.7481 | 10.3894 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407
Total EUE (MWh) | 1.6672 | 2.8349 | 10.5223 | 23.2792 | 34.4131 | 46.2985 | 60.6713 | 77.0813 | 96.9845 | 112.8792 | 134.54 | 168.9751 | 179.1971 | 240.2831 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.072084 | 0.12257 | 0.45496 | 1.0065 | 1.488 | 2.0019 | 2.6233 | 3.3328 | 4.1934 | 4.8807 | 5.8172 | 7.3061 | 7.7481 | 10.3894 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407 | 15.0407
Total EUE (MWh) | 1.6672 | 2.8349 | 10.5223 | 23.2792 | 34.4131 | 46.2985 | 60.6713 | 77.0813 | 96.9845 | 112.8792 | 134.54 | 168.9751 | 179.1971 | 240.2831 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858

## Key Model Assumption & Inputs
Select ZSS & Region | OFR | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
High | 110% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1A New PHS ZSS + Four new feeders | 1A New PHS ZSS + Four new feeders
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Option 6 - Non Network | Non Network
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N |  |  |  | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Added Capacity (MVA) Option 4 N-1 |  |  |  | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Added Capacity (MVA) Option 4 N-2 |  |  |  | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | 4.9331 | 5.3578 | 5.8974 | 6.2801 | 6.508 | 6.6905 | 6.8373 | 6.9783 | 7.1006 | 7.1597 | 7.2494 | 7.3524 | 7.4568 | 7.5899 | 7.6081
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Transfers (MVA) Option 3 |  |  |  | 14.5 | 14.5 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Transfers (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 5 |  |  |  | 14.5 | 14.5 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | OFR
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 56.9594 | 61.9907 | 68.9791 | 74.0072 | 76.6284 | 78.9811 | 80.4506 | 82.1352 | 83.4813 | 84.3346 | 86.446 | 87.894 | 88.627 | 90.0391 | 89.5765
Summer POE10 | 10 |  |  | 64.073 | 69.589 | 76.597 | 81.5678 | 84.5283 | 86.8984 | 88.8048 | 90.6365 | 92.2256 | 92.9929 | 94.1573 | 95.4952 | 96.8516 | 98.5806 | 98.8168
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 50.4065 | 56.1183 | 63.2802 | 69.3039 | 72.5305 | 74.8582 | 77.5373 | 79.5294 | 81.7407 | 82.8706 | 83.8526 | 86.3425 | 84.7668 | 88.8524 | 94.1939
Winter POE10 | 10 |  |  | 53.6497 | 59.4536 | 66.5595 | 72.8129 | 76.0509 | 78.6773 | 81.1629 | 83.2732 | 85.4834 | 86.4197 | 87.7259 | 90.1815 | 89.3155 | 92.5351 | 94.3753
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | OFR | 0 | 3.3 | 3.25 | 3.2 | 3.15 | 3.11 | 3.06 | 3.01 | 2.97 | 2.92 | 2.88 | 2.84 | 2.79 | 2.75 | 2.71
|  | PowerFactor | 1

## Load Duration Curves
Station
OFR
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.0203% | 0.8916 | 0.01722% | 0.75633 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.0812% | 3.5664 | 0.02583% | 1.1345 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.1083% | 4.7552 | 0.04305% | 1.8908 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.1759% | 7.7272 | 0.07749% | 3.4035 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.8932% | 39.2302 | 0.2066% | 9.0759 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 2.68% | 117.6906 | 0.3702% | 16.2611 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 6.11% | 268.3703 | 0.5683% | 24.9588 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 10.38% | 455.9026 | 0.7491% | 32.9003 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 15.73% | 690.9866 | 0.9557% | 41.9762 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 22.03% | 967.6784 | 1.541% | 67.6914 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 29.44% | 1292.8136 | 2.247% | 98.7009 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 37.5% | 1647.0743 | 3.496% | 153.5347 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 47.91% | 2104.1657 | 5.881% | 258.2862 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 62.3% | 2736.0097 | 11.13% | 488.9664 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 79.32% | 3483.7613 | 21.13% | 928.0152 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 87.21% | 3830.2948 | 34.85% | 1530.4309 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 90.02% | 3953.6322 | 59.02% | 2592.3162 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 92.46% | 4060.9208 | 83.32% | 3659.4958 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 94.84% | 4165.2375 | 91.2% | 4005.5161 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 97.23% | 4270.4458 | 97.48% | 4281.1979 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.59% | 4373.8709 | 99.99% | 4391.6218 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.0203% | 0.8916 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.0812% | 3.5664 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.1083% | 4.7552 | 0.01722% | 0.75633 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.1759% | 7.7272 | 0.04305% | 1.8908 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.8932% | 39.2302 | 0.1033% | 4.538 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 2.68% | 117.6906 | 0.2066% | 9.0759 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 6.11% | 268.3703 | 0.6286% | 27.606 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 10.38% | 455.9026 | 1.309% | 57.481 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 15.73% | 690.9866 | 2.419% | 106.2642 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 22.03% | 967.6784 | 4.598% | 201.9397 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 29.44% | 1292.8136 | 9.17% | 402.745 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 37.5% | 1647.0743 | 14.93% | 655.7369 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 47.91% | 2104.1657 | 22.35% | 981.7145 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 62.3% | 2736.0097 | 36.95% | 1622.7029 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 79.32% | 3483.7613 | 55.62% | 2442.9413 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 87.21% | 3830.2948 | 68.46% | 3006.7842 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 90.02% | 3953.6322 | 74.6% | 3276.4154 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 92.46% | 4060.9208 | 78.93% | 3466.632 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 94.84% | 4165.2375 | 84.56% | 3713.9514 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 97.23% | 4270.4458 | 92.06% | 4043.3325 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.59% | 4373.8709 | 99.06% | 4350.7801 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 1 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 3 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 93.2 | 93.2 | 93.2 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4
SCR N Rating (MVA) - Option 4 | 93.2 | 93.2 | 93.2 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4
Capacity Added (MVA) | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 5 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 6 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 7 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 8 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 1 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 3 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 48 | 48 | 48 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N-1 Rating (MVA) - Option 4 | 45.2 | 45.2 | 45.2 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4
Capacity Added (MVA) | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 5 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 6 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 7 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 8 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 55.4472 | 61.7301 | 69.6082 | 76.2343 | 79.7836 | 82.344 | 85.2911 | 87.4823 | 89.9147 | 91.1577 | 92.2379 | 94.9767 | 93.2434 | 97.7376 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133 | 103.6133
Maximum Demand (MVA) - P10 | 59.0147 | 65.3989 | 73.2154 | 80.0942 | 83.656 | 86.545 | 89.2792 | 91.6006 | 94.0318 | 95.0617 | 96.4984 | 99.1996 | 98.247 | 101.7886 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128 | 103.8128
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 3.3 | 3.25 | 3.2 | 3.15 | 3.11 | 3.06 | 3.01 | 2.97 | 2.92 | 2.88 | 2.84 | 2.79 | 2.75 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 79.234 | 82.2311 | 84.4723 | 86.9447 | 88.2377 | 89.3579 | 92.1367 | 90.4534 | 94.9876 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 83.435 | 86.2192 | 88.5906 | 91.0618 | 92.1417 | 93.6184 | 96.3596 | 95.457 | 99.0386 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 62.6554 | 68.1897 | 75.877 | 81.408 | 84.2913 | 86.8792 | 88.4957 | 90.3488 | 91.8294 | 92.7681 | 95.0906 | 96.6834 | 97.4897 | 99.043 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342 | 98.5342
Maximum Demand (MVA) - P10 | 70.4803 | 76.5479 | 84.2567 | 89.7246 | 92.9811 | 95.5883 | 97.6853 | 99.7002 | 101.4482 | 102.2922 | 103.573 | 105.0447 | 106.5367 | 108.4387 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985 | 108.6985
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 3.3 | 3.25 | 3.2 | 3.15 | 3.11 | 3.06 | 3.01 | 2.97 | 2.92 | 2.88 | 2.84 | 2.79 | 2.75 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 83.7692 | 85.4357 | 87.3388 | 88.8594 | 89.8481 | 92.2106 | 93.8434 | 94.6997 | 96.293 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 92.4783 | 94.6253 | 96.6902 | 98.4782 | 99.3722 | 100.693 | 102.2047 | 103.7467 | 105.6887 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885
Option 2 - 1A New PHS ZSS + Four new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 64.734 | 67.7311 | 69.9723 | 72.4447 | 73.7377 | 74.8579 | 77.6367 | 75.9534 | 80.4876 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 68.935 | 71.7192 | 74.0906 | 76.5618 | 77.6417 | 79.1184 | 81.8596 | 80.957 | 84.5386 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 69.2692 | 70.9357 | 72.8388 | 74.3594 | 75.3481 | 77.7106 | 79.3434 | 80.1997 | 81.793 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 77.9783 | 80.1253 | 82.1902 | 83.9782 | 84.8722 | 86.193 | 87.7047 | 89.2467 | 91.1887 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 14.5 | 14.5 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 55.4472 | 58.4301 | 66.3582 | 58.5343 | 62.1336 | 50.234 | 53.2311 | 55.4723 | 57.9447 | 59.2377 | 60.3579 | 63.1367 | 61.4534 | 65.9876 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 59.0147 | 62.0989 | 69.9654 | 62.3942 | 66.006 | 54.435 | 57.2192 | 59.5906 | 62.0618 | 63.1417 | 64.6184 | 67.3596 | 66.457 | 70.0386 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 62.6554 | 64.8897 | 72.627 | 63.708 | 66.6413 | 54.7692 | 56.4357 | 58.3388 | 59.8594 | 60.8481 | 63.2106 | 64.8434 | 65.6997 | 67.293 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 70.4803 | 73.2479 | 81.0067 | 72.0246 | 75.3311 | 63.4783 | 65.6253 | 67.6902 | 69.4782 | 70.3722 | 71.693 | 73.2047 | 74.7467 | 76.6887 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 79.234 | 82.2311 | 84.4723 | 86.9447 | 88.2377 | 89.3579 | 92.1367 | 90.4534 | 94.9876 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 83.435 | 86.2192 | 88.5906 | 91.0618 | 92.1417 | 93.6184 | 96.3596 | 95.457 | 99.0386 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 83.7692 | 85.4357 | 87.3388 | 88.8594 | 89.8481 | 92.2106 | 93.8434 | 94.6997 | 96.293 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 92.4783 | 94.6253 | 96.6902 | 98.4782 | 99.3722 | 100.693 | 102.2047 | 103.7467 | 105.6887 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 14.5 | 14.5 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 55.4472 | 58.4301 | 66.3582 | 58.5343 | 62.1336 | 50.234 | 53.2311 | 55.4723 | 57.9447 | 59.2377 | 60.3579 | 63.1367 | 61.4534 | 65.9876 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 59.0147 | 62.0989 | 69.9654 | 62.3942 | 66.006 | 54.435 | 57.2192 | 59.5906 | 62.0618 | 63.1417 | 64.6184 | 67.3596 | 66.457 | 70.0386 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 62.6554 | 64.8897 | 72.627 | 63.708 | 66.6413 | 54.7692 | 56.4357 | 58.3388 | 59.8594 | 60.8481 | 63.2106 | 64.8434 | 65.6997 | 67.293 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 70.4803 | 73.2479 | 81.0067 | 72.0246 | 75.3311 | 63.4783 | 65.6253 | 67.6902 | 69.4782 | 70.3722 | 71.693 | 73.2047 | 74.7467 | 76.6887 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885
Option 6 - Non Network
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 4.9331 | 5.3578 | 5.8974 | 6.2801 | 6.508 | 6.6905 | 6.8373 | 6.9783 | 7.1006 | 7.1597 | 7.2494 | 7.3524 | 7.4568 | 7.5899 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081 | 7.6081
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 50.5141 | 53.0723 | 60.4609 | 66.7542 | 70.1256 | 72.5435 | 75.3938 | 77.494 | 79.8441 | 81.078 | 82.1085 | 84.7844 | 82.9966 | 87.3977 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 54.0816 | 56.7411 | 64.068 | 70.6141 | 73.998 | 76.7445 | 79.382 | 81.6123 | 83.9612 | 84.982 | 86.3691 | 89.0073 | 88.0002 | 91.4487 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 57.7223 | 59.5319 | 66.7297 | 71.9279 | 74.6333 | 77.0787 | 78.5984 | 80.3605 | 81.7588 | 82.6884 | 84.9613 | 86.491 | 87.2429 | 88.7031 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 65.5472 | 67.8901 | 75.1093 | 80.2445 | 83.3231 | 85.7878 | 87.788 | 89.7119 | 91.3775 | 92.2125 | 93.4437 | 94.8523 | 96.2899 | 98.0987 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 79.234 | 82.2311 | 84.4723 | 86.9447 | 88.2377 | 89.3579 | 92.1367 | 90.4534 | 94.9876 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 83.435 | 86.2192 | 88.5906 | 91.0618 | 92.1417 | 93.6184 | 96.3596 | 95.457 | 99.0386 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 83.7692 | 85.4357 | 87.3388 | 88.8594 | 89.8481 | 92.2106 | 93.8434 | 94.6997 | 96.293 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 92.4783 | 94.6253 | 96.6902 | 98.4782 | 99.3722 | 100.693 | 102.2047 | 103.7467 | 105.6887 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 79.234 | 82.2311 | 84.4723 | 86.9447 | 88.2377 | 89.3579 | 92.1367 | 90.4534 | 94.9876 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 83.435 | 86.2192 | 88.5906 | 91.0618 | 92.1417 | 93.6184 | 96.3596 | 95.457 | 99.0386 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 83.7692 | 85.4357 | 87.3388 | 88.8594 | 89.8481 | 92.2106 | 93.8434 | 94.6997 | 96.293 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 92.4783 | 94.6253 | 96.6902 | 98.4782 | 99.3722 | 100.693 | 102.2047 | 103.7467 | 105.6887 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 79.234 | 82.2311 | 84.4723 | 86.9447 | 88.2377 | 89.3579 | 92.1367 | 90.4534 | 94.9876 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100% | 0 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 83.435 | 86.2192 | 88.5906 | 91.0618 | 92.1417 | 93.6184 | 96.3596 | 95.457 | 99.0386 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028
99% | 0.8916 | 54.8927 | 57.8458 | 65.6947 | 72.3039 | 75.8673 | 78.4417 | 81.4088 | 83.6276 | 86.0753 | 87.3553 | 88.4643 | 91.2154 | 89.5489 | 94.0377 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99% | 0.8916 | 58.4246 | 61.4779 | 69.2657 | 76.1252 | 79.701 | 82.6007 | 85.357 | 87.7047 | 90.1512 | 91.2203 | 92.6823 | 95.396 | 94.5025 | 98.0482 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918
98% | 3.5664 | 54.3382 | 57.2615 | 65.0311 | 71.5736 | 75.1009 | 77.6493 | 80.5865 | 82.7829 | 85.2058 | 86.4729 | 87.5707 | 90.294 | 88.6444 | 93.0878 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98% | 3.5664 | 57.8344 | 60.8569 | 68.5661 | 75.3563 | 78.8959 | 81.7663 | 84.4948 | 86.8188 | 89.2406 | 90.2989 | 91.7461 | 94.4324 | 93.5479 | 97.0578 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807
97% | 4.7552 | 53.7838 | 56.6772 | 64.3675 | 70.8433 | 74.3346 | 76.857 | 79.7641 | 81.9382 | 84.3364 | 85.5905 | 86.6771 | 89.3726 | 87.7398 | 92.138 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97% | 4.7552 | 57.2443 | 60.2359 | 67.8664 | 74.5874 | 78.0908 | 80.932 | 83.6327 | 85.9329 | 88.3299 | 89.3774 | 90.8099 | 93.4688 | 92.5933 | 96.0674 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697
95% | 7.7272 | 52.6748 | 55.5086 | 63.0403 | 69.3826 | 72.8019 | 75.2723 | 78.1195 | 80.2487 | 82.5975 | 83.8258 | 84.89 | 87.5299 | 85.9308 | 90.2382 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95% | 7.7272 | 56.064 | 58.994 | 66.4671 | 73.0495 | 76.4807 | 79.2633 | 81.9083 | 84.161 | 86.5087 | 87.5346 | 88.9375 | 91.5416 | 90.6842 | 94.0866 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477
90% | 39.2302 | 49.9025 | 52.5871 | 59.7224 | 65.7309 | 68.9702 | 71.3106 | 74.008 | 76.0251 | 78.2502 | 79.4139 | 80.4221 | 82.9231 | 81.4081 | 85.4888 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90% | 39.2302 | 53.1132 | 55.889 | 62.9689 | 69.2048 | 72.4554 | 75.0915 | 77.5973 | 79.7315 | 81.9556 | 82.9275 | 84.2566 | 86.7237 | 85.9113 | 89.1347 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925
85% | 117.6906 | 47.1301 | 49.6656 | 56.4045 | 62.0791 | 65.1386 | 67.3489 | 69.8964 | 71.8015 | 73.903 | 75.002 | 75.9542 | 78.3162 | 76.8854 | 80.7395 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85% | 117.6906 | 50.1625 | 52.7841 | 59.4706 | 65.3601 | 68.4301 | 70.9198 | 73.2863 | 75.302 | 77.4025 | 78.3204 | 79.5757 | 81.9057 | 81.1385 | 84.1828 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374
80% | 268.3703 | 44.3577 | 46.7441 | 53.0866 | 58.4274 | 61.3069 | 63.3872 | 65.7849 | 67.5779 | 69.5558 | 70.5901 | 71.4863 | 73.7094 | 72.3627 | 75.9901 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80% | 268.3703 | 47.2118 | 49.6791 | 55.9723 | 61.5153 | 64.4048 | 66.748 | 68.9754 | 70.8725 | 72.8494 | 73.7134 | 74.8948 | 77.0877 | 76.3656 | 79.2309 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822
75% | 455.9026 | 41.5854 | 43.8226 | 49.7687 | 54.7757 | 57.4752 | 59.4255 | 61.6733 | 63.3542 | 65.2085 | 66.1783 | 67.0184 | 69.1025 | 67.8401 | 71.2407 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75% | 455.9026 | 44.261 | 46.5742 | 52.474 | 57.6706 | 60.3795 | 62.5763 | 64.6644 | 66.4429 | 68.2963 | 69.1063 | 70.2138 | 72.2697 | 71.5928 | 74.2789 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271
70% | 690.9866 | 38.813 | 40.9011 | 46.4508 | 51.124 | 53.6435 | 55.4638 | 57.5618 | 59.1306 | 60.8613 | 61.7664 | 62.5505 | 64.4957 | 63.3174 | 66.4913 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70% | 690.9866 | 41.3103 | 43.4692 | 48.9758 | 53.8259 | 56.3542 | 58.4045 | 60.3535 | 62.0134 | 63.7433 | 64.4992 | 65.5329 | 67.4517 | 66.8199 | 69.327 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772
65% | 967.6784 | 36.0407 | 37.9796 | 43.1329 | 47.4723 | 49.8118 | 51.5021 | 53.4502 | 54.907 | 56.5141 | 57.3545 | 58.0826 | 59.8889 | 58.7947 | 61.7419 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65% | 967.6784 | 38.3596 | 40.3643 | 45.4775 | 49.9812 | 52.3289 | 54.2328 | 56.0425 | 57.5839 | 59.1902 | 59.8921 | 60.852 | 62.6338 | 62.0471 | 64.3751 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168
60% | 1292.8136 | 33.2683 | 35.0581 | 39.8149 | 43.8206 | 45.9802 | 47.5404 | 49.3386 | 50.6834 | 52.1668 | 52.9426 | 53.6147 | 55.282 | 54.2721 | 56.9926 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60% | 1292.8136 | 35.4088 | 37.2594 | 41.9792 | 46.1365 | 48.3036 | 50.061 | 51.7315 | 53.1543 | 54.6371 | 55.285 | 56.1711 | 57.8158 | 57.2742 | 59.4231 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617
55% | 1647.0743 | 30.496 | 32.1366 | 36.497 | 40.1689 | 42.1485 | 43.5787 | 45.2271 | 46.4598 | 47.8196 | 48.5307 | 49.1468 | 50.6752 | 49.7494 | 52.2432 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55% | 1647.0743 | 32.4581 | 34.1544 | 38.481 | 42.2918 | 44.2783 | 45.8893 | 47.4206 | 48.7248 | 50.084 | 50.6779 | 51.4901 | 52.9978 | 52.5014 | 54.4712 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065
50% | 2104.1657 | 27.7236 | 29.2151 | 33.1791 | 36.5171 | 38.3168 | 39.617 | 41.1155 | 42.2362 | 43.4724 | 44.1188 | 44.6789 | 46.0684 | 45.2267 | 47.4938 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50% | 2104.1657 | 29.5074 | 31.0495 | 34.9827 | 38.4471 | 40.253 | 41.7175 | 43.1096 | 44.2953 | 45.5309 | 46.0708 | 46.8092 | 48.1798 | 47.7285 | 49.5193 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514
45% | 2736.0097 | 24.9512 | 26.2936 | 29.8612 | 32.8654 | 34.4851 | 35.6553 | 37.004 | 38.0125 | 39.1251 | 39.707 | 40.211 | 41.4615 | 40.704 | 42.7444 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45% | 2736.0097 | 26.5566 | 27.9445 | 31.4844 | 34.6024 | 36.2277 | 37.5458 | 38.7987 | 39.8658 | 40.9778 | 41.4638 | 42.1283 | 43.3618 | 42.9557 | 44.5674 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963
40% | 3483.7613 | 22.1789 | 23.372 | 26.5433 | 29.2137 | 30.6534 | 31.6936 | 32.8924 | 33.7889 | 34.7779 | 35.2951 | 35.7431 | 36.8547 | 36.1814 | 37.995 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40% | 3483.7613 | 23.6059 | 24.8396 | 27.9862 | 30.7577 | 32.2024 | 33.374 | 34.4877 | 35.4362 | 36.4247 | 36.8567 | 37.4474 | 38.5438 | 38.1828 | 39.6154 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411
35% | 3830.2948 | 19.4065 | 20.4505 | 23.2254 | 25.562 | 26.8218 | 27.7319 | 28.7809 | 29.5653 | 30.4307 | 30.8832 | 31.2753 | 32.2479 | 31.6587 | 33.2457 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35% | 3830.2948 | 20.6551 | 21.7346 | 24.4879 | 26.913 | 28.1771 | 29.2023 | 30.1767 | 31.0067 | 31.8716 | 32.2496 | 32.7665 | 33.7259 | 33.41 | 34.6635 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386
30% | 3953.6322 | 16.6342 | 17.529 | 19.9075 | 21.9103 | 22.9901 | 23.7702 | 24.6693 | 25.3417 | 26.0834 | 26.4713 | 26.8074 | 27.641 | 27.136 | 28.4963 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30% | 3953.6322 | 17.7044 | 18.6297 | 20.9896 | 23.0683 | 24.1518 | 25.0305 | 25.8658 | 26.5772 | 27.3185 | 27.6425 | 28.0855 | 28.9079 | 28.6371 | 29.7116 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308
25% | 4060.9208 | 13.8618 | 14.6075 | 16.5896 | 18.2586 | 19.1584 | 19.8085 | 20.5578 | 21.1181 | 21.7362 | 22.0594 | 22.3395 | 23.0342 | 22.6134 | 23.7469 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25% | 4060.9208 | 14.7537 | 15.5247 | 17.4913 | 19.2235 | 20.1265 | 20.8588 | 21.5548 | 22.1476 | 22.7654 | 23.0354 | 23.4046 | 24.0899 | 23.8643 | 24.7596 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757
20% | 4165.2375 | 11.0894 | 11.686 | 13.2716 | 14.6069 | 15.3267 | 15.8468 | 16.4462 | 16.8945 | 17.3889 | 17.6475 | 17.8716 | 18.4273 | 18.0907 | 18.9975 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20% | 4165.2375 | 11.8029 | 12.4198 | 13.9931 | 15.3788 | 16.1012 | 16.687 | 17.2438 | 17.7181 | 18.2124 | 18.4283 | 18.7237 | 19.2719 | 19.0914 | 19.8077 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206
15% | 4270.4458 | 8.3171 | 8.7645 | 9.9537 | 10.9551 | 11.495 | 11.8851 | 12.3347 | 12.6708 | 13.0417 | 13.2357 | 13.4037 | 13.8205 | 13.568 | 14.2481 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15% | 4270.4458 | 8.8522 | 9.3148 | 10.4948 | 11.5341 | 12.0759 | 12.5153 | 12.9329 | 13.2886 | 13.6593 | 13.8213 | 14.0428 | 14.4539 | 14.3186 | 14.8558 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654
10% | 4373.8709 | 5.5447 | 5.843 | 6.6358 | 7.3034 | 7.6634 | 7.9234 | 8.2231 | 8.4472 | 8.6945 | 8.8238 | 8.9358 | 9.2137 | 9.0453 | 9.4988 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10% | 4373.8709 | 5.9015 | 6.2099 | 6.9965 | 7.6894 | 8.0506 | 8.3435 | 8.6219 | 8.8591 | 9.1062 | 9.2142 | 9.3618 | 9.636 | 9.5457 | 9.9039 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103
5% | 4391.7028 | 2.7724 | 2.9215 | 3.3179 | 3.6517 | 3.8317 | 3.9617 | 4.1116 | 4.2236 | 4.3472 | 4.4119 | 4.4679 | 4.6068 | 4.5227 | 4.7494 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5% | 4391.7028 | 2.9507 | 3.1049 | 3.4983 | 3.8447 | 4.0253 | 4.1718 | 4.311 | 4.4295 | 4.5531 | 4.6071 | 4.6809 | 4.818 | 4.7729 | 4.9519 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551
9.992e-14% | 4391.7028 | 5.5403e-14 | 5.8383e-14 | 6.6305e-14 | 7.2976e-14 | 7.6572e-14 | 7.9171e-14 | 8.2165e-14 | 8.4405e-14 | 8.6875e-14 | 8.8167e-14 | 8.9286e-14 | 9.2063e-14 | 9.0381e-14 | 9.4912e-14 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 9.992e-14% | 4391.7028 | 5.8968e-14 | 6.2049e-14 | 6.9909e-14 | 7.6833e-14 | 8.0442e-14 | 8.3368e-14 | 8.615e-14 | 8.852e-14 | 9.0989e-14 | 9.2068e-14 | 9.3544e-14 | 9.6283e-14 | 9.5381e-14 | 9.8959e-14 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 83.7692 | 85.4357 | 87.3388 | 88.8594 | 89.8481 | 92.2106 | 93.8434 | 94.6997 | 96.293 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 100% | 0 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 92.4783 | 94.6253 | 96.6902 | 98.4782 | 99.3722 | 100.693 | 102.2047 | 103.7467 | 105.6887 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885
99% | 0 | 62.0288 | 64.2408 | 71.9008 | 77.4259 | 80.3299 | 82.9315 | 84.5813 | 86.4654 | 87.9708 | 88.9496 | 91.2885 | 92.905 | 93.7527 | 95.3301 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 99% | 0.75633 | 69.7755 | 72.5154 | 80.1966 | 85.6593 | 88.9328 | 91.5535 | 93.679 | 95.7233 | 97.4934 | 98.3784 | 99.6861 | 101.1827 | 102.7093 | 104.6318 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286
98% | 0.37816 | 61.4023 | 63.5919 | 71.1745 | 76.6438 | 79.5185 | 82.0938 | 83.727 | 85.592 | 87.0822 | 88.0511 | 90.3664 | 91.9665 | 92.8057 | 94.3672 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 98% | 1.1345 | 69.0707 | 71.7829 | 79.3865 | 84.7941 | 88.0345 | 90.6287 | 92.7328 | 94.7564 | 96.5086 | 97.3847 | 98.6792 | 100.1606 | 101.6718 | 103.5749 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687
97% | 0.75633 | 60.7757 | 62.943 | 70.4482 | 75.8617 | 78.707 | 81.2561 | 82.8726 | 84.7186 | 86.1937 | 87.1526 | 89.4443 | 91.0281 | 91.8587 | 93.4043 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 97% | 1.8908 | 68.3659 | 71.0504 | 78.5765 | 83.9289 | 87.1362 | 89.7039 | 91.7865 | 93.7895 | 95.5238 | 96.391 | 97.6722 | 99.1386 | 100.6343 | 102.518 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088
95% | 1.8908 | 59.5226 | 61.6453 | 68.9957 | 74.2976 | 77.0842 | 79.5807 | 81.1639 | 82.9718 | 84.4165 | 85.3557 | 87.6001 | 89.1512 | 89.9648 | 91.4784 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 95% | 3.4035 | 66.9563 | 69.5855 | 76.9563 | 82.1984 | 85.3396 | 87.8544 | 89.894 | 91.8557 | 93.5543 | 94.4036 | 95.6584 | 97.0945 | 98.5594 | 100.4042 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689
90% | 4.538 | 56.3898 | 58.4008 | 65.3643 | 70.3872 | 73.0272 | 75.3923 | 76.8921 | 78.6049 | 79.9735 | 80.8633 | 82.9896 | 84.4591 | 85.2298 | 86.6637 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 90% | 9.0759 | 63.4323 | 65.9231 | 72.906 | 77.8721 | 80.848 | 83.2305 | 85.1628 | 87.0212 | 88.6303 | 89.4349 | 90.6237 | 91.9842 | 93.3721 | 95.1198 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896
85% | 9.0759 | 53.2571 | 55.1563 | 61.733 | 66.4768 | 68.9701 | 71.2038 | 72.6203 | 74.238 | 75.5305 | 76.3709 | 78.379 | 79.7669 | 80.4948 | 81.8491 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 85% | 16.2611 | 59.9082 | 62.2607 | 68.8557 | 73.5459 | 76.3565 | 78.6065 | 80.4315 | 82.1867 | 83.7064 | 84.4663 | 85.5891 | 86.874 | 88.1847 | 89.8354 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902
80% | 27.606 | 50.1243 | 51.9118 | 58.1016 | 62.5664 | 64.913 | 67.0154 | 68.3485 | 69.871 | 71.0876 | 71.8785 | 73.7685 | 75.0747 | 75.7598 | 77.0344 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 80% | 24.9588 | 56.3842 | 58.5983 | 64.8053 | 69.2197 | 71.8649 | 73.9826 | 75.7002 | 77.3522 | 78.7825 | 79.4977 | 80.5544 | 81.7638 | 82.9974 | 84.5509 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908
75% | 57.481 | 46.9915 | 48.6673 | 54.4703 | 58.656 | 60.856 | 62.8269 | 64.0767 | 65.5041 | 66.6446 | 67.3861 | 69.158 | 70.3826 | 71.0248 | 72.2198 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 75% | 32.9003 | 52.8602 | 54.9359 | 60.755 | 64.8934 | 67.3733 | 69.3587 | 70.969 | 72.5176 | 73.8586 | 74.5291 | 75.5198 | 76.6535 | 77.81 | 79.2665 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914
70% | 106.2642 | 43.8588 | 45.4228 | 50.8389 | 54.7456 | 56.7989 | 58.6384 | 59.805 | 61.1371 | 62.2016 | 62.8937 | 64.5474 | 65.6904 | 66.2898 | 67.4051 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 70% | 41.9762 | 49.3362 | 51.2735 | 56.7047 | 60.5672 | 62.8818 | 64.7348 | 66.2377 | 67.6831 | 68.9347 | 69.5605 | 70.4851 | 71.5433 | 72.6227 | 73.9821 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919
65% | 201.9397 | 40.726 | 42.1783 | 47.2076 | 50.8352 | 52.7418 | 54.45 | 55.5332 | 56.7702 | 57.7586 | 58.4013 | 59.9369 | 60.9982 | 61.5548 | 62.5905 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 65% | 67.6914 | 45.8122 | 47.6111 | 52.6543 | 56.241 | 58.3902 | 60.1109 | 61.5064 | 62.8486 | 64.0108 | 64.5919 | 65.4505 | 66.4331 | 67.4354 | 68.6976 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925
60% | 402.745 | 37.5932 | 38.9338 | 43.5762 | 46.9248 | 48.6848 | 50.2615 | 51.2614 | 52.4033 | 53.3157 | 53.9089 | 55.3264 | 56.306 | 56.8198 | 57.7758 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 60% | 98.7009 | 42.2882 | 43.9487 | 48.604 | 51.9148 | 53.8987 | 55.487 | 56.7752 | 58.0141 | 59.0869 | 59.6233 | 60.4158 | 61.3228 | 62.248 | 63.4132 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931
55% | 655.7369 | 34.4605 | 35.6894 | 39.9449 | 43.0144 | 44.6277 | 46.0731 | 46.9896 | 48.0363 | 48.8727 | 49.4165 | 50.7158 | 51.6139 | 52.0849 | 52.9612 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 55% | 153.5347 | 38.7642 | 40.2863 | 44.5537 | 47.5885 | 49.4071 | 50.8631 | 52.0439 | 53.1796 | 54.163 | 54.6547 | 55.3812 | 56.2126 | 57.0607 | 58.1288 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937
50% | 981.7145 | 31.3277 | 32.4449 | 36.3135 | 39.104 | 40.5706 | 41.8846 | 42.7178 | 43.6694 | 44.4297 | 44.924 | 46.1053 | 46.9217 | 47.3499 | 48.1465 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 50% | 258.2862 | 35.2401 | 36.6239 | 40.5033 | 43.2623 | 44.9156 | 46.2391 | 47.3126 | 48.3451 | 49.2391 | 49.6861 | 50.3465 | 51.1024 | 51.8734 | 52.8443 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942
45% | 1622.7029 | 28.1949 | 29.2004 | 32.6822 | 35.1936 | 36.5136 | 37.6961 | 38.446 | 39.3024 | 39.9867 | 40.4316 | 41.4948 | 42.2295 | 42.6149 | 43.3319 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 45% | 488.9664 | 31.7161 | 32.9615 | 36.453 | 38.9361 | 40.424 | 41.6152 | 42.5814 | 43.5106 | 44.3152 | 44.7175 | 45.3119 | 45.9921 | 46.686 | 47.5599 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948
40% | 2442.9413 | 25.0621 | 25.9559 | 29.0508 | 31.2832 | 32.4565 | 33.5077 | 34.1743 | 34.9355 | 35.5438 | 35.9392 | 36.8842 | 37.5374 | 37.8799 | 38.5172 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 40% | 928.0152 | 28.1921 | 29.2991 | 32.4027 | 34.6098 | 35.9325 | 36.9913 | 37.8501 | 38.6761 | 39.3913 | 39.7489 | 40.2772 | 40.8819 | 41.4987 | 42.2755 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954
35% | 3006.7842 | 21.9294 | 22.7114 | 25.4195 | 27.3728 | 28.3994 | 29.3192 | 29.9025 | 30.5686 | 31.1008 | 31.4468 | 32.2737 | 32.8452 | 33.1449 | 33.7026 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 35% | 1530.4309 | 24.6681 | 25.6368 | 28.3523 | 30.2836 | 31.4409 | 32.3674 | 33.1189 | 33.8416 | 34.4674 | 34.7803 | 35.2426 | 35.7716 | 36.3114 | 36.991 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096
30% | 3276.4154 | 18.7966 | 19.4669 | 21.7881 | 23.4624 | 24.3424 | 25.1308 | 25.6307 | 26.2016 | 26.6578 | 26.9544 | 27.6632 | 28.153 | 28.4099 | 28.8879 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 30% | 2592.3162 | 21.1441 | 21.9744 | 24.302 | 25.9574 | 26.9493 | 27.7435 | 28.3876 | 29.0071 | 29.5434 | 29.8116 | 30.2079 | 30.6614 | 31.124 | 31.7066 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965
25% | 3466.632 | 15.6638 | 16.2224 | 18.1568 | 19.552 | 20.2853 | 20.9423 | 21.3589 | 21.8347 | 22.2149 | 22.462 | 23.0527 | 23.4609 | 23.6749 | 24.0733 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 25% | 3659.4958 | 17.6201 | 18.312 | 20.2517 | 21.6311 | 22.4578 | 23.1196 | 23.6563 | 24.1725 | 24.6195 | 24.843 | 25.1733 | 25.5512 | 25.9367 | 26.4222 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971
20% | 3713.9514 | 12.5311 | 12.9779 | 14.5254 | 15.6416 | 16.2283 | 16.7538 | 17.0871 | 17.4678 | 17.7719 | 17.9696 | 18.4421 | 18.7687 | 18.9399 | 19.2586 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 20% | 4005.5161 | 14.0961 | 14.6496 | 16.2013 | 17.3049 | 17.9662 | 18.4957 | 18.9251 | 19.338 | 19.6956 | 19.8744 | 20.1386 | 20.4409 | 20.7493 | 21.1377 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977
15% | 4043.3325 | 9.3983 | 9.7335 | 10.8941 | 11.7312 | 12.1712 | 12.5654 | 12.8153 | 13.1008 | 13.3289 | 13.4772 | 13.8316 | 14.0765 | 14.205 | 14.444 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 15% | 4281.1979 | 10.572 | 10.9872 | 12.151 | 12.9787 | 13.4747 | 13.8717 | 14.1938 | 14.5035 | 14.7717 | 14.9058 | 15.104 | 15.3307 | 15.562 | 15.8533 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983
10% | 4350.7801 | 6.2655 | 6.489 | 7.2627 | 7.8208 | 8.1141 | 8.3769 | 8.5436 | 8.7339 | 8.8859 | 8.9848 | 9.2211 | 9.3843 | 9.47 | 9.6293 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 10% | 4391.6218 | 7.048 | 7.3248 | 8.1007 | 8.6525 | 8.9831 | 9.2478 | 9.4625 | 9.669 | 9.8478 | 9.9372 | 10.0693 | 10.2205 | 10.3747 | 10.5689 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988
5% | 4391.6218 | 3.1328 | 3.2445 | 3.6314 | 3.9104 | 4.0571 | 4.1885 | 4.2718 | 4.3669 | 4.443 | 4.4924 | 4.6105 | 4.6922 | 4.735 | 4.8147 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 5% | 4391.6218 | 3.524 | 3.6624 | 4.0503 | 4.3262 | 4.4916 | 4.6239 | 4.7313 | 4.8345 | 4.9239 | 4.9686 | 5.0347 | 5.1102 | 5.1873 | 5.2844 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994
9.992e-14% | 4391.6218 | 6.2605e-14 | 6.4838e-14 | 7.2569e-14 | 7.8145e-14 | 8.1076e-14 | 8.3702e-14 | 8.5367e-14 | 8.7269e-14 | 8.8788e-14 | 8.9776e-14 | 9.2137e-14 | 9.3768e-14 | 9.4624e-14 | 9.6216e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.992e-14% | 4391.6218 | 7.0424e-14 | 7.3189e-14 | 8.0942e-14 | 8.6455e-14 | 8.9759e-14 | 9.2404e-14 | 9.455e-14 | 9.6613e-14 | 9.8399e-14 | 9.9293e-14 | 1.0061e-13 | 1.0212e-13 | 1.0366e-13 | 1.056e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 64.734 | 67.7311 | 69.9723 | 72.4447 | 73.7377 | 74.8579 | 77.6367 | 75.9534 | 80.4876 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 86.4033 | 100% | 0 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 68.935 | 71.7192 | 74.0906 | 76.5618 | 77.6417 | 79.1184 | 81.8596 | 80.957 | 84.5386 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028 | 86.6028
99% | 0.8916 | 54.8927 | 57.8458 | 65.6947 | 72.3039 | 75.8673 | 64.0867 | 67.0538 | 69.2726 | 71.7203 | 73.0003 | 74.1093 | 76.8604 | 75.1939 | 79.6827 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 85.5392 | 99% | 0.8916 | 58.4246 | 61.4779 | 69.2657 | 76.1252 | 79.701 | 68.2457 | 71.002 | 73.3497 | 75.7962 | 76.8653 | 78.3273 | 81.041 | 80.1475 | 83.6932 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368 | 85.7368
98% | 3.5664 | 54.3382 | 57.2615 | 65.0311 | 71.5736 | 75.1009 | 63.4393 | 66.3765 | 68.5729 | 70.9958 | 72.2629 | 73.3607 | 76.084 | 74.4344 | 78.8778 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 84.6752 | 98% | 3.5664 | 57.8344 | 60.8569 | 68.5661 | 75.3563 | 78.8959 | 67.5563 | 70.2848 | 72.6088 | 75.0306 | 76.0889 | 77.5361 | 80.2224 | 79.3379 | 82.8478 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707 | 84.8707
97% | 4.7552 | 53.7838 | 56.6772 | 64.3675 | 70.8433 | 74.3346 | 62.792 | 65.6991 | 67.8732 | 70.2714 | 71.5255 | 72.6121 | 75.3076 | 73.6748 | 78.073 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 83.8112 | 97% | 4.7552 | 57.2443 | 60.2359 | 67.8664 | 74.5874 | 78.0908 | 66.867 | 69.5677 | 71.8679 | 74.2649 | 75.3124 | 76.7449 | 79.4038 | 78.5283 | 82.0024 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047 | 84.0047
95% | 7.7272 | 52.6748 | 55.5086 | 63.0403 | 69.3826 | 72.8019 | 61.4973 | 64.3445 | 66.4737 | 68.8225 | 70.0508 | 71.115 | 73.7549 | 72.1558 | 76.4632 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 82.0831 | 95% | 7.7272 | 56.064 | 58.994 | 66.4671 | 73.0495 | 76.4807 | 65.4883 | 68.1333 | 70.386 | 72.7337 | 73.7596 | 75.1625 | 77.7666 | 76.9092 | 80.3116 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727 | 82.2727
90% | 39.2302 | 49.9025 | 52.5871 | 59.7224 | 65.7309 | 68.9702 | 58.2606 | 60.958 | 62.9751 | 65.2002 | 66.3639 | 67.3721 | 69.8731 | 68.3581 | 72.4388 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 77.7629 | 90% | 39.2302 | 53.1132 | 55.889 | 62.9689 | 69.2048 | 72.4554 | 62.0415 | 64.5473 | 66.6815 | 68.9056 | 69.8775 | 71.2066 | 73.6737 | 72.8613 | 76.0847 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425 | 77.9425
85% | 117.6906 | 47.1301 | 49.6656 | 56.4045 | 62.0791 | 65.1386 | 55.0239 | 57.5714 | 59.4765 | 61.578 | 62.677 | 63.6292 | 65.9912 | 64.5604 | 68.4145 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 73.4428 | 85% | 117.6906 | 50.1625 | 52.7841 | 59.4706 | 65.3601 | 68.4301 | 58.5948 | 60.9613 | 62.977 | 65.0775 | 65.9954 | 67.2507 | 69.5807 | 68.8135 | 71.8578 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124 | 73.6124
80% | 268.3703 | 44.3577 | 46.7441 | 53.0866 | 58.4274 | 61.3069 | 51.7872 | 54.1849 | 55.9779 | 57.9558 | 58.9901 | 59.8863 | 62.1094 | 60.7627 | 64.3901 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 69.1226 | 80% | 268.3703 | 47.2118 | 49.6791 | 55.9723 | 61.5153 | 64.4048 | 55.148 | 57.3754 | 59.2725 | 61.2494 | 62.1134 | 63.2948 | 65.4877 | 64.7656 | 67.6309 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822 | 69.2822
75% | 455.9026 | 41.5854 | 43.8226 | 49.7687 | 54.7757 | 57.4752 | 48.5505 | 50.7983 | 52.4792 | 54.3335 | 55.3033 | 56.1434 | 58.2275 | 56.9651 | 60.3657 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 64.8025 | 75% | 455.9026 | 44.261 | 46.5742 | 52.474 | 57.6706 | 60.3795 | 51.7013 | 53.7894 | 55.5679 | 57.4213 | 58.2313 | 59.3388 | 61.3947 | 60.7178 | 63.4039 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521 | 64.9521
70% | 690.9866 | 38.813 | 40.9011 | 46.4508 | 51.124 | 53.6435 | 45.3138 | 47.4118 | 48.9806 | 50.7113 | 51.6164 | 52.4005 | 54.3457 | 53.1674 | 56.3413 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 60.4823 | 70% | 690.9866 | 41.3103 | 43.4692 | 48.9758 | 53.8259 | 56.3542 | 48.2545 | 50.2035 | 51.8634 | 53.5933 | 54.3492 | 55.3829 | 57.3017 | 56.6699 | 59.177 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622 | 60.622
65% | 967.6784 | 36.0407 | 37.9796 | 43.1329 | 47.4723 | 49.8118 | 42.0771 | 44.0252 | 45.482 | 47.0891 | 47.9295 | 48.6576 | 50.4639 | 49.3697 | 52.3169 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 56.1621 | 65% | 967.6784 | 38.3596 | 40.3643 | 45.4775 | 49.9812 | 52.3289 | 44.8078 | 46.6175 | 48.1589 | 49.7652 | 50.4671 | 51.427 | 53.2088 | 52.6221 | 54.9501 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918 | 56.2918
60% | 1292.8136 | 33.2683 | 35.0581 | 39.8149 | 43.8206 | 45.9802 | 38.8404 | 40.6386 | 41.9834 | 43.4668 | 44.2426 | 44.9147 | 46.582 | 45.5721 | 48.2926 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 51.842 | 60% | 1292.8136 | 35.4088 | 37.2594 | 41.9792 | 46.1365 | 48.3036 | 41.361 | 43.0315 | 44.4543 | 45.9371 | 46.585 | 47.4711 | 49.1158 | 48.5742 | 50.7231 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617 | 51.9617
55% | 1647.0743 | 30.496 | 32.1366 | 36.497 | 40.1689 | 42.1485 | 35.6037 | 37.2521 | 38.4848 | 39.8446 | 40.5557 | 41.1718 | 42.7002 | 41.7744 | 44.2682 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 47.5218 | 55% | 1647.0743 | 32.4581 | 34.1544 | 38.481 | 42.2918 | 44.2783 | 37.9143 | 39.4456 | 40.7498 | 42.109 | 42.7029 | 43.5151 | 45.0228 | 44.5264 | 46.4962 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315 | 47.6315
50% | 2104.1657 | 27.7236 | 29.2151 | 33.1791 | 36.5171 | 38.3168 | 32.367 | 33.8655 | 34.9862 | 36.2224 | 36.8688 | 37.4289 | 38.8184 | 37.9767 | 40.2438 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 43.2016 | 50% | 2104.1657 | 29.5074 | 31.0495 | 34.9827 | 38.4471 | 40.253 | 34.4675 | 35.8596 | 37.0453 | 38.2809 | 38.8208 | 39.5592 | 40.9298 | 40.4785 | 42.2693 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014 | 43.3014
45% | 2736.0097 | 24.9512 | 26.2936 | 29.8612 | 32.8654 | 34.4851 | 29.1303 | 30.479 | 31.4875 | 32.6001 | 33.182 | 33.686 | 34.9365 | 34.179 | 36.2194 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 38.8815 | 45% | 2736.0097 | 26.5566 | 27.9445 | 31.4844 | 34.6024 | 36.2277 | 31.0208 | 32.2737 | 33.3408 | 34.4528 | 34.9388 | 35.6033 | 36.8368 | 36.4307 | 38.0424 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713 | 38.9713
40% | 3483.7613 | 22.1789 | 23.372 | 26.5433 | 29.2137 | 30.6534 | 25.8936 | 27.0924 | 27.9889 | 28.9779 | 29.4951 | 29.9431 | 31.0547 | 30.3814 | 32.195 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 34.5613 | 40% | 3483.7613 | 23.6059 | 24.8396 | 27.9862 | 30.7577 | 32.2024 | 27.574 | 28.6877 | 29.6362 | 30.6247 | 31.0567 | 31.6474 | 32.7438 | 32.3828 | 33.8154 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411 | 34.6411
35% | 3830.2948 | 19.4065 | 20.4505 | 23.2254 | 25.562 | 26.8218 | 22.6569 | 23.7059 | 24.4903 | 25.3557 | 25.8082 | 26.2003 | 27.1729 | 26.5837 | 28.1707 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 30.2411 | 35% | 3830.2948 | 20.6551 | 21.7346 | 24.4879 | 26.913 | 28.1771 | 24.1273 | 25.1017 | 25.9317 | 26.7966 | 27.1746 | 27.6915 | 28.6509 | 28.335 | 29.5885 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311 | 30.311
30% | 3953.6322 | 16.6342 | 17.529 | 19.9075 | 21.9103 | 22.9901 | 19.4202 | 20.3193 | 20.9917 | 21.7334 | 22.1213 | 22.4574 | 23.291 | 22.786 | 24.1463 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 25.921 | 30% | 3953.6322 | 17.7044 | 18.6297 | 20.9896 | 23.0683 | 24.1518 | 20.6805 | 21.5158 | 22.2272 | 22.9685 | 23.2925 | 23.7355 | 24.5579 | 24.2871 | 25.3616 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808 | 25.9808
25% | 4060.9208 | 13.8618 | 14.6075 | 16.5896 | 18.2586 | 19.1584 | 16.1835 | 16.9328 | 17.4931 | 18.1112 | 18.4344 | 18.7145 | 19.4092 | 18.9884 | 20.1219 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 21.6008 | 25% | 4060.9208 | 14.7537 | 15.5247 | 17.4913 | 19.2235 | 20.1265 | 17.2338 | 17.9298 | 18.5226 | 19.1404 | 19.4104 | 19.7796 | 20.4649 | 20.2393 | 21.1346 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507 | 21.6507
20% | 4165.2375 | 11.0894 | 11.686 | 13.2716 | 14.6069 | 15.3267 | 12.9468 | 13.5462 | 13.9945 | 14.4889 | 14.7475 | 14.9716 | 15.5273 | 15.1907 | 16.0975 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 17.2807 | 20% | 4165.2375 | 11.8029 | 12.4198 | 13.9931 | 15.3788 | 16.1012 | 13.787 | 14.3438 | 14.8181 | 15.3124 | 15.5283 | 15.8237 | 16.3719 | 16.1914 | 16.9077 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206 | 17.3206
15% | 4270.4458 | 8.3171 | 8.7645 | 9.9537 | 10.9551 | 11.495 | 9.7101 | 10.1597 | 10.4958 | 10.8667 | 11.0607 | 11.2287 | 11.6455 | 11.393 | 12.0731 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 12.9605 | 15% | 4270.4458 | 8.8522 | 9.3148 | 10.4948 | 11.5341 | 12.0759 | 10.3403 | 10.7579 | 11.1136 | 11.4843 | 11.6463 | 11.8678 | 12.2789 | 12.1436 | 12.6808 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904 | 12.9904
10% | 4373.8709 | 5.5447 | 5.843 | 6.6358 | 7.3034 | 7.6634 | 6.4734 | 6.7731 | 6.9972 | 7.2445 | 7.3738 | 7.4858 | 7.7637 | 7.5953 | 8.0488 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 8.6403 | 10% | 4373.8709 | 5.9015 | 6.2099 | 6.9965 | 7.6894 | 8.0506 | 6.8935 | 7.1719 | 7.4091 | 7.6562 | 7.7642 | 7.9118 | 8.186 | 8.0957 | 8.4539 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603 | 8.6603
5% | 4391.7028 | 2.7724 | 2.9215 | 3.3179 | 3.6517 | 3.8317 | 3.2367 | 3.3866 | 3.4986 | 3.6222 | 3.6869 | 3.7429 | 3.8818 | 3.7977 | 4.0244 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 4.3202 | 5% | 4391.7028 | 2.9507 | 3.1049 | 3.4983 | 3.8447 | 4.0253 | 3.4468 | 3.586 | 3.7045 | 3.8281 | 3.8821 | 3.9559 | 4.093 | 4.0479 | 4.2269 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301 | 4.3301
9.992e-14% | 4391.7028 | 5.5403e-14 | 5.8383e-14 | 6.6305e-14 | 7.2976e-14 | 7.6572e-14 | 6.4682e-14 | 6.7677e-14 | 6.9916e-14 | 7.2387e-14 | 7.3679e-14 | 7.4798e-14 | 7.7575e-14 | 7.5893e-14 | 8.0423e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 8.6334e-14 | 9.992e-14% | 4391.7028 | 5.8968e-14 | 6.2049e-14 | 6.9909e-14 | 7.6833e-14 | 8.0442e-14 | 6.888e-14 | 7.1662e-14 | 7.4031e-14 | 7.6501e-14 | 7.758e-14 | 7.9055e-14 | 8.1794e-14 | 8.0892e-14 | 8.4471e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14 | 8.6534e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 69.2692 | 70.9357 | 72.8388 | 74.3594 | 75.3481 | 77.7106 | 79.3434 | 80.1997 | 81.793 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 81.3242 | 100% | 0 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 77.9783 | 80.1253 | 82.1902 | 83.9782 | 84.8722 | 86.193 | 87.7047 | 89.2467 | 91.1887 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885 | 91.4885
99% | 0 | 62.0288 | 64.2408 | 71.9008 | 77.4259 | 80.3299 | 68.5765 | 70.2263 | 72.1104 | 73.6158 | 74.5946 | 76.9335 | 78.55 | 79.3977 | 80.9751 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 80.5109 | 99% | 0.75633 | 69.7755 | 72.5154 | 80.1966 | 85.6593 | 88.9328 | 77.1985 | 79.324 | 81.3683 | 83.1384 | 84.0234 | 85.3311 | 86.8277 | 88.3543 | 90.2768 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736 | 90.5736
98% | 0.37816 | 61.4023 | 63.5919 | 71.1745 | 76.6438 | 79.5185 | 67.8838 | 69.517 | 71.382 | 72.8722 | 73.8411 | 76.1564 | 77.7565 | 78.5957 | 80.1572 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 79.6977 | 98% | 1.1345 | 69.0707 | 71.7829 | 79.3865 | 84.7941 | 88.0345 | 76.4187 | 78.5228 | 80.5464 | 82.2986 | 83.1747 | 84.4692 | 85.9506 | 87.4618 | 89.3649 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587 | 89.6587
97% | 0.75633 | 60.7757 | 62.943 | 70.4482 | 75.8617 | 78.707 | 67.1911 | 68.8076 | 70.6536 | 72.1287 | 73.0876 | 75.3793 | 76.9631 | 77.7937 | 79.3393 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 78.8844 | 97% | 1.8908 | 68.3659 | 71.0504 | 78.5765 | 83.9289 | 87.1362 | 75.6389 | 77.7215 | 79.7245 | 81.4588 | 82.326 | 83.6072 | 85.0736 | 86.5693 | 88.453 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438 | 88.7438
95% | 1.8908 | 59.5226 | 61.6453 | 68.9957 | 74.2976 | 77.0842 | 65.8057 | 67.3889 | 69.1968 | 70.6415 | 71.5807 | 73.8251 | 75.3762 | 76.1898 | 77.7034 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 77.258 | 95% | 3.4035 | 66.9563 | 69.5855 | 76.9563 | 82.1984 | 85.3396 | 74.0794 | 76.119 | 78.0807 | 79.7793 | 80.6286 | 81.8834 | 83.3195 | 84.7844 | 86.6292 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914 | 86.914
90% | 4.538 | 56.3898 | 58.4008 | 65.3643 | 70.3872 | 73.0272 | 62.3423 | 63.8421 | 65.5549 | 66.9235 | 67.8133 | 69.9396 | 71.4091 | 72.1798 | 73.6137 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 73.1917 | 90% | 9.0759 | 63.4323 | 65.9231 | 72.906 | 77.8721 | 80.848 | 70.1805 | 72.1128 | 73.9712 | 75.5803 | 76.3849 | 77.5737 | 78.9342 | 80.3221 | 82.0698 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396 | 82.3396
85% | 9.0759 | 53.2571 | 55.1563 | 61.733 | 66.4768 | 68.9701 | 58.8788 | 60.2953 | 61.913 | 63.2055 | 64.0459 | 66.054 | 67.4419 | 68.1698 | 69.5241 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 69.1255 | 85% | 16.2611 | 59.9082 | 62.2607 | 68.8557 | 73.5459 | 76.3565 | 66.2815 | 68.1065 | 69.8617 | 71.3814 | 72.1413 | 73.2641 | 74.549 | 75.8597 | 77.5104 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652 | 77.7652
80% | 27.606 | 50.1243 | 51.9118 | 58.1016 | 62.5664 | 64.913 | 55.4154 | 56.7485 | 58.271 | 59.4876 | 60.2785 | 62.1685 | 63.4747 | 64.1598 | 65.4344 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 65.0593 | 80% | 24.9588 | 56.3842 | 58.5983 | 64.8053 | 69.2197 | 71.8649 | 62.3826 | 64.1002 | 65.7522 | 67.1825 | 67.8977 | 68.9544 | 70.1638 | 71.3974 | 72.9509 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908 | 73.1908
75% | 57.481 | 46.9915 | 48.6673 | 54.4703 | 58.656 | 60.856 | 51.9519 | 53.2017 | 54.6291 | 55.7696 | 56.5111 | 58.283 | 59.5076 | 60.1498 | 61.3448 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 60.9931 | 75% | 32.9003 | 52.8602 | 54.9359 | 60.755 | 64.8934 | 67.3733 | 58.4837 | 60.094 | 61.6426 | 62.9836 | 63.6541 | 64.6448 | 65.7785 | 66.935 | 68.3915 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164 | 68.6164
70% | 106.2642 | 43.8588 | 45.4228 | 50.8389 | 54.7456 | 56.7989 | 48.4884 | 49.655 | 50.9871 | 52.0516 | 52.7437 | 54.3974 | 55.5404 | 56.1398 | 57.2551 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 56.9269 | 70% | 41.9762 | 49.3362 | 51.2735 | 56.7047 | 60.5672 | 62.8818 | 54.5848 | 56.0877 | 57.5331 | 58.7847 | 59.4105 | 60.3351 | 61.3933 | 62.4727 | 63.8321 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419 | 64.0419
65% | 201.9397 | 40.726 | 42.1783 | 47.2076 | 50.8352 | 52.7418 | 45.025 | 46.1082 | 47.3452 | 48.3336 | 48.9763 | 50.5119 | 51.5732 | 52.1298 | 53.1655 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 52.8607 | 65% | 67.6914 | 45.8122 | 47.6111 | 52.6543 | 56.241 | 58.3902 | 50.6859 | 52.0814 | 53.4236 | 54.5858 | 55.1669 | 56.0255 | 57.0081 | 58.0104 | 59.2726 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675 | 59.4675
60% | 402.745 | 37.5932 | 38.9338 | 43.5762 | 46.9248 | 48.6848 | 41.5615 | 42.5614 | 43.7033 | 44.6157 | 45.2089 | 46.6264 | 47.606 | 48.1198 | 49.0758 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 48.7945 | 60% | 98.7009 | 42.2882 | 43.9487 | 48.604 | 51.9148 | 53.8987 | 46.787 | 48.0752 | 49.3141 | 50.3869 | 50.9233 | 51.7158 | 52.6228 | 53.548 | 54.7132 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931 | 54.8931
55% | 655.7369 | 34.4605 | 35.6894 | 39.9449 | 43.0144 | 44.6277 | 38.0981 | 39.0146 | 40.0613 | 40.8977 | 41.4415 | 42.7408 | 43.6389 | 44.1099 | 44.9862 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 44.7283 | 55% | 153.5347 | 38.7642 | 40.2863 | 44.5537 | 47.5885 | 49.4071 | 42.8881 | 44.0689 | 45.2046 | 46.188 | 46.6797 | 47.4062 | 48.2376 | 49.0857 | 50.1538 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187 | 50.3187
50% | 981.7145 | 31.3277 | 32.4449 | 36.3135 | 39.104 | 40.5706 | 34.6346 | 35.4678 | 36.4194 | 37.1797 | 37.674 | 38.8553 | 39.6717 | 40.0999 | 40.8965 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 40.6621 | 50% | 258.2862 | 35.2401 | 36.6239 | 40.5033 | 43.2623 | 44.9156 | 38.9891 | 40.0626 | 41.0951 | 41.9891 | 42.4361 | 43.0965 | 43.8524 | 44.6234 | 45.5943 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442 | 45.7442
45% | 1622.7029 | 28.1949 | 29.2004 | 32.6822 | 35.1936 | 36.5136 | 31.1711 | 31.921 | 32.7774 | 33.4617 | 33.9066 | 34.9698 | 35.7045 | 36.0899 | 36.8069 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 36.5959 | 45% | 488.9664 | 31.7161 | 32.9615 | 36.453 | 38.9361 | 40.424 | 35.0902 | 36.0564 | 36.9856 | 37.7902 | 38.1925 | 38.7869 | 39.4671 | 40.161 | 41.0349 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698 | 41.1698
40% | 2442.9413 | 25.0621 | 25.9559 | 29.0508 | 31.2832 | 32.4565 | 27.7077 | 28.3743 | 29.1355 | 29.7438 | 30.1392 | 31.0842 | 31.7374 | 32.0799 | 32.7172 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 32.5297 | 40% | 928.0152 | 28.1921 | 29.2991 | 32.4027 | 34.6098 | 35.9325 | 31.1913 | 32.0501 | 32.8761 | 33.5913 | 33.9489 | 34.4772 | 35.0819 | 35.6987 | 36.4755 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954 | 36.5954
35% | 3006.7842 | 21.9294 | 22.7114 | 25.4195 | 27.3728 | 28.3994 | 24.2442 | 24.8275 | 25.4936 | 26.0258 | 26.3718 | 27.1987 | 27.7702 | 28.0699 | 28.6276 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 28.4635 | 35% | 1530.4309 | 24.6681 | 25.6368 | 28.3523 | 30.2836 | 31.4409 | 27.2924 | 28.0439 | 28.7666 | 29.3924 | 29.7053 | 30.1676 | 30.6966 | 31.2364 | 31.916 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021 | 32.021
30% | 3276.4154 | 18.7966 | 19.4669 | 21.7881 | 23.4624 | 24.3424 | 20.7808 | 21.2807 | 21.8516 | 22.3078 | 22.6044 | 23.3132 | 23.803 | 24.0599 | 24.5379 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 24.3972 | 30% | 2592.3162 | 21.1441 | 21.9744 | 24.302 | 25.9574 | 26.9493 | 23.3935 | 24.0376 | 24.6571 | 25.1934 | 25.4616 | 25.8579 | 26.3114 | 26.774 | 27.3566 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465 | 27.4465
25% | 3466.632 | 15.6638 | 16.2224 | 18.1568 | 19.552 | 20.2853 | 17.3173 | 17.7339 | 18.2097 | 18.5899 | 18.837 | 19.4277 | 19.8359 | 20.0499 | 20.4483 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 20.331 | 25% | 3659.4958 | 17.6201 | 18.312 | 20.2517 | 21.6311 | 22.4578 | 19.4946 | 20.0313 | 20.5475 | 20.9945 | 21.218 | 21.5483 | 21.9262 | 22.3117 | 22.7972 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721 | 22.8721
20% | 3713.9514 | 12.5311 | 12.9779 | 14.5254 | 15.6416 | 16.2283 | 13.8538 | 14.1871 | 14.5678 | 14.8719 | 15.0696 | 15.5421 | 15.8687 | 16.0399 | 16.3586 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 16.2648 | 20% | 4005.5161 | 14.0961 | 14.6496 | 16.2013 | 17.3049 | 17.9662 | 15.5957 | 16.0251 | 16.438 | 16.7956 | 16.9744 | 17.2386 | 17.5409 | 17.8493 | 18.2377 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977 | 18.2977
15% | 4043.3325 | 9.3983 | 9.7335 | 10.8941 | 11.7312 | 12.1712 | 10.3904 | 10.6403 | 10.9258 | 11.1539 | 11.3022 | 11.6566 | 11.9015 | 12.03 | 12.269 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 12.1986 | 15% | 4281.1979 | 10.572 | 10.9872 | 12.151 | 12.9787 | 13.4747 | 11.6967 | 12.0188 | 12.3285 | 12.5967 | 12.7308 | 12.929 | 13.1557 | 13.387 | 13.6783 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233 | 13.7233
10% | 4350.7801 | 6.2655 | 6.489 | 7.2627 | 7.8208 | 8.1141 | 6.9269 | 7.0936 | 7.2839 | 7.4359 | 7.5348 | 7.7711 | 7.9343 | 8.02 | 8.1793 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 8.1324 | 10% | 4391.6218 | 7.048 | 7.3248 | 8.1007 | 8.6525 | 8.9831 | 7.7978 | 8.0125 | 8.219 | 8.3978 | 8.4872 | 8.6193 | 8.7705 | 8.9247 | 9.1189 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488 | 9.1488
5% | 4391.6218 | 3.1328 | 3.2445 | 3.6314 | 3.9104 | 4.0571 | 3.4635 | 3.5468 | 3.6419 | 3.718 | 3.7674 | 3.8855 | 3.9672 | 4.01 | 4.0897 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 4.0662 | 5% | 4391.6218 | 3.524 | 3.6624 | 4.0503 | 4.3262 | 4.4916 | 3.8989 | 4.0063 | 4.1095 | 4.1989 | 4.2436 | 4.3097 | 4.3852 | 4.4623 | 4.5594 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744 | 4.5744
9.992e-14% | 4391.6218 | 6.2605e-14 | 6.4838e-14 | 7.2569e-14 | 7.8145e-14 | 8.1076e-14 | 6.9214e-14 | 7.0879e-14 | 7.2781e-14 | 7.43e-14 | 7.5288e-14 | 7.7649e-14 | 7.928e-14 | 8.0136e-14 | 8.1728e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 8.1259e-14 | 9.992e-14% | 4391.6218 | 7.0424e-14 | 7.3189e-14 | 8.0942e-14 | 8.6455e-14 | 8.9759e-14 | 7.7916e-14 | 8.0061e-14 | 8.2125e-14 | 8.3911e-14 | 8.4804e-14 | 8.6124e-14 | 8.7635e-14 | 8.9175e-14 | 9.1116e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14 | 9.1415e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 55.4472 | 58.4301 | 66.3582 | 58.5343 | 62.1336 | 50.234 | 53.2311 | 55.4723 | 57.9447 | 59.2377 | 60.3579 | 63.1367 | 61.4534 | 65.9876 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 100% | 0 | 59.0147 | 62.0989 | 69.9654 | 62.3942 | 66.006 | 54.435 | 57.2192 | 59.5906 | 62.0618 | 63.1417 | 64.6184 | 67.3596 | 66.457 | 70.0386 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028
99% | 0.8916 | 54.8927 | 57.8458 | 65.6947 | 57.9489 | 61.5123 | 49.7317 | 52.6988 | 54.9176 | 57.3653 | 58.6453 | 59.7543 | 62.5054 | 60.8389 | 65.3277 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 99% | 0.8916 | 58.4246 | 61.4779 | 69.2657 | 61.7702 | 65.346 | 53.8907 | 56.647 | 58.9947 | 61.4412 | 62.5103 | 63.9723 | 66.686 | 65.7925 | 69.3382 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818
98% | 3.5664 | 54.3382 | 57.2615 | 65.0311 | 57.3636 | 60.8909 | 49.2293 | 52.1665 | 54.3629 | 56.7858 | 58.0529 | 59.1507 | 61.874 | 60.2244 | 64.6678 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 98% | 3.5664 | 57.8344 | 60.8569 | 68.5661 | 61.1463 | 64.6859 | 53.3463 | 56.0748 | 58.3988 | 60.8206 | 61.8789 | 63.3261 | 66.0124 | 65.1279 | 68.6378 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607
97% | 4.7552 | 53.7838 | 56.6772 | 64.3675 | 56.7783 | 60.2696 | 48.727 | 51.6341 | 53.8082 | 56.2064 | 57.4605 | 58.5471 | 61.2426 | 59.6098 | 64.008 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 97% | 4.7552 | 57.2443 | 60.2359 | 67.8664 | 60.5224 | 64.0258 | 52.802 | 55.5027 | 57.8029 | 60.1999 | 61.2474 | 62.6799 | 65.3388 | 64.4633 | 67.9374 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397
95% | 7.7272 | 52.6748 | 55.5086 | 63.0403 | 55.6076 | 59.0269 | 47.7223 | 50.5695 | 52.6987 | 55.0475 | 56.2758 | 57.34 | 59.9799 | 58.3808 | 62.6882 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 95% | 7.7272 | 56.064 | 58.994 | 66.4671 | 59.2745 | 62.7057 | 51.7133 | 54.3583 | 56.611 | 58.9587 | 59.9846 | 61.3875 | 63.9916 | 63.1342 | 66.5366 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977
90% | 39.2302 | 49.9025 | 52.5871 | 59.7224 | 52.6809 | 55.9202 | 45.2106 | 47.908 | 49.9251 | 52.1502 | 53.3139 | 54.3221 | 56.8231 | 55.3081 | 59.3888 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 90% | 39.2302 | 53.1132 | 55.889 | 62.9689 | 56.1548 | 59.4054 | 48.9915 | 51.4973 | 53.6315 | 55.8556 | 56.8275 | 58.1566 | 60.6237 | 59.8113 | 63.0347 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925
85% | 117.6906 | 47.1301 | 49.6656 | 56.4045 | 49.7541 | 52.8136 | 42.6989 | 45.2464 | 47.1515 | 49.253 | 50.352 | 51.3042 | 53.6662 | 52.2354 | 56.0895 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 85% | 117.6906 | 50.1625 | 52.7841 | 59.4706 | 53.0351 | 56.1051 | 46.2698 | 48.6363 | 50.652 | 52.7525 | 53.6704 | 54.9257 | 57.2557 | 56.4885 | 59.5328 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874
80% | 268.3703 | 44.3577 | 46.7441 | 53.0866 | 46.8274 | 49.7069 | 40.1872 | 42.5849 | 44.3779 | 46.3558 | 47.3901 | 48.2863 | 50.5094 | 49.1627 | 52.7901 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 80% | 268.3703 | 47.2118 | 49.6791 | 55.9723 | 49.9153 | 52.8048 | 43.548 | 45.7754 | 47.6725 | 49.6494 | 50.5134 | 51.6948 | 53.8877 | 53.1656 | 56.0309 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822
75% | 455.9026 | 41.5854 | 43.8226 | 49.7687 | 43.9007 | 46.6002 | 37.6755 | 39.9233 | 41.6042 | 43.4585 | 44.4283 | 45.2684 | 47.3525 | 46.0901 | 49.4907 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 75% | 455.9026 | 44.261 | 46.5742 | 52.474 | 46.7956 | 49.5045 | 40.8263 | 42.9144 | 44.6929 | 46.5463 | 47.3563 | 48.4638 | 50.5197 | 49.8428 | 52.5289 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771
70% | 690.9866 | 38.813 | 40.9011 | 46.4508 | 40.974 | 43.4935 | 35.1638 | 37.2618 | 38.8306 | 40.5613 | 41.4664 | 42.2505 | 44.1957 | 43.0174 | 46.1913 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 70% | 690.9866 | 41.3103 | 43.4692 | 48.9758 | 43.6759 | 46.2042 | 38.1045 | 40.0535 | 41.7134 | 43.4433 | 44.1992 | 45.2329 | 47.1517 | 46.5199 | 49.027 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472
65% | 967.6784 | 36.0407 | 37.9796 | 43.1329 | 38.0473 | 40.3868 | 32.6521 | 34.6002 | 36.057 | 37.6641 | 38.5045 | 39.2326 | 41.0389 | 39.9447 | 42.8919 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 65% | 967.6784 | 38.3596 | 40.3643 | 45.4775 | 40.5562 | 42.9039 | 35.3828 | 37.1925 | 38.7339 | 40.3402 | 41.0421 | 42.002 | 43.7838 | 43.1971 | 45.5251 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668
60% | 1292.8136 | 33.2683 | 35.0581 | 39.8149 | 35.1206 | 37.2802 | 30.1404 | 31.9386 | 33.2834 | 34.7668 | 35.5426 | 36.2147 | 37.882 | 36.8721 | 39.5926 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 60% | 1292.8136 | 35.4088 | 37.2594 | 41.9792 | 37.4365 | 39.6036 | 32.661 | 34.3315 | 35.7543 | 37.2371 | 37.885 | 38.7711 | 40.4158 | 39.8742 | 42.0231 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617
55% | 1647.0743 | 30.496 | 32.1366 | 36.497 | 32.1939 | 34.1735 | 27.6287 | 29.2771 | 30.5098 | 31.8696 | 32.5807 | 33.1968 | 34.7252 | 33.7994 | 36.2932 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 55% | 1647.0743 | 32.4581 | 34.1544 | 38.481 | 34.3168 | 36.3033 | 29.9393 | 31.4706 | 32.7748 | 34.134 | 34.7279 | 35.5401 | 37.0478 | 36.5514 | 38.5212 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565
50% | 2104.1657 | 27.7236 | 29.2151 | 33.1791 | 29.2671 | 31.0668 | 25.117 | 26.6155 | 27.7362 | 28.9724 | 29.6188 | 30.1789 | 31.5684 | 30.7267 | 32.9938 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 50% | 2104.1657 | 29.5074 | 31.0495 | 34.9827 | 31.1971 | 33.003 | 27.2175 | 28.6096 | 29.7953 | 31.0309 | 31.5708 | 32.3092 | 33.6798 | 33.2285 | 35.0193 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514
45% | 2736.0097 | 24.9512 | 26.2936 | 29.8612 | 26.3404 | 27.9601 | 22.6053 | 23.954 | 24.9625 | 26.0751 | 26.657 | 27.161 | 28.4115 | 27.654 | 29.6944 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 45% | 2736.0097 | 26.5566 | 27.9445 | 31.4844 | 28.0774 | 29.7027 | 24.4958 | 25.7487 | 26.8158 | 27.9278 | 28.4138 | 29.0783 | 30.3118 | 29.9057 | 31.5174 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463
40% | 3483.7613 | 22.1789 | 23.372 | 26.5433 | 23.4137 | 24.8534 | 20.0936 | 21.2924 | 22.1889 | 23.1779 | 23.6951 | 24.1431 | 25.2547 | 24.5814 | 26.395 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 40% | 3483.7613 | 23.6059 | 24.8396 | 27.9862 | 24.9577 | 26.4024 | 21.774 | 22.8877 | 23.8362 | 24.8247 | 25.2567 | 25.8474 | 26.9438 | 26.5828 | 28.0154 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411
35% | 3830.2948 | 19.4065 | 20.4505 | 23.2254 | 20.487 | 21.7468 | 17.5819 | 18.6309 | 19.4153 | 20.2807 | 20.7332 | 21.1253 | 22.0979 | 21.5087 | 23.0957 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 35% | 3830.2948 | 20.6551 | 21.7346 | 24.4879 | 21.838 | 23.1021 | 19.0523 | 20.0267 | 20.8567 | 21.7216 | 22.0996 | 22.6165 | 23.5759 | 23.26 | 24.5135 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236
30% | 3953.6322 | 16.6342 | 17.529 | 19.9075 | 17.5603 | 18.6401 | 15.0702 | 15.9693 | 16.6417 | 17.3834 | 17.7713 | 18.1074 | 18.941 | 18.436 | 19.7963 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 30% | 3953.6322 | 17.7044 | 18.6297 | 20.9896 | 18.7183 | 19.8018 | 16.3305 | 17.1658 | 17.8772 | 18.6185 | 18.9425 | 19.3855 | 20.2079 | 19.9371 | 21.0116 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308
25% | 4060.9208 | 13.8618 | 14.6075 | 16.5896 | 14.6336 | 15.5334 | 12.5585 | 13.3078 | 13.8681 | 14.4862 | 14.8094 | 15.0895 | 15.7842 | 15.3634 | 16.4969 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 25% | 4060.9208 | 14.7537 | 15.5247 | 17.4913 | 15.5985 | 16.5015 | 13.6088 | 14.3048 | 14.8976 | 15.5154 | 15.7854 | 16.1546 | 16.8399 | 16.6143 | 17.5096 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257
20% | 4165.2375 | 11.0894 | 11.686 | 13.2716 | 11.7069 | 12.4267 | 10.0468 | 10.6462 | 11.0945 | 11.5889 | 11.8475 | 12.0716 | 12.6273 | 12.2907 | 13.1975 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 20% | 4165.2375 | 11.8029 | 12.4198 | 13.9931 | 12.4788 | 13.2012 | 10.887 | 11.4438 | 11.9181 | 12.4124 | 12.6283 | 12.9237 | 13.4719 | 13.2914 | 14.0077 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206
15% | 4270.4458 | 8.3171 | 8.7645 | 9.9537 | 8.7801 | 9.32 | 7.5351 | 7.9847 | 8.3208 | 8.6917 | 8.8857 | 9.0537 | 9.4705 | 9.218 | 9.8981 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 15% | 4270.4458 | 8.8522 | 9.3148 | 10.4948 | 9.3591 | 9.9009 | 8.1653 | 8.5829 | 8.9386 | 9.3093 | 9.4713 | 9.6928 | 10.1039 | 9.9686 | 10.5058 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154
10% | 4373.8709 | 5.5447 | 5.843 | 6.6358 | 5.8534 | 6.2134 | 5.0234 | 5.3231 | 5.5472 | 5.7945 | 5.9238 | 6.0358 | 6.3137 | 6.1453 | 6.5988 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 10% | 4373.8709 | 5.9015 | 6.2099 | 6.9965 | 6.2394 | 6.6006 | 5.4435 | 5.7219 | 5.9591 | 6.2062 | 6.3142 | 6.4618 | 6.736 | 6.6457 | 7.0039 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103
5% | 4391.7028 | 2.7724 | 2.9215 | 3.3179 | 2.9267 | 3.1067 | 2.5117 | 2.6616 | 2.7736 | 2.8972 | 2.9619 | 3.0179 | 3.1568 | 3.0727 | 3.2994 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 5% | 4391.7028 | 2.9507 | 3.1049 | 3.4983 | 3.1197 | 3.3003 | 2.7218 | 2.861 | 2.9795 | 3.1031 | 3.1571 | 3.2309 | 3.368 | 3.3229 | 3.5019 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051
9.992e-14% | 4391.7028 | 5.5403e-14 | 5.8383e-14 | 6.6305e-14 | 5.8488e-14 | 6.2084e-14 | 5.0194e-14 | 5.3189e-14 | 5.5428e-14 | 5.7898e-14 | 5.919e-14 | 6.031e-14 | 6.3086e-14 | 6.1404e-14 | 6.5935e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 9.992e-14% | 4391.7028 | 5.8968e-14 | 6.2049e-14 | 6.9909e-14 | 6.2344e-14 | 6.5953e-14 | 5.4392e-14 | 5.7173e-14 | 5.9543e-14 | 6.2012e-14 | 6.3091e-14 | 6.4567e-14 | 6.7306e-14 | 6.6404e-14 | 6.9983e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.6554 | 64.8897 | 72.627 | 63.708 | 66.6413 | 54.7692 | 56.4357 | 58.3388 | 59.8594 | 60.8481 | 63.2106 | 64.8434 | 65.6997 | 67.293 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 100% | 0 | 70.4803 | 73.2479 | 81.0067 | 72.0246 | 75.3311 | 63.4783 | 65.6253 | 67.6902 | 69.4782 | 70.3722 | 71.693 | 73.2047 | 74.7467 | 76.6887 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885
99% | 0 | 62.0288 | 64.2408 | 71.9008 | 63.0709 | 65.9749 | 54.2215 | 55.8713 | 57.7554 | 59.2608 | 60.2396 | 62.5785 | 64.195 | 65.0427 | 66.6201 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 99% | 0.75633 | 69.7755 | 72.5154 | 80.1966 | 71.3043 | 74.5778 | 62.8435 | 64.969 | 67.0133 | 68.7834 | 69.6684 | 70.9761 | 72.4727 | 73.9993 | 75.9218 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186
98% | 0.37816 | 61.4023 | 63.5919 | 71.1745 | 62.4338 | 65.3085 | 53.6738 | 55.307 | 57.172 | 58.6622 | 59.6311 | 61.9464 | 63.5465 | 64.3857 | 65.9472 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 98% | 1.1345 | 69.0707 | 71.7829 | 79.3865 | 70.5841 | 73.8245 | 62.2087 | 64.3128 | 66.3364 | 68.0886 | 68.9647 | 70.2592 | 71.7406 | 73.2518 | 75.1549 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487
97% | 0.75633 | 60.7757 | 62.943 | 70.4482 | 61.7967 | 64.642 | 53.1261 | 54.7426 | 56.5886 | 58.0637 | 59.0226 | 61.3143 | 62.8981 | 63.7287 | 65.2743 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 97% | 1.8908 | 68.3659 | 71.0504 | 78.5765 | 69.8639 | 73.0712 | 61.5739 | 63.6565 | 65.6595 | 67.3938 | 68.261 | 69.5422 | 71.0086 | 72.5043 | 74.388 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788
95% | 1.8908 | 59.5226 | 61.6453 | 68.9957 | 60.5226 | 63.3092 | 52.0307 | 53.6139 | 55.4218 | 56.8665 | 57.8057 | 60.0501 | 61.6012 | 62.4148 | 63.9284 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 95% | 3.4035 | 66.9563 | 69.5855 | 76.9563 | 68.4234 | 71.5646 | 60.3044 | 62.344 | 64.3057 | 66.0043 | 66.8536 | 68.1084 | 69.5445 | 71.0094 | 72.8542 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139
90% | 4.538 | 56.3898 | 58.4008 | 65.3643 | 57.3372 | 59.9772 | 49.2923 | 50.7921 | 52.5049 | 53.8735 | 54.7633 | 56.8896 | 58.3591 | 59.1298 | 60.5637 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 90% | 9.0759 | 63.4323 | 65.9231 | 72.906 | 64.8221 | 67.798 | 57.1305 | 59.0628 | 60.9212 | 62.5303 | 63.3349 | 64.5237 | 65.8842 | 67.2721 | 69.0198 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896
85% | 9.0759 | 53.2571 | 55.1563 | 61.733 | 54.1518 | 56.6451 | 46.5538 | 47.9703 | 49.588 | 50.8805 | 51.7209 | 53.729 | 55.1169 | 55.8448 | 57.1991 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 85% | 16.2611 | 59.9082 | 62.2607 | 68.8557 | 61.2209 | 64.0315 | 53.9565 | 55.7815 | 57.5367 | 59.0564 | 59.8163 | 60.9391 | 62.224 | 63.5347 | 65.1854 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402
80% | 27.606 | 50.1243 | 51.9118 | 58.1016 | 50.9664 | 53.313 | 43.8154 | 45.1485 | 46.671 | 47.8876 | 48.6785 | 50.5685 | 51.8747 | 52.5598 | 53.8344 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 80% | 24.9588 | 56.3842 | 58.5983 | 64.8053 | 57.6197 | 60.2649 | 50.7826 | 52.5002 | 54.1522 | 55.5825 | 56.2977 | 57.3544 | 58.5638 | 59.7974 | 61.3509 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908
75% | 57.481 | 46.9915 | 48.6673 | 54.4703 | 47.781 | 49.981 | 41.0769 | 42.3267 | 43.7541 | 44.8946 | 45.6361 | 47.408 | 48.6326 | 49.2748 | 50.4698 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 75% | 32.9003 | 52.8602 | 54.9359 | 60.755 | 54.0184 | 56.4983 | 47.6087 | 49.219 | 50.7676 | 52.1086 | 52.7791 | 53.7698 | 54.9035 | 56.06 | 57.5165 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414
70% | 106.2642 | 43.8588 | 45.4228 | 50.8389 | 44.5956 | 46.6489 | 38.3384 | 39.505 | 40.8371 | 41.9016 | 42.5937 | 44.2474 | 45.3904 | 45.9898 | 47.1051 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 70% | 41.9762 | 49.3362 | 51.2735 | 56.7047 | 50.4172 | 52.7318 | 44.4348 | 45.9377 | 47.3831 | 48.6347 | 49.2605 | 50.1851 | 51.2433 | 52.3227 | 53.6821 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919
65% | 201.9397 | 40.726 | 42.1783 | 47.2076 | 41.4102 | 43.3168 | 35.6 | 36.6832 | 37.9202 | 38.9086 | 39.5513 | 41.0869 | 42.1482 | 42.7048 | 43.7405 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 65% | 67.6914 | 45.8122 | 47.6111 | 52.6543 | 46.816 | 48.9652 | 41.2609 | 42.6564 | 43.9986 | 45.1608 | 45.7419 | 46.6005 | 47.5831 | 48.5854 | 49.8476 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425
60% | 402.745 | 37.5932 | 38.9338 | 43.5762 | 38.2248 | 39.9848 | 32.8615 | 33.8614 | 35.0033 | 35.9157 | 36.5089 | 37.9264 | 38.906 | 39.4198 | 40.3758 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 60% | 98.7009 | 42.2882 | 43.9487 | 48.604 | 43.2148 | 45.1987 | 38.087 | 39.3752 | 40.6141 | 41.6869 | 42.2233 | 43.0158 | 43.9228 | 44.848 | 46.0132 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931
55% | 655.7369 | 34.4605 | 35.6894 | 39.9449 | 35.0394 | 36.6527 | 30.1231 | 31.0396 | 32.0863 | 32.9227 | 33.4665 | 34.7658 | 35.6639 | 36.1349 | 37.0112 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 55% | 153.5347 | 38.7642 | 40.2863 | 44.5537 | 39.6135 | 41.4321 | 34.9131 | 36.0939 | 37.2296 | 38.213 | 38.7047 | 39.4312 | 40.2626 | 41.1107 | 42.1788 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437
50% | 981.7145 | 31.3277 | 32.4449 | 36.3135 | 31.854 | 33.3206 | 27.3846 | 28.2178 | 29.1694 | 29.9297 | 30.424 | 31.6053 | 32.4217 | 32.8499 | 33.6465 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 50% | 258.2862 | 35.2401 | 36.6239 | 40.5033 | 36.0123 | 37.6656 | 31.7391 | 32.8126 | 33.8451 | 34.7391 | 35.1861 | 35.8465 | 36.6024 | 37.3734 | 38.3443 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942
45% | 1622.7029 | 28.1949 | 29.2004 | 32.6822 | 28.6686 | 29.9886 | 24.6461 | 25.396 | 26.2524 | 26.9367 | 27.3816 | 28.4448 | 29.1795 | 29.5649 | 30.2819 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 45% | 488.9664 | 31.7161 | 32.9615 | 36.453 | 32.4111 | 33.899 | 28.5652 | 29.5314 | 30.4606 | 31.2652 | 31.6675 | 32.2619 | 32.9421 | 33.636 | 34.5099 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448
40% | 2442.9413 | 25.0621 | 25.9559 | 29.0508 | 25.4832 | 26.6565 | 21.9077 | 22.5743 | 23.3355 | 23.9438 | 24.3392 | 25.2842 | 25.9374 | 26.2799 | 26.9172 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 40% | 928.0152 | 28.1921 | 29.2991 | 32.4027 | 28.8098 | 30.1325 | 25.3913 | 26.2501 | 27.0761 | 27.7913 | 28.1489 | 28.6772 | 29.2819 | 29.8987 | 30.6755 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954
35% | 3006.7842 | 21.9294 | 22.7114 | 25.4195 | 22.2978 | 23.3244 | 19.1692 | 19.7525 | 20.4186 | 20.9508 | 21.2968 | 22.1237 | 22.6952 | 22.9949 | 23.5526 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 35% | 1530.4309 | 24.6681 | 25.6368 | 28.3523 | 25.2086 | 26.3659 | 22.2174 | 22.9689 | 23.6916 | 24.3174 | 24.6303 | 25.0926 | 25.6216 | 26.1614 | 26.841 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946
30% | 3276.4154 | 18.7966 | 19.4669 | 21.7881 | 19.1124 | 19.9924 | 16.4308 | 16.9307 | 17.5016 | 17.9578 | 18.2544 | 18.9632 | 19.453 | 19.7099 | 20.1879 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 30% | 2592.3162 | 21.1441 | 21.9744 | 24.302 | 21.6074 | 22.5993 | 19.0435 | 19.6876 | 20.3071 | 20.8434 | 21.1116 | 21.5079 | 21.9614 | 22.424 | 23.0066 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965
25% | 3466.632 | 15.6638 | 16.2224 | 18.1568 | 15.927 | 16.6603 | 13.6923 | 14.1089 | 14.5847 | 14.9649 | 15.212 | 15.8027 | 16.2109 | 16.4249 | 16.8233 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 25% | 3659.4958 | 17.6201 | 18.312 | 20.2517 | 18.0061 | 18.8328 | 15.8696 | 16.4063 | 16.9225 | 17.3695 | 17.593 | 17.9233 | 18.3012 | 18.6867 | 19.1722 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471
20% | 3713.9514 | 12.5311 | 12.9779 | 14.5254 | 12.7416 | 13.3283 | 10.9538 | 11.2871 | 11.6678 | 11.9719 | 12.1696 | 12.6421 | 12.9687 | 13.1399 | 13.4586 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 20% | 4005.5161 | 14.0961 | 14.6496 | 16.2013 | 14.4049 | 15.0662 | 12.6957 | 13.1251 | 13.538 | 13.8956 | 14.0744 | 14.3386 | 14.6409 | 14.9493 | 15.3377 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977
15% | 4043.3325 | 9.3983 | 9.7335 | 10.8941 | 9.5562 | 9.9962 | 8.2154 | 8.4653 | 8.7508 | 8.9789 | 9.1272 | 9.4816 | 9.7265 | 9.855 | 10.094 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 15% | 4281.1979 | 10.572 | 10.9872 | 12.151 | 10.8037 | 11.2997 | 9.5217 | 9.8438 | 10.1535 | 10.4217 | 10.5558 | 10.754 | 10.9807 | 11.212 | 11.5033 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483
10% | 4350.7801 | 6.2655 | 6.489 | 7.2627 | 6.3708 | 6.6641 | 5.4769 | 5.6436 | 5.8339 | 5.9859 | 6.0848 | 6.3211 | 6.4843 | 6.57 | 6.7293 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 10% | 4391.6218 | 7.048 | 7.3248 | 8.1007 | 7.2025 | 7.5331 | 6.3478 | 6.5625 | 6.769 | 6.9478 | 7.0372 | 7.1693 | 7.3205 | 7.4747 | 7.6689 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988
5% | 4391.6218 | 3.1328 | 3.2445 | 3.6314 | 3.1854 | 3.3321 | 2.7385 | 2.8218 | 2.9169 | 2.993 | 3.0424 | 3.1605 | 3.2422 | 3.285 | 3.3647 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 5% | 4391.6218 | 3.524 | 3.6624 | 4.0503 | 3.6012 | 3.7666 | 3.1739 | 3.2813 | 3.3845 | 3.4739 | 3.5186 | 3.5847 | 3.6602 | 3.7373 | 3.8344 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494
9.992e-14% | 4391.6218 | 6.2605e-14 | 6.4838e-14 | 7.2569e-14 | 6.3657e-14 | 6.6588e-14 | 5.4725e-14 | 5.6391e-14 | 5.8292e-14 | 5.9812e-14 | 6.0799e-14 | 6.316e-14 | 6.4792e-14 | 6.5647e-14 | 6.7239e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 9.992e-14% | 4391.6218 | 7.0424e-14 | 7.3189e-14 | 8.0942e-14 | 7.1967e-14 | 7.5271e-14 | 6.3428e-14 | 6.5573e-14 | 6.7636e-14 | 6.9423e-14 | 7.0316e-14 | 7.1636e-14 | 7.3146e-14 | 7.4687e-14 | 7.6627e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 79.234 | 82.2311 | 84.4723 | 86.9447 | 88.2377 | 89.3579 | 92.1367 | 90.4534 | 94.9876 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100% | 0 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 83.435 | 86.2192 | 88.5906 | 91.0618 | 92.1417 | 93.6184 | 96.3596 | 95.457 | 99.0386 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028
99% | 0.8916 | 54.8927 | 57.8458 | 65.6947 | 72.3039 | 75.8673 | 78.4417 | 81.4088 | 83.6276 | 86.0753 | 87.3553 | 88.4643 | 91.2154 | 89.5489 | 94.0377 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99% | 0.8916 | 58.4246 | 61.4779 | 69.2657 | 76.1252 | 79.701 | 82.6007 | 85.357 | 87.7047 | 90.1512 | 91.2203 | 92.6823 | 95.396 | 94.5025 | 98.0482 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918
98% | 3.5664 | 54.3382 | 57.2615 | 65.0311 | 71.5736 | 75.1009 | 77.6493 | 80.5865 | 82.7829 | 85.2058 | 86.4729 | 87.5707 | 90.294 | 88.6444 | 93.0878 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98% | 3.5664 | 57.8344 | 60.8569 | 68.5661 | 75.3563 | 78.8959 | 81.7663 | 84.4948 | 86.8188 | 89.2406 | 90.2989 | 91.7461 | 94.4324 | 93.5479 | 97.0578 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807
97% | 4.7552 | 53.7838 | 56.6772 | 64.3675 | 70.8433 | 74.3346 | 76.857 | 79.7641 | 81.9382 | 84.3364 | 85.5905 | 86.6771 | 89.3726 | 87.7398 | 92.138 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97% | 4.7552 | 57.2443 | 60.2359 | 67.8664 | 74.5874 | 78.0908 | 80.932 | 83.6327 | 85.9329 | 88.3299 | 89.3774 | 90.8099 | 93.4688 | 92.5933 | 96.0674 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697
95% | 7.7272 | 52.6748 | 55.5086 | 63.0403 | 69.3826 | 72.8019 | 75.2723 | 78.1195 | 80.2487 | 82.5975 | 83.8258 | 84.89 | 87.5299 | 85.9308 | 90.2382 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95% | 7.7272 | 56.064 | 58.994 | 66.4671 | 73.0495 | 76.4807 | 79.2633 | 81.9083 | 84.161 | 86.5087 | 87.5346 | 88.9375 | 91.5416 | 90.6842 | 94.0866 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477
90% | 39.2302 | 49.9025 | 52.5871 | 59.7224 | 65.7309 | 68.9702 | 71.3106 | 74.008 | 76.0251 | 78.2502 | 79.4139 | 80.4221 | 82.9231 | 81.4081 | 85.4888 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90% | 39.2302 | 53.1132 | 55.889 | 62.9689 | 69.2048 | 72.4554 | 75.0915 | 77.5973 | 79.7315 | 81.9556 | 82.9275 | 84.2566 | 86.7237 | 85.9113 | 89.1347 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925
85% | 117.6906 | 47.1301 | 49.6656 | 56.4045 | 62.0791 | 65.1386 | 67.3489 | 69.8964 | 71.8015 | 73.903 | 75.002 | 75.9542 | 78.3162 | 76.8854 | 80.7395 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85% | 117.6906 | 50.1625 | 52.7841 | 59.4706 | 65.3601 | 68.4301 | 70.9198 | 73.2863 | 75.302 | 77.4025 | 78.3204 | 79.5757 | 81.9057 | 81.1385 | 84.1828 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374
80% | 268.3703 | 44.3577 | 46.7441 | 53.0866 | 58.4274 | 61.3069 | 63.3872 | 65.7849 | 67.5779 | 69.5558 | 70.5901 | 71.4863 | 73.7094 | 72.3627 | 75.9901 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80% | 268.3703 | 47.2118 | 49.6791 | 55.9723 | 61.5153 | 64.4048 | 66.748 | 68.9754 | 70.8725 | 72.8494 | 73.7134 | 74.8948 | 77.0877 | 76.3656 | 79.2309 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822
75% | 455.9026 | 41.5854 | 43.8226 | 49.7687 | 54.7757 | 57.4752 | 59.4255 | 61.6733 | 63.3542 | 65.2085 | 66.1783 | 67.0184 | 69.1025 | 67.8401 | 71.2407 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75% | 455.9026 | 44.261 | 46.5742 | 52.474 | 57.6706 | 60.3795 | 62.5763 | 64.6644 | 66.4429 | 68.2963 | 69.1063 | 70.2138 | 72.2697 | 71.5928 | 74.2789 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271
70% | 690.9866 | 38.813 | 40.9011 | 46.4508 | 51.124 | 53.6435 | 55.4638 | 57.5618 | 59.1306 | 60.8613 | 61.7664 | 62.5505 | 64.4957 | 63.3174 | 66.4913 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70% | 690.9866 | 41.3103 | 43.4692 | 48.9758 | 53.8259 | 56.3542 | 58.4045 | 60.3535 | 62.0134 | 63.7433 | 64.4992 | 65.5329 | 67.4517 | 66.8199 | 69.327 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772
65% | 967.6784 | 36.0407 | 37.9796 | 43.1329 | 47.4723 | 49.8118 | 51.5021 | 53.4502 | 54.907 | 56.5141 | 57.3545 | 58.0826 | 59.8889 | 58.7947 | 61.7419 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65% | 967.6784 | 38.3596 | 40.3643 | 45.4775 | 49.9812 | 52.3289 | 54.2328 | 56.0425 | 57.5839 | 59.1902 | 59.8921 | 60.852 | 62.6338 | 62.0471 | 64.3751 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168
60% | 1292.8136 | 33.2683 | 35.0581 | 39.8149 | 43.8206 | 45.9802 | 47.5404 | 49.3386 | 50.6834 | 52.1668 | 52.9426 | 53.6147 | 55.282 | 54.2721 | 56.9926 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60% | 1292.8136 | 35.4088 | 37.2594 | 41.9792 | 46.1365 | 48.3036 | 50.061 | 51.7315 | 53.1543 | 54.6371 | 55.285 | 56.1711 | 57.8158 | 57.2742 | 59.4231 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617
55% | 1647.0743 | 30.496 | 32.1366 | 36.497 | 40.1689 | 42.1485 | 43.5787 | 45.2271 | 46.4598 | 47.8196 | 48.5307 | 49.1468 | 50.6752 | 49.7494 | 52.2432 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55% | 1647.0743 | 32.4581 | 34.1544 | 38.481 | 42.2918 | 44.2783 | 45.8893 | 47.4206 | 48.7248 | 50.084 | 50.6779 | 51.4901 | 52.9978 | 52.5014 | 54.4712 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065
50% | 2104.1657 | 27.7236 | 29.2151 | 33.1791 | 36.5171 | 38.3168 | 39.617 | 41.1155 | 42.2362 | 43.4724 | 44.1188 | 44.6789 | 46.0684 | 45.2267 | 47.4938 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50% | 2104.1657 | 29.5074 | 31.0495 | 34.9827 | 38.4471 | 40.253 | 41.7175 | 43.1096 | 44.2953 | 45.5309 | 46.0708 | 46.8092 | 48.1798 | 47.7285 | 49.5193 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514
45% | 2736.0097 | 24.9512 | 26.2936 | 29.8612 | 32.8654 | 34.4851 | 35.6553 | 37.004 | 38.0125 | 39.1251 | 39.707 | 40.211 | 41.4615 | 40.704 | 42.7444 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45% | 2736.0097 | 26.5566 | 27.9445 | 31.4844 | 34.6024 | 36.2277 | 37.5458 | 38.7987 | 39.8658 | 40.9778 | 41.4638 | 42.1283 | 43.3618 | 42.9557 | 44.5674 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963
40% | 3483.7613 | 22.1789 | 23.372 | 26.5433 | 29.2137 | 30.6534 | 31.6936 | 32.8924 | 33.7889 | 34.7779 | 35.2951 | 35.7431 | 36.8547 | 36.1814 | 37.995 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40% | 3483.7613 | 23.6059 | 24.8396 | 27.9862 | 30.7577 | 32.2024 | 33.374 | 34.4877 | 35.4362 | 36.4247 | 36.8567 | 37.4474 | 38.5438 | 38.1828 | 39.6154 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411
35% | 3830.2948 | 19.4065 | 20.4505 | 23.2254 | 25.562 | 26.8218 | 27.7319 | 28.7809 | 29.5653 | 30.4307 | 30.8832 | 31.2753 | 32.2479 | 31.6587 | 33.2457 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35% | 3830.2948 | 20.6551 | 21.7346 | 24.4879 | 26.913 | 28.1771 | 29.2023 | 30.1767 | 31.0067 | 31.8716 | 32.2496 | 32.7665 | 33.7259 | 33.41 | 34.6635 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386
30% | 3953.6322 | 16.6342 | 17.529 | 19.9075 | 21.9103 | 22.9901 | 23.7702 | 24.6693 | 25.3417 | 26.0834 | 26.4713 | 26.8074 | 27.641 | 27.136 | 28.4963 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30% | 3953.6322 | 17.7044 | 18.6297 | 20.9896 | 23.0683 | 24.1518 | 25.0305 | 25.8658 | 26.5772 | 27.3185 | 27.6425 | 28.0855 | 28.9079 | 28.6371 | 29.7116 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308
25% | 4060.9208 | 13.8618 | 14.6075 | 16.5896 | 18.2586 | 19.1584 | 19.8085 | 20.5578 | 21.1181 | 21.7362 | 22.0594 | 22.3395 | 23.0342 | 22.6134 | 23.7469 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25% | 4060.9208 | 14.7537 | 15.5247 | 17.4913 | 19.2235 | 20.1265 | 20.8588 | 21.5548 | 22.1476 | 22.7654 | 23.0354 | 23.4046 | 24.0899 | 23.8643 | 24.7596 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757
20% | 4165.2375 | 11.0894 | 11.686 | 13.2716 | 14.6069 | 15.3267 | 15.8468 | 16.4462 | 16.8945 | 17.3889 | 17.6475 | 17.8716 | 18.4273 | 18.0907 | 18.9975 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20% | 4165.2375 | 11.8029 | 12.4198 | 13.9931 | 15.3788 | 16.1012 | 16.687 | 17.2438 | 17.7181 | 18.2124 | 18.4283 | 18.7237 | 19.2719 | 19.0914 | 19.8077 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206
15% | 4270.4458 | 8.3171 | 8.7645 | 9.9537 | 10.9551 | 11.495 | 11.8851 | 12.3347 | 12.6708 | 13.0417 | 13.2357 | 13.4037 | 13.8205 | 13.568 | 14.2481 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15% | 4270.4458 | 8.8522 | 9.3148 | 10.4948 | 11.5341 | 12.0759 | 12.5153 | 12.9329 | 13.2886 | 13.6593 | 13.8213 | 14.0428 | 14.4539 | 14.3186 | 14.8558 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654
10% | 4373.8709 | 5.5447 | 5.843 | 6.6358 | 7.3034 | 7.6634 | 7.9234 | 8.2231 | 8.4472 | 8.6945 | 8.8238 | 8.9358 | 9.2137 | 9.0453 | 9.4988 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10% | 4373.8709 | 5.9015 | 6.2099 | 6.9965 | 7.6894 | 8.0506 | 8.3435 | 8.6219 | 8.8591 | 9.1062 | 9.2142 | 9.3618 | 9.636 | 9.5457 | 9.9039 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103
5% | 4391.7028 | 2.7724 | 2.9215 | 3.3179 | 3.6517 | 3.8317 | 3.9617 | 4.1116 | 4.2236 | 4.3472 | 4.4119 | 4.4679 | 4.6068 | 4.5227 | 4.7494 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5% | 4391.7028 | 2.9507 | 3.1049 | 3.4983 | 3.8447 | 4.0253 | 4.1718 | 4.311 | 4.4295 | 4.5531 | 4.6071 | 4.6809 | 4.818 | 4.7729 | 4.9519 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551
9.992e-14% | 4391.7028 | 5.5403e-14 | 5.8383e-14 | 6.6305e-14 | 7.2976e-14 | 7.6572e-14 | 7.9171e-14 | 8.2165e-14 | 8.4405e-14 | 8.6875e-14 | 8.8167e-14 | 8.9286e-14 | 9.2063e-14 | 9.0381e-14 | 9.4912e-14 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 9.992e-14% | 4391.7028 | 5.8968e-14 | 6.2049e-14 | 6.9909e-14 | 7.6833e-14 | 8.0442e-14 | 8.3368e-14 | 8.615e-14 | 8.852e-14 | 9.0989e-14 | 9.2068e-14 | 9.3544e-14 | 9.6283e-14 | 9.5381e-14 | 9.8959e-14 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 83.7692 | 85.4357 | 87.3388 | 88.8594 | 89.8481 | 92.2106 | 93.8434 | 94.6997 | 96.293 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 100% | 0 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 92.4783 | 94.6253 | 96.6902 | 98.4782 | 99.3722 | 100.693 | 102.2047 | 103.7467 | 105.6887 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885
99% | 0 | 62.0288 | 64.2408 | 71.9008 | 77.4259 | 80.3299 | 82.9315 | 84.5813 | 86.4654 | 87.9708 | 88.9496 | 91.2885 | 92.905 | 93.7527 | 95.3301 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 99% | 0.75633 | 69.7755 | 72.5154 | 80.1966 | 85.6593 | 88.9328 | 91.5535 | 93.679 | 95.7233 | 97.4934 | 98.3784 | 99.6861 | 101.1827 | 102.7093 | 104.6318 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286
98% | 0.37816 | 61.4023 | 63.5919 | 71.1745 | 76.6438 | 79.5185 | 82.0938 | 83.727 | 85.592 | 87.0822 | 88.0511 | 90.3664 | 91.9665 | 92.8057 | 94.3672 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 98% | 1.1345 | 69.0707 | 71.7829 | 79.3865 | 84.7941 | 88.0345 | 90.6287 | 92.7328 | 94.7564 | 96.5086 | 97.3847 | 98.6792 | 100.1606 | 101.6718 | 103.5749 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687
97% | 0.75633 | 60.7757 | 62.943 | 70.4482 | 75.8617 | 78.707 | 81.2561 | 82.8726 | 84.7186 | 86.1937 | 87.1526 | 89.4443 | 91.0281 | 91.8587 | 93.4043 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 97% | 1.8908 | 68.3659 | 71.0504 | 78.5765 | 83.9289 | 87.1362 | 89.7039 | 91.7865 | 93.7895 | 95.5238 | 96.391 | 97.6722 | 99.1386 | 100.6343 | 102.518 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088
95% | 1.8908 | 59.5226 | 61.6453 | 68.9957 | 74.2976 | 77.0842 | 79.5807 | 81.1639 | 82.9718 | 84.4165 | 85.3557 | 87.6001 | 89.1512 | 89.9648 | 91.4784 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 95% | 3.4035 | 66.9563 | 69.5855 | 76.9563 | 82.1984 | 85.3396 | 87.8544 | 89.894 | 91.8557 | 93.5543 | 94.4036 | 95.6584 | 97.0945 | 98.5594 | 100.4042 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689
90% | 4.538 | 56.3898 | 58.4008 | 65.3643 | 70.3872 | 73.0272 | 75.3923 | 76.8921 | 78.6049 | 79.9735 | 80.8633 | 82.9896 | 84.4591 | 85.2298 | 86.6637 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 90% | 9.0759 | 63.4323 | 65.9231 | 72.906 | 77.8721 | 80.848 | 83.2305 | 85.1628 | 87.0212 | 88.6303 | 89.4349 | 90.6237 | 91.9842 | 93.3721 | 95.1198 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896
85% | 9.0759 | 53.2571 | 55.1563 | 61.733 | 66.4768 | 68.9701 | 71.2038 | 72.6203 | 74.238 | 75.5305 | 76.3709 | 78.379 | 79.7669 | 80.4948 | 81.8491 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 85% | 16.2611 | 59.9082 | 62.2607 | 68.8557 | 73.5459 | 76.3565 | 78.6065 | 80.4315 | 82.1867 | 83.7064 | 84.4663 | 85.5891 | 86.874 | 88.1847 | 89.8354 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902
80% | 27.606 | 50.1243 | 51.9118 | 58.1016 | 62.5664 | 64.913 | 67.0154 | 68.3485 | 69.871 | 71.0876 | 71.8785 | 73.7685 | 75.0747 | 75.7598 | 77.0344 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 80% | 24.9588 | 56.3842 | 58.5983 | 64.8053 | 69.2197 | 71.8649 | 73.9826 | 75.7002 | 77.3522 | 78.7825 | 79.4977 | 80.5544 | 81.7638 | 82.9974 | 84.5509 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908
75% | 57.481 | 46.9915 | 48.6673 | 54.4703 | 58.656 | 60.856 | 62.8269 | 64.0767 | 65.5041 | 66.6446 | 67.3861 | 69.158 | 70.3826 | 71.0248 | 72.2198 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 75% | 32.9003 | 52.8602 | 54.9359 | 60.755 | 64.8934 | 67.3733 | 69.3587 | 70.969 | 72.5176 | 73.8586 | 74.5291 | 75.5198 | 76.6535 | 77.81 | 79.2665 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914
70% | 106.2642 | 43.8588 | 45.4228 | 50.8389 | 54.7456 | 56.7989 | 58.6384 | 59.805 | 61.1371 | 62.2016 | 62.8937 | 64.5474 | 65.6904 | 66.2898 | 67.4051 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 70% | 41.9762 | 49.3362 | 51.2735 | 56.7047 | 60.5672 | 62.8818 | 64.7348 | 66.2377 | 67.6831 | 68.9347 | 69.5605 | 70.4851 | 71.5433 | 72.6227 | 73.9821 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919
65% | 201.9397 | 40.726 | 42.1783 | 47.2076 | 50.8352 | 52.7418 | 54.45 | 55.5332 | 56.7702 | 57.7586 | 58.4013 | 59.9369 | 60.9982 | 61.5548 | 62.5905 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 65% | 67.6914 | 45.8122 | 47.6111 | 52.6543 | 56.241 | 58.3902 | 60.1109 | 61.5064 | 62.8486 | 64.0108 | 64.5919 | 65.4505 | 66.4331 | 67.4354 | 68.6976 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925
60% | 402.745 | 37.5932 | 38.9338 | 43.5762 | 46.9248 | 48.6848 | 50.2615 | 51.2614 | 52.4033 | 53.3157 | 53.9089 | 55.3264 | 56.306 | 56.8198 | 57.7758 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 60% | 98.7009 | 42.2882 | 43.9487 | 48.604 | 51.9148 | 53.8987 | 55.487 | 56.7752 | 58.0141 | 59.0869 | 59.6233 | 60.4158 | 61.3228 | 62.248 | 63.4132 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931
55% | 655.7369 | 34.4605 | 35.6894 | 39.9449 | 43.0144 | 44.6277 | 46.0731 | 46.9896 | 48.0363 | 48.8727 | 49.4165 | 50.7158 | 51.6139 | 52.0849 | 52.9612 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 55% | 153.5347 | 38.7642 | 40.2863 | 44.5537 | 47.5885 | 49.4071 | 50.8631 | 52.0439 | 53.1796 | 54.163 | 54.6547 | 55.3812 | 56.2126 | 57.0607 | 58.1288 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937
50% | 981.7145 | 31.3277 | 32.4449 | 36.3135 | 39.104 | 40.5706 | 41.8846 | 42.7178 | 43.6694 | 44.4297 | 44.924 | 46.1053 | 46.9217 | 47.3499 | 48.1465 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 50% | 258.2862 | 35.2401 | 36.6239 | 40.5033 | 43.2623 | 44.9156 | 46.2391 | 47.3126 | 48.3451 | 49.2391 | 49.6861 | 50.3465 | 51.1024 | 51.8734 | 52.8443 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942
45% | 1622.7029 | 28.1949 | 29.2004 | 32.6822 | 35.1936 | 36.5136 | 37.6961 | 38.446 | 39.3024 | 39.9867 | 40.4316 | 41.4948 | 42.2295 | 42.6149 | 43.3319 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 45% | 488.9664 | 31.7161 | 32.9615 | 36.453 | 38.9361 | 40.424 | 41.6152 | 42.5814 | 43.5106 | 44.3152 | 44.7175 | 45.3119 | 45.9921 | 46.686 | 47.5599 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948
40% | 2442.9413 | 25.0621 | 25.9559 | 29.0508 | 31.2832 | 32.4565 | 33.5077 | 34.1743 | 34.9355 | 35.5438 | 35.9392 | 36.8842 | 37.5374 | 37.8799 | 38.5172 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 40% | 928.0152 | 28.1921 | 29.2991 | 32.4027 | 34.6098 | 35.9325 | 36.9913 | 37.8501 | 38.6761 | 39.3913 | 39.7489 | 40.2772 | 40.8819 | 41.4987 | 42.2755 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954
35% | 3006.7842 | 21.9294 | 22.7114 | 25.4195 | 27.3728 | 28.3994 | 29.3192 | 29.9025 | 30.5686 | 31.1008 | 31.4468 | 32.2737 | 32.8452 | 33.1449 | 33.7026 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 35% | 1530.4309 | 24.6681 | 25.6368 | 28.3523 | 30.2836 | 31.4409 | 32.3674 | 33.1189 | 33.8416 | 34.4674 | 34.7803 | 35.2426 | 35.7716 | 36.3114 | 36.991 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096
30% | 3276.4154 | 18.7966 | 19.4669 | 21.7881 | 23.4624 | 24.3424 | 25.1308 | 25.6307 | 26.2016 | 26.6578 | 26.9544 | 27.6632 | 28.153 | 28.4099 | 28.8879 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 30% | 2592.3162 | 21.1441 | 21.9744 | 24.302 | 25.9574 | 26.9493 | 27.7435 | 28.3876 | 29.0071 | 29.5434 | 29.8116 | 30.2079 | 30.6614 | 31.124 | 31.7066 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965
25% | 3466.632 | 15.6638 | 16.2224 | 18.1568 | 19.552 | 20.2853 | 20.9423 | 21.3589 | 21.8347 | 22.2149 | 22.462 | 23.0527 | 23.4609 | 23.6749 | 24.0733 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 25% | 3659.4958 | 17.6201 | 18.312 | 20.2517 | 21.6311 | 22.4578 | 23.1196 | 23.6563 | 24.1725 | 24.6195 | 24.843 | 25.1733 | 25.5512 | 25.9367 | 26.4222 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971
20% | 3713.9514 | 12.5311 | 12.9779 | 14.5254 | 15.6416 | 16.2283 | 16.7538 | 17.0871 | 17.4678 | 17.7719 | 17.9696 | 18.4421 | 18.7687 | 18.9399 | 19.2586 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 20% | 4005.5161 | 14.0961 | 14.6496 | 16.2013 | 17.3049 | 17.9662 | 18.4957 | 18.9251 | 19.338 | 19.6956 | 19.8744 | 20.1386 | 20.4409 | 20.7493 | 21.1377 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977
15% | 4043.3325 | 9.3983 | 9.7335 | 10.8941 | 11.7312 | 12.1712 | 12.5654 | 12.8153 | 13.1008 | 13.3289 | 13.4772 | 13.8316 | 14.0765 | 14.205 | 14.444 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 15% | 4281.1979 | 10.572 | 10.9872 | 12.151 | 12.9787 | 13.4747 | 13.8717 | 14.1938 | 14.5035 | 14.7717 | 14.9058 | 15.104 | 15.3307 | 15.562 | 15.8533 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983
10% | 4350.7801 | 6.2655 | 6.489 | 7.2627 | 7.8208 | 8.1141 | 8.3769 | 8.5436 | 8.7339 | 8.8859 | 8.9848 | 9.2211 | 9.3843 | 9.47 | 9.6293 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 10% | 4391.6218 | 7.048 | 7.3248 | 8.1007 | 8.6525 | 8.9831 | 9.2478 | 9.4625 | 9.669 | 9.8478 | 9.9372 | 10.0693 | 10.2205 | 10.3747 | 10.5689 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988
5% | 4391.6218 | 3.1328 | 3.2445 | 3.6314 | 3.9104 | 4.0571 | 4.1885 | 4.2718 | 4.3669 | 4.443 | 4.4924 | 4.6105 | 4.6922 | 4.735 | 4.8147 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 5% | 4391.6218 | 3.524 | 3.6624 | 4.0503 | 4.3262 | 4.4916 | 4.6239 | 4.7313 | 4.8345 | 4.9239 | 4.9686 | 5.0347 | 5.1102 | 5.1873 | 5.2844 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994
9.992e-14% | 4391.6218 | 6.2605e-14 | 6.4838e-14 | 7.2569e-14 | 7.8145e-14 | 8.1076e-14 | 8.3702e-14 | 8.5367e-14 | 8.7269e-14 | 8.8788e-14 | 8.9776e-14 | 9.2137e-14 | 9.3768e-14 | 9.4624e-14 | 9.6216e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.992e-14% | 4391.6218 | 7.0424e-14 | 7.3189e-14 | 8.0942e-14 | 8.6455e-14 | 8.9759e-14 | 9.2404e-14 | 9.455e-14 | 9.6613e-14 | 9.8399e-14 | 9.9293e-14 | 1.0061e-13 | 1.0212e-13 | 1.0366e-13 | 1.056e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 55.4472 | 58.4301 | 66.3582 | 58.5343 | 62.1336 | 50.234 | 53.2311 | 55.4723 | 57.9447 | 59.2377 | 60.3579 | 63.1367 | 61.4534 | 65.9876 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 71.9033 | 100% | 0 | 59.0147 | 62.0989 | 69.9654 | 62.3942 | 66.006 | 54.435 | 57.2192 | 59.5906 | 62.0618 | 63.1417 | 64.6184 | 67.3596 | 66.457 | 70.0386 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028 | 72.1028
99% | 0.8916 | 54.8927 | 57.8458 | 65.6947 | 57.9489 | 61.5123 | 49.7317 | 52.6988 | 54.9176 | 57.3653 | 58.6453 | 59.7543 | 62.5054 | 60.8389 | 65.3277 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 71.1842 | 99% | 0.8916 | 58.4246 | 61.4779 | 69.2657 | 61.7702 | 65.346 | 53.8907 | 56.647 | 58.9947 | 61.4412 | 62.5103 | 63.9723 | 66.686 | 65.7925 | 69.3382 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818 | 71.3818
98% | 3.5664 | 54.3382 | 57.2615 | 65.0311 | 57.3636 | 60.8909 | 49.2293 | 52.1665 | 54.3629 | 56.7858 | 58.0529 | 59.1507 | 61.874 | 60.2244 | 64.6678 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 70.4652 | 98% | 3.5664 | 57.8344 | 60.8569 | 68.5661 | 61.1463 | 64.6859 | 53.3463 | 56.0748 | 58.3988 | 60.8206 | 61.8789 | 63.3261 | 66.0124 | 65.1279 | 68.6378 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607 | 70.6607
97% | 4.7552 | 53.7838 | 56.6772 | 64.3675 | 56.7783 | 60.2696 | 48.727 | 51.6341 | 53.8082 | 56.2064 | 57.4605 | 58.5471 | 61.2426 | 59.6098 | 64.008 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 69.7462 | 97% | 4.7552 | 57.2443 | 60.2359 | 67.8664 | 60.5224 | 64.0258 | 52.802 | 55.5027 | 57.8029 | 60.1999 | 61.2474 | 62.6799 | 65.3388 | 64.4633 | 67.9374 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397 | 69.9397
95% | 7.7272 | 52.6748 | 55.5086 | 63.0403 | 55.6076 | 59.0269 | 47.7223 | 50.5695 | 52.6987 | 55.0475 | 56.2758 | 57.34 | 59.9799 | 58.3808 | 62.6882 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 68.3081 | 95% | 7.7272 | 56.064 | 58.994 | 66.4671 | 59.2745 | 62.7057 | 51.7133 | 54.3583 | 56.611 | 58.9587 | 59.9846 | 61.3875 | 63.9916 | 63.1342 | 66.5366 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977 | 68.4977
90% | 39.2302 | 49.9025 | 52.5871 | 59.7224 | 52.6809 | 55.9202 | 45.2106 | 47.908 | 49.9251 | 52.1502 | 53.3139 | 54.3221 | 56.8231 | 55.3081 | 59.3888 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 64.7129 | 90% | 39.2302 | 53.1132 | 55.889 | 62.9689 | 56.1548 | 59.4054 | 48.9915 | 51.4973 | 53.6315 | 55.8556 | 56.8275 | 58.1566 | 60.6237 | 59.8113 | 63.0347 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925 | 64.8925
85% | 117.6906 | 47.1301 | 49.6656 | 56.4045 | 49.7541 | 52.8136 | 42.6989 | 45.2464 | 47.1515 | 49.253 | 50.352 | 51.3042 | 53.6662 | 52.2354 | 56.0895 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 61.1178 | 85% | 117.6906 | 50.1625 | 52.7841 | 59.4706 | 53.0351 | 56.1051 | 46.2698 | 48.6363 | 50.652 | 52.7525 | 53.6704 | 54.9257 | 57.2557 | 56.4885 | 59.5328 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874 | 61.2874
80% | 268.3703 | 44.3577 | 46.7441 | 53.0866 | 46.8274 | 49.7069 | 40.1872 | 42.5849 | 44.3779 | 46.3558 | 47.3901 | 48.2863 | 50.5094 | 49.1627 | 52.7901 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 57.5226 | 80% | 268.3703 | 47.2118 | 49.6791 | 55.9723 | 49.9153 | 52.8048 | 43.548 | 45.7754 | 47.6725 | 49.6494 | 50.5134 | 51.6948 | 53.8877 | 53.1656 | 56.0309 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822 | 57.6822
75% | 455.9026 | 41.5854 | 43.8226 | 49.7687 | 43.9007 | 46.6002 | 37.6755 | 39.9233 | 41.6042 | 43.4585 | 44.4283 | 45.2684 | 47.3525 | 46.0901 | 49.4907 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 53.9275 | 75% | 455.9026 | 44.261 | 46.5742 | 52.474 | 46.7956 | 49.5045 | 40.8263 | 42.9144 | 44.6929 | 46.5463 | 47.3563 | 48.4638 | 50.5197 | 49.8428 | 52.5289 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771 | 54.0771
70% | 690.9866 | 38.813 | 40.9011 | 46.4508 | 40.974 | 43.4935 | 35.1638 | 37.2618 | 38.8306 | 40.5613 | 41.4664 | 42.2505 | 44.1957 | 43.0174 | 46.1913 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 50.3323 | 70% | 690.9866 | 41.3103 | 43.4692 | 48.9758 | 43.6759 | 46.2042 | 38.1045 | 40.0535 | 41.7134 | 43.4433 | 44.1992 | 45.2329 | 47.1517 | 46.5199 | 49.027 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472 | 50.472
65% | 967.6784 | 36.0407 | 37.9796 | 43.1329 | 38.0473 | 40.3868 | 32.6521 | 34.6002 | 36.057 | 37.6641 | 38.5045 | 39.2326 | 41.0389 | 39.9447 | 42.8919 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 46.7371 | 65% | 967.6784 | 38.3596 | 40.3643 | 45.4775 | 40.5562 | 42.9039 | 35.3828 | 37.1925 | 38.7339 | 40.3402 | 41.0421 | 42.002 | 43.7838 | 43.1971 | 45.5251 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668 | 46.8668
60% | 1292.8136 | 33.2683 | 35.0581 | 39.8149 | 35.1206 | 37.2802 | 30.1404 | 31.9386 | 33.2834 | 34.7668 | 35.5426 | 36.2147 | 37.882 | 36.8721 | 39.5926 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 43.142 | 60% | 1292.8136 | 35.4088 | 37.2594 | 41.9792 | 37.4365 | 39.6036 | 32.661 | 34.3315 | 35.7543 | 37.2371 | 37.885 | 38.7711 | 40.4158 | 39.8742 | 42.0231 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617 | 43.2617
55% | 1647.0743 | 30.496 | 32.1366 | 36.497 | 32.1939 | 34.1735 | 27.6287 | 29.2771 | 30.5098 | 31.8696 | 32.5807 | 33.1968 | 34.7252 | 33.7994 | 36.2932 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 39.5468 | 55% | 1647.0743 | 32.4581 | 34.1544 | 38.481 | 34.3168 | 36.3033 | 29.9393 | 31.4706 | 32.7748 | 34.134 | 34.7279 | 35.5401 | 37.0478 | 36.5514 | 38.5212 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565 | 39.6565
50% | 2104.1657 | 27.7236 | 29.2151 | 33.1791 | 29.2671 | 31.0668 | 25.117 | 26.6155 | 27.7362 | 28.9724 | 29.6188 | 30.1789 | 31.5684 | 30.7267 | 32.9938 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 35.9516 | 50% | 2104.1657 | 29.5074 | 31.0495 | 34.9827 | 31.1971 | 33.003 | 27.2175 | 28.6096 | 29.7953 | 31.0309 | 31.5708 | 32.3092 | 33.6798 | 33.2285 | 35.0193 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514 | 36.0514
45% | 2736.0097 | 24.9512 | 26.2936 | 29.8612 | 26.3404 | 27.9601 | 22.6053 | 23.954 | 24.9625 | 26.0751 | 26.657 | 27.161 | 28.4115 | 27.654 | 29.6944 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 32.3565 | 45% | 2736.0097 | 26.5566 | 27.9445 | 31.4844 | 28.0774 | 29.7027 | 24.4958 | 25.7487 | 26.8158 | 27.9278 | 28.4138 | 29.0783 | 30.3118 | 29.9057 | 31.5174 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463 | 32.4463
40% | 3483.7613 | 22.1789 | 23.372 | 26.5433 | 23.4137 | 24.8534 | 20.0936 | 21.2924 | 22.1889 | 23.1779 | 23.6951 | 24.1431 | 25.2547 | 24.5814 | 26.395 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 28.7613 | 40% | 3483.7613 | 23.6059 | 24.8396 | 27.9862 | 24.9577 | 26.4024 | 21.774 | 22.8877 | 23.8362 | 24.8247 | 25.2567 | 25.8474 | 26.9438 | 26.5828 | 28.0154 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411 | 28.8411
35% | 3830.2948 | 19.4065 | 20.4505 | 23.2254 | 20.487 | 21.7468 | 17.5819 | 18.6309 | 19.4153 | 20.2807 | 20.7332 | 21.1253 | 22.0979 | 21.5087 | 23.0957 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 25.1661 | 35% | 3830.2948 | 20.6551 | 21.7346 | 24.4879 | 21.838 | 23.1021 | 19.0523 | 20.0267 | 20.8567 | 21.7216 | 22.0996 | 22.6165 | 23.5759 | 23.26 | 24.5135 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236 | 25.236
30% | 3953.6322 | 16.6342 | 17.529 | 19.9075 | 17.5603 | 18.6401 | 15.0702 | 15.9693 | 16.6417 | 17.3834 | 17.7713 | 18.1074 | 18.941 | 18.436 | 19.7963 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 21.571 | 30% | 3953.6322 | 17.7044 | 18.6297 | 20.9896 | 18.7183 | 19.8018 | 16.3305 | 17.1658 | 17.8772 | 18.6185 | 18.9425 | 19.3855 | 20.2079 | 19.9371 | 21.0116 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308 | 21.6308
25% | 4060.9208 | 13.8618 | 14.6075 | 16.5896 | 14.6336 | 15.5334 | 12.5585 | 13.3078 | 13.8681 | 14.4862 | 14.8094 | 15.0895 | 15.7842 | 15.3634 | 16.4969 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 17.9758 | 25% | 4060.9208 | 14.7537 | 15.5247 | 17.4913 | 15.5985 | 16.5015 | 13.6088 | 14.3048 | 14.8976 | 15.5154 | 15.7854 | 16.1546 | 16.8399 | 16.6143 | 17.5096 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257 | 18.0257
20% | 4165.2375 | 11.0894 | 11.686 | 13.2716 | 11.7069 | 12.4267 | 10.0468 | 10.6462 | 11.0945 | 11.5889 | 11.8475 | 12.0716 | 12.6273 | 12.2907 | 13.1975 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 14.3807 | 20% | 4165.2375 | 11.8029 | 12.4198 | 13.9931 | 12.4788 | 13.2012 | 10.887 | 11.4438 | 11.9181 | 12.4124 | 12.6283 | 12.9237 | 13.4719 | 13.2914 | 14.0077 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206 | 14.4206
15% | 4270.4458 | 8.3171 | 8.7645 | 9.9537 | 8.7801 | 9.32 | 7.5351 | 7.9847 | 8.3208 | 8.6917 | 8.8857 | 9.0537 | 9.4705 | 9.218 | 9.8981 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 10.7855 | 15% | 4270.4458 | 8.8522 | 9.3148 | 10.4948 | 9.3591 | 9.9009 | 8.1653 | 8.5829 | 8.9386 | 9.3093 | 9.4713 | 9.6928 | 10.1039 | 9.9686 | 10.5058 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154 | 10.8154
10% | 4373.8709 | 5.5447 | 5.843 | 6.6358 | 5.8534 | 6.2134 | 5.0234 | 5.3231 | 5.5472 | 5.7945 | 5.9238 | 6.0358 | 6.3137 | 6.1453 | 6.5988 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 7.1903 | 10% | 4373.8709 | 5.9015 | 6.2099 | 6.9965 | 6.2394 | 6.6006 | 5.4435 | 5.7219 | 5.9591 | 6.2062 | 6.3142 | 6.4618 | 6.736 | 6.6457 | 7.0039 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103 | 7.2103
5% | 4391.7028 | 2.7724 | 2.9215 | 3.3179 | 2.9267 | 3.1067 | 2.5117 | 2.6616 | 2.7736 | 2.8972 | 2.9619 | 3.0179 | 3.1568 | 3.0727 | 3.2994 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 3.5952 | 5% | 4391.7028 | 2.9507 | 3.1049 | 3.4983 | 3.1197 | 3.3003 | 2.7218 | 2.861 | 2.9795 | 3.1031 | 3.1571 | 3.2309 | 3.368 | 3.3229 | 3.5019 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051 | 3.6051
9.992e-14% | 4391.7028 | 5.5403e-14 | 5.8383e-14 | 6.6305e-14 | 5.8488e-14 | 6.2084e-14 | 5.0194e-14 | 5.3189e-14 | 5.5428e-14 | 5.7898e-14 | 5.919e-14 | 6.031e-14 | 6.3086e-14 | 6.1404e-14 | 6.5935e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 7.1846e-14 | 9.992e-14% | 4391.7028 | 5.8968e-14 | 6.2049e-14 | 6.9909e-14 | 6.2344e-14 | 6.5953e-14 | 5.4392e-14 | 5.7173e-14 | 5.9543e-14 | 6.2012e-14 | 6.3091e-14 | 6.4567e-14 | 6.7306e-14 | 6.6404e-14 | 6.9983e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14 | 7.2045e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.6554 | 64.8897 | 72.627 | 63.708 | 66.6413 | 54.7692 | 56.4357 | 58.3388 | 59.8594 | 60.8481 | 63.2106 | 64.8434 | 65.6997 | 67.293 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 66.8242 | 100% | 0 | 70.4803 | 73.2479 | 81.0067 | 72.0246 | 75.3311 | 63.4783 | 65.6253 | 67.6902 | 69.4782 | 70.3722 | 71.693 | 73.2047 | 74.7467 | 76.6887 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885 | 76.9885
99% | 0 | 62.0288 | 64.2408 | 71.9008 | 63.0709 | 65.9749 | 54.2215 | 55.8713 | 57.7554 | 59.2608 | 60.2396 | 62.5785 | 64.195 | 65.0427 | 66.6201 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 66.1559 | 99% | 0.75633 | 69.7755 | 72.5154 | 80.1966 | 71.3043 | 74.5778 | 62.8435 | 64.969 | 67.0133 | 68.7834 | 69.6684 | 70.9761 | 72.4727 | 73.9993 | 75.9218 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186 | 76.2186
98% | 0.37816 | 61.4023 | 63.5919 | 71.1745 | 62.4338 | 65.3085 | 53.6738 | 55.307 | 57.172 | 58.6622 | 59.6311 | 61.9464 | 63.5465 | 64.3857 | 65.9472 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 65.4877 | 98% | 1.1345 | 69.0707 | 71.7829 | 79.3865 | 70.5841 | 73.8245 | 62.2087 | 64.3128 | 66.3364 | 68.0886 | 68.9647 | 70.2592 | 71.7406 | 73.2518 | 75.1549 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487 | 75.4487
97% | 0.75633 | 60.7757 | 62.943 | 70.4482 | 61.7967 | 64.642 | 53.1261 | 54.7426 | 56.5886 | 58.0637 | 59.0226 | 61.3143 | 62.8981 | 63.7287 | 65.2743 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 64.8194 | 97% | 1.8908 | 68.3659 | 71.0504 | 78.5765 | 69.8639 | 73.0712 | 61.5739 | 63.6565 | 65.6595 | 67.3938 | 68.261 | 69.5422 | 71.0086 | 72.5043 | 74.388 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788 | 74.6788
95% | 1.8908 | 59.5226 | 61.6453 | 68.9957 | 60.5226 | 63.3092 | 52.0307 | 53.6139 | 55.4218 | 56.8665 | 57.8057 | 60.0501 | 61.6012 | 62.4148 | 63.9284 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 63.483 | 95% | 3.4035 | 66.9563 | 69.5855 | 76.9563 | 68.4234 | 71.5646 | 60.3044 | 62.344 | 64.3057 | 66.0043 | 66.8536 | 68.1084 | 69.5445 | 71.0094 | 72.8542 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139 | 73.139
90% | 4.538 | 56.3898 | 58.4008 | 65.3643 | 57.3372 | 59.9772 | 49.2923 | 50.7921 | 52.5049 | 53.8735 | 54.7633 | 56.8896 | 58.3591 | 59.1298 | 60.5637 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 60.1417 | 90% | 9.0759 | 63.4323 | 65.9231 | 72.906 | 64.8221 | 67.798 | 57.1305 | 59.0628 | 60.9212 | 62.5303 | 63.3349 | 64.5237 | 65.8842 | 67.2721 | 69.0198 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896 | 69.2896
85% | 9.0759 | 53.2571 | 55.1563 | 61.733 | 54.1518 | 56.6451 | 46.5538 | 47.9703 | 49.588 | 50.8805 | 51.7209 | 53.729 | 55.1169 | 55.8448 | 57.1991 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 56.8005 | 85% | 16.2611 | 59.9082 | 62.2607 | 68.8557 | 61.2209 | 64.0315 | 53.9565 | 55.7815 | 57.5367 | 59.0564 | 59.8163 | 60.9391 | 62.224 | 63.5347 | 65.1854 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402 | 65.4402
80% | 27.606 | 50.1243 | 51.9118 | 58.1016 | 50.9664 | 53.313 | 43.8154 | 45.1485 | 46.671 | 47.8876 | 48.6785 | 50.5685 | 51.8747 | 52.5598 | 53.8344 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 53.4593 | 80% | 24.9588 | 56.3842 | 58.5983 | 64.8053 | 57.6197 | 60.2649 | 50.7826 | 52.5002 | 54.1522 | 55.5825 | 56.2977 | 57.3544 | 58.5638 | 59.7974 | 61.3509 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908 | 61.5908
75% | 57.481 | 46.9915 | 48.6673 | 54.4703 | 47.781 | 49.981 | 41.0769 | 42.3267 | 43.7541 | 44.8946 | 45.6361 | 47.408 | 48.6326 | 49.2748 | 50.4698 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 50.1181 | 75% | 32.9003 | 52.8602 | 54.9359 | 60.755 | 54.0184 | 56.4983 | 47.6087 | 49.219 | 50.7676 | 52.1086 | 52.7791 | 53.7698 | 54.9035 | 56.06 | 57.5165 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414 | 57.7414
70% | 106.2642 | 43.8588 | 45.4228 | 50.8389 | 44.5956 | 46.6489 | 38.3384 | 39.505 | 40.8371 | 41.9016 | 42.5937 | 44.2474 | 45.3904 | 45.9898 | 47.1051 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 46.7769 | 70% | 41.9762 | 49.3362 | 51.2735 | 56.7047 | 50.4172 | 52.7318 | 44.4348 | 45.9377 | 47.3831 | 48.6347 | 49.2605 | 50.1851 | 51.2433 | 52.3227 | 53.6821 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919 | 53.8919
65% | 201.9397 | 40.726 | 42.1783 | 47.2076 | 41.4102 | 43.3168 | 35.6 | 36.6832 | 37.9202 | 38.9086 | 39.5513 | 41.0869 | 42.1482 | 42.7048 | 43.7405 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 43.4357 | 65% | 67.6914 | 45.8122 | 47.6111 | 52.6543 | 46.816 | 48.9652 | 41.2609 | 42.6564 | 43.9986 | 45.1608 | 45.7419 | 46.6005 | 47.5831 | 48.5854 | 49.8476 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425 | 50.0425
60% | 402.745 | 37.5932 | 38.9338 | 43.5762 | 38.2248 | 39.9848 | 32.8615 | 33.8614 | 35.0033 | 35.9157 | 36.5089 | 37.9264 | 38.906 | 39.4198 | 40.3758 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 40.0945 | 60% | 98.7009 | 42.2882 | 43.9487 | 48.604 | 43.2148 | 45.1987 | 38.087 | 39.3752 | 40.6141 | 41.6869 | 42.2233 | 43.0158 | 43.9228 | 44.848 | 46.0132 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931 | 46.1931
55% | 655.7369 | 34.4605 | 35.6894 | 39.9449 | 35.0394 | 36.6527 | 30.1231 | 31.0396 | 32.0863 | 32.9227 | 33.4665 | 34.7658 | 35.6639 | 36.1349 | 37.0112 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 36.7533 | 55% | 153.5347 | 38.7642 | 40.2863 | 44.5537 | 39.6135 | 41.4321 | 34.9131 | 36.0939 | 37.2296 | 38.213 | 38.7047 | 39.4312 | 40.2626 | 41.1107 | 42.1788 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437 | 42.3437
50% | 981.7145 | 31.3277 | 32.4449 | 36.3135 | 31.854 | 33.3206 | 27.3846 | 28.2178 | 29.1694 | 29.9297 | 30.424 | 31.6053 | 32.4217 | 32.8499 | 33.6465 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 33.4121 | 50% | 258.2862 | 35.2401 | 36.6239 | 40.5033 | 36.0123 | 37.6656 | 31.7391 | 32.8126 | 33.8451 | 34.7391 | 35.1861 | 35.8465 | 36.6024 | 37.3734 | 38.3443 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942 | 38.4942
45% | 1622.7029 | 28.1949 | 29.2004 | 32.6822 | 28.6686 | 29.9886 | 24.6461 | 25.396 | 26.2524 | 26.9367 | 27.3816 | 28.4448 | 29.1795 | 29.5649 | 30.2819 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 30.0709 | 45% | 488.9664 | 31.7161 | 32.9615 | 36.453 | 32.4111 | 33.899 | 28.5652 | 29.5314 | 30.4606 | 31.2652 | 31.6675 | 32.2619 | 32.9421 | 33.636 | 34.5099 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448 | 34.6448
40% | 2442.9413 | 25.0621 | 25.9559 | 29.0508 | 25.4832 | 26.6565 | 21.9077 | 22.5743 | 23.3355 | 23.9438 | 24.3392 | 25.2842 | 25.9374 | 26.2799 | 26.9172 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 26.7297 | 40% | 928.0152 | 28.1921 | 29.2991 | 32.4027 | 28.8098 | 30.1325 | 25.3913 | 26.2501 | 27.0761 | 27.7913 | 28.1489 | 28.6772 | 29.2819 | 29.8987 | 30.6755 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954 | 30.7954
35% | 3006.7842 | 21.9294 | 22.7114 | 25.4195 | 22.2978 | 23.3244 | 19.1692 | 19.7525 | 20.4186 | 20.9508 | 21.2968 | 22.1237 | 22.6952 | 22.9949 | 23.5526 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 23.3885 | 35% | 1530.4309 | 24.6681 | 25.6368 | 28.3523 | 25.2086 | 26.3659 | 22.2174 | 22.9689 | 23.6916 | 24.3174 | 24.6303 | 25.0926 | 25.6216 | 26.1614 | 26.841 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946 | 26.946
30% | 3276.4154 | 18.7966 | 19.4669 | 21.7881 | 19.1124 | 19.9924 | 16.4308 | 16.9307 | 17.5016 | 17.9578 | 18.2544 | 18.9632 | 19.453 | 19.7099 | 20.1879 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 20.0472 | 30% | 2592.3162 | 21.1441 | 21.9744 | 24.302 | 21.6074 | 22.5993 | 19.0435 | 19.6876 | 20.3071 | 20.8434 | 21.1116 | 21.5079 | 21.9614 | 22.424 | 23.0066 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965 | 23.0965
25% | 3466.632 | 15.6638 | 16.2224 | 18.1568 | 15.927 | 16.6603 | 13.6923 | 14.1089 | 14.5847 | 14.9649 | 15.212 | 15.8027 | 16.2109 | 16.4249 | 16.8233 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 16.706 | 25% | 3659.4958 | 17.6201 | 18.312 | 20.2517 | 18.0061 | 18.8328 | 15.8696 | 16.4063 | 16.9225 | 17.3695 | 17.593 | 17.9233 | 18.3012 | 18.6867 | 19.1722 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471 | 19.2471
20% | 3713.9514 | 12.5311 | 12.9779 | 14.5254 | 12.7416 | 13.3283 | 10.9538 | 11.2871 | 11.6678 | 11.9719 | 12.1696 | 12.6421 | 12.9687 | 13.1399 | 13.4586 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 13.3648 | 20% | 4005.5161 | 14.0961 | 14.6496 | 16.2013 | 14.4049 | 15.0662 | 12.6957 | 13.1251 | 13.538 | 13.8956 | 14.0744 | 14.3386 | 14.6409 | 14.9493 | 15.3377 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977 | 15.3977
15% | 4043.3325 | 9.3983 | 9.7335 | 10.8941 | 9.5562 | 9.9962 | 8.2154 | 8.4653 | 8.7508 | 8.9789 | 9.1272 | 9.4816 | 9.7265 | 9.855 | 10.094 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 10.0236 | 15% | 4281.1979 | 10.572 | 10.9872 | 12.151 | 10.8037 | 11.2997 | 9.5217 | 9.8438 | 10.1535 | 10.4217 | 10.5558 | 10.754 | 10.9807 | 11.212 | 11.5033 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483 | 11.5483
10% | 4350.7801 | 6.2655 | 6.489 | 7.2627 | 6.3708 | 6.6641 | 5.4769 | 5.6436 | 5.8339 | 5.9859 | 6.0848 | 6.3211 | 6.4843 | 6.57 | 6.7293 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 6.6824 | 10% | 4391.6218 | 7.048 | 7.3248 | 8.1007 | 7.2025 | 7.5331 | 6.3478 | 6.5625 | 6.769 | 6.9478 | 7.0372 | 7.1693 | 7.3205 | 7.4747 | 7.6689 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988 | 7.6988
5% | 4391.6218 | 3.1328 | 3.2445 | 3.6314 | 3.1854 | 3.3321 | 2.7385 | 2.8218 | 2.9169 | 2.993 | 3.0424 | 3.1605 | 3.2422 | 3.285 | 3.3647 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 3.3412 | 5% | 4391.6218 | 3.524 | 3.6624 | 4.0503 | 3.6012 | 3.7666 | 3.1739 | 3.2813 | 3.3845 | 3.4739 | 3.5186 | 3.5847 | 3.6602 | 3.7373 | 3.8344 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494 | 3.8494
9.992e-14% | 4391.6218 | 6.2605e-14 | 6.4838e-14 | 7.2569e-14 | 6.3657e-14 | 6.6588e-14 | 5.4725e-14 | 5.6391e-14 | 5.8292e-14 | 5.9812e-14 | 6.0799e-14 | 6.316e-14 | 6.4792e-14 | 6.5647e-14 | 6.7239e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 6.6771e-14 | 9.992e-14% | 4391.6218 | 7.0424e-14 | 7.3189e-14 | 8.0942e-14 | 7.1967e-14 | 7.5271e-14 | 6.3428e-14 | 6.5573e-14 | 6.7636e-14 | 6.9423e-14 | 7.0316e-14 | 7.1636e-14 | 7.3146e-14 | 7.4687e-14 | 7.6627e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14 | 7.6927e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 50.5141 | 53.0723 | 60.4609 | 66.7542 | 70.1256 | 72.5435 | 75.3938 | 77.494 | 79.8441 | 81.078 | 82.1085 | 84.7844 | 82.9966 | 87.3977 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 93.2952 | 100% | 0 | 54.0816 | 56.7411 | 64.068 | 70.6141 | 73.998 | 76.7445 | 79.382 | 81.6123 | 83.9612 | 84.982 | 86.3691 | 89.0073 | 88.0002 | 91.4487 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947 | 93.4947
99% | 0.8916 | 50.0089 | 52.5416 | 59.8563 | 66.0867 | 69.4243 | 71.8181 | 74.6399 | 76.7191 | 79.0456 | 80.2672 | 81.2874 | 83.9365 | 82.1667 | 86.5237 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 92.3622 | 99% | 0.8916 | 53.5408 | 56.1737 | 63.4274 | 69.908 | 73.258 | 75.9771 | 78.5881 | 80.7962 | 83.1215 | 84.1322 | 85.5054 | 88.1172 | 87.1202 | 90.5342 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597 | 92.5597
98% | 3.5664 | 49.5038 | 52.0109 | 59.2517 | 65.4191 | 68.7231 | 71.0926 | 73.8859 | 75.9442 | 78.2472 | 79.4564 | 80.4663 | 83.0887 | 81.3367 | 85.6497 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 91.4293 | 98% | 3.5664 | 53 | 55.6063 | 62.7867 | 69.2018 | 72.5181 | 75.2096 | 77.7943 | 79.98 | 82.2819 | 83.2823 | 84.6417 | 87.2271 | 86.2402 | 89.6197 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248 | 91.6248
97% | 4.7552 | 48.9987 | 51.4802 | 58.6471 | 64.7516 | 68.0218 | 70.3672 | 73.132 | 75.1692 | 77.4488 | 78.6456 | 79.6452 | 82.2408 | 80.5067 | 84.7757 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 90.4963 | 97% | 4.7552 | 52.4591 | 55.0389 | 62.146 | 68.4957 | 71.7781 | 74.4422 | 77.0005 | 79.1639 | 81.4423 | 82.4325 | 83.778 | 86.337 | 85.3602 | 88.7052 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899 | 90.6899
95% | 7.7272 | 47.9884 | 50.4187 | 57.4378 | 63.4165 | 66.6193 | 68.9163 | 71.6241 | 73.6193 | 75.8519 | 77.0241 | 78.0031 | 80.5451 | 78.8468 | 83.0278 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 88.6304 | 95% | 7.7272 | 51.3775 | 53.9041 | 60.8646 | 67.0834 | 70.2981 | 72.9073 | 75.4129 | 77.5317 | 79.7631 | 80.7329 | 82.0506 | 84.5569 | 83.6002 | 86.8762 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82 | 88.82
90% | 39.2302 | 45.4627 | 47.7651 | 54.4148 | 60.0788 | 63.113 | 65.2892 | 67.8544 | 69.7446 | 71.8597 | 72.9702 | 73.8977 | 76.3059 | 74.697 | 78.6579 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 83.9657 | 90% | 39.2302 | 48.6734 | 51.067 | 57.6612 | 63.5527 | 66.5982 | 69.0701 | 71.4438 | 73.4511 | 75.565 | 76.4838 | 77.7322 | 80.1065 | 79.2002 | 82.3038 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452 | 84.1452
85% | 117.6906 | 42.937 | 45.1115 | 51.3918 | 56.7411 | 59.6067 | 61.662 | 64.0847 | 65.8699 | 67.8675 | 68.9163 | 69.7922 | 72.0667 | 70.5471 | 74.288 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 79.3009 | 85% | 117.6906 | 45.9694 | 48.23 | 54.4578 | 60.022 | 62.8983 | 65.2328 | 67.4747 | 69.3704 | 71.367 | 72.2347 | 73.4137 | 75.6562 | 74.8002 | 77.7314 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705 | 79.4705
80% | 268.3703 | 40.4113 | 42.4579 | 48.3687 | 53.4034 | 56.1005 | 58.0348 | 60.3151 | 61.9952 | 63.8753 | 64.8624 | 65.6868 | 67.8275 | 66.3973 | 69.9181 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 74.6361 | 80% | 268.3703 | 43.2653 | 45.3929 | 51.2544 | 56.4913 | 59.1984 | 61.3956 | 63.5056 | 65.2898 | 67.1689 | 67.9856 | 69.0953 | 71.2058 | 70.4002 | 73.1589 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958 | 74.7958
75% | 455.9026 | 37.8856 | 39.8042 | 45.3457 | 50.0657 | 52.5942 | 54.4076 | 56.5454 | 58.1205 | 59.8831 | 60.8085 | 61.5814 | 63.5883 | 62.2475 | 65.5483 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 69.9714 | 75% | 455.9026 | 40.5612 | 42.5558 | 48.051 | 52.9606 | 55.4985 | 57.5584 | 59.5365 | 61.2092 | 62.9709 | 63.7365 | 64.7768 | 66.7554 | 66.0002 | 68.5865 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121 | 70.121
70% | 690.9866 | 35.3599 | 37.1506 | 42.3226 | 46.728 | 49.0879 | 50.7805 | 52.7757 | 54.2458 | 55.8909 | 56.7546 | 57.476 | 59.349 | 58.0976 | 61.1784 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 65.3066 | 70% | 690.9866 | 37.8571 | 39.7188 | 44.8476 | 49.4299 | 51.7986 | 53.7212 | 55.5674 | 57.1286 | 58.7728 | 59.4874 | 60.4584 | 62.3051 | 61.6002 | 64.0141 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463 | 65.4463
65% | 967.6784 | 32.8341 | 34.497 | 39.2996 | 43.3902 | 45.5816 | 47.1533 | 49.006 | 50.3711 | 51.8987 | 52.7007 | 53.3705 | 55.1098 | 53.9478 | 56.8085 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 60.6419 | 65% | 967.6784 | 35.153 | 36.8817 | 41.6442 | 45.8992 | 48.0987 | 49.8839 | 51.5983 | 53.048 | 54.5747 | 55.2383 | 56.1399 | 57.8547 | 57.2001 | 59.4416 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715 | 60.7715
60% | 1292.8136 | 30.3084 | 31.8434 | 36.2765 | 40.0525 | 42.0753 | 43.5261 | 45.2363 | 46.4964 | 47.9064 | 48.6468 | 49.2651 | 50.8706 | 49.798 | 52.4386 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 55.9771 | 60% | 1292.8136 | 32.449 | 34.0447 | 38.4408 | 42.3685 | 44.3988 | 46.0467 | 47.6292 | 48.9674 | 50.3767 | 50.9892 | 51.8214 | 53.4044 | 52.8001 | 54.8692 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968 | 56.0968
55% | 1647.0743 | 27.7827 | 29.1898 | 33.2535 | 36.7148 | 38.5691 | 39.8989 | 41.4666 | 42.6217 | 43.9142 | 44.5929 | 45.1597 | 46.6314 | 45.6481 | 48.0687 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 51.3123 | 55% | 1647.0743 | 29.7449 | 31.2076 | 35.2374 | 38.8378 | 40.6989 | 42.2095 | 43.6601 | 44.8868 | 46.1786 | 46.7401 | 47.503 | 48.954 | 48.4001 | 50.2968 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221 | 51.4221
50% | 2104.1657 | 25.257 | 26.5362 | 30.2304 | 33.3771 | 35.0628 | 36.2718 | 37.6969 | 38.747 | 39.922 | 40.539 | 41.0543 | 42.3922 | 41.4983 | 43.6988 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 46.6476 | 50% | 2104.1657 | 27.0408 | 28.3706 | 32.034 | 35.3071 | 36.999 | 38.3723 | 39.691 | 40.8061 | 41.9806 | 42.491 | 43.1845 | 44.5036 | 44.0001 | 45.7243 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473 | 46.7473
45% | 2736.0097 | 22.7313 | 23.8825 | 27.2074 | 30.0394 | 31.5565 | 32.6446 | 33.9272 | 34.8723 | 35.9298 | 36.4851 | 36.9488 | 38.153 | 37.3485 | 39.329 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 41.9828 | 45% | 2736.0097 | 24.3367 | 25.5335 | 28.8306 | 31.7763 | 33.2991 | 34.535 | 35.7219 | 36.7255 | 37.7825 | 38.2419 | 38.8661 | 40.0533 | 39.6001 | 41.1519 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726 | 42.0726
40% | 3483.7613 | 20.2056 | 21.2289 | 24.1844 | 26.7017 | 28.0502 | 29.0174 | 30.1575 | 30.9976 | 31.9376 | 32.4312 | 32.8434 | 33.9137 | 33.1987 | 34.9591 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 37.3181 | 40% | 3483.7613 | 21.6326 | 22.6964 | 25.6272 | 28.2456 | 29.5992 | 30.6978 | 31.7528 | 32.6449 | 33.5845 | 33.9928 | 34.5476 | 35.6029 | 35.2001 | 36.5795 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979 | 37.3979
35% | 3830.2948 | 17.6799 | 18.5753 | 21.1613 | 23.364 | 24.544 | 25.3902 | 26.3878 | 27.1229 | 27.9454 | 28.3773 | 28.738 | 29.6745 | 29.0488 | 30.5892 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 32.6533 | 35% | 3830.2948 | 18.9286 | 19.8594 | 22.4238 | 24.7149 | 25.8993 | 26.8606 | 27.7837 | 28.5643 | 29.3864 | 29.7437 | 30.2292 | 31.1525 | 30.8001 | 32.007 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231 | 32.7231
30% | 3953.6322 | 15.1542 | 15.9217 | 18.1383 | 20.0263 | 21.0377 | 21.7631 | 22.6181 | 23.2482 | 23.9532 | 24.3234 | 24.6326 | 25.4353 | 24.899 | 26.2193 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 27.9886 | 30% | 3953.6322 | 16.2245 | 17.0223 | 19.2204 | 21.1842 | 22.1994 | 23.0234 | 23.8146 | 24.4837 | 25.1883 | 25.4946 | 25.9107 | 26.7022 | 26.4001 | 27.4346 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484 | 28.0484
25% | 4060.9208 | 12.6285 | 13.2681 | 15.1152 | 16.6886 | 17.5314 | 18.1359 | 18.8485 | 19.3735 | 19.961 | 20.2695 | 20.5271 | 21.1961 | 20.7492 | 21.8494 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 23.3238 | 25% | 4060.9208 | 13.5204 | 14.1853 | 16.017 | 17.6535 | 18.4995 | 19.1861 | 19.8455 | 20.4031 | 20.9903 | 21.2455 | 21.5923 | 22.2518 | 22.0001 | 22.8622 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737 | 23.3737
20% | 4165.2375 | 10.1028 | 10.6145 | 12.0922 | 13.3508 | 14.0251 | 14.5087 | 15.0788 | 15.4988 | 15.9688 | 16.2156 | 16.4217 | 16.9569 | 16.5993 | 17.4795 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 18.659 | 20% | 4165.2375 | 10.8163 | 11.3482 | 12.8136 | 14.1228 | 14.7996 | 15.3489 | 15.8764 | 16.3225 | 16.7922 | 16.9964 | 17.2738 | 17.8015 | 17.6 | 18.2897 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989 | 18.6989
15% | 4270.4458 | 7.5771 | 7.9608 | 9.0691 | 10.0131 | 10.5188 | 10.8815 | 11.3091 | 11.6241 | 11.9766 | 12.1617 | 12.3163 | 12.7177 | 12.4495 | 13.1097 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 13.9943 | 15% | 4270.4458 | 8.1122 | 8.5112 | 9.6102 | 10.5921 | 11.0997 | 11.5117 | 11.9073 | 12.2418 | 12.5942 | 12.7473 | 12.9554 | 13.3511 | 13.2 | 13.7173 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242 | 14.0242
10% | 4373.8709 | 5.0514 | 5.3072 | 6.0461 | 6.6754 | 7.0126 | 7.2544 | 7.5394 | 7.7494 | 7.9844 | 8.1078 | 8.2109 | 8.4784 | 8.2997 | 8.7398 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 9.3295 | 10% | 4373.8709 | 5.4082 | 5.6741 | 6.4068 | 7.0614 | 7.3998 | 7.6745 | 7.9382 | 8.1612 | 8.3961 | 8.4982 | 8.6369 | 8.9007 | 8.8 | 9.1449 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495 | 9.3495
5% | 4391.7028 | 2.5257 | 2.6536 | 3.023 | 3.3377 | 3.5063 | 3.6272 | 3.7697 | 3.8747 | 3.9922 | 4.0539 | 4.1054 | 4.2392 | 4.1498 | 4.3699 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 4.6648 | 5% | 4391.7028 | 2.7041 | 2.8371 | 3.2034 | 3.5307 | 3.6999 | 3.8372 | 3.9691 | 4.0806 | 4.1981 | 4.2491 | 4.3185 | 4.4504 | 4.4 | 4.5724 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747 | 4.6747
9.992e-14% | 4391.7028 | 5.0474e-14 | 5.303e-14 | 6.0413e-14 | 6.6701e-14 | 7.007e-14 | 7.2486e-14 | 7.5334e-14 | 7.7432e-14 | 7.978e-14 | 8.1013e-14 | 8.2043e-14 | 8.4717e-14 | 8.293e-14 | 8.7328e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.3221e-14 | 9.992e-14% | 4391.7028 | 5.4038e-14 | 5.6696e-14 | 6.4017e-14 | 7.0558e-14 | 7.3939e-14 | 7.6683e-14 | 7.9319e-14 | 8.1547e-14 | 8.3894e-14 | 8.4914e-14 | 8.63e-14 | 8.8936e-14 | 8.793e-14 | 9.1376e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14 | 9.342e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 57.7223 | 59.5319 | 66.7297 | 71.9279 | 74.6333 | 77.0787 | 78.5984 | 80.3605 | 81.7588 | 82.6884 | 84.9613 | 86.491 | 87.2429 | 88.7031 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 88.2161 | 100% | 0 | 65.5472 | 67.8901 | 75.1093 | 80.2445 | 83.3231 | 85.7878 | 87.788 | 89.7119 | 91.3775 | 92.2125 | 93.4437 | 94.8523 | 96.2899 | 98.0987 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804 | 98.3804
99% | 0 | 57.145 | 58.9366 | 66.0624 | 71.2086 | 73.8869 | 76.3079 | 77.8124 | 79.5569 | 80.9412 | 81.8615 | 84.1116 | 85.6261 | 86.3705 | 87.8161 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 87.3339 | 99% | 0.75633 | 64.8917 | 67.2112 | 74.3582 | 79.4421 | 82.4899 | 84.9299 | 86.9101 | 88.8148 | 90.4637 | 91.2903 | 92.5092 | 93.9038 | 95.327 | 97.1178 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966 | 97.3966
98% | 0.37816 | 56.5678 | 58.3413 | 65.3951 | 70.4893 | 73.1406 | 75.5371 | 77.0264 | 78.7533 | 80.1236 | 81.0346 | 83.262 | 84.7612 | 85.4981 | 86.9291 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 86.4517 | 98% | 1.1345 | 64.2362 | 66.5323 | 73.6071 | 78.6396 | 81.6567 | 84.072 | 86.0323 | 87.9177 | 89.55 | 90.3682 | 91.5748 | 92.9553 | 94.3641 | 96.1368 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128 | 96.4128
97% | 0.75633 | 55.9906 | 57.746 | 64.7278 | 69.77 | 72.3943 | 74.7664 | 76.2404 | 77.9497 | 79.306 | 80.2077 | 82.4124 | 83.8963 | 84.6256 | 86.042 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 85.5696 | 97% | 1.8908 | 63.5808 | 65.8534 | 72.856 | 77.8372 | 80.8234 | 83.2142 | 85.1544 | 87.0205 | 88.6362 | 89.4461 | 90.6403 | 92.0068 | 93.4012 | 95.1558 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289 | 95.4289
95% | 1.8908 | 54.8361 | 56.5553 | 63.3932 | 68.3315 | 70.9016 | 73.2248 | 74.6685 | 76.3425 | 77.6709 | 78.554 | 80.7132 | 82.1665 | 82.8808 | 84.268 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 83.8052 | 95% | 3.4035 | 62.2698 | 64.4956 | 71.3538 | 76.2323 | 79.157 | 81.4984 | 83.3986 | 85.2263 | 86.8086 | 87.6018 | 88.7715 | 90.1097 | 91.4754 | 93.1938 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613 | 93.4613
90% | 4.538 | 51.95 | 53.5787 | 60.0567 | 64.7351 | 67.1699 | 69.3708 | 70.7386 | 72.3244 | 73.5829 | 74.4195 | 76.4651 | 77.8419 | 78.5186 | 79.8328 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 79.3944 | 90% | 9.0759 | 58.9925 | 61.1011 | 67.5984 | 72.2201 | 74.9908 | 77.209 | 79.0092 | 80.7407 | 82.2398 | 82.9912 | 84.0993 | 85.3671 | 86.6609 | 88.2889 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423 | 88.5423
85% | 9.0759 | 49.0639 | 50.6021 | 56.7202 | 61.1387 | 63.4383 | 65.5169 | 66.8086 | 68.3064 | 69.495 | 70.2851 | 72.2171 | 73.5174 | 74.1565 | 75.3977 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 74.9836 | 85% | 16.2611 | 55.7151 | 57.7066 | 63.8429 | 68.2078 | 70.8247 | 72.9196 | 74.6198 | 76.2551 | 77.6709 | 78.3806 | 79.4271 | 80.6245 | 81.8464 | 83.3839 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233 | 83.6233
80% | 27.606 | 46.1778 | 47.6256 | 53.3837 | 57.5423 | 59.7066 | 61.663 | 62.8787 | 64.2884 | 65.407 | 66.1507 | 67.969 | 69.1928 | 69.7943 | 70.9625 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 70.5728 | 80% | 24.9588 | 52.4377 | 54.312 | 60.0874 | 64.1956 | 66.6585 | 68.6302 | 70.2304 | 71.7695 | 73.102 | 73.77 | 74.7549 | 75.8819 | 77.0319 | 78.479 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043 | 78.7043
75% | 57.481 | 43.2917 | 44.649 | 50.0472 | 53.9459 | 55.975 | 57.809 | 58.9488 | 60.2704 | 61.3191 | 62.0163 | 63.7209 | 64.8683 | 65.4322 | 66.5273 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 66.162 | 75% | 32.9003 | 49.1604 | 50.9175 | 56.332 | 60.1834 | 62.4923 | 64.3408 | 65.841 | 67.2839 | 68.5331 | 69.1593 | 70.0827 | 71.1392 | 72.2174 | 73.5741 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853 | 73.7853
70% | 106.2642 | 40.4056 | 41.6724 | 46.7108 | 50.3495 | 52.2433 | 53.9551 | 55.0189 | 56.2523 | 57.2312 | 57.8819 | 59.4729 | 60.5437 | 61.0701 | 62.0922 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 61.7512 | 70% | 41.9762 | 45.883 | 47.523 | 52.5765 | 56.1712 | 58.3262 | 60.0515 | 61.4516 | 62.7983 | 63.9643 | 64.5487 | 65.4106 | 66.3966 | 67.4029 | 68.6691 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663 | 68.8663
65% | 201.9397 | 37.5195 | 38.6958 | 43.3743 | 46.7531 | 48.5116 | 50.1012 | 51.089 | 52.2343 | 53.1432 | 53.7474 | 55.2248 | 56.2192 | 56.7079 | 57.657 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 57.3404 | 65% | 67.6914 | 42.6057 | 44.1285 | 48.821 | 52.1589 | 54.16 | 55.7621 | 57.0622 | 58.3127 | 59.3954 | 59.9381 | 60.7384 | 61.654 | 62.5885 | 63.7642 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472 | 63.9472
60% | 402.745 | 34.6334 | 35.7192 | 40.0378 | 43.1567 | 44.78 | 46.2472 | 47.159 | 48.2163 | 49.0553 | 49.613 | 50.9768 | 51.8946 | 52.3458 | 53.2219 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 52.9296 | 60% | 98.7009 | 39.3283 | 40.734 | 45.0656 | 48.1467 | 49.9939 | 51.4727 | 52.6728 | 53.8271 | 54.8265 | 55.3275 | 56.0662 | 56.9114 | 57.774 | 58.8592 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282 | 59.0282
55% | 655.7369 | 31.7472 | 32.7426 | 36.7013 | 39.5603 | 41.0483 | 42.3933 | 43.2291 | 44.1983 | 44.9673 | 45.4786 | 46.7287 | 47.5701 | 47.9836 | 48.7867 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 48.5188 | 55% | 153.5347 | 36.0509 | 37.3395 | 41.3101 | 44.1345 | 45.8277 | 47.1833 | 48.2834 | 49.3415 | 50.2576 | 50.7168 | 51.394 | 52.1688 | 52.9595 | 53.9543 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092 | 54.1092
50% | 981.7145 | 28.8611 | 29.766 | 33.3648 | 35.9639 | 37.3166 | 38.5394 | 39.2992 | 40.1802 | 40.8794 | 41.3442 | 42.4806 | 43.2455 | 43.6215 | 44.3516 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 44.108 | 50% | 258.2862 | 32.7736 | 33.945 | 37.5547 | 40.1223 | 41.6616 | 42.8939 | 43.894 | 44.856 | 45.6888 | 46.1062 | 46.7218 | 47.4262 | 48.145 | 49.0494 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902 | 49.1902
45% | 1622.7029 | 25.975 | 26.7894 | 30.0283 | 32.3675 | 33.585 | 34.6854 | 35.3693 | 36.1622 | 36.7915 | 37.2098 | 38.2326 | 38.921 | 39.2593 | 39.9164 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 39.6972 | 45% | 488.9664 | 29.4962 | 30.5505 | 33.7992 | 36.11 | 37.4954 | 38.6045 | 39.5046 | 40.3704 | 41.1199 | 41.4956 | 42.0496 | 42.6835 | 43.3305 | 44.1444 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712 | 44.2712
40% | 2442.9413 | 23.0889 | 23.8128 | 26.6919 | 28.7712 | 29.8533 | 30.8315 | 31.4394 | 32.1442 | 32.7035 | 33.0754 | 33.9845 | 34.5964 | 34.8972 | 35.4812 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 35.2864 | 40% | 928.0152 | 26.2189 | 27.156 | 30.0437 | 32.0978 | 33.3292 | 34.3151 | 35.1152 | 35.8848 | 36.551 | 36.885 | 37.3775 | 37.9409 | 38.516 | 39.2395 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521 | 39.3521
35% | 3006.7842 | 20.2028 | 20.8362 | 23.3554 | 25.1748 | 26.1216 | 26.9775 | 27.5094 | 28.1262 | 28.6156 | 28.9409 | 29.7364 | 30.2719 | 30.535 | 31.0461 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 30.8756 | 35% | 1530.4309 | 22.9415 | 23.7615 | 26.2883 | 28.0856 | 29.1631 | 30.0257 | 30.7258 | 31.3992 | 31.9821 | 32.2744 | 32.7053 | 33.1983 | 33.7015 | 34.3346 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331 | 34.4331
30% | 3276.4154 | 17.3167 | 17.8596 | 20.0189 | 21.5784 | 22.39 | 23.1236 | 23.5795 | 24.1081 | 24.5276 | 24.8065 | 25.4884 | 25.9473 | 26.1729 | 26.6109 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 26.4648 | 30% | 2592.3162 | 19.6642 | 20.367 | 22.5328 | 24.0734 | 24.9969 | 25.7363 | 26.3364 | 26.9136 | 27.4133 | 27.6637 | 28.0331 | 28.4557 | 28.887 | 29.4296 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141 | 29.5141
25% | 3466.632 | 14.4306 | 14.883 | 16.6824 | 17.982 | 18.6583 | 19.2697 | 19.6496 | 20.0901 | 20.4397 | 20.6721 | 21.2403 | 21.6228 | 21.8107 | 22.1758 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 22.054 | 25% | 3659.4958 | 16.3868 | 16.9725 | 18.7773 | 20.0611 | 20.8308 | 21.4469 | 21.947 | 22.428 | 22.8444 | 23.0531 | 23.3609 | 23.7131 | 24.0725 | 24.5247 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951 | 24.5951
20% | 3713.9514 | 11.5445 | 11.9064 | 13.3459 | 14.3856 | 14.9267 | 15.4157 | 15.7197 | 16.0721 | 16.3518 | 16.5377 | 16.9923 | 17.2982 | 17.4486 | 17.7406 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 17.6432 | 20% | 4005.5161 | 13.1094 | 13.578 | 15.0219 | 16.0489 | 16.6646 | 17.1576 | 17.5576 | 17.9424 | 18.2755 | 18.4425 | 18.6887 | 18.9705 | 19.258 | 19.6197 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761 | 19.6761
15% | 4043.3325 | 8.6583 | 8.9298 | 10.0094 | 10.7892 | 11.195 | 11.5618 | 11.7898 | 12.0541 | 12.2638 | 12.4033 | 12.7442 | 12.9737 | 13.0864 | 13.3055 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 13.2324 | 15% | 4281.1979 | 9.8321 | 10.1835 | 11.2664 | 12.0367 | 12.4985 | 12.8682 | 13.1682 | 13.4568 | 13.7066 | 13.8319 | 14.0165 | 14.2278 | 14.4435 | 14.7148 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571 | 14.7571
10% | 4350.7801 | 5.7722 | 5.9532 | 6.673 | 7.1928 | 7.4633 | 7.7079 | 7.8598 | 8.036 | 8.1759 | 8.2688 | 8.4961 | 8.6491 | 8.7243 | 8.8703 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 8.8216 | 10% | 4391.6218 | 6.5547 | 6.789 | 7.5109 | 8.0245 | 8.3323 | 8.5788 | 8.7788 | 8.9712 | 9.1378 | 9.2212 | 9.3444 | 9.4852 | 9.629 | 9.8099 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838 | 9.838
5% | 4391.6218 | 2.8861 | 2.9766 | 3.3365 | 3.5964 | 3.7317 | 3.8539 | 3.9299 | 4.018 | 4.0879 | 4.1344 | 4.2481 | 4.3246 | 4.3621 | 4.4352 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 4.4108 | 5% | 4391.6218 | 3.2774 | 3.3945 | 3.7555 | 4.0122 | 4.1662 | 4.2894 | 4.3894 | 4.4856 | 4.5689 | 4.6106 | 4.6722 | 4.7426 | 4.8145 | 4.9049 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919 | 4.919
9.992e-14% | 4391.6218 | 5.7676e-14 | 5.9484e-14 | 6.6676e-14 | 7.187e-14 | 7.4574e-14 | 7.7017e-14 | 7.8536e-14 | 8.0296e-14 | 8.1693e-14 | 8.2622e-14 | 8.4893e-14 | 8.6422e-14 | 8.7173e-14 | 8.8632e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 8.8146e-14 | 9.992e-14% | 4391.6218 | 6.5495e-14 | 6.7836e-14 | 7.5049e-14 | 8.018e-14 | 8.3257e-14 | 8.5719e-14 | 8.7718e-14 | 8.964e-14 | 9.1304e-14 | 9.2139e-14 | 9.3369e-14 | 9.4777e-14 | 9.6213e-14 | 9.802e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14 | 9.8302e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 79.234 | 82.2311 | 84.4723 | 86.9447 | 88.2377 | 89.3579 | 92.1367 | 90.4534 | 94.9876 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100% | 0 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 83.435 | 86.2192 | 88.5906 | 91.0618 | 92.1417 | 93.6184 | 96.3596 | 95.457 | 99.0386 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028
99% | 0.8916 | 54.8927 | 57.8458 | 65.6947 | 72.3039 | 75.8673 | 78.4417 | 81.4088 | 83.6276 | 86.0753 | 87.3553 | 88.4643 | 91.2154 | 89.5489 | 94.0377 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99% | 0.8916 | 58.4246 | 61.4779 | 69.2657 | 76.1252 | 79.701 | 82.6007 | 85.357 | 87.7047 | 90.1512 | 91.2203 | 92.6823 | 95.396 | 94.5025 | 98.0482 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918
98% | 3.5664 | 54.3382 | 57.2615 | 65.0311 | 71.5736 | 75.1009 | 77.6493 | 80.5865 | 82.7829 | 85.2058 | 86.4729 | 87.5707 | 90.294 | 88.6444 | 93.0878 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98% | 3.5664 | 57.8344 | 60.8569 | 68.5661 | 75.3563 | 78.8959 | 81.7663 | 84.4948 | 86.8188 | 89.2406 | 90.2989 | 91.7461 | 94.4324 | 93.5479 | 97.0578 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807
97% | 4.7552 | 53.7838 | 56.6772 | 64.3675 | 70.8433 | 74.3346 | 76.857 | 79.7641 | 81.9382 | 84.3364 | 85.5905 | 86.6771 | 89.3726 | 87.7398 | 92.138 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97% | 4.7552 | 57.2443 | 60.2359 | 67.8664 | 74.5874 | 78.0908 | 80.932 | 83.6327 | 85.9329 | 88.3299 | 89.3774 | 90.8099 | 93.4688 | 92.5933 | 96.0674 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697
95% | 7.7272 | 52.6748 | 55.5086 | 63.0403 | 69.3826 | 72.8019 | 75.2723 | 78.1195 | 80.2487 | 82.5975 | 83.8258 | 84.89 | 87.5299 | 85.9308 | 90.2382 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95% | 7.7272 | 56.064 | 58.994 | 66.4671 | 73.0495 | 76.4807 | 79.2633 | 81.9083 | 84.161 | 86.5087 | 87.5346 | 88.9375 | 91.5416 | 90.6842 | 94.0866 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477
90% | 39.2302 | 49.9025 | 52.5871 | 59.7224 | 65.7309 | 68.9702 | 71.3106 | 74.008 | 76.0251 | 78.2502 | 79.4139 | 80.4221 | 82.9231 | 81.4081 | 85.4888 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90% | 39.2302 | 53.1132 | 55.889 | 62.9689 | 69.2048 | 72.4554 | 75.0915 | 77.5973 | 79.7315 | 81.9556 | 82.9275 | 84.2566 | 86.7237 | 85.9113 | 89.1347 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925
85% | 117.6906 | 47.1301 | 49.6656 | 56.4045 | 62.0791 | 65.1386 | 67.3489 | 69.8964 | 71.8015 | 73.903 | 75.002 | 75.9542 | 78.3162 | 76.8854 | 80.7395 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85% | 117.6906 | 50.1625 | 52.7841 | 59.4706 | 65.3601 | 68.4301 | 70.9198 | 73.2863 | 75.302 | 77.4025 | 78.3204 | 79.5757 | 81.9057 | 81.1385 | 84.1828 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374
80% | 268.3703 | 44.3577 | 46.7441 | 53.0866 | 58.4274 | 61.3069 | 63.3872 | 65.7849 | 67.5779 | 69.5558 | 70.5901 | 71.4863 | 73.7094 | 72.3627 | 75.9901 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80% | 268.3703 | 47.2118 | 49.6791 | 55.9723 | 61.5153 | 64.4048 | 66.748 | 68.9754 | 70.8725 | 72.8494 | 73.7134 | 74.8948 | 77.0877 | 76.3656 | 79.2309 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822
75% | 455.9026 | 41.5854 | 43.8226 | 49.7687 | 54.7757 | 57.4752 | 59.4255 | 61.6733 | 63.3542 | 65.2085 | 66.1783 | 67.0184 | 69.1025 | 67.8401 | 71.2407 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75% | 455.9026 | 44.261 | 46.5742 | 52.474 | 57.6706 | 60.3795 | 62.5763 | 64.6644 | 66.4429 | 68.2963 | 69.1063 | 70.2138 | 72.2697 | 71.5928 | 74.2789 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271
70% | 690.9866 | 38.813 | 40.9011 | 46.4508 | 51.124 | 53.6435 | 55.4638 | 57.5618 | 59.1306 | 60.8613 | 61.7664 | 62.5505 | 64.4957 | 63.3174 | 66.4913 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70% | 690.9866 | 41.3103 | 43.4692 | 48.9758 | 53.8259 | 56.3542 | 58.4045 | 60.3535 | 62.0134 | 63.7433 | 64.4992 | 65.5329 | 67.4517 | 66.8199 | 69.327 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772
65% | 967.6784 | 36.0407 | 37.9796 | 43.1329 | 47.4723 | 49.8118 | 51.5021 | 53.4502 | 54.907 | 56.5141 | 57.3545 | 58.0826 | 59.8889 | 58.7947 | 61.7419 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65% | 967.6784 | 38.3596 | 40.3643 | 45.4775 | 49.9812 | 52.3289 | 54.2328 | 56.0425 | 57.5839 | 59.1902 | 59.8921 | 60.852 | 62.6338 | 62.0471 | 64.3751 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168
60% | 1292.8136 | 33.2683 | 35.0581 | 39.8149 | 43.8206 | 45.9802 | 47.5404 | 49.3386 | 50.6834 | 52.1668 | 52.9426 | 53.6147 | 55.282 | 54.2721 | 56.9926 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60% | 1292.8136 | 35.4088 | 37.2594 | 41.9792 | 46.1365 | 48.3036 | 50.061 | 51.7315 | 53.1543 | 54.6371 | 55.285 | 56.1711 | 57.8158 | 57.2742 | 59.4231 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617
55% | 1647.0743 | 30.496 | 32.1366 | 36.497 | 40.1689 | 42.1485 | 43.5787 | 45.2271 | 46.4598 | 47.8196 | 48.5307 | 49.1468 | 50.6752 | 49.7494 | 52.2432 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55% | 1647.0743 | 32.4581 | 34.1544 | 38.481 | 42.2918 | 44.2783 | 45.8893 | 47.4206 | 48.7248 | 50.084 | 50.6779 | 51.4901 | 52.9978 | 52.5014 | 54.4712 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065
50% | 2104.1657 | 27.7236 | 29.2151 | 33.1791 | 36.5171 | 38.3168 | 39.617 | 41.1155 | 42.2362 | 43.4724 | 44.1188 | 44.6789 | 46.0684 | 45.2267 | 47.4938 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50% | 2104.1657 | 29.5074 | 31.0495 | 34.9827 | 38.4471 | 40.253 | 41.7175 | 43.1096 | 44.2953 | 45.5309 | 46.0708 | 46.8092 | 48.1798 | 47.7285 | 49.5193 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514
45% | 2736.0097 | 24.9512 | 26.2936 | 29.8612 | 32.8654 | 34.4851 | 35.6553 | 37.004 | 38.0125 | 39.1251 | 39.707 | 40.211 | 41.4615 | 40.704 | 42.7444 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45% | 2736.0097 | 26.5566 | 27.9445 | 31.4844 | 34.6024 | 36.2277 | 37.5458 | 38.7987 | 39.8658 | 40.9778 | 41.4638 | 42.1283 | 43.3618 | 42.9557 | 44.5674 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963
40% | 3483.7613 | 22.1789 | 23.372 | 26.5433 | 29.2137 | 30.6534 | 31.6936 | 32.8924 | 33.7889 | 34.7779 | 35.2951 | 35.7431 | 36.8547 | 36.1814 | 37.995 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40% | 3483.7613 | 23.6059 | 24.8396 | 27.9862 | 30.7577 | 32.2024 | 33.374 | 34.4877 | 35.4362 | 36.4247 | 36.8567 | 37.4474 | 38.5438 | 38.1828 | 39.6154 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411
35% | 3830.2948 | 19.4065 | 20.4505 | 23.2254 | 25.562 | 26.8218 | 27.7319 | 28.7809 | 29.5653 | 30.4307 | 30.8832 | 31.2753 | 32.2479 | 31.6587 | 33.2457 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35% | 3830.2948 | 20.6551 | 21.7346 | 24.4879 | 26.913 | 28.1771 | 29.2023 | 30.1767 | 31.0067 | 31.8716 | 32.2496 | 32.7665 | 33.7259 | 33.41 | 34.6635 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386
30% | 3953.6322 | 16.6342 | 17.529 | 19.9075 | 21.9103 | 22.9901 | 23.7702 | 24.6693 | 25.3417 | 26.0834 | 26.4713 | 26.8074 | 27.641 | 27.136 | 28.4963 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30% | 3953.6322 | 17.7044 | 18.6297 | 20.9896 | 23.0683 | 24.1518 | 25.0305 | 25.8658 | 26.5772 | 27.3185 | 27.6425 | 28.0855 | 28.9079 | 28.6371 | 29.7116 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308
25% | 4060.9208 | 13.8618 | 14.6075 | 16.5896 | 18.2586 | 19.1584 | 19.8085 | 20.5578 | 21.1181 | 21.7362 | 22.0594 | 22.3395 | 23.0342 | 22.6134 | 23.7469 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25% | 4060.9208 | 14.7537 | 15.5247 | 17.4913 | 19.2235 | 20.1265 | 20.8588 | 21.5548 | 22.1476 | 22.7654 | 23.0354 | 23.4046 | 24.0899 | 23.8643 | 24.7596 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757
20% | 4165.2375 | 11.0894 | 11.686 | 13.2716 | 14.6069 | 15.3267 | 15.8468 | 16.4462 | 16.8945 | 17.3889 | 17.6475 | 17.8716 | 18.4273 | 18.0907 | 18.9975 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20% | 4165.2375 | 11.8029 | 12.4198 | 13.9931 | 15.3788 | 16.1012 | 16.687 | 17.2438 | 17.7181 | 18.2124 | 18.4283 | 18.7237 | 19.2719 | 19.0914 | 19.8077 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206
15% | 4270.4458 | 8.3171 | 8.7645 | 9.9537 | 10.9551 | 11.495 | 11.8851 | 12.3347 | 12.6708 | 13.0417 | 13.2357 | 13.4037 | 13.8205 | 13.568 | 14.2481 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15% | 4270.4458 | 8.8522 | 9.3148 | 10.4948 | 11.5341 | 12.0759 | 12.5153 | 12.9329 | 13.2886 | 13.6593 | 13.8213 | 14.0428 | 14.4539 | 14.3186 | 14.8558 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654
10% | 4373.8709 | 5.5447 | 5.843 | 6.6358 | 7.3034 | 7.6634 | 7.9234 | 8.2231 | 8.4472 | 8.6945 | 8.8238 | 8.9358 | 9.2137 | 9.0453 | 9.4988 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10% | 4373.8709 | 5.9015 | 6.2099 | 6.9965 | 7.6894 | 8.0506 | 8.3435 | 8.6219 | 8.8591 | 9.1062 | 9.2142 | 9.3618 | 9.636 | 9.5457 | 9.9039 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103
5% | 4391.7028 | 2.7724 | 2.9215 | 3.3179 | 3.6517 | 3.8317 | 3.9617 | 4.1116 | 4.2236 | 4.3472 | 4.4119 | 4.4679 | 4.6068 | 4.5227 | 4.7494 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5% | 4391.7028 | 2.9507 | 3.1049 | 3.4983 | 3.8447 | 4.0253 | 4.1718 | 4.311 | 4.4295 | 4.5531 | 4.6071 | 4.6809 | 4.818 | 4.7729 | 4.9519 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551
9.992e-14% | 4391.7028 | 5.5403e-14 | 5.8383e-14 | 6.6305e-14 | 7.2976e-14 | 7.6572e-14 | 7.9171e-14 | 8.2165e-14 | 8.4405e-14 | 8.6875e-14 | 8.8167e-14 | 8.9286e-14 | 9.2063e-14 | 9.0381e-14 | 9.4912e-14 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 9.992e-14% | 4391.7028 | 5.8968e-14 | 6.2049e-14 | 6.9909e-14 | 7.6833e-14 | 8.0442e-14 | 8.3368e-14 | 8.615e-14 | 8.852e-14 | 9.0989e-14 | 9.2068e-14 | 9.3544e-14 | 9.6283e-14 | 9.5381e-14 | 9.8959e-14 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 83.7692 | 85.4357 | 87.3388 | 88.8594 | 89.8481 | 92.2106 | 93.8434 | 94.6997 | 96.293 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 100% | 0 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 92.4783 | 94.6253 | 96.6902 | 98.4782 | 99.3722 | 100.693 | 102.2047 | 103.7467 | 105.6887 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885
99% | 0 | 62.0288 | 64.2408 | 71.9008 | 77.4259 | 80.3299 | 82.9315 | 84.5813 | 86.4654 | 87.9708 | 88.9496 | 91.2885 | 92.905 | 93.7527 | 95.3301 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 99% | 0.75633 | 69.7755 | 72.5154 | 80.1966 | 85.6593 | 88.9328 | 91.5535 | 93.679 | 95.7233 | 97.4934 | 98.3784 | 99.6861 | 101.1827 | 102.7093 | 104.6318 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286
98% | 0.37816 | 61.4023 | 63.5919 | 71.1745 | 76.6438 | 79.5185 | 82.0938 | 83.727 | 85.592 | 87.0822 | 88.0511 | 90.3664 | 91.9665 | 92.8057 | 94.3672 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 98% | 1.1345 | 69.0707 | 71.7829 | 79.3865 | 84.7941 | 88.0345 | 90.6287 | 92.7328 | 94.7564 | 96.5086 | 97.3847 | 98.6792 | 100.1606 | 101.6718 | 103.5749 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687
97% | 0.75633 | 60.7757 | 62.943 | 70.4482 | 75.8617 | 78.707 | 81.2561 | 82.8726 | 84.7186 | 86.1937 | 87.1526 | 89.4443 | 91.0281 | 91.8587 | 93.4043 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 97% | 1.8908 | 68.3659 | 71.0504 | 78.5765 | 83.9289 | 87.1362 | 89.7039 | 91.7865 | 93.7895 | 95.5238 | 96.391 | 97.6722 | 99.1386 | 100.6343 | 102.518 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088
95% | 1.8908 | 59.5226 | 61.6453 | 68.9957 | 74.2976 | 77.0842 | 79.5807 | 81.1639 | 82.9718 | 84.4165 | 85.3557 | 87.6001 | 89.1512 | 89.9648 | 91.4784 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 95% | 3.4035 | 66.9563 | 69.5855 | 76.9563 | 82.1984 | 85.3396 | 87.8544 | 89.894 | 91.8557 | 93.5543 | 94.4036 | 95.6584 | 97.0945 | 98.5594 | 100.4042 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689
90% | 4.538 | 56.3898 | 58.4008 | 65.3643 | 70.3872 | 73.0272 | 75.3923 | 76.8921 | 78.6049 | 79.9735 | 80.8633 | 82.9896 | 84.4591 | 85.2298 | 86.6637 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 90% | 9.0759 | 63.4323 | 65.9231 | 72.906 | 77.8721 | 80.848 | 83.2305 | 85.1628 | 87.0212 | 88.6303 | 89.4349 | 90.6237 | 91.9842 | 93.3721 | 95.1198 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896
85% | 9.0759 | 53.2571 | 55.1563 | 61.733 | 66.4768 | 68.9701 | 71.2038 | 72.6203 | 74.238 | 75.5305 | 76.3709 | 78.379 | 79.7669 | 80.4948 | 81.8491 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 85% | 16.2611 | 59.9082 | 62.2607 | 68.8557 | 73.5459 | 76.3565 | 78.6065 | 80.4315 | 82.1867 | 83.7064 | 84.4663 | 85.5891 | 86.874 | 88.1847 | 89.8354 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902
80% | 27.606 | 50.1243 | 51.9118 | 58.1016 | 62.5664 | 64.913 | 67.0154 | 68.3485 | 69.871 | 71.0876 | 71.8785 | 73.7685 | 75.0747 | 75.7598 | 77.0344 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 80% | 24.9588 | 56.3842 | 58.5983 | 64.8053 | 69.2197 | 71.8649 | 73.9826 | 75.7002 | 77.3522 | 78.7825 | 79.4977 | 80.5544 | 81.7638 | 82.9974 | 84.5509 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908
75% | 57.481 | 46.9915 | 48.6673 | 54.4703 | 58.656 | 60.856 | 62.8269 | 64.0767 | 65.5041 | 66.6446 | 67.3861 | 69.158 | 70.3826 | 71.0248 | 72.2198 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 75% | 32.9003 | 52.8602 | 54.9359 | 60.755 | 64.8934 | 67.3733 | 69.3587 | 70.969 | 72.5176 | 73.8586 | 74.5291 | 75.5198 | 76.6535 | 77.81 | 79.2665 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914
70% | 106.2642 | 43.8588 | 45.4228 | 50.8389 | 54.7456 | 56.7989 | 58.6384 | 59.805 | 61.1371 | 62.2016 | 62.8937 | 64.5474 | 65.6904 | 66.2898 | 67.4051 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 70% | 41.9762 | 49.3362 | 51.2735 | 56.7047 | 60.5672 | 62.8818 | 64.7348 | 66.2377 | 67.6831 | 68.9347 | 69.5605 | 70.4851 | 71.5433 | 72.6227 | 73.9821 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919
65% | 201.9397 | 40.726 | 42.1783 | 47.2076 | 50.8352 | 52.7418 | 54.45 | 55.5332 | 56.7702 | 57.7586 | 58.4013 | 59.9369 | 60.9982 | 61.5548 | 62.5905 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 65% | 67.6914 | 45.8122 | 47.6111 | 52.6543 | 56.241 | 58.3902 | 60.1109 | 61.5064 | 62.8486 | 64.0108 | 64.5919 | 65.4505 | 66.4331 | 67.4354 | 68.6976 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925
60% | 402.745 | 37.5932 | 38.9338 | 43.5762 | 46.9248 | 48.6848 | 50.2615 | 51.2614 | 52.4033 | 53.3157 | 53.9089 | 55.3264 | 56.306 | 56.8198 | 57.7758 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 60% | 98.7009 | 42.2882 | 43.9487 | 48.604 | 51.9148 | 53.8987 | 55.487 | 56.7752 | 58.0141 | 59.0869 | 59.6233 | 60.4158 | 61.3228 | 62.248 | 63.4132 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931
55% | 655.7369 | 34.4605 | 35.6894 | 39.9449 | 43.0144 | 44.6277 | 46.0731 | 46.9896 | 48.0363 | 48.8727 | 49.4165 | 50.7158 | 51.6139 | 52.0849 | 52.9612 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 55% | 153.5347 | 38.7642 | 40.2863 | 44.5537 | 47.5885 | 49.4071 | 50.8631 | 52.0439 | 53.1796 | 54.163 | 54.6547 | 55.3812 | 56.2126 | 57.0607 | 58.1288 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937
50% | 981.7145 | 31.3277 | 32.4449 | 36.3135 | 39.104 | 40.5706 | 41.8846 | 42.7178 | 43.6694 | 44.4297 | 44.924 | 46.1053 | 46.9217 | 47.3499 | 48.1465 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 50% | 258.2862 | 35.2401 | 36.6239 | 40.5033 | 43.2623 | 44.9156 | 46.2391 | 47.3126 | 48.3451 | 49.2391 | 49.6861 | 50.3465 | 51.1024 | 51.8734 | 52.8443 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942
45% | 1622.7029 | 28.1949 | 29.2004 | 32.6822 | 35.1936 | 36.5136 | 37.6961 | 38.446 | 39.3024 | 39.9867 | 40.4316 | 41.4948 | 42.2295 | 42.6149 | 43.3319 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 45% | 488.9664 | 31.7161 | 32.9615 | 36.453 | 38.9361 | 40.424 | 41.6152 | 42.5814 | 43.5106 | 44.3152 | 44.7175 | 45.3119 | 45.9921 | 46.686 | 47.5599 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948
40% | 2442.9413 | 25.0621 | 25.9559 | 29.0508 | 31.2832 | 32.4565 | 33.5077 | 34.1743 | 34.9355 | 35.5438 | 35.9392 | 36.8842 | 37.5374 | 37.8799 | 38.5172 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 40% | 928.0152 | 28.1921 | 29.2991 | 32.4027 | 34.6098 | 35.9325 | 36.9913 | 37.8501 | 38.6761 | 39.3913 | 39.7489 | 40.2772 | 40.8819 | 41.4987 | 42.2755 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954
35% | 3006.7842 | 21.9294 | 22.7114 | 25.4195 | 27.3728 | 28.3994 | 29.3192 | 29.9025 | 30.5686 | 31.1008 | 31.4468 | 32.2737 | 32.8452 | 33.1449 | 33.7026 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 35% | 1530.4309 | 24.6681 | 25.6368 | 28.3523 | 30.2836 | 31.4409 | 32.3674 | 33.1189 | 33.8416 | 34.4674 | 34.7803 | 35.2426 | 35.7716 | 36.3114 | 36.991 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096
30% | 3276.4154 | 18.7966 | 19.4669 | 21.7881 | 23.4624 | 24.3424 | 25.1308 | 25.6307 | 26.2016 | 26.6578 | 26.9544 | 27.6632 | 28.153 | 28.4099 | 28.8879 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 30% | 2592.3162 | 21.1441 | 21.9744 | 24.302 | 25.9574 | 26.9493 | 27.7435 | 28.3876 | 29.0071 | 29.5434 | 29.8116 | 30.2079 | 30.6614 | 31.124 | 31.7066 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965
25% | 3466.632 | 15.6638 | 16.2224 | 18.1568 | 19.552 | 20.2853 | 20.9423 | 21.3589 | 21.8347 | 22.2149 | 22.462 | 23.0527 | 23.4609 | 23.6749 | 24.0733 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 25% | 3659.4958 | 17.6201 | 18.312 | 20.2517 | 21.6311 | 22.4578 | 23.1196 | 23.6563 | 24.1725 | 24.6195 | 24.843 | 25.1733 | 25.5512 | 25.9367 | 26.4222 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971
20% | 3713.9514 | 12.5311 | 12.9779 | 14.5254 | 15.6416 | 16.2283 | 16.7538 | 17.0871 | 17.4678 | 17.7719 | 17.9696 | 18.4421 | 18.7687 | 18.9399 | 19.2586 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 20% | 4005.5161 | 14.0961 | 14.6496 | 16.2013 | 17.3049 | 17.9662 | 18.4957 | 18.9251 | 19.338 | 19.6956 | 19.8744 | 20.1386 | 20.4409 | 20.7493 | 21.1377 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977
15% | 4043.3325 | 9.3983 | 9.7335 | 10.8941 | 11.7312 | 12.1712 | 12.5654 | 12.8153 | 13.1008 | 13.3289 | 13.4772 | 13.8316 | 14.0765 | 14.205 | 14.444 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 15% | 4281.1979 | 10.572 | 10.9872 | 12.151 | 12.9787 | 13.4747 | 13.8717 | 14.1938 | 14.5035 | 14.7717 | 14.9058 | 15.104 | 15.3307 | 15.562 | 15.8533 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983
10% | 4350.7801 | 6.2655 | 6.489 | 7.2627 | 7.8208 | 8.1141 | 8.3769 | 8.5436 | 8.7339 | 8.8859 | 8.9848 | 9.2211 | 9.3843 | 9.47 | 9.6293 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 10% | 4391.6218 | 7.048 | 7.3248 | 8.1007 | 8.6525 | 8.9831 | 9.2478 | 9.4625 | 9.669 | 9.8478 | 9.9372 | 10.0693 | 10.2205 | 10.3747 | 10.5689 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988
5% | 4391.6218 | 3.1328 | 3.2445 | 3.6314 | 3.9104 | 4.0571 | 4.1885 | 4.2718 | 4.3669 | 4.443 | 4.4924 | 4.6105 | 4.6922 | 4.735 | 4.8147 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 5% | 4391.6218 | 3.524 | 3.6624 | 4.0503 | 4.3262 | 4.4916 | 4.6239 | 4.7313 | 4.8345 | 4.9239 | 4.9686 | 5.0347 | 5.1102 | 5.1873 | 5.2844 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994
9.992e-14% | 4391.6218 | 6.2605e-14 | 6.4838e-14 | 7.2569e-14 | 7.8145e-14 | 8.1076e-14 | 8.3702e-14 | 8.5367e-14 | 8.7269e-14 | 8.8788e-14 | 8.9776e-14 | 9.2137e-14 | 9.3768e-14 | 9.4624e-14 | 9.6216e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.992e-14% | 4391.6218 | 7.0424e-14 | 7.3189e-14 | 8.0942e-14 | 8.6455e-14 | 8.9759e-14 | 9.2404e-14 | 9.455e-14 | 9.6613e-14 | 9.8399e-14 | 9.9293e-14 | 1.0061e-13 | 1.0212e-13 | 1.0366e-13 | 1.056e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 55.4472 | 58.4301 | 66.3582 | 73.0343 | 76.6336 | 79.234 | 82.2311 | 84.4723 | 86.9447 | 88.2377 | 89.3579 | 92.1367 | 90.4534 | 94.9876 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 100% | 0 | 59.0147 | 62.0989 | 69.9654 | 76.8942 | 80.506 | 83.435 | 86.2192 | 88.5906 | 91.0618 | 92.1417 | 93.6184 | 96.3596 | 95.457 | 99.0386 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028 | 101.1028
99% | 0.8916 | 54.8927 | 57.8458 | 65.6947 | 72.3039 | 75.8673 | 78.4417 | 81.4088 | 83.6276 | 86.0753 | 87.3553 | 88.4643 | 91.2154 | 89.5489 | 94.0377 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99.8942 | 99% | 0.8916 | 58.4246 | 61.4779 | 69.2657 | 76.1252 | 79.701 | 82.6007 | 85.357 | 87.7047 | 90.1512 | 91.2203 | 92.6823 | 95.396 | 94.5025 | 98.0482 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918 | 100.0918
98% | 3.5664 | 54.3382 | 57.2615 | 65.0311 | 71.5736 | 75.1009 | 77.6493 | 80.5865 | 82.7829 | 85.2058 | 86.4729 | 87.5707 | 90.294 | 88.6444 | 93.0878 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98.8852 | 98% | 3.5664 | 57.8344 | 60.8569 | 68.5661 | 75.3563 | 78.8959 | 81.7663 | 84.4948 | 86.8188 | 89.2406 | 90.2989 | 91.7461 | 94.4324 | 93.5479 | 97.0578 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807 | 99.0807
97% | 4.7552 | 53.7838 | 56.6772 | 64.3675 | 70.8433 | 74.3346 | 76.857 | 79.7641 | 81.9382 | 84.3364 | 85.5905 | 86.6771 | 89.3726 | 87.7398 | 92.138 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97.8762 | 97% | 4.7552 | 57.2443 | 60.2359 | 67.8664 | 74.5874 | 78.0908 | 80.932 | 83.6327 | 85.9329 | 88.3299 | 89.3774 | 90.8099 | 93.4688 | 92.5933 | 96.0674 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697 | 98.0697
95% | 7.7272 | 52.6748 | 55.5086 | 63.0403 | 69.3826 | 72.8019 | 75.2723 | 78.1195 | 80.2487 | 82.5975 | 83.8258 | 84.89 | 87.5299 | 85.9308 | 90.2382 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95.8581 | 95% | 7.7272 | 56.064 | 58.994 | 66.4671 | 73.0495 | 76.4807 | 79.2633 | 81.9083 | 84.161 | 86.5087 | 87.5346 | 88.9375 | 91.5416 | 90.6842 | 94.0866 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477 | 96.0477
90% | 39.2302 | 49.9025 | 52.5871 | 59.7224 | 65.7309 | 68.9702 | 71.3106 | 74.008 | 76.0251 | 78.2502 | 79.4139 | 80.4221 | 82.9231 | 81.4081 | 85.4888 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90.8129 | 90% | 39.2302 | 53.1132 | 55.889 | 62.9689 | 69.2048 | 72.4554 | 75.0915 | 77.5973 | 79.7315 | 81.9556 | 82.9275 | 84.2566 | 86.7237 | 85.9113 | 89.1347 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925 | 90.9925
85% | 117.6906 | 47.1301 | 49.6656 | 56.4045 | 62.0791 | 65.1386 | 67.3489 | 69.8964 | 71.8015 | 73.903 | 75.002 | 75.9542 | 78.3162 | 76.8854 | 80.7395 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85.7678 | 85% | 117.6906 | 50.1625 | 52.7841 | 59.4706 | 65.3601 | 68.4301 | 70.9198 | 73.2863 | 75.302 | 77.4025 | 78.3204 | 79.5757 | 81.9057 | 81.1385 | 84.1828 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374 | 85.9374
80% | 268.3703 | 44.3577 | 46.7441 | 53.0866 | 58.4274 | 61.3069 | 63.3872 | 65.7849 | 67.5779 | 69.5558 | 70.5901 | 71.4863 | 73.7094 | 72.3627 | 75.9901 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80.7226 | 80% | 268.3703 | 47.2118 | 49.6791 | 55.9723 | 61.5153 | 64.4048 | 66.748 | 68.9754 | 70.8725 | 72.8494 | 73.7134 | 74.8948 | 77.0877 | 76.3656 | 79.2309 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822 | 80.8822
75% | 455.9026 | 41.5854 | 43.8226 | 49.7687 | 54.7757 | 57.4752 | 59.4255 | 61.6733 | 63.3542 | 65.2085 | 66.1783 | 67.0184 | 69.1025 | 67.8401 | 71.2407 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75.6775 | 75% | 455.9026 | 44.261 | 46.5742 | 52.474 | 57.6706 | 60.3795 | 62.5763 | 64.6644 | 66.4429 | 68.2963 | 69.1063 | 70.2138 | 72.2697 | 71.5928 | 74.2789 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271 | 75.8271
70% | 690.9866 | 38.813 | 40.9011 | 46.4508 | 51.124 | 53.6435 | 55.4638 | 57.5618 | 59.1306 | 60.8613 | 61.7664 | 62.5505 | 64.4957 | 63.3174 | 66.4913 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70.6323 | 70% | 690.9866 | 41.3103 | 43.4692 | 48.9758 | 53.8259 | 56.3542 | 58.4045 | 60.3535 | 62.0134 | 63.7433 | 64.4992 | 65.5329 | 67.4517 | 66.8199 | 69.327 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772 | 70.772
65% | 967.6784 | 36.0407 | 37.9796 | 43.1329 | 47.4723 | 49.8118 | 51.5021 | 53.4502 | 54.907 | 56.5141 | 57.3545 | 58.0826 | 59.8889 | 58.7947 | 61.7419 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65.5871 | 65% | 967.6784 | 38.3596 | 40.3643 | 45.4775 | 49.9812 | 52.3289 | 54.2328 | 56.0425 | 57.5839 | 59.1902 | 59.8921 | 60.852 | 62.6338 | 62.0471 | 64.3751 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168 | 65.7168
60% | 1292.8136 | 33.2683 | 35.0581 | 39.8149 | 43.8206 | 45.9802 | 47.5404 | 49.3386 | 50.6834 | 52.1668 | 52.9426 | 53.6147 | 55.282 | 54.2721 | 56.9926 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60.542 | 60% | 1292.8136 | 35.4088 | 37.2594 | 41.9792 | 46.1365 | 48.3036 | 50.061 | 51.7315 | 53.1543 | 54.6371 | 55.285 | 56.1711 | 57.8158 | 57.2742 | 59.4231 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617 | 60.6617
55% | 1647.0743 | 30.496 | 32.1366 | 36.497 | 40.1689 | 42.1485 | 43.5787 | 45.2271 | 46.4598 | 47.8196 | 48.5307 | 49.1468 | 50.6752 | 49.7494 | 52.2432 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55.4968 | 55% | 1647.0743 | 32.4581 | 34.1544 | 38.481 | 42.2918 | 44.2783 | 45.8893 | 47.4206 | 48.7248 | 50.084 | 50.6779 | 51.4901 | 52.9978 | 52.5014 | 54.4712 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065 | 55.6065
50% | 2104.1657 | 27.7236 | 29.2151 | 33.1791 | 36.5171 | 38.3168 | 39.617 | 41.1155 | 42.2362 | 43.4724 | 44.1188 | 44.6789 | 46.0684 | 45.2267 | 47.4938 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50.4516 | 50% | 2104.1657 | 29.5074 | 31.0495 | 34.9827 | 38.4471 | 40.253 | 41.7175 | 43.1096 | 44.2953 | 45.5309 | 46.0708 | 46.8092 | 48.1798 | 47.7285 | 49.5193 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514 | 50.5514
45% | 2736.0097 | 24.9512 | 26.2936 | 29.8612 | 32.8654 | 34.4851 | 35.6553 | 37.004 | 38.0125 | 39.1251 | 39.707 | 40.211 | 41.4615 | 40.704 | 42.7444 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45.4065 | 45% | 2736.0097 | 26.5566 | 27.9445 | 31.4844 | 34.6024 | 36.2277 | 37.5458 | 38.7987 | 39.8658 | 40.9778 | 41.4638 | 42.1283 | 43.3618 | 42.9557 | 44.5674 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963 | 45.4963
40% | 3483.7613 | 22.1789 | 23.372 | 26.5433 | 29.2137 | 30.6534 | 31.6936 | 32.8924 | 33.7889 | 34.7779 | 35.2951 | 35.7431 | 36.8547 | 36.1814 | 37.995 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40.3613 | 40% | 3483.7613 | 23.6059 | 24.8396 | 27.9862 | 30.7577 | 32.2024 | 33.374 | 34.4877 | 35.4362 | 36.4247 | 36.8567 | 37.4474 | 38.5438 | 38.1828 | 39.6154 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411 | 40.4411
35% | 3830.2948 | 19.4065 | 20.4505 | 23.2254 | 25.562 | 26.8218 | 27.7319 | 28.7809 | 29.5653 | 30.4307 | 30.8832 | 31.2753 | 32.2479 | 31.6587 | 33.2457 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35.3161 | 35% | 3830.2948 | 20.6551 | 21.7346 | 24.4879 | 26.913 | 28.1771 | 29.2023 | 30.1767 | 31.0067 | 31.8716 | 32.2496 | 32.7665 | 33.7259 | 33.41 | 34.6635 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386 | 35.386
30% | 3953.6322 | 16.6342 | 17.529 | 19.9075 | 21.9103 | 22.9901 | 23.7702 | 24.6693 | 25.3417 | 26.0834 | 26.4713 | 26.8074 | 27.641 | 27.136 | 28.4963 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30.271 | 30% | 3953.6322 | 17.7044 | 18.6297 | 20.9896 | 23.0683 | 24.1518 | 25.0305 | 25.8658 | 26.5772 | 27.3185 | 27.6425 | 28.0855 | 28.9079 | 28.6371 | 29.7116 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308 | 30.3308
25% | 4060.9208 | 13.8618 | 14.6075 | 16.5896 | 18.2586 | 19.1584 | 19.8085 | 20.5578 | 21.1181 | 21.7362 | 22.0594 | 22.3395 | 23.0342 | 22.6134 | 23.7469 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25.2258 | 25% | 4060.9208 | 14.7537 | 15.5247 | 17.4913 | 19.2235 | 20.1265 | 20.8588 | 21.5548 | 22.1476 | 22.7654 | 23.0354 | 23.4046 | 24.0899 | 23.8643 | 24.7596 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757 | 25.2757
20% | 4165.2375 | 11.0894 | 11.686 | 13.2716 | 14.6069 | 15.3267 | 15.8468 | 16.4462 | 16.8945 | 17.3889 | 17.6475 | 17.8716 | 18.4273 | 18.0907 | 18.9975 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20.1807 | 20% | 4165.2375 | 11.8029 | 12.4198 | 13.9931 | 15.3788 | 16.1012 | 16.687 | 17.2438 | 17.7181 | 18.2124 | 18.4283 | 18.7237 | 19.2719 | 19.0914 | 19.8077 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206 | 20.2206
15% | 4270.4458 | 8.3171 | 8.7645 | 9.9537 | 10.9551 | 11.495 | 11.8851 | 12.3347 | 12.6708 | 13.0417 | 13.2357 | 13.4037 | 13.8205 | 13.568 | 14.2481 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15.1355 | 15% | 4270.4458 | 8.8522 | 9.3148 | 10.4948 | 11.5341 | 12.0759 | 12.5153 | 12.9329 | 13.2886 | 13.6593 | 13.8213 | 14.0428 | 14.4539 | 14.3186 | 14.8558 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654 | 15.1654
10% | 4373.8709 | 5.5447 | 5.843 | 6.6358 | 7.3034 | 7.6634 | 7.9234 | 8.2231 | 8.4472 | 8.6945 | 8.8238 | 8.9358 | 9.2137 | 9.0453 | 9.4988 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10.0903 | 10% | 4373.8709 | 5.9015 | 6.2099 | 6.9965 | 7.6894 | 8.0506 | 8.3435 | 8.6219 | 8.8591 | 9.1062 | 9.2142 | 9.3618 | 9.636 | 9.5457 | 9.9039 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103 | 10.1103
5% | 4391.7028 | 2.7724 | 2.9215 | 3.3179 | 3.6517 | 3.8317 | 3.9617 | 4.1116 | 4.2236 | 4.3472 | 4.4119 | 4.4679 | 4.6068 | 4.5227 | 4.7494 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5.0452 | 5% | 4391.7028 | 2.9507 | 3.1049 | 3.4983 | 3.8447 | 4.0253 | 4.1718 | 4.311 | 4.4295 | 4.5531 | 4.6071 | 4.6809 | 4.818 | 4.7729 | 4.9519 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551 | 5.0551
9.992e-14% | 4391.7028 | 5.5403e-14 | 5.8383e-14 | 6.6305e-14 | 7.2976e-14 | 7.6572e-14 | 7.9171e-14 | 8.2165e-14 | 8.4405e-14 | 8.6875e-14 | 8.8167e-14 | 8.9286e-14 | 9.2063e-14 | 9.0381e-14 | 9.4912e-14 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 1.0082e-13 | 9.992e-14% | 4391.7028 | 5.8968e-14 | 6.2049e-14 | 6.9909e-14 | 7.6833e-14 | 8.0442e-14 | 8.3368e-14 | 8.615e-14 | 8.852e-14 | 9.0989e-14 | 9.2068e-14 | 9.3544e-14 | 9.6283e-14 | 9.5381e-14 | 9.8959e-14 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13 | 1.0102e-13
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 62.6554 | 64.8897 | 72.627 | 78.208 | 81.1413 | 83.7692 | 85.4357 | 87.3388 | 88.8594 | 89.8481 | 92.2106 | 93.8434 | 94.6997 | 96.293 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 95.8242 | 100% | 0 | 70.4803 | 73.2479 | 81.0067 | 86.5246 | 89.8311 | 92.4783 | 94.6253 | 96.6902 | 98.4782 | 99.3722 | 100.693 | 102.2047 | 103.7467 | 105.6887 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885 | 105.9885
99% | 0 | 62.0288 | 64.2408 | 71.9008 | 77.4259 | 80.3299 | 82.9315 | 84.5813 | 86.4654 | 87.9708 | 88.9496 | 91.2885 | 92.905 | 93.7527 | 95.3301 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 94.8659 | 99% | 0.75633 | 69.7755 | 72.5154 | 80.1966 | 85.6593 | 88.9328 | 91.5535 | 93.679 | 95.7233 | 97.4934 | 98.3784 | 99.6861 | 101.1827 | 102.7093 | 104.6318 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286 | 104.9286
98% | 0.37816 | 61.4023 | 63.5919 | 71.1745 | 76.6438 | 79.5185 | 82.0938 | 83.727 | 85.592 | 87.0822 | 88.0511 | 90.3664 | 91.9665 | 92.8057 | 94.3672 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 93.9077 | 98% | 1.1345 | 69.0707 | 71.7829 | 79.3865 | 84.7941 | 88.0345 | 90.6287 | 92.7328 | 94.7564 | 96.5086 | 97.3847 | 98.6792 | 100.1606 | 101.6718 | 103.5749 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687 | 103.8687
97% | 0.75633 | 60.7757 | 62.943 | 70.4482 | 75.8617 | 78.707 | 81.2561 | 82.8726 | 84.7186 | 86.1937 | 87.1526 | 89.4443 | 91.0281 | 91.8587 | 93.4043 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 92.9494 | 97% | 1.8908 | 68.3659 | 71.0504 | 78.5765 | 83.9289 | 87.1362 | 89.7039 | 91.7865 | 93.7895 | 95.5238 | 96.391 | 97.6722 | 99.1386 | 100.6343 | 102.518 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088 | 102.8088
95% | 1.8908 | 59.5226 | 61.6453 | 68.9957 | 74.2976 | 77.0842 | 79.5807 | 81.1639 | 82.9718 | 84.4165 | 85.3557 | 87.6001 | 89.1512 | 89.9648 | 91.4784 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 91.033 | 95% | 3.4035 | 66.9563 | 69.5855 | 76.9563 | 82.1984 | 85.3396 | 87.8544 | 89.894 | 91.8557 | 93.5543 | 94.4036 | 95.6584 | 97.0945 | 98.5594 | 100.4042 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689 | 100.689
90% | 4.538 | 56.3898 | 58.4008 | 65.3643 | 70.3872 | 73.0272 | 75.3923 | 76.8921 | 78.6049 | 79.9735 | 80.8633 | 82.9896 | 84.4591 | 85.2298 | 86.6637 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 86.2417 | 90% | 9.0759 | 63.4323 | 65.9231 | 72.906 | 77.8721 | 80.848 | 83.2305 | 85.1628 | 87.0212 | 88.6303 | 89.4349 | 90.6237 | 91.9842 | 93.3721 | 95.1198 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896 | 95.3896
85% | 9.0759 | 53.2571 | 55.1563 | 61.733 | 66.4768 | 68.9701 | 71.2038 | 72.6203 | 74.238 | 75.5305 | 76.3709 | 78.379 | 79.7669 | 80.4948 | 81.8491 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 81.4505 | 85% | 16.2611 | 59.9082 | 62.2607 | 68.8557 | 73.5459 | 76.3565 | 78.6065 | 80.4315 | 82.1867 | 83.7064 | 84.4663 | 85.5891 | 86.874 | 88.1847 | 89.8354 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902 | 90.0902
80% | 27.606 | 50.1243 | 51.9118 | 58.1016 | 62.5664 | 64.913 | 67.0154 | 68.3485 | 69.871 | 71.0876 | 71.8785 | 73.7685 | 75.0747 | 75.7598 | 77.0344 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 76.6593 | 80% | 24.9588 | 56.3842 | 58.5983 | 64.8053 | 69.2197 | 71.8649 | 73.9826 | 75.7002 | 77.3522 | 78.7825 | 79.4977 | 80.5544 | 81.7638 | 82.9974 | 84.5509 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908 | 84.7908
75% | 57.481 | 46.9915 | 48.6673 | 54.4703 | 58.656 | 60.856 | 62.8269 | 64.0767 | 65.5041 | 66.6446 | 67.3861 | 69.158 | 70.3826 | 71.0248 | 72.2198 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 71.8681 | 75% | 32.9003 | 52.8602 | 54.9359 | 60.755 | 64.8934 | 67.3733 | 69.3587 | 70.969 | 72.5176 | 73.8586 | 74.5291 | 75.5198 | 76.6535 | 77.81 | 79.2665 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914 | 79.4914
70% | 106.2642 | 43.8588 | 45.4228 | 50.8389 | 54.7456 | 56.7989 | 58.6384 | 59.805 | 61.1371 | 62.2016 | 62.8937 | 64.5474 | 65.6904 | 66.2898 | 67.4051 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 67.0769 | 70% | 41.9762 | 49.3362 | 51.2735 | 56.7047 | 60.5672 | 62.8818 | 64.7348 | 66.2377 | 67.6831 | 68.9347 | 69.5605 | 70.4851 | 71.5433 | 72.6227 | 73.9821 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919 | 74.1919
65% | 201.9397 | 40.726 | 42.1783 | 47.2076 | 50.8352 | 52.7418 | 54.45 | 55.5332 | 56.7702 | 57.7586 | 58.4013 | 59.9369 | 60.9982 | 61.5548 | 62.5905 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 62.2857 | 65% | 67.6914 | 45.8122 | 47.6111 | 52.6543 | 56.241 | 58.3902 | 60.1109 | 61.5064 | 62.8486 | 64.0108 | 64.5919 | 65.4505 | 66.4331 | 67.4354 | 68.6976 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925 | 68.8925
60% | 402.745 | 37.5932 | 38.9338 | 43.5762 | 46.9248 | 48.6848 | 50.2615 | 51.2614 | 52.4033 | 53.3157 | 53.9089 | 55.3264 | 56.306 | 56.8198 | 57.7758 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 57.4945 | 60% | 98.7009 | 42.2882 | 43.9487 | 48.604 | 51.9148 | 53.8987 | 55.487 | 56.7752 | 58.0141 | 59.0869 | 59.6233 | 60.4158 | 61.3228 | 62.248 | 63.4132 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931 | 63.5931
55% | 655.7369 | 34.4605 | 35.6894 | 39.9449 | 43.0144 | 44.6277 | 46.0731 | 46.9896 | 48.0363 | 48.8727 | 49.4165 | 50.7158 | 51.6139 | 52.0849 | 52.9612 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 52.7033 | 55% | 153.5347 | 38.7642 | 40.2863 | 44.5537 | 47.5885 | 49.4071 | 50.8631 | 52.0439 | 53.1796 | 54.163 | 54.6547 | 55.3812 | 56.2126 | 57.0607 | 58.1288 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937 | 58.2937
50% | 981.7145 | 31.3277 | 32.4449 | 36.3135 | 39.104 | 40.5706 | 41.8846 | 42.7178 | 43.6694 | 44.4297 | 44.924 | 46.1053 | 46.9217 | 47.3499 | 48.1465 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 47.9121 | 50% | 258.2862 | 35.2401 | 36.6239 | 40.5033 | 43.2623 | 44.9156 | 46.2391 | 47.3126 | 48.3451 | 49.2391 | 49.6861 | 50.3465 | 51.1024 | 51.8734 | 52.8443 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942 | 52.9942
45% | 1622.7029 | 28.1949 | 29.2004 | 32.6822 | 35.1936 | 36.5136 | 37.6961 | 38.446 | 39.3024 | 39.9867 | 40.4316 | 41.4948 | 42.2295 | 42.6149 | 43.3319 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 43.1209 | 45% | 488.9664 | 31.7161 | 32.9615 | 36.453 | 38.9361 | 40.424 | 41.6152 | 42.5814 | 43.5106 | 44.3152 | 44.7175 | 45.3119 | 45.9921 | 46.686 | 47.5599 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948 | 47.6948
40% | 2442.9413 | 25.0621 | 25.9559 | 29.0508 | 31.2832 | 32.4565 | 33.5077 | 34.1743 | 34.9355 | 35.5438 | 35.9392 | 36.8842 | 37.5374 | 37.8799 | 38.5172 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 38.3297 | 40% | 928.0152 | 28.1921 | 29.2991 | 32.4027 | 34.6098 | 35.9325 | 36.9913 | 37.8501 | 38.6761 | 39.3913 | 39.7489 | 40.2772 | 40.8819 | 41.4987 | 42.2755 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954 | 42.3954
35% | 3006.7842 | 21.9294 | 22.7114 | 25.4195 | 27.3728 | 28.3994 | 29.3192 | 29.9025 | 30.5686 | 31.1008 | 31.4468 | 32.2737 | 32.8452 | 33.1449 | 33.7026 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 33.5385 | 35% | 1530.4309 | 24.6681 | 25.6368 | 28.3523 | 30.2836 | 31.4409 | 32.3674 | 33.1189 | 33.8416 | 34.4674 | 34.7803 | 35.2426 | 35.7716 | 36.3114 | 36.991 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096 | 37.096
30% | 3276.4154 | 18.7966 | 19.4669 | 21.7881 | 23.4624 | 24.3424 | 25.1308 | 25.6307 | 26.2016 | 26.6578 | 26.9544 | 27.6632 | 28.153 | 28.4099 | 28.8879 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 28.7472 | 30% | 2592.3162 | 21.1441 | 21.9744 | 24.302 | 25.9574 | 26.9493 | 27.7435 | 28.3876 | 29.0071 | 29.5434 | 29.8116 | 30.2079 | 30.6614 | 31.124 | 31.7066 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965 | 31.7965
25% | 3466.632 | 15.6638 | 16.2224 | 18.1568 | 19.552 | 20.2853 | 20.9423 | 21.3589 | 21.8347 | 22.2149 | 22.462 | 23.0527 | 23.4609 | 23.6749 | 24.0733 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 23.956 | 25% | 3659.4958 | 17.6201 | 18.312 | 20.2517 | 21.6311 | 22.4578 | 23.1196 | 23.6563 | 24.1725 | 24.6195 | 24.843 | 25.1733 | 25.5512 | 25.9367 | 26.4222 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971 | 26.4971
20% | 3713.9514 | 12.5311 | 12.9779 | 14.5254 | 15.6416 | 16.2283 | 16.7538 | 17.0871 | 17.4678 | 17.7719 | 17.9696 | 18.4421 | 18.7687 | 18.9399 | 19.2586 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 19.1648 | 20% | 4005.5161 | 14.0961 | 14.6496 | 16.2013 | 17.3049 | 17.9662 | 18.4957 | 18.9251 | 19.338 | 19.6956 | 19.8744 | 20.1386 | 20.4409 | 20.7493 | 21.1377 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977 | 21.1977
15% | 4043.3325 | 9.3983 | 9.7335 | 10.8941 | 11.7312 | 12.1712 | 12.5654 | 12.8153 | 13.1008 | 13.3289 | 13.4772 | 13.8316 | 14.0765 | 14.205 | 14.444 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 14.3736 | 15% | 4281.1979 | 10.572 | 10.9872 | 12.151 | 12.9787 | 13.4747 | 13.8717 | 14.1938 | 14.5035 | 14.7717 | 14.9058 | 15.104 | 15.3307 | 15.562 | 15.8533 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983 | 15.8983
10% | 4350.7801 | 6.2655 | 6.489 | 7.2627 | 7.8208 | 8.1141 | 8.3769 | 8.5436 | 8.7339 | 8.8859 | 8.9848 | 9.2211 | 9.3843 | 9.47 | 9.6293 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 9.5824 | 10% | 4391.6218 | 7.048 | 7.3248 | 8.1007 | 8.6525 | 8.9831 | 9.2478 | 9.4625 | 9.669 | 9.8478 | 9.9372 | 10.0693 | 10.2205 | 10.3747 | 10.5689 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988 | 10.5988
5% | 4391.6218 | 3.1328 | 3.2445 | 3.6314 | 3.9104 | 4.0571 | 4.1885 | 4.2718 | 4.3669 | 4.443 | 4.4924 | 4.6105 | 4.6922 | 4.735 | 4.8147 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 4.7912 | 5% | 4391.6218 | 3.524 | 3.6624 | 4.0503 | 4.3262 | 4.4916 | 4.6239 | 4.7313 | 4.8345 | 4.9239 | 4.9686 | 5.0347 | 5.1102 | 5.1873 | 5.2844 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994 | 5.2994
9.992e-14% | 4391.6218 | 6.2605e-14 | 6.4838e-14 | 7.2569e-14 | 7.8145e-14 | 8.1076e-14 | 8.3702e-14 | 8.5367e-14 | 8.7269e-14 | 8.8788e-14 | 8.9776e-14 | 9.2137e-14 | 9.3768e-14 | 9.4624e-14 | 9.6216e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.5748e-14 | 9.992e-14% | 4391.6218 | 7.0424e-14 | 7.3189e-14 | 8.0942e-14 | 8.6455e-14 | 8.9759e-14 | 9.2404e-14 | 9.455e-14 | 9.6613e-14 | 9.8399e-14 | 9.9293e-14 | 1.0061e-13 | 1.0212e-13 | 1.0366e-13 | 1.056e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13 | 1.059e-13

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 105212961.6203 | 61.5% | 30.2784
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 59818974.1027 | 34.97% | 12.0256
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 2268426.58 | 1.326% | 0.44409
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 3766583.5488 | 2.202% | 0.4899
|  | 171066945.8518 |  | 43.238 | KW/h
|  |  |  | 43237.9539 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 1.1704; FY39: 6.4184; FY40: 6.4184; FY41: 6.4184; FY42: 6.4184; FY43: 6.4184; FY44: 6.4184; FY45: 6.4184; FY46: 6.4184; FY47: 6.4184; FY48: 6.4184; FY49: 6.4184; FY50: 6.4184; FY51: 6.4184; FY52: 6.4184; FY53: 6.4184; FY54: 6.4184 | [11 empty] | 0.083376 | 2.3875 | 1.5868 | 4.7641 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954
98% | FY38: 0.98808; FY39: 16.5562; FY40: 16.5562; FY41: 16.5562; FY42: 16.5562; FY43: 16.5562; FY44: 16.5562; FY45: 16.5562; FY46: 16.5562; FY47: 16.5562; FY48: 16.5562; FY49: 16.5562; FY50: 16.5562; FY51: 16.5562; FY52: 16.5562; FY53: 16.5562; FY54: 16.5562 | [12 empty] | 4.5852 | 2.2072 | 11.6433 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819
97% | FY39: 6.1588; FY40: 6.1588; FY41: 6.1588; FY42: 6.1588; FY43: 6.1588; FY44: 6.1588; FY45: 6.1588; FY46: 6.1588; FY47: 6.1588; FY48: 6.1588; FY49: 6.1588; FY50: 6.1588; FY51: 6.1588; FY52: 6.1588; FY53: 6.1588; FY54: 6.1588 | [12 empty] | 0.89235 | 0.075359 | 3.9975 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39
95% | FY39: 10.8987; FY40: 10.8987; FY41: 10.8987; FY42: 10.8987; FY43: 10.8987; FY44: 10.8987; FY45: 10.8987; FY46: 10.8987; FY47: 10.8987; FY48: 10.8987; FY49: 10.8987; FY50: 10.8987; FY51: 10.8987; FY52: 10.8987; FY53: 10.8987; FY54: 10.8987 | [12 empty] | 0.055727 |  | 5.5785 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468
90% | FY39: 22.0594; FY40: 22.0594; FY41: 22.0594; FY42: 22.0594; FY43: 22.0594; FY44: 22.0594; FY45: 22.0594; FY46: 22.0594; FY47: 22.0594; FY48: 22.0594; FY49: 22.0594; FY50: 22.0594; FY51: 22.0594; FY52: 22.0594; FY53: 22.0594; FY54: 22.0594 | [14 empty] | 2.5006 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1584 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083376 | 7.9208 | 3.8693 | 28.4841 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5109 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025013 | 2.3762 | 1.1608 | 8.5452 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0.72015 | 2.2741 | 3.6196 | 4.2924 | 5.2864 | 6.424 | 7.5845 | 9.0459 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715
98% | [12 empty] | 0.061002 | 0.62346 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | [7 empty] | 0.045855 | 0.7714 | 1.4374 | 1.7704 | 2.2624 | 2.8255 | 3.3999 | 4.1233 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349
97% | FY38: 0.25931; FY39: 0.09882; FY40: 0.09882; FY41: 0.09882; FY42: 0.09882; FY43: 0.09882; FY44: 0.09882; FY45: 0.09882; FY46: 0.09882; FY47: 0.09882; FY48: 0.09882; FY49: 0.09882; FY50: 0.09882; FY51: 0.09882; FY52: 0.09882; FY53: 0.09882; FY54: 0.09882 | [8 empty] | 0.8115 | 2.13 | 2.7892 | 3.7633 | 4.878 | 6.0151 | 7.4472 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682
95% | FY38: 0.012288 | [8 empty] | 0.13591 | 2.0255 | 3.3237 | 5.2418 | 7.437 | 9.6763 | 12.4963 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316
90% | [39 empty] | 0.072287 | 0.82688 | 3.4046 | 8.4178 | 15.6885 | 25.8779 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509
85% | [43 empty] | 0.020502 | 2.5056 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061002 | 0.89506 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.76601 | 3.9929 | 9.2848 | 13.0026 | 19.9585 | 29.9823 | 42.3847 | 61.4961 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042702 | 0.62654 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.2298 | 1.1979 | 2.7854 | 3.9008 | 5.9875 | 8.9947 | 12.7154 | 18.4488 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY39: 0.0043278; FY40: 0.0043278; FY41: 0.0043278; FY42: 0.0043278; FY43: 0.0043278; FY44: 0.0043278; FY45: 0.0043278; FY46: 0.0043278; FY47: 0.0043278; FY48: 0.0043278; FY49: 0.0043278; FY50: 0.0043278; FY51: 0.0043278; FY52: 0.0043278; FY53: 0.0043278; FY54: 0.0043278 | [15 empty] | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | 0.0043278 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408 | 0.041408
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | 0.0030294 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422 | 0.012422
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [41 empty] | 0.024027 | 0.89101 | 1.9729 | 3.3341 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546 | 3.546
98% | [42 empty] | 0.098744 | 0.6223 | 1.2961 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401 | 1.401
97% | [43 empty] | 0.51633 | 1.8502 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579 | 2.0579
95% | [43 empty] | 0.015903 | 1.4746 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835 | 1.8835
90% | [45 empty] | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381 | 0.039381
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.024027 | 0.98975 | 3.1274 | 7.9549 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277 | 8.9277
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007208 | 0.29693 | 0.93822 | 2.3865 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783 | 2.6783
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 1.1704; FY39: 6.4184; FY40: 6.4184; FY41: 6.4184; FY42: 6.4184; FY43: 6.4184; FY44: 6.4184; FY45: 6.4184; FY46: 6.4184; FY47: 6.4184; FY48: 6.4184; FY49: 6.4184; FY50: 6.4184; FY51: 6.4184; FY52: 6.4184; FY53: 6.4184; FY54: 6.4184 | [11 empty] | 0.083376 | 2.3875 | 1.5868 | 4.7641 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954
98% | FY38: 0.98808; FY39: 16.5562; FY40: 16.5562; FY41: 16.5562; FY42: 16.5562; FY43: 16.5562; FY44: 16.5562; FY45: 16.5562; FY46: 16.5562; FY47: 16.5562; FY48: 16.5562; FY49: 16.5562; FY50: 16.5562; FY51: 16.5562; FY52: 16.5562; FY53: 16.5562; FY54: 16.5562 | [12 empty] | 4.5852 | 2.2072 | 11.6433 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819
97% | FY39: 6.1588; FY40: 6.1588; FY41: 6.1588; FY42: 6.1588; FY43: 6.1588; FY44: 6.1588; FY45: 6.1588; FY46: 6.1588; FY47: 6.1588; FY48: 6.1588; FY49: 6.1588; FY50: 6.1588; FY51: 6.1588; FY52: 6.1588; FY53: 6.1588; FY54: 6.1588 | [12 empty] | 0.89235 | 0.075359 | 3.9975 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39
95% | FY39: 10.8987; FY40: 10.8987; FY41: 10.8987; FY42: 10.8987; FY43: 10.8987; FY44: 10.8987; FY45: 10.8987; FY46: 10.8987; FY47: 10.8987; FY48: 10.8987; FY49: 10.8987; FY50: 10.8987; FY51: 10.8987; FY52: 10.8987; FY53: 10.8987; FY54: 10.8987 | [12 empty] | 0.055727 |  | 5.5785 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468
90% | FY39: 22.0594; FY40: 22.0594; FY41: 22.0594; FY42: 22.0594; FY43: 22.0594; FY44: 22.0594; FY45: 22.0594; FY46: 22.0594; FY47: 22.0594; FY48: 22.0594; FY49: 22.0594; FY50: 22.0594; FY51: 22.0594; FY52: 22.0594; FY53: 22.0594; FY54: 22.0594 | [14 empty] | 2.5006 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1584 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083376 | 7.9208 | 3.8693 | 28.4841 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5109 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025013 | 2.3762 | 1.1608 | 8.5452 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0.72015 | 2.2741 | 3.6196 | 4.2924 | 5.2864 | 6.424 | 7.5845 | 9.0459 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715
98% | [12 empty] | 0.061002 | 0.62346 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | [7 empty] | 0.045855 | 0.7714 | 1.4374 | 1.7704 | 2.2624 | 2.8255 | 3.3999 | 4.1233 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349
97% | FY38: 0.25931; FY39: 0.09882; FY40: 0.09882; FY41: 0.09882; FY42: 0.09882; FY43: 0.09882; FY44: 0.09882; FY45: 0.09882; FY46: 0.09882; FY47: 0.09882; FY48: 0.09882; FY49: 0.09882; FY50: 0.09882; FY51: 0.09882; FY52: 0.09882; FY53: 0.09882; FY54: 0.09882 | [8 empty] | 0.8115 | 2.13 | 2.7892 | 3.7633 | 4.878 | 6.0151 | 7.4472 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682
95% | FY38: 0.012288 | [8 empty] | 0.13591 | 2.0255 | 3.3237 | 5.2418 | 7.437 | 9.6763 | 12.4963 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316
90% | [39 empty] | 0.072287 | 0.82688 | 3.4046 | 8.4178 | 15.6885 | 25.8779 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509
85% | [43 empty] | 0.020502 | 2.5056 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061002 | 0.89506 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.76601 | 3.9929 | 9.2848 | 13.0026 | 19.9585 | 29.9823 | 42.3847 | 61.4961 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042702 | 0.62654 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.2298 | 1.1979 | 2.7854 | 3.9008 | 5.9875 | 8.9947 | 12.7154 | 18.4488 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY38: 1.1704; FY39: 6.4184; FY40: 6.4184; FY41: 6.4184; FY42: 6.4184; FY43: 6.4184; FY44: 6.4184; FY45: 6.4184; FY46: 6.4184; FY47: 6.4184; FY48: 6.4184; FY49: 6.4184; FY50: 6.4184; FY51: 6.4184; FY52: 6.4184; FY53: 6.4184; FY54: 6.4184 | [11 empty] | 0.083376 | 2.3875 | 1.5868 | 4.7641 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954
98% | FY38: 0.98808; FY39: 16.5562; FY40: 16.5562; FY41: 16.5562; FY42: 16.5562; FY43: 16.5562; FY44: 16.5562; FY45: 16.5562; FY46: 16.5562; FY47: 16.5562; FY48: 16.5562; FY49: 16.5562; FY50: 16.5562; FY51: 16.5562; FY52: 16.5562; FY53: 16.5562; FY54: 16.5562 | [12 empty] | 4.5852 | 2.2072 | 11.6433 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819
97% | FY39: 6.1588; FY40: 6.1588; FY41: 6.1588; FY42: 6.1588; FY43: 6.1588; FY44: 6.1588; FY45: 6.1588; FY46: 6.1588; FY47: 6.1588; FY48: 6.1588; FY49: 6.1588; FY50: 6.1588; FY51: 6.1588; FY52: 6.1588; FY53: 6.1588; FY54: 6.1588 | [12 empty] | 0.89235 | 0.075359 | 3.9975 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39
95% | FY39: 10.8987; FY40: 10.8987; FY41: 10.8987; FY42: 10.8987; FY43: 10.8987; FY44: 10.8987; FY45: 10.8987; FY46: 10.8987; FY47: 10.8987; FY48: 10.8987; FY49: 10.8987; FY50: 10.8987; FY51: 10.8987; FY52: 10.8987; FY53: 10.8987; FY54: 10.8987 | [12 empty] | 0.055727 |  | 5.5785 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468
90% | FY39: 22.0594; FY40: 22.0594; FY41: 22.0594; FY42: 22.0594; FY43: 22.0594; FY44: 22.0594; FY45: 22.0594; FY46: 22.0594; FY47: 22.0594; FY48: 22.0594; FY49: 22.0594; FY50: 22.0594; FY51: 22.0594; FY52: 22.0594; FY53: 22.0594; FY54: 22.0594 | [14 empty] | 2.5006 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1584 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083376 | 7.9208 | 3.8693 | 28.4841 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5109 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025013 | 2.3762 | 1.1608 | 8.5452 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0.72015 | 2.2741 | 3.6196 | 4.2924 | 5.2864 | 6.424 | 7.5845 | 9.0459 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715 | 9.2715
98% | [12 empty] | 0.061002 | 0.62346 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | 0.4488 | [7 empty] | 0.045855 | 0.7714 | 1.4374 | 1.7704 | 2.2624 | 2.8255 | 3.3999 | 4.1233 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349 | 4.2349
97% | FY38: 0.25931; FY39: 0.09882; FY40: 0.09882; FY41: 0.09882; FY42: 0.09882; FY43: 0.09882; FY44: 0.09882; FY45: 0.09882; FY46: 0.09882; FY47: 0.09882; FY48: 0.09882; FY49: 0.09882; FY50: 0.09882; FY51: 0.09882; FY52: 0.09882; FY53: 0.09882; FY54: 0.09882 | [8 empty] | 0.8115 | 2.13 | 2.7892 | 3.7633 | 4.878 | 6.0151 | 7.4472 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682 | 7.6682
95% | FY38: 0.012288 | [8 empty] | 0.13591 | 2.0255 | 3.3237 | 5.2418 | 7.437 | 9.6763 | 12.4963 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316 | 12.9316
90% | [39 empty] | 0.072287 | 0.82688 | 3.4046 | 8.4178 | 15.6885 | 25.8779 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509 | 27.4509
85% | [43 empty] | 0.020502 | 2.5056 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502 | 3.2502
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061002 | 0.89506 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | 0.54762 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.76601 | 3.9929 | 9.2848 | 13.0026 | 19.9585 | 29.9823 | 42.3847 | 61.4961 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074 | 64.8074
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.042702 | 0.62654 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | 0.38334 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0.2298 | 1.1979 | 2.7854 | 3.9008 | 5.9875 | 8.9947 | 12.7154 | 18.4488 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422 | 19.4422

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.3927 | 9.039 | 16.0723 | 21.9949 | 25.188 | 27.4949 | 30.1537 | 32.142 | 34.3353 | 35.4824 | 36.4761 | 38.9414 | 37.4481 | 41.4705 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 |  | 9.5576 | 12.2937 | 19.2723 | 25.4191 | 28.6233 | 31.2218 | 33.6917 | 35.7954 | 37.9878 | 38.9458 | 40.2559 | 42.6877 | 41.8869 | 45.0643 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955
98% | 17.695 | 25.554 | 46.442 | 64.0311 | 73.5141 | 80.3653 | 88.2616 | 94.1665 | 100.6804 | 104.0869 | 107.0383 | 114.3596 | 109.9247 | 121.8707 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 |  | 27.0942 | 35.2201 | 55.9456 | 74.2006 | 83.7166 | 91.4335 | 98.769 | 105.0167 | 111.5276 | 114.3727 | 118.2635 | 125.4856 | 123.1075 | 132.5437 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822
97% | 7.2053 | 10.6627 | 19.852 | 27.59 | 31.7619 | 34.776 | 38.2498 | 40.8476 | 43.7133 | 45.2119 | 46.5103 | 49.7312 | 47.7801 | 53.0356 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 |  | 11.3403 | 14.9151 | 24.033 | 32.0639 | 36.2503 | 39.6453 | 42.8724 | 45.6209 | 48.4853 | 49.7369 | 51.4486 | 54.6258 | 53.5797 | 57.7309 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235
95% | 15.5414 | 24.052 | 46.6718 | 65.7193 | 75.9885 | 83.4077 | 91.9587 | 98.3532 | 105.4072 | 109.0961 | 112.2922 | 120.2205 | 115.4179 | 128.3544 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 |  | 25.7199 | 34.5195 | 56.9634 | 76.7319 | 87.0369 | 95.3936 | 103.3373 | 110.103 | 117.1536 | 120.2347 | 124.448 | 132.2689 | 129.6937 | 139.9123 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017
90% | 103.6024 | 190.5261 | 421.5543 | 616.0961 | 720.9809 | 796.7577 | 884.0936 | 949.4042 | 1021.4505 | 1059.1276 | 1091.7704 | 1172.7471 | 1123.6953 | 1255.8225 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 |  | 207.561 | 297.436 | 526.6677 | 728.5745 | 833.8249 | 919.1765 | 1000.3096 | 1069.4112 | 1141.4233 | 1172.892 | 1215.9248 | 1295.8038 | 1269.5018 | 1373.8693 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214
85% | 51.2159 | 245.2952 | 789.5839 | 1247.9131 | 1495.0154 | 1673.5411 | 1879.2993 | 2033.1672 | 2202.9039 | 2291.6691 | 2368.5734 | 2559.3499 | 2443.7868 | 2755.0705 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 |  | 285.4285 | 497.1685 | 1037.2249 | 1512.9055 | 1760.8691 | 1961.9526 | 2153.0972 | 2315.8967 | 2485.5528 | 2559.6911 | 2661.074 | 2849.2642 | 2787.2981 | 3033.1819 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967
80% |  | 71.542 | 1016.4181 | 1846.3213 | 2293.7529 | 2617.0119 | 2989.5813 | 3268.1921 | 3575.5368 | 3736.2652 | 3875.5169 | 4220.9587 | 4011.7069 | 4575.3528 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 |  | 119.4005 | 486.9374 | 1464.8252 | 2326.1467 | 2775.1381 | 3139.2428 | 3485.351 | 3780.1344 | 4087.3333 | 4221.5765 | 4405.1519 | 4745.9106 | 4633.7077 | 5078.933 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538
75% |  |  | 642.7938 | 1613.0728 | 2136.1861 | 2514.1234 | 2949.7118 | 3275.4488 | 3634.7801 | 3822.6951 | 3985.5009 | 4389.3731 | 4144.727 | 4803.7119 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 |  |  | 85.1457 | 1167.0476 | 2174.0593 | 2698.9962 | 3124.6882 | 3529.3396 | 3873.9847 | 4233.1453 | 4390.0955 | 4604.7221 | 5003.1191 | 4871.9374 | 5392.4713 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803
70% |  |  | 110.8231 | 1163.633 | 1777.0831 | 2220.2866 | 2731.097 | 3113.0857 | 3534.4701 | 3754.8363 | 3945.7571 | 4419.3742 | 4132.48 | 4905.2654 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 |  |  |  | 640.5835 | 1821.4966 | 2437.0851 | 2936.2901 | 3410.821 | 3814.983 | 4236.1674 | 4420.2213 | 4671.912 | 5139.1083 | 4985.2728 | 5595.698 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157
65% |  |  |  | 369.7364 | 1031.4166 | 1517.0876 | 2076.8435 | 2495.4341 | 2957.1953 | 3198.6768 | 3407.8915 | 3926.8903 | 3612.5062 | 4459.3394 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 |  |  |  | 37.6543 | 1080.0858 | 1754.6596 | 2301.6981 | 2821.6983 | 3264.5868 | 3726.1288 | 3927.8186 | 4203.6261 | 4715.5889 | 4547.013 | 5215.9288 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574
60% |  |  |  |  | 139.2776 | 503.2799 | 1103.6475 | 1559.0898 | 2061.5032 | 2324.2442 | 2551.8777 | 3116.5679 | 2774.5061 | 3695.8924 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 |  |  |  |  | 165.9716 | 753.0993 | 1348.2977 | 1914.0774 | 2395.9568 | 2898.1318 | 3117.5779 | 3417.6668 | 3974.7016 | 3791.2846 | 4519.0901 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597
55% | [6 empty] | 77.2006 | 301.9799 | 707.4432 | 969.4921 | 1197.6749 | 1763.7277 | 1420.8405 | 2344.4503 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | [5 empty] | 4.0564 | 180.3574 | 572.1301 | 1041.3777 | 1544.7645 | 1764.7402 | 2065.5533 | 2623.9322 | 2440.0727 | 3169.6345 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163
50% | [9 empty] | 14.5909 | 67.2768 | 355.0439 | 154.6496 | 866.4004 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | [8 empty] | 27.1064 | 217.9999 | 355.7507 | 594.7409 | 1183.3194 | 970.2492 | 1826.1955 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531
45% | FY39: 376.3722; FY40: 376.3722; FY41: 376.3722; FY42: 376.3722; FY43: 376.3722; FY44: 376.3722; FY45: 376.3722; FY46: 376.3722; FY47: 376.3722; FY48: 376.3722; FY49: 376.3722; FY50: 376.3722; FY51: 376.3722; FY52: 376.3722; FY53: 376.3722; FY54: 376.3722 | [12 empty] | 2.1201 |  | 147.2604 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 201.6526 | 576.6711 | 3110.2114 | 7036.1081 | 9800.165 | 12068.132 | 14940.0983 | 17261.3111 | 19979.4193 | 21465.4746 | 22794.1564 | 26247.2855 | 24129.4693 | 30006.0367 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | E @ R (MWh) | 686.1021 | 1463.636 | 5030.2175 | 10017.6555 | 13253.356 | 16169.3978 | 19165.4946 | 21879.9737 | 24885.8013 | 26253.6541 | 28174.7879 | 31887.9362 | 30644.6052 | 35727.5141 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631
Option 1 Winter POE50 W E @ R (MWh) N 1 | 141.1569 | 403.6698 | 2177.148 | 4925.2757 | 6860.1155 | 8447.6924 | 10458.0688 | 12082.9178 | 13985.5935 | 15025.8322 | 15955.9095 | 18373.0998 | 16890.6285 | 21004.2257 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 205.8306 | 439.0908 | 1509.0653 | 3005.2966 | 3976.0068 | 4850.8193 | 5749.6484 | 6563.9921 | 7465.7404 | 7876.0962 | 8452.4364 | 9566.3809 | 9193.3815 | 10718.2542 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.8537 | 20.9364 | 26.7753 | 30.9278 | 33.4161 | 35.4082 | 37.0239 | 38.5779 | 39.9234 | 40.5962 | 41.5902 | 42.7278 | 43.8882 | 45.3496 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752
98% | 6.2456 | 7.0779 | 9.9599 | 12.0388 | 13.1314 | 14.1103 | 14.7311 | 15.44 | 16.0064 | 16.3747 | 17.2547 | 17.8629 | 18.1819 | 18.7753 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 |  | 9.1603 | 10.1912 | 13.0813 | 15.1367 | 16.3683 | 17.3544 | 18.1541 | 18.9233 | 19.5893 | 19.9223 | 20.4143 | 20.9774 | 21.5518 | 22.2751 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868
97% | 6.0086 | 6.8325 | 9.6853 | 11.743 | 12.8246 | 13.7935 | 14.408 | 15.1097 | 15.6704 | 16.0349 | 16.906 | 17.508 | 17.8237 | 18.4112 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 |  | 17.7875 | 19.8284 | 25.5499 | 29.6189 | 32.0573 | 34.0093 | 35.5926 | 37.1153 | 38.4337 | 39.093 | 40.067 | 41.1818 | 42.3189 | 43.7509 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972
95% | 16.9597 | 19.3932 | 27.82 | 33.8982 | 37.093 | 39.9551 | 41.77 | 43.8427 | 45.4989 | 46.5757 | 49.1487 | 50.927 | 51.8597 | 53.5949 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 |  | 33.9759 | 37.9948 | 49.2618 | 57.2747 | 62.0762 | 65.9203 | 69.0381 | 72.0367 | 74.633 | 75.9313 | 77.8494 | 80.0445 | 82.2838 | 85.1038 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391
90% | 33.7676 | 39.2387 | 58.1843 | 71.8499 | 79.0325 | 85.4672 | 89.5478 | 94.2077 | 97.9313 | 100.3521 | 106.137 | 110.1351 | 112.2319 | 116.1333 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 |  | 113.4167 | 127.9383 | 168.649 | 197.6017 | 214.9512 | 228.8409 | 240.1063 | 250.9409 | 260.3224 | 265.0133 | 271.9439 | 279.8757 | 287.9668 | 298.1562 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292
85% | 43.6709 | 52.543 | 83.2656 | 105.426 | 117.0734 | 127.5082 | 134.1252 | 141.6819 | 147.7201 | 151.6458 | 161.0267 | 167.5101 | 170.9103 | 177.2369 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 |  | 118.3407 | 135.7404 | 184.5199 | 219.211 | 239.9991 | 256.6418 | 270.14 | 283.122 | 294.3629 | 299.9835 | 308.2877 | 317.7916 | 327.4862 | 339.6952 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58
80% | 120.2726 | 154.4301 | 272.7122 | 358.0296 | 402.8721 | 443.0459 | 468.5217 | 497.6149 | 520.8618 | 535.9757 | 572.0924 | 597.0532 | 610.1442 | 634.5015 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 |  | 112.6035 | 132.4627 | 188.1373 | 227.7321 | 251.4587 | 270.4538 | 285.86 | 300.6771 | 313.5069 | 319.922 | 329.4 | 340.2474 | 351.3124 | 365.2472 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984
75% | 100.3174 | 152.0501 | 331.1923 | 460.4083 | 528.3238 | 589.1684 | 627.7522 | 671.815 | 707.0232 | 729.9136 | 784.6135 | 822.4175 | 842.2443 | 879.1343 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 |  | 74.8261 | 91.8595 | 139.612 | 173.5728 | 193.9233 | 210.2155 | 223.4295 | 236.1383 | 247.1425 | 252.6448 | 260.7741 | 270.078 | 279.5685 | 291.5205 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656
70% | 24.9895 | 90.0079 | 363.6588 | 561.0443 | 664.7895 | 757.7333 | 816.6725 | 883.9811 | 937.7638 | 972.7304 | 1056.288 | 1114.0359 | 1144.3225 | 1200.6742 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 |  | 53.5318 | 71.7426 | 122.796 | 159.1043 | 180.8615 | 198.2799 | 212.4074 | 225.9946 | 237.7595 | 243.6421 | 252.3334 | 262.2803 | 272.4269 | 285.205 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777
65% |  | 0.73201 | 365.7907 | 726.2132 | 915.65 | 1085.3638 | 1192.9858 | 1315.8901 | 1414.0963 | 1477.9446 | 1630.5193 | 1735.9661 | 1791.2689 | 1894.1661 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 |  | 61.0527 | 109.0916 | 243.7669 | 339.5457 | 396.9397 | 442.8884 | 480.1556 | 515.9976 | 547.0326 | 562.5505 | 585.4776 | 611.717 | 638.4831 | 672.1908 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946
60% |  |  | 111.4336 | 738.9582 | 1107.0997 | 1436.9124 | 1646.0591 | 1884.9047 | 2075.7535 | 2199.8329 | 2496.3384 | 2701.258 | 2808.7305 | 3008.6955 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 |  | 1.6489 | 24.6112 | 168.3555 | 275.2981 | 339.3818 | 390.6862 | 432.2971 | 472.3169 | 506.9692 | 524.2958 | 549.8953 | 579.193 | 609.0789 | 646.7156 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259
55% |  |  |  | 96.2323 | 378.628 | 750.7007 | 993.1218 | 1269.9669 | 1491.179 | 1634.9989 | 1978.6772 | 2216.1987 | 2340.7696 | 2572.5483 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 |  |  |  | 78.4343 | 249.5839 | 353.8371 | 437.3006 | 504.9945 | 570.0998 | 626.4733 | 654.6607 | 696.3066 | 743.9691 | 792.5883 | 853.8167 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691
50% | [5 empty] | 29.6615 | 122.1993 | 300.2563 | 494.8265 | 645.0196 | 1046.5764 | 1326.0081 | 1472.5592 | 1745.2346 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 |  |  |  |  | 69.0686 | 206.397 | 351.033 | 469.1066 | 582.665 | 680.9932 | 730.1585 | 802.7984 | 885.9327 | 970.7356 | 1077.532 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191
45% | [10 empty] | 56.9726 | 202.4712 | 312.8424 | 577.9293 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | [6 empty] | 26.9353 | 108.8071 | 235.9916 | 382.1514 | 467.1756 | 606.501 | 772.1407 | 941.1051 | 1153.8901 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396
40% | [41 empty] | 0.54558 | 26.9538 | 93.4527 | 231.3516 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 352.2319 | 522.3053 | 1633.7029 | 3175.8418 | 4256.518 | 5373.4204 | 6161.8944 | 7134.711 | 7964.3311 | 8527.3987 | 9972.5509 | 11079.3518 | 11693.8891 | 12897.0355 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | E @ R (MWh) | 615.1978 | 782.3971 | 1408.9389 | 2043.6763 | 2521.6672 | 2965.9678 | 3387.1128 | 3840.5968 | 4269.2935 | 4495.5896 | 4844.1844 | 5275.1107 | 5754.2472 | 6411.8004 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5
Option 1 Summer POE50 W E @ R (MWh) N 1 | 246.5624 | 365.6137 | 1143.592 | 2223.0893 | 2979.5626 | 3761.3943 | 4313.3261 | 4994.2977 | 5575.0318 | 5969.1791 | 6980.7857 | 7755.5463 | 8185.7224 | 9027.9249 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 184.5593 | 234.7191 | 422.6817 | 613.1029 | 756.5002 | 889.7903 | 1016.1338 | 1152.179 | 1280.788 | 1348.6769 | 1453.2553 | 1582.5332 | 1726.2742 | 1923.5401 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.3927 | 9.039 | 16.0723 | 21.9949 | 25.188 | 14.6314 | 17.2902 | 19.2785 | 21.4718 | 22.6189 | 23.6126 | 26.0779 | 24.5846 | 28.607 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 | 33.855 |  | 9.5576 | 12.2937 | 19.2723 | 25.4191 | 28.6233 | 18.3583 | 20.8282 | 22.9319 | 25.1243 | 26.0823 | 27.3924 | 29.8242 | 29.0234 | 32.2008 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032 | 34.032
98% | 17.695 | 25.554 | 46.442 | 64.0311 | 73.5141 | 42.1626 | 50.0589 | 55.9639 | 62.4778 | 65.8843 | 68.8356 | 76.157 | 71.7221 | 83.6681 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 | 99.2539 |  | 27.0942 | 35.2201 | 55.9456 | 74.2006 | 83.7166 | 53.2309 | 60.5664 | 66.8141 | 73.3249 | 76.1701 | 80.0608 | 87.2829 | 84.9049 | 94.3411 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796 | 99.7796
97% | 7.2053 | 10.6627 | 19.852 | 27.59 | 31.7619 | 17.9694 | 21.4432 | 24.041 | 26.9067 | 28.4053 | 29.7037 | 32.9246 | 30.9735 | 36.229 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 | 43.0857 |  | 11.3403 | 14.9151 | 24.033 | 32.0639 | 36.2503 | 22.8387 | 26.0658 | 28.8144 | 31.6787 | 32.9304 | 34.642 | 37.8193 | 36.7731 | 40.9244 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317 | 43.317
95% | 15.5414 | 24.052 | 46.6718 | 65.7193 | 75.9885 | 42.0377 | 50.5887 | 56.9832 | 64.0372 | 67.7261 | 70.9221 | 78.8505 | 74.0479 | 86.9843 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 | 103.8624 |  | 25.7199 | 34.5195 | 56.9634 | 76.7319 | 87.0369 | 54.0236 | 61.9673 | 68.733 | 75.7836 | 78.8647 | 83.078 | 90.8989 | 88.3237 | 98.5422 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317 | 104.4317
90% | 103.6024 | 190.5261 | 421.5543 | 616.0961 | 720.9809 | 374.2231 | 461.559 | 526.8696 | 598.9159 | 636.593 | 669.2358 | 750.2125 | 701.1608 | 833.2879 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 | 1005.6727 |  | 207.561 | 297.436 | 526.6677 | 728.5745 | 833.8249 | 496.642 | 577.775 | 646.8766 | 718.8887 | 750.3574 | 793.3902 | 873.2692 | 846.9672 | 951.3347 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868 | 1011.4868
85% | 51.2159 | 245.2952 | 789.5839 | 1247.9131 | 1495.0154 | 678.0745 | 883.8328 | 1037.7007 | 1207.4374 | 1296.2026 | 1373.1069 | 1563.8834 | 1448.3203 | 1759.604 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 | 2165.7324 |  | 285.4285 | 497.1685 | 1037.2249 | 1512.9055 | 1760.8691 | 966.4861 | 1157.6307 | 1320.4301 | 1490.0863 | 1564.2246 | 1665.6075 | 1853.7977 | 1791.8316 | 2037.7154 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302 | 2179.4302
80% |  | 71.542 | 1016.4181 | 1846.3213 | 2293.7529 | 814.5065 | 1187.0759 | 1465.6867 | 1773.0314 | 1933.7597 | 2073.0115 | 2418.4532 | 2209.2015 | 2772.8473 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 | 3508.2298 |  | 119.4005 | 486.9374 | 1464.8252 | 2326.1467 | 2775.1381 | 1336.7374 | 1682.8456 | 1977.629 | 2284.8278 | 2419.0711 | 2602.6465 | 2943.4051 | 2831.2023 | 3276.4276 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326 | 3533.0326
75% |  |  | 642.7938 | 1613.0728 | 2136.1861 | 406.7294 | 842.3178 | 1168.0548 | 1527.3861 | 1715.3011 | 1878.1069 | 2281.9791 | 2037.333 | 2696.318 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 | 3556.0882 |  |  | 85.1457 | 1167.0476 | 2174.0593 | 2698.9962 | 1017.2942 | 1421.9456 | 1766.5907 | 2125.7514 | 2282.7015 | 2497.3282 | 2895.7251 | 2764.5435 | 3285.0774 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863 | 3585.0863
70% |  |  | 110.8231 | 1163.633 | 1777.0831 | 11.0054 | 271.7861 | 641.7647 | 1063.149 | 1283.5152 | 1474.4361 | 1948.0532 | 1661.159 | 2433.9444 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 | 3442.1889 |  |  |  | 640.5835 | 1821.4966 | 2437.0851 | 464.9691 | 939.5 | 1343.662 | 1764.8464 | 1948.9003 | 2200.5909 | 2667.7873 | 2513.9518 | 3124.377 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947 | 3476.1947
65% |  |  |  | 369.7364 | 1031.4166 |  |  | 38.0259 | 280.7668 | 490.742 | 699.7702 | 1218.7689 | 904.3848 | 1751.218 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 | 2856.0718 |  |  |  | 37.6543 | 1080.0858 | 1754.6596 | 2.5999 | 187.3147 | 556.4654 | 1018.0074 | 1219.6973 | 1495.5047 | 2007.4675 | 1838.8916 | 2507.8074 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336 | 2893.336
60% |  |  |  |  | 139.2776 | [5 empty] | 18.7831 | 254.2333 | 80.3129 | 749.3547 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 | 1951.4771 |  |  |  |  | 165.9716 | 753.0993 |  |  | 1.1077 | 132.3191 | 254.8841 | 482.6263 | 1028.1638 | 844.7469 | 1572.5523 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022 | 1992.022
55% | FY38: 3.7672; FY39: 605.2012; FY40: 605.2012; FY41: 605.2012; FY42: 605.2012; FY43: 605.2012; FY44: 605.2012; FY45: 605.2012; FY46: 605.2012; FY47: 605.2012; FY48: 605.2012; FY49: 605.2012; FY50: 605.2012; FY51: 605.2012; FY52: 605.2012; FY53: 605.2012; FY54: 605.2012 | [5 empty] | 4.0564 | [6 empty] | 53.8774 | 14.4284 | 310.7491 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217 | 642.0217
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 201.6526 | 576.6711 | 3110.2114 | 7036.1081 | 9800.165 | 2401.3401 | 3785.9526 | 5034.3689 | 6625.5802 | 7540.7484 | 8379.5245 | 10649.5937 | 9243.2003 | 13235.8299 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | 19370.719 | E @ R (MWh) | 686.1021 | 1463.636 | 5030.2175 | 10017.6555 | 13253.356 | 4433.1802 | 6136.4393 | 7800.0549 | 9740.6386 | 10653.8838 | 11962.8675 | 14569.3184 | 13685.5882 | 17332.0494 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706 | 19594.1706
Option 2 Winter POE50 W E @ R (MWh) N 1 | 141.1569 | 403.6698 | 2177.148 | 4925.2757 | 6860.1155 | 1680.9381 | 2650.1668 | 3524.0582 | 4637.9061 | 5278.5238 | 5865.6672 | 7454.7156 | 6470.2402 | 9265.0809 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | 13559.5033 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 205.8306 | 439.0908 | 1509.0653 | 3005.2966 | 3976.0068 | 1329.9541 | 1840.9318 | 2340.0165 | 2922.1916 | 3196.1651 | 3588.8603 | 4370.7955 | 4105.6765 | 5199.6148 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512 | 5878.2512
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.8537 | 20.9364 | 26.7753 | 30.9278 | 33.4161 | 24.4963 | 26.112 | 27.6659 | 29.0115 | 29.6842 | 30.6782 | 31.8159 | 32.9763 | 34.4377 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633 | 34.6633
98% | 6.2456 | 7.0779 | 9.9599 | 12.0388 | 13.1314 | 8.7092 | 9.3299 | 10.0388 | 10.6053 | 10.9735 | 11.8535 | 12.4617 | 12.7807 | 13.3742 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 | 13.1996 |  | 9.1603 | 10.1912 | 13.0813 | 15.1367 | 16.3683 | 11.9532 | 12.753 | 13.5222 | 14.1882 | 14.5212 | 15.0132 | 15.5763 | 16.1507 | 16.874 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857 | 16.9857
97% | 6.0086 | 6.8325 | 9.6853 | 11.743 | 12.8246 | 8.4472 | 9.0617 | 9.7634 | 10.3241 | 10.6886 | 11.5597 | 12.1617 | 12.4774 | 13.0649 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 | 12.892 |  | 17.7875 | 19.8284 | 25.5499 | 29.6189 | 32.0573 | 23.3167 | 24.9 | 26.4227 | 27.7412 | 28.4004 | 29.3744 | 30.4892 | 31.6263 | 33.0583 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794 | 33.2794
95% | 16.9597 | 19.3932 | 27.82 | 33.8982 | 37.093 | 24.1629 | 25.9779 | 28.0506 | 29.7068 | 30.7835 | 33.3566 | 35.1349 | 36.0675 | 37.8028 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 | 37.2921 |  | 33.9759 | 37.9948 | 49.2618 | 57.2747 | 62.0762 | 44.8641 | 47.9819 | 50.9805 | 53.5769 | 54.8751 | 56.7932 | 58.9884 | 61.2276 | 64.0476 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483 | 64.483
90% | 33.7676 | 39.2387 | 58.1843 | 71.8499 | 79.0325 | 49.9623 | 54.0429 | 58.7028 | 62.4264 | 64.8472 | 70.6321 | 74.6302 | 76.727 | 80.6284 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 | 79.4803 |  | 113.4167 | 127.9383 | 168.649 | 197.6017 | 214.9512 | 152.759 | 164.0244 | 174.859 | 184.2405 | 188.9314 | 195.8619 | 203.7938 | 211.8848 | 222.0743 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473 | 223.6473
85% | 43.6709 | 52.543 | 83.2656 | 105.426 | 117.0734 | 69.9326 | 76.5497 | 84.1064 | 90.1446 | 94.0702 | 103.4512 | 109.9345 | 113.3348 | 119.6614 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 | 117.7996 |  | 118.3407 | 135.7404 | 184.5199 | 219.211 | 239.9991 | 165.4806 | 178.9787 | 191.9607 | 203.2016 | 208.8222 | 217.1264 | 226.6303 | 236.325 | 248.534 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188 | 250.4188
80% | 120.2726 | 154.4301 | 272.7122 | 358.0296 | 402.8721 | 221.3802 | 246.8559 | 275.9492 | 299.1961 | 314.31 | 350.4267 | 375.3875 | 388.4785 | 412.8358 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 | 405.6679 |  | 112.6035 | 132.4627 | 188.1373 | 227.7321 | 251.4587 | 166.4067 | 181.8129 | 196.6299 | 209.4598 | 215.8748 | 225.3529 | 236.2002 | 247.2652 | 261.2 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512 | 263.3512
75% | 100.3174 | 152.0501 | 331.1923 | 460.4083 | 528.3238 | 253.4483 | 292.0321 | 336.0949 | 371.3031 | 394.1935 | 448.8935 | 486.6975 | 506.5242 | 543.4142 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 | 532.5581 |  | 74.8261 | 91.8595 | 139.612 | 173.5728 | 193.9233 | 120.9735 | 134.1875 | 146.8962 | 157.9004 | 163.4027 | 171.5321 | 180.8359 | 190.3265 | 202.2784 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236 | 204.1236
70% | 24.9895 | 90.0079 | 363.6588 | 561.0443 | 664.7895 | 244.9 | 303.8392 | 371.1478 | 424.9305 | 459.897 | 543.4546 | 601.2026 | 631.4892 | 687.8409 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 | 671.2575 |  | 53.5318 | 71.7426 | 122.796 | 159.1043 | 180.8615 | 102.8691 | 116.9965 | 130.5837 | 142.3486 | 148.2312 | 156.9225 | 166.8695 | 177.0161 | 189.7942 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669 | 191.7669
65% |  | 0.73201 | 365.7907 | 726.2132 | 915.65 | 149.3624 | 256.5612 | 379.4655 | 477.6718 | 541.5201 | 694.0948 | 799.5415 | 854.8443 | 957.7416 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 | 927.4605 |  | 61.0527 | 109.0916 | 243.7669 | 339.5457 | 396.9397 | 191.2012 | 228.4683 | 264.3104 | 295.3454 | 310.8633 | 333.7904 | 360.0298 | 386.7958 | 420.5036 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074 | 425.7074
60% |  |  | 111.4336 | 738.9582 | 1107.0997 |  | 23.3484 | 126.8668 | 265.1768 | 380.0354 | 676.5409 | 881.4606 | 988.933 | 1188.898 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 | 1130.0515 |  | 1.6489 | 24.6112 | 168.3555 | 275.2981 | 339.3818 | 109.6628 | 151.2738 | 191.2935 | 225.9459 | 243.2725 | 268.8719 | 298.1697 | 328.0556 | 365.6922 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025 | 371.5025
55% |  |  |  | 96.2323 | 378.628 |  |  |  |  | 0.0026328 | 66.2359 | 184.5878 | 268.9384 | 464.6425 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 | 401.9417 |  |  |  | 78.4343 | 249.5839 | 353.8371 | 17.7098 | 56.5728 | 112.9228 | 169.2963 | 197.4837 | 239.1296 | 286.7921 | 335.4113 | 396.6397 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921 | 406.0921
50% | [34 empty] | 69.0686 | 206.397 |  |  | 0.00027076 | 12.1758 | 27.0232 | 59.1511 | 110.2034 | 177.2175 | 280.1111 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982 | 296.5982
45% | [44 empty] | 3.9337 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682 | 7.4682
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 352.2319 | 522.3053 | 1633.7029 | 3175.8418 | 4256.518 | 1030.3052 | 1297.599 | 1680.1862 | 2041.4853 | 2301.3217 | 3010.4995 | 3573.2005 | 3890.5951 | 4519.9047 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | 4329.6007 | E @ R (MWh) | 615.1978 | 782.3971 | 1408.9389 | 2043.6763 | 2521.6672 | 1131.693 | 1324.0619 | 1528.0478 | 1724.432 | 1831.386 | 1999.5979 | 2206.3942 | 2432.2787 | 2739.179 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876 | 2790.0876
Option 2 Summer POE50 W E @ R (MWh) N 1 | 246.5624 | 365.6137 | 1143.592 | 2223.0893 | 2979.5626 | 721.2137 | 908.3193 | 1176.1304 | 1429.0397 | 1610.9252 | 2107.3496 | 2501.2404 | 2723.4166 | 3163.9333 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | 3030.7205 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 184.5593 | 234.7191 | 422.6817 | 613.1029 | 756.5002 | 339.5079 | 397.2186 | 458.4143 | 517.3296 | 549.4158 | 599.8794 | 661.9183 | 729.6836 | 821.7537 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263 | 837.0263
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.3927 | 9.039 | 16.0723 | 9.1314 | 12.3245 | 1.7679 | 4.4267 | 6.415 | 8.6084 | 9.7554 | 10.7491 | 13.2144 | 11.7211 | 15.7435 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 |  | 9.5576 | 12.2937 | 19.2723 | 12.5556 | 15.7598 | 5.4948 | 7.9647 | 10.0685 | 12.2608 | 13.2188 | 14.5289 | 16.9607 | 16.1599 | 19.3373 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685
98% | 17.695 | 25.554 | 46.442 | 25.8285 | 35.3114 | 3.96 | 11.8563 | 17.7612 | 24.2752 | 27.6817 | 30.633 | 37.9543 | 33.5194 | 45.4654 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 |  | 27.0942 | 35.2201 | 55.9456 | 35.998 | 45.514 | 15.0283 | 22.3637 | 28.6114 | 35.1223 | 37.9674 | 41.8582 | 49.0803 | 46.7022 | 56.1384 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577
97% | 7.2053 | 10.6627 | 19.852 | 10.7835 | 14.9553 | 1.1628 | 4.6367 | 7.2344 | 10.1001 | 11.5987 | 12.8971 | 16.118 | 14.167 | 19.4224 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 |  | 11.3403 | 14.9151 | 24.033 | 15.2574 | 19.4438 | 6.0321 | 9.2592 | 12.0078 | 14.8721 | 16.1238 | 17.8355 | 21.0127 | 19.9665 | 24.1178 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104
95% | 15.5414 | 24.052 | 46.6718 | 24.3492 | 34.6184 | 0.78169 | 9.2186 | 15.6131 | 22.6671 | 26.3561 | 29.5521 | 37.4805 | 32.6778 | 45.6143 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 |  | 25.7199 | 34.5195 | 56.9634 | 35.3619 | 45.6669 | 12.6536 | 20.5972 | 27.3629 | 34.4136 | 37.4946 | 41.708 | 49.5288 | 46.9536 | 57.1722 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616
90% | 103.6024 | 190.5261 | 421.5543 | 193.5616 | 298.4463 |  | 39.0745 | 104.335 | 176.3813 | 214.0584 | 246.7012 | 327.6779 | 278.6262 | 410.7533 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 |  | 207.561 | 297.436 | 526.6677 | 306.0399 | 411.2903 | 74.1074 | 155.2404 | 224.3421 | 296.3541 | 327.8228 | 370.8556 | 450.7346 | 424.4326 | 528.8001 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522
85% | 51.2159 | 245.2952 | 789.5839 | 252.4466 | 499.5489 |  |  | 52.4177 | 211.9709 | 300.7361 | 377.6404 | 568.4169 | 452.8538 | 764.1375 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 |  | 285.4285 | 497.1685 | 1037.2249 | 517.439 | 765.4026 | 14.1699 | 162.1642 | 324.9636 | 494.6198 | 568.7581 | 670.141 | 858.3312 | 796.3651 | 1042.2489 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637
80% |  | 71.542 | 1016.4181 | 79.2092 | 491.2475 |  |  |  | 40.8273 | 140.7149 | 270.5061 | 615.9478 | 406.6961 | 970.3419 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 |  | 119.4005 | 486.9374 | 1464.8252 | 523.6413 | 972.6327 |  | 10.6635 | 177.8363 | 482.3224 | 616.5657 | 800.1411 | 1140.8997 | 1028.6969 | 1473.9222 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272
75% |  |  | 642.7938 |  | 87.9329 | [5 empty] | 2.5466 | 187.0365 | 41.2569 | 588.924 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 |  |  | 85.1457 | 1167.0476 | 110.2616 | 591.6022 |  |  |  | 82.2094 | 187.615 | 389.9342 | 788.3311 | 657.1495 | 1177.6834 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924
70% |  |  | 110.8231 | [10 empty] | 79.1662 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 |  |  |  | 640.5835 |  | 80.6184 | [5 empty] | 7.8268 | 221.5785 | 120.1223 | 653.056 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737
65% | FY39: 209.3217; FY40: 209.3217; FY41: 209.3217; FY42: 209.3217; FY43: 209.3217; FY44: 209.3217; FY45: 209.3217; FY46: 209.3217; FY47: 209.3217; FY48: 209.3217; FY49: 209.3217; FY50: 209.3217; FY51: 209.3217; FY52: 209.3217; FY53: 209.3217; FY54: 209.3217 |  |  |  | 37.6543 | [10 empty] | 41.668 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 201.6526 | 576.6711 | 3110.2114 | 595.3099 | 1474.3852 | 7.6724 | 69.2128 | 203.7766 | 494.8302 | 730.9013 | 981.2256 | 1803.8464 | 1271.5182 | 2939.5686 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | E @ R (MWh) | 686.1021 | 1463.636 | 5030.2175 | 1556.5547 | 2947.9307 | 127.486 | 388.253 | 805.1926 | 1452.1745 | 1805.5662 | 2354.8292 | 3596.4576 | 3156.5487 | 5074.1444 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181
Option 3 Winter POE50 W E @ R (MWh) N 1 | 141.1569 | 403.6698 | 2177.148 | 416.7169 | 1032.0696 | 5.3707 | 48.449 | 142.6436 | 346.3812 | 511.6309 | 686.8579 | 1262.6925 | 890.0627 | 2057.698 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 205.8306 | 439.0908 | 1509.0653 | 466.9664 | 884.3792 | 38.2458 | 116.4759 | 241.5578 | 435.6524 | 541.6699 | 706.4487 | 1078.9373 | 946.9646 | 1522.2433 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.8537 | 20.9364 | 26.7753 | 20.0158 | 22.5042 | 13.5843 | 15.2001 | 16.754 | 18.0995 | 18.7723 | 19.7663 | 20.9039 | 22.0644 | 23.5258 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514
98% | 6.2456 | 7.0779 | 9.9599 | 6.6377 | 7.7303 | 3.3081 | 3.9288 | 4.6377 | 5.2041 | 5.5724 | 6.4524 | 7.0606 | 7.3796 | 7.9731 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 |  | 9.1603 | 10.1912 | 13.0813 | 9.7355 | 10.9672 | 6.5521 | 7.3519 | 8.121 | 8.787 | 9.12 | 9.612 | 10.1751 | 10.7495 | 11.4729 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845
97% | 6.0086 | 6.8325 | 9.6853 | 6.3967 | 7.4783 | 3.1009 | 3.7154 | 4.4171 | 4.9778 | 5.3423 | 6.2134 | 6.8154 | 7.1311 | 7.7186 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 |  | 17.7875 | 19.8284 | 25.5499 | 18.9264 | 21.3647 | 12.6241 | 14.2074 | 15.7301 | 17.0486 | 17.7078 | 18.6818 | 19.7966 | 20.9337 | 22.3657 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868
95% | 16.9597 | 19.3932 | 27.82 | 18.1061 | 21.3008 | 8.3708 | 10.1857 | 12.2584 | 13.9146 | 14.9914 | 17.5644 | 19.3427 | 20.2754 | 22.0107 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 |  | 33.9759 | 37.9948 | 49.2618 | 36.2185 | 41.0201 | 23.8079 | 26.9257 | 29.9243 | 32.5207 | 33.8189 | 35.737 | 37.9322 | 40.1714 | 42.9914 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268
90% | 33.7676 | 39.2387 | 58.1843 | 36.345 | 43.5276 | 14.4574 | 18.538 | 23.1979 | 26.9215 | 29.3423 | 35.1272 | 39.1253 | 41.2221 | 45.1235 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 |  | 113.4167 | 127.9383 | 168.649 | 121.5198 | 138.8693 | 76.6771 | 87.9425 | 98.7771 | 108.1586 | 112.8494 | 119.78 | 127.7118 | 135.8029 | 145.9923 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654
85% | 43.6709 | 52.543 | 83.2656 | 47.8505 | 59.4979 | 12.3571 | 18.9742 | 26.5309 | 32.5691 | 36.4947 | 45.8757 | 52.359 | 55.7593 | 62.0859 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 |  | 118.3407 | 135.7404 | 184.5199 | 128.0498 | 148.8379 | 74.3193 | 87.8175 | 100.7995 | 112.0404 | 117.661 | 125.9652 | 135.4691 | 145.1638 | 157.3728 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576
80% | 120.2726 | 154.4301 | 272.7122 | 136.3639 | 181.2064 | 6.201 | 25.1989 | 54.2835 | 77.5304 | 92.6442 | 128.761 | 153.7218 | 166.8128 | 191.1701 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 |  | 112.6035 | 132.4627 | 188.1373 | 123.6849 | 147.4115 | 62.3595 | 77.7657 | 92.5828 | 105.4126 | 111.8277 | 121.3057 | 132.153 | 143.2181 | 157.1528 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304
75% | 100.3174 | 152.0501 | 331.1923 | 124.6883 | 192.6038 |  |  | 11.0812 | 36.0486 | 58.4734 | 113.1734 | 150.9774 | 170.8041 | 207.6941 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 |  | 74.8261 | 91.8595 | 139.612 | 84.3307 | 104.6812 | 31.7314 | 44.9455 | 57.6542 | 68.6584 | 74.1607 | 82.29 | 91.5939 | 101.0844 | 113.0364 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815
70% | 24.9895 | 90.0079 | 363.6588 | 51.0085 | 151.9562 |  |  |  |  | 1.5245 | 37.6241 | 88.3693 | 118.6559 | 175.0076 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 |  | 53.5318 | 71.7426 | 122.796 | 63.6934 | 85.4506 | 8.2954 | 21.5857 | 35.1729 | 46.9378 | 52.8204 | 61.5117 | 71.4586 | 81.6052 | 94.3833 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356
65% |  | 0.73201 | 365.7907 |  | 30.1393 | [6 empty] | 0.53481 | 9.0843 | 51.6037 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 |  | 61.0527 | 109.0916 | 243.7669 | 87.8585 | 145.2524 |  | 2.1325 | 18.1062 | 43.6639 | 59.1761 | 82.1031 | 108.3425 | 135.1086 | 168.8164 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201
60% | FY27: 111.4336 |  | 1.6489 | 24.6112 | 168.3555 | 11.2432 | 58.3584 |  |  |  |  | 1.294 | 8.4832 | 24.0561 | 47.5461 | 84.6689 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792
55% | [33 empty] | 78.4343 | [10 empty] | 4.7284 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 352.2319 | 522.3053 | 1633.7029 | 427.3966 | 695.4405 | 47.7954 | 80.541 | 136.4067 | 197.166 | 244.3853 | 390.7916 | 518.3063 | 597.1246 | 770.3872 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | E @ R (MWh) | 615.1978 | 782.3971 | 1408.9389 | 705.2765 | 924.7175 | 309.9513 | 385.8743 | 473.6219 | 561.3274 | 609.2082 | 685.2361 | 779.5928 | 883.4482 | 1026.5072 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375
Option 3 Summer POE50 W E @ R (MWh) N 1 | 246.5624 | 365.6137 | 1143.592 | 299.1776 | 486.8084 | 33.4568 | 56.3787 | 95.4847 | 138.0162 | 171.0697 | 273.5541 | 362.8144 | 417.9872 | 539.271 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 184.5593 | 234.7191 | 422.6817 | 211.583 | 277.4152 | 92.9854 | 115.7623 | 142.0866 | 168.3982 | 182.7625 | 205.5708 | 233.8778 | 265.0344 | 307.9521 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.3927 | 9.039 | 16.0723 | [10 empty] | 1.1704 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 | 6.4184 |  | 9.5576 | 12.2937 | 19.2723 | [7 empty] | 0.083376 | 2.3875 | 1.5868 | 4.7641 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954 | 6.5954
98% | 17.695 | 25.554 | 46.442 | [10 empty] | 0.98808 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 | 16.5562 |  | 27.0942 | 35.2201 | 55.9456 | [8 empty] | 4.5852 | 2.2072 | 11.6433 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819 | 17.0819
97% | 7.2053 | 10.6627 | 19.852 | [11 empty] | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 | 6.1588 |  | 11.3403 | 14.9151 | 24.033 | [8 empty] | 0.89235 | 0.075359 | 3.9975 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39 | 6.39
95% | 15.5414 | 24.052 | 46.6718 | [11 empty] | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 | 10.8987 |  | 25.7199 | 34.5195 | 56.9634 | [8 empty] | 0.055727 |  | 5.5785 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468 | 11.468
90% | 103.6024 | 190.5261 | 421.5543 | [11 empty] | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 | 22.0594 |  | 207.561 | 297.436 | 526.6677 | [10 empty] | 2.5006 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677 | 25.2677
85% | FY25: 51.2159; FY26: 245.2952; FY27: 789.5839 |  | 285.4285 | 497.1685 | 1037.2249
80% | FY26: 71.542; FY27: 1016.4181 |  | 119.4005 | 486.9374 | 1464.8252
75% | FY27: 642.7938 |  |  | 85.1457 | 1167.0476
70% | FY27: 110.8231 |  |  |  | 640.5835
65% | [33 empty] | 37.6543
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 201.6526 | 576.6711 | 3110.2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1584 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | 62.0915 | E @ R (MWh) | 686.1021 | 1463.636 | 5030.2175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083376 | 7.9208 | 3.8693 | 28.4841 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803 | 66.803
Option 4 Winter POE50 W E @ R (MWh) N 1 | 141.1569 | 403.6698 | 2177.148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5109 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | 43.464 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 205.8306 | 439.0908 | 1509.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025013 | 2.3762 | 1.1608 | 8.5452 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409 | 20.0409
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.8537 | 20.9364 | 26.7753 |  |  | 1.2221 | 2.8379 | 4.3918 | 5.7373 | 6.4101 | 7.4041 | 8.5417 | 9.7022 | 11.1636 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892 | 11.3892
98% | 6.2456 | 7.0779 | 9.9599 | [7 empty] | 0.16188 | 0.76985 | 1.0888 | 1.6823 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 | 1.5077 |  | 9.1603 | 10.1912 | 13.0813 |  |  | 0.26135 | 1.0611 | 1.8303 | 2.4963 | 2.8293 | 3.3213 | 3.8844 | 4.4588 | 5.1821 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938 | 5.2938
97% | 6.0086 | 6.8325 | 9.6853 | [8 empty] | 0.41497 | 0.73071 | 1.3182 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 | 1.1453 |  | 17.7875 | 19.8284 | 25.5499 |  |  | 0.021393 | 1.4065 | 2.9292 | 4.2477 | 4.907 | 5.881 | 6.9957 | 8.1328 | 9.5649 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786 | 9.786
95% | 16.9597 | 19.3932 | 27.82 | [8 empty] | 0.11923 | 0.63731 | 2.3159 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 | 1.8052 |  | 33.9759 | 37.9948 | 49.2618 |  |  |  | 0.76831 | 3.6645 | 6.2609 | 7.5592 | 9.4773 | 11.6724 | 13.9117 | 16.7317 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167 | 17.167
90% | 33.7676 | 39.2387 | 58.1843 | [10 empty] | 0.3197 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 | 0.11067 |  | 113.4167 | 127.9383 | 168.649 |  |  |  |  | 1.2432 | 5.7309 | 9.1495 | 15.5485 | 23.4803 | 31.5714 | 41.7608 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338 | 43.3338
85% | FY25: 43.6709; FY26: 52.543; FY27: 83.2656 |  | 118.3407 | 135.7404 | 184.5199 | [7 empty] | 0.035714 | 1.7644 | 6.1175 | 15.1445 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776 | 16.8776
80% | FY25: 120.2726; FY26: 154.4301; FY27: 272.7122 |  | 112.6035 | 132.4627 | 188.1373
75% | FY25: 100.3174; FY26: 152.0501; FY27: 331.1923 |  | 74.8261 | 91.8595 | 139.612
70% | FY25: 24.9895; FY26: 90.0079; FY27: 363.6588 |  | 53.5318 | 71.7426 | 122.796
65% | FY26: 0.73201; FY27: 365.7907 |  | 61.0527 | 109.0916 | 243.7669
60% | FY27: 111.4336 |  | 1.6489 | 24.6112 | 168.3555
55% | [33 empty] | 78.4343
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 352.2319 | 522.3053 | 1633.7029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16188 | 1.3041 | 2.4568 | 5.6361 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | 4.5688 | E @ R (MWh) | 615.1978 | 782.3971 | 1408.9389 | 0 | 0 | 1.5049 | 6.0738 | 14.059 | 24.4732 | 30.855 | 41.6678 | 56.339 | 73.8943 | 99.5475 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474 | 103.8474
Option 4 Summer POE50 W E @ R (MWh) N 1 | 246.5624 | 365.6137 | 1143.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11332 | 0.91284 | 1.7198 | 3.9452 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | 3.1982 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 184.5593 | 234.7191 | 422.6817 | 0 | 0 | 0.45147 | 1.8221 | 4.2177 | 7.3419 | 9.2565 | 12.5003 | 16.9017 | 22.1683 | 29.8643 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542 | 31.1542
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.3927 | 9.039 | 16.0723 | 9.1314 | 12.3245 | 1.7679 | 4.4267 | 6.415 | 8.6084 | 9.7554 | 10.7491 | 13.2144 | 11.7211 | 15.7435 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 | 20.9915 |  | 9.5576 | 12.2937 | 19.2723 | 12.5556 | 15.7598 | 5.4948 | 7.9647 | 10.0685 | 12.2608 | 13.2188 | 14.5289 | 16.9607 | 16.1599 | 19.3373 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685 | 21.1685
98% | 17.695 | 25.554 | 46.442 | 25.8285 | 35.3114 | 3.96 | 11.8563 | 17.7612 | 24.2752 | 27.6817 | 30.633 | 37.9543 | 33.5194 | 45.4654 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 | 61.0513 |  | 27.0942 | 35.2201 | 55.9456 | 35.998 | 45.514 | 15.0283 | 22.3637 | 28.6114 | 35.1223 | 37.9674 | 41.8582 | 49.0803 | 46.7022 | 56.1384 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577 | 61.577
97% | 7.2053 | 10.6627 | 19.852 | 10.7835 | 14.9553 | 1.1628 | 4.6367 | 7.2344 | 10.1001 | 11.5987 | 12.8971 | 16.118 | 14.167 | 19.4224 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 | 26.2791 |  | 11.3403 | 14.9151 | 24.033 | 15.2574 | 19.4438 | 6.0321 | 9.2592 | 12.0078 | 14.8721 | 16.1238 | 17.8355 | 21.0127 | 19.9665 | 24.1178 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104 | 26.5104
95% | 15.5414 | 24.052 | 46.6718 | 24.3492 | 34.6184 | 0.78169 | 9.2186 | 15.6131 | 22.6671 | 26.3561 | 29.5521 | 37.4805 | 32.6778 | 45.6143 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 | 62.4924 |  | 25.7199 | 34.5195 | 56.9634 | 35.3619 | 45.6669 | 12.6536 | 20.5972 | 27.3629 | 34.4136 | 37.4946 | 41.708 | 49.5288 | 46.9536 | 57.1722 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616 | 63.0616
90% | 103.6024 | 190.5261 | 421.5543 | 193.5616 | 298.4463 |  | 39.0745 | 104.335 | 176.3813 | 214.0584 | 246.7012 | 327.6779 | 278.6262 | 410.7533 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 | 583.1381 |  | 207.561 | 297.436 | 526.6677 | 306.0399 | 411.2903 | 74.1074 | 155.2404 | 224.3421 | 296.3541 | 327.8228 | 370.8556 | 450.7346 | 424.4326 | 528.8001 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522 | 588.9522
85% | 51.2159 | 245.2952 | 789.5839 | 252.4466 | 499.5489 |  |  | 52.4177 | 211.9709 | 300.7361 | 377.6404 | 568.4169 | 452.8538 | 764.1375 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 | 1170.2659 |  | 285.4285 | 497.1685 | 1037.2249 | 517.439 | 765.4026 | 14.1699 | 162.1642 | 324.9636 | 494.6198 | 568.7581 | 670.141 | 858.3312 | 796.3651 | 1042.2489 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637 | 1183.9637
80% |  | 71.542 | 1016.4181 | 79.2092 | 491.2475 |  |  |  | 40.8273 | 140.7149 | 270.5061 | 615.9478 | 406.6961 | 970.3419 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 | 1705.7244 |  | 119.4005 | 486.9374 | 1464.8252 | 523.6413 | 972.6327 |  | 10.6635 | 177.8363 | 482.3224 | 616.5657 | 800.1411 | 1140.8997 | 1028.6969 | 1473.9222 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272 | 1730.5272
75% |  |  | 642.7938 |  | 87.9329 | [5 empty] | 2.5466 | 187.0365 | 41.2569 | 588.924 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 | 1448.6943 |  |  | 85.1457 | 1167.0476 | 110.2616 | 591.6022 |  |  |  | 82.2094 | 187.615 | 389.9342 | 788.3311 | 657.1495 | 1177.6834 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924 | 1477.6924
70% |  |  | 110.8231 | [10 empty] | 79.1662 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 | 970.8679 |  |  |  | 640.5835 |  | 80.6184 | [5 empty] | 7.8268 | 221.5785 | 120.1223 | 653.056 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737 | 1004.8737
65% | FY39: 209.3217; FY40: 209.3217; FY41: 209.3217; FY42: 209.3217; FY43: 209.3217; FY44: 209.3217; FY45: 209.3217; FY46: 209.3217; FY47: 209.3217; FY48: 209.3217; FY49: 209.3217; FY50: 209.3217; FY51: 209.3217; FY52: 209.3217; FY53: 209.3217; FY54: 209.3217 |  |  |  | 37.6543 | [10 empty] | 41.668 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914 | 234.4914
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 201.6526 | 576.6711 | 3110.2114 | 595.3099 | 1474.3852 | 7.6724 | 69.2128 | 203.7766 | 494.8302 | 730.9013 | 981.2256 | 1803.8464 | 1271.5182 | 2939.5686 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | 6258.8264 | E @ R (MWh) | 686.1021 | 1463.636 | 5030.2175 | 1556.5547 | 2947.9307 | 127.486 | 388.253 | 805.1926 | 1452.1745 | 1805.5662 | 2354.8292 | 3596.4576 | 3156.5487 | 5074.1444 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181 | 6392.8181
Option 5 Winter POE50 W E @ R (MWh) N 1 | 141.1569 | 403.6698 | 2177.148 | 416.7169 | 1032.0696 | 5.3707 | 48.449 | 142.6436 | 346.3812 | 511.6309 | 686.8579 | 1262.6925 | 890.0627 | 2057.698 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | 4381.1785 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 205.8306 | 439.0908 | 1509.0653 | 466.9664 | 884.3792 | 38.2458 | 116.4759 | 241.5578 | 435.6524 | 541.6699 | 706.4487 | 1078.9373 | 946.9646 | 1522.2433 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454 | 1917.8454
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.8537 | 20.9364 | 26.7753 | 20.0158 | 22.5042 | 13.5843 | 15.2001 | 16.754 | 18.0995 | 18.7723 | 19.7663 | 20.9039 | 22.0644 | 23.5258 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514 | 23.7514
98% | 6.2456 | 7.0779 | 9.9599 | 6.6377 | 7.7303 | 3.3081 | 3.9288 | 4.6377 | 5.2041 | 5.5724 | 6.4524 | 7.0606 | 7.3796 | 7.9731 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 | 7.7984 |  | 9.1603 | 10.1912 | 13.0813 | 9.7355 | 10.9672 | 6.5521 | 7.3519 | 8.121 | 8.787 | 9.12 | 9.612 | 10.1751 | 10.7495 | 11.4729 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845 | 11.5845
97% | 6.0086 | 6.8325 | 9.6853 | 6.3967 | 7.4783 | 3.1009 | 3.7154 | 4.4171 | 4.9778 | 5.3423 | 6.2134 | 6.8154 | 7.1311 | 7.7186 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 | 7.5457 |  | 17.7875 | 19.8284 | 25.5499 | 18.9264 | 21.3647 | 12.6241 | 14.2074 | 15.7301 | 17.0486 | 17.7078 | 18.6818 | 19.7966 | 20.9337 | 22.3657 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868 | 22.5868
95% | 16.9597 | 19.3932 | 27.82 | 18.1061 | 21.3008 | 8.3708 | 10.1857 | 12.2584 | 13.9146 | 14.9914 | 17.5644 | 19.3427 | 20.2754 | 22.0107 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 |  | 33.9759 | 37.9948 | 49.2618 | 36.2185 | 41.0201 | 23.8079 | 26.9257 | 29.9243 | 32.5207 | 33.8189 | 35.737 | 37.9322 | 40.1714 | 42.9914 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268 | 43.4268
90% | 33.7676 | 39.2387 | 58.1843 | 36.345 | 43.5276 | 14.4574 | 18.538 | 23.1979 | 26.9215 | 29.3423 | 35.1272 | 39.1253 | 41.2221 | 45.1235 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 | 43.9754 |  | 113.4167 | 127.9383 | 168.649 | 121.5198 | 138.8693 | 76.6771 | 87.9425 | 98.7771 | 108.1586 | 112.8494 | 119.78 | 127.7118 | 135.8029 | 145.9923 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654 | 147.5654
85% | 43.6709 | 52.543 | 83.2656 | 47.8505 | 59.4979 | 12.3571 | 18.9742 | 26.5309 | 32.5691 | 36.4947 | 45.8757 | 52.359 | 55.7593 | 62.0859 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 | 60.2241 |  | 118.3407 | 135.7404 | 184.5199 | 128.0498 | 148.8379 | 74.3193 | 87.8175 | 100.7995 | 112.0404 | 117.661 | 125.9652 | 135.4691 | 145.1638 | 157.3728 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576 | 159.2576
80% | 120.2726 | 154.4301 | 272.7122 | 136.3639 | 181.2064 | 6.201 | 25.1989 | 54.2835 | 77.5304 | 92.6442 | 128.761 | 153.7218 | 166.8128 | 191.1701 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 | 184.0021 |  | 112.6035 | 132.4627 | 188.1373 | 123.6849 | 147.4115 | 62.3595 | 77.7657 | 92.5828 | 105.4126 | 111.8277 | 121.3057 | 132.153 | 143.2181 | 157.1528 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304 | 159.304
75% | 100.3174 | 152.0501 | 331.1923 | 124.6883 | 192.6038 |  |  | 11.0812 | 36.0486 | 58.4734 | 113.1734 | 150.9774 | 170.8041 | 207.6941 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 | 196.838 |  | 74.8261 | 91.8595 | 139.612 | 84.3307 | 104.6812 | 31.7314 | 44.9455 | 57.6542 | 68.6584 | 74.1607 | 82.29 | 91.5939 | 101.0844 | 113.0364 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815 | 114.8815
70% | 24.9895 | 90.0079 | 363.6588 | 51.0085 | 151.9562 |  |  |  |  | 1.5245 | 37.6241 | 88.3693 | 118.6559 | 175.0076 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 | 158.4242 |  | 53.5318 | 71.7426 | 122.796 | 63.6934 | 85.4506 | 8.2954 | 21.5857 | 35.1729 | 46.9378 | 52.8204 | 61.5117 | 71.4586 | 81.6052 | 94.3833 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356 | 96.356
65% |  | 0.73201 | 365.7907 |  | 30.1393 | [6 empty] | 0.53481 | 9.0843 | 51.6037 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 | 35.6027 |  | 61.0527 | 109.0916 | 243.7669 | 87.8585 | 145.2524 |  | 2.1325 | 18.1062 | 43.6639 | 59.1761 | 82.1031 | 108.3425 | 135.1086 | 168.8164 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201 | 174.0201
60% | FY27: 111.4336 |  | 1.6489 | 24.6112 | 168.3555 | 11.2432 | 58.3584 |  |  |  |  | 1.294 | 8.4832 | 24.0561 | 47.5461 | 84.6689 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792 | 90.4792
55% | [33 empty] | 78.4343 | [10 empty] | 4.7284 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241 | 7.0241
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 352.2319 | 522.3053 | 1633.7029 | 427.3966 | 695.4405 | 47.7954 | 80.541 | 136.4067 | 197.166 | 244.3853 | 390.7916 | 518.3063 | 597.1246 | 770.3872 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | 715.9106 | E @ R (MWh) | 615.1978 | 782.3971 | 1408.9389 | 705.2765 | 924.7175 | 309.9513 | 385.8743 | 473.6219 | 561.3274 | 609.2082 | 685.2361 | 779.5928 | 883.4482 | 1026.5072 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375 | 1050.2375
Option 5 Summer POE50 W E @ R (MWh) N 1 | 246.5624 | 365.6137 | 1143.592 | 299.1776 | 486.8084 | 33.4568 | 56.3787 | 95.4847 | 138.0162 | 171.0697 | 273.5541 | 362.8144 | 417.9872 | 539.271 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | 501.1374 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 184.5593 | 234.7191 | 422.6817 | 211.583 | 277.4152 | 92.9854 | 115.7623 | 142.0866 | 168.3982 | 182.7625 | 205.5708 | 233.8778 | 265.0344 | 307.9521 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713 | 315.0713
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 2.0163 | 4.2859 | 10.8405 | 16.4236 | 19.4145 | 21.5595 | 24.0881 | 25.9513 | 28.0361 | 29.1307 | 30.045 | 32.4188 | 30.8328 | 34.7372 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 | 39.9691 |  | 5.1812 | 7.5406 | 14.0406 | 19.8478 | 22.8498 | 25.2864 | 27.6261 | 29.6047 | 31.6885 | 32.5941 | 33.8247 | 36.1651 | 35.2717 | 38.331 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461 | 40.1461
98% | 4.6979 | 11.438 | 30.9044 | 47.4852 | 56.3676 | 62.7381 | 70.2477 | 75.7811 | 81.9726 | 85.2235 | 87.9386 | 94.9886 | 90.2785 | 101.8738 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 | 117.4118 |  | 14.0971 | 21.1041 | 40.4081 | 57.6547 | 66.5702 | 73.8063 | 80.7551 | 86.6313 | 92.8197 | 95.5093 | 99.1638 | 106.1145 | 103.4613 | 112.5468 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374 | 117.9374
97% | 1.4874 | 4.4526 | 13.0165 | 20.311 | 24.2186 | 27.0212 | 30.3249 | 32.7592 | 35.4831 | 36.9133 | 38.1077 | 41.2092 | 39.1371 | 44.2383 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 | 51.0739 |  | 5.6225 | 8.7051 | 17.1975 | 24.7849 | 28.7071 | 31.8905 | 34.9475 | 37.5326 | 40.2551 | 41.4383 | 43.0461 | 46.1039 | 44.9367 | 48.9337 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052 | 51.3052
95% | 1.4669 | 8.7657 | 29.846 | 47.8016 | 57.4204 | 64.319 | 72.4512 | 78.4434 | 85.1483 | 88.6687 | 91.609 | 99.2434 | 94.1429 | 106.6995 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 | 123.5257 |  | 11.6452 | 19.2331 | 40.1376 | 58.8142 | 68.4689 | 76.305 | 83.8299 | 90.1932 | 96.8948 | 99.8073 | 103.7648 | 111.2918 | 108.4187 | 118.2574 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095 | 124.095
90% |  | 34.7257 | 249.7034 | 433.0928 | 531.3355 | 601.7947 | 684.8535 | 746.0545 | 814.5356 | 850.4913 | 880.5216 | 958.4967 | 906.4018 | 1034.6497 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 | 1206.5046 |  | 63.8086 | 141.308 | 354.8168 | 545.5712 | 644.1795 | 724.2135 | 801.0695 | 866.0615 | 934.5084 | 964.2557 | 1004.6761 | 1081.5534 | 1052.2082 | 1152.6965 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187 | 1212.3187
85% |  |  | 384.7134 | 816.7681 | 1048.222 | 1214.2197 | 1409.9014 | 1554.0873 | 1715.4247 | 1800.1343 | 1870.8838 | 2054.5886 | 1931.856 | 2234.0005 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 | 2638.8805 |  | 6.5795 | 129.3404 | 632.3544 | 1081.7604 | 1314.0757 | 1502.6313 | 1683.6993 | 1836.8168 | 1998.0736 | 2068.1563 | 2163.3844 | 2344.5028 | 2275.3673 | 2512.1119 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783 | 2652.5783
80% |  |  | 283.3133 | 1065.6408 | 1484.7378 | 1785.3122 | 2139.6359 | 2400.7153 | 2692.8513 | 2846.236 | 2974.3433 | 3306.9801 | 3084.7465 | 3631.8438 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 | 4364.9658 |  |  | 1.4042 | 731.7203 | 1545.4662 | 1966.1229 | 2307.5432 | 2635.4056 | 2912.6576 | 3204.6477 | 3331.5474 | 3503.9783 | 3831.932 | 3706.7473 | 4135.4241 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686 | 4389.7686
75% |  |  | 4.2168 | 700.3424 | 1190.3284 | 1541.7442 | 1956.0006 | 2261.2408 | 2602.7908 | 2782.1202 | 2931.8963 | 3320.7977 | 3060.9739 | 3700.6112 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 | 4557.7386 |  |  |  | 309.9402 | 1261.3289 | 1753.1385 | 2152.3089 | 2535.6284 | 2859.7767 | 3201.1561 | 3349.5205 | 3551.1176 | 3934.5437 | 3788.1843 | 4289.3706 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367 | 4586.7367
70% |  |  |  | 150.2667 | 667.8847 | 1079.9866 | 1565.7812 | 1923.7336 | 2324.266 | 2534.5638 | 2710.2049 | 3166.2659 | 2861.573 | 3611.6696 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 | 4616.8149 |  |  |  | 0.095547 | 751.1463 | 1327.8867 | 1795.9902 | 2245.5053 | 2625.6309 | 3025.9633 | 3199.9489 | 3436.3598 | 3886.0001 | 3714.3658 | 4302.1022 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207 | 4650.8207
65% |  |  |  |  | 46.6985 | 294.8697 | 799.868 | 1192.1191 | 1631.0302 | 1861.4787 | 2053.9496 | 2553.7101 | 2219.8217 | 3041.792 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 | 4143.2496 |  |  |  |  | 80.1123 | 539.1786 | 1052.1354 | 1544.7227 | 1961.2718 | 2399.9637 | 2590.6205 | 2849.6842 | 3342.4087 | 3154.3285 | 3798.3814 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139 | 4180.5139
60% | [6 empty] | 43.6423 | 235.8866 | 618.9423 | 869.3224 | 1078.738 | 1622.4962 | 1259.2131 | 2153.5476 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | 3351.9749 | [5 empty] | 0.42813 | 150.3664 | 530.3121 | 977.9011 | 1455.2144 | 1662.6561 | 1944.5272 | 2480.6299 | 2275.9916 | 2976.7453 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198 | 3392.5198
55% | [9 empty] | 18.278 | 69.0534 | 344.315 | 137.9843 | 798.3836 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | 1999.7029 | [8 empty] | 40.621 | 238.3364 | 372.4797 | 598.9906 | 1126.2551 | 921.123 | 1623.5678 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456 | 2040.3456
50% | FY38: 0.24698; FY39: 537.5444; FY40: 537.5444; FY41: 537.5444; FY42: 537.5444; FY43: 537.5444; FY44: 537.5444; FY45: 537.5444; FY46: 537.5444; FY47: 537.5444; FY48: 537.5444; FY49: 537.5444; FY50: 537.5444; FY51: 537.5444; FY52: 537.5444; FY53: 537.5444; FY54: 537.5444 | [12 empty] | 46.7374 | 8.3158 | 263.6674 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275 | 572.5275
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 9.6686 | 63.6679 | 1006.5544 | 3298.1321 | 5126.6281 | 6693.565 | 8796.7949 | 10526.7721 | 12630.4811 | 13802.561 | 14817.2913 | 17595.5105 | 15716.9617 | 20494.2936 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | 27749.3567 | E @ R (MWh) | 106.9341 | 328.6355 | 2140.711 | 5426.4869 | 7731.6061 | 9892.477 | 12203.5015 | 14324.6991 | 16719.5218 | 17808.5341 | 19332.5175 | 22374.2386 | 21188.7202 | 25372.1359 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135 | 28011.6135
Option 6 Winter POE50 W E @ R (MWh) N 1 | 6.768 | 44.5675 | 704.588 | 2308.6924 | 3588.6397 | 4685.4955 | 6157.7564 | 7368.7405 | 8841.3368 | 9661.7927 | 10372.1039 | 12316.8573 | 11001.8732 | 14346.0055 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | 19424.5497 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 32.0802 | 98.5906 | 642.2133 | 1627.9461 | 2319.4818 | 2967.7431 | 3661.0505 | 4297.4097 | 5015.8565 | 5342.5602 | 5799.7552 | 6712.2716 | 6356.6161 | 7611.6408 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841 | 8403.4841
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15.1413 | 16.9044 | 22.3372 | 26.2017 | 28.5185 | 30.3733 | 31.8786 | 33.3264 | 34.5798 | 35.2081 | 36.1347 | 37.1948 | 38.2766 | 39.6379 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498 | 39.8498
98% | 4.408 | 5.0821 | 7.7632 | 9.6995 | 10.7073 | 11.6182 | 12.1842 | 12.8406 | 13.3615 | 13.7077 | 14.5543 | 15.1242 | 15.4043 | 15.9482 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 | 15.7667 |  | 7.3228 | 8.1955 | 10.8846 | 12.7974 | 13.9442 | 14.8622 | 15.6073 | 16.3239 | 16.9444 | 17.2554 | 17.714 | 18.2387 | 18.7742 | 19.448 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529 | 19.5529
97% | 4.1898 | 4.857 | 7.5109 | 9.4275 | 10.425 | 11.3267 | 11.887 | 12.5367 | 13.0523 | 13.395 | 14.2331 | 14.7971 | 15.0743 | 15.6127 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 |  | 14.1498 | 15.8775 | 21.2011 | 24.9879 | 27.2581 | 29.0756 | 30.5506 | 31.9693 | 33.1976 | 33.8133 | 34.7212 | 35.76 | 36.8201 | 38.154 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616 | 38.3616
95% | 11.587 | 13.5579 | 21.3971 | 27.0585 | 30.005 | 32.6684 | 34.3235 | 36.2426 | 37.7655 | 38.7779 | 41.2533 | 42.9194 | 43.7384 | 45.3287 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 | 44.7982 |  | 26.8123 | 30.2145 | 40.6979 | 48.155 | 52.6256 | 56.2047 | 59.1094 | 61.9031 | 64.3218 | 65.5343 | 67.3222 | 69.3678 | 71.4554 | 74.0821 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491 | 74.491
90% | 21.6883 | 26.1195 | 43.744 | 56.4724 | 63.0969 | 69.0848 | 72.8059 | 77.1206 | 80.5445 | 82.8207 | 88.3861 | 92.132 | 93.9731 | 97.5485 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 | 96.3559 |  | 87.5326 | 99.8258 | 137.7053 | 164.65 | 180.8035 | 193.7357 | 204.231 | 214.3256 | 223.0652 | 227.4461 | 233.9062 | 241.2976 | 248.8407 | 258.3316 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093 | 259.8093
85% | 24.0829 | 31.2687 | 59.8488 | 80.4895 | 91.2319 | 100.9421 | 106.9763 | 113.973 | 119.5254 | 123.2165 | 132.2415 | 138.3158 | 141.3014 | 147.0994 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 | 145.1654 |  | 87.3264 | 102.0561 | 147.4433 | 179.7283 | 199.0834 | 214.5788 | 227.1542 | 239.2496 | 249.7213 | 254.9705 | 262.711 | 271.5673 | 280.6055 | 291.9775 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748 | 293.748
80% | 44.8587 | 72.5238 | 182.5576 | 262.0243 | 303.3823 | 340.7665 | 363.9984 | 390.9357 | 412.3123 | 426.5231 | 461.2693 | 484.6554 | 496.1499 | 518.4722 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 | 511.0262 |  | 77.2051 | 94.0169 | 145.8198 | 182.6684 | 204.7594 | 222.4451 | 236.7981 | 250.6032 | 262.5551 | 268.5463 | 277.381 | 287.4892 | 297.8049 | 310.7844 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051 | 312.8051
75% | 4.9484 | 29.5242 | 194.6501 | 315.0051 | 377.6432 | 434.2627 | 469.4483 | 510.2458 | 542.6213 | 564.144 | 616.7682 | 652.1873 | 669.5961 | 703.4039 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 | 692.1268 |  | 44.4646 | 58.8842 | 103.316 | 134.9213 | 153.8689 | 169.0381 | 181.3487 | 193.1895 | 203.4407 | 208.5794 | 216.157 | 224.8269 | 233.6747 | 244.8073 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406 | 246.5406
70% |  |  | 155.0821 | 338.9318 | 434.6155 | 521.1053 | 574.8534 | 637.1741 | 686.6297 | 719.5069 | 799.8938 | 853.9986 | 880.5917 | 932.2352 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 | 915.0087 |  | 21.0716 | 36.488 | 83.991 | 117.781 | 138.0384 | 154.2561 | 167.4178 | 180.077 | 191.0368 | 196.5307 | 204.6321 | 213.9013 | 223.3607 | 235.2629 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159 | 237.1159
65% |  |  | 32.7248 | 320.6397 | 495.3564 | 653.2852 | 751.4283 | 865.2248 | 955.5299 | 1015.5632 | 1162.3481 | 1261.1426 | 1309.7011 | 1404.0012 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 | 1372.5458 |  | 1.8302 | 20.4408 | 141.4021 | 230.5378 | 283.9754 | 326.7566 | 361.4761 | 394.8702 | 423.7816 | 438.2741 | 459.645 | 484.0964 | 509.0498 | 540.4469 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335 | 545.335
60% |  |  |  | 67.3427 | 295.0703 | 597.2339 | 787.9599 | 1009.1059 | 1184.6001 | 1301.2654 | 1586.5195 | 1778.5114 | 1872.8774 | 2056.1351 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 | 1995.0065 |  |  |  | 54.1338 | 153.5845 | 213.2506 | 261.0183 | 299.7846 | 337.0711 | 369.3523 | 385.534 | 409.3959 | 436.6973 | 464.5592 | 499.6159 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737 | 505.0737
55% | [5 empty] | 35.996 | 123.5321 | 286.4237 | 459.9215 | 593.4729 | 924.1097 | 1146.6468 | 1256.0261 | 1468.4393 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 | 1397.5854 |  |  |  |  | 59.3347 | 148.6432 | 226.3532 | 289.4193 | 350.078 | 402.5941 | 428.9189 | 467.7382 | 512.1529 | 557.4794 | 614.5106 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897 | 623.3897
50% | [9 empty] | 3.0601 | 89.6618 | 211.7088 | 289.5182 | 472.7623 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | 407.0144 | [5 empty] | 4.9536 | 48.0294 | 113.446 | 200.279 | 290.4968 | 336.4134 | 404.123 | 481.5924 | 560.6522 | 660.1276 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147 | 675.6147
45% | [39 empty] | 6.0307 | 20.5444 | 57.1732 | 120.5251 | 207.773 | 348.4393 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249 | 373.3249
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 115.7631 | 182.9334 | 705.2786 | 1487.0911 | 2111.5337 | 2808.2897 | 3309.3973 | 3951.8234 | 4505.864 | 4895.4534 | 5931.2387 | 6692.1393 | 7083.952 | 7876.9866 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | 7607.833 | E @ R (MWh) | 382.8566 | 482.9036 | 908.9321 | 1335.348 | 1649.7228 | 1946.7272 | 2218.2217 | 2503.2659 | 2771.1182 | 2917.5689 | 3148.7547 | 3434.7077 | 3749.1264 | 4175.6259 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121 | 4245.0121
Option 6 Summer POE50 W E @ R (MWh) N 1 | 81.0342 | 128.0533 | 493.695 | 1040.9638 | 1478.0736 | 1965.8028 | 2316.5781 | 2766.2764 | 3154.1048 | 3426.8174 | 4151.8671 | 4684.4975 | 4958.7664 | 5513.8906 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | 5325.4831 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 114.857 | 144.8711 | 272.6796 | 400.6044 | 494.9168 | 584.0181 | 665.4665 | 750.9798 | 831.3354 | 875.2707 | 944.6264 | 1030.4123 | 1124.7379 | 1252.6878 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036 | 1273.5036
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.3927 | 9.039 | 16.0723 | 21.9949 | 25.188 | 27.4949 | 30.1537 | 32.142 | 34.3353 | 35.4824 | 36.4761 | 38.9414 | 37.4481 | 41.4705 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 |  | 9.5576 | 12.2937 | 19.2723 | 25.4191 | 28.6233 | 31.2218 | 33.6917 | 35.7954 | 37.9878 | 38.9458 | 40.2559 | 42.6877 | 41.8869 | 45.0643 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955
98% | 17.695 | 25.554 | 46.442 | 64.0311 | 73.5141 | 80.3653 | 88.2616 | 94.1665 | 100.6804 | 104.0869 | 107.0383 | 114.3596 | 109.9247 | 121.8707 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 |  | 27.0942 | 35.2201 | 55.9456 | 74.2006 | 83.7166 | 91.4335 | 98.769 | 105.0167 | 111.5276 | 114.3727 | 118.2635 | 125.4856 | 123.1075 | 132.5437 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822
97% | 7.2053 | 10.6627 | 19.852 | 27.59 | 31.7619 | 34.776 | 38.2498 | 40.8476 | 43.7133 | 45.2119 | 46.5103 | 49.7312 | 47.7801 | 53.0356 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 |  | 11.3403 | 14.9151 | 24.033 | 32.0639 | 36.2503 | 39.6453 | 42.8724 | 45.6209 | 48.4853 | 49.7369 | 51.4486 | 54.6258 | 53.5797 | 57.7309 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235
95% | 15.5414 | 24.052 | 46.6718 | 65.7193 | 75.9885 | 83.4077 | 91.9587 | 98.3532 | 105.4072 | 109.0961 | 112.2922 | 120.2205 | 115.4179 | 128.3544 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 |  | 25.7199 | 34.5195 | 56.9634 | 76.7319 | 87.0369 | 95.3936 | 103.3373 | 110.103 | 117.1536 | 120.2347 | 124.448 | 132.2689 | 129.6937 | 139.9123 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017
90% | 103.6024 | 190.5261 | 421.5543 | 616.0961 | 720.9809 | 796.7577 | 884.0936 | 949.4042 | 1021.4505 | 1059.1276 | 1091.7704 | 1172.7471 | 1123.6953 | 1255.8225 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 |  | 207.561 | 297.436 | 526.6677 | 728.5745 | 833.8249 | 919.1765 | 1000.3096 | 1069.4112 | 1141.4233 | 1172.892 | 1215.9248 | 1295.8038 | 1269.5018 | 1373.8693 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214
85% | 51.2159 | 245.2952 | 789.5839 | 1247.9131 | 1495.0154 | 1673.5411 | 1879.2993 | 2033.1672 | 2202.9039 | 2291.6691 | 2368.5734 | 2559.3499 | 2443.7868 | 2755.0705 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 |  | 285.4285 | 497.1685 | 1037.2249 | 1512.9055 | 1760.8691 | 1961.9526 | 2153.0972 | 2315.8967 | 2485.5528 | 2559.6911 | 2661.074 | 2849.2642 | 2787.2981 | 3033.1819 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967
80% |  | 71.542 | 1016.4181 | 1846.3213 | 2293.7529 | 2617.0119 | 2989.5813 | 3268.1921 | 3575.5368 | 3736.2652 | 3875.5169 | 4220.9587 | 4011.7069 | 4575.3528 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 |  | 119.4005 | 486.9374 | 1464.8252 | 2326.1467 | 2775.1381 | 3139.2428 | 3485.351 | 3780.1344 | 4087.3333 | 4221.5765 | 4405.1519 | 4745.9106 | 4633.7077 | 5078.933 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538
75% |  |  | 642.7938 | 1613.0728 | 2136.1861 | 2514.1234 | 2949.7118 | 3275.4488 | 3634.7801 | 3822.6951 | 3985.5009 | 4389.3731 | 4144.727 | 4803.7119 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 |  |  | 85.1457 | 1167.0476 | 2174.0593 | 2698.9962 | 3124.6882 | 3529.3396 | 3873.9847 | 4233.1453 | 4390.0955 | 4604.7221 | 5003.1191 | 4871.9374 | 5392.4713 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803
70% |  |  | 110.8231 | 1163.633 | 1777.0831 | 2220.2866 | 2731.097 | 3113.0857 | 3534.4701 | 3754.8363 | 3945.7571 | 4419.3742 | 4132.48 | 4905.2654 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 |  |  |  | 640.5835 | 1821.4966 | 2437.0851 | 2936.2901 | 3410.821 | 3814.983 | 4236.1674 | 4420.2213 | 4671.912 | 5139.1083 | 4985.2728 | 5595.698 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157
65% |  |  |  | 369.7364 | 1031.4166 | 1517.0876 | 2076.8435 | 2495.4341 | 2957.1953 | 3198.6768 | 3407.8915 | 3926.8903 | 3612.5062 | 4459.3394 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 |  |  |  | 37.6543 | 1080.0858 | 1754.6596 | 2301.6981 | 2821.6983 | 3264.5868 | 3726.1288 | 3927.8186 | 4203.6261 | 4715.5889 | 4547.013 | 5215.9288 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574
60% |  |  |  |  | 139.2776 | 503.2799 | 1103.6475 | 1559.0898 | 2061.5032 | 2324.2442 | 2551.8777 | 3116.5679 | 2774.5061 | 3695.8924 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 |  |  |  |  | 165.9716 | 753.0993 | 1348.2977 | 1914.0774 | 2395.9568 | 2898.1318 | 3117.5779 | 3417.6668 | 3974.7016 | 3791.2846 | 4519.0901 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597
55% | [6 empty] | 77.2006 | 301.9799 | 707.4432 | 969.4921 | 1197.6749 | 1763.7277 | 1420.8405 | 2344.4503 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | [5 empty] | 4.0564 | 180.3574 | 572.1301 | 1041.3777 | 1544.7645 | 1764.7402 | 2065.5533 | 2623.9322 | 2440.0727 | 3169.6345 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163
50% | [9 empty] | 14.5909 | 67.2768 | 355.0439 | 154.6496 | 866.4004 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | [8 empty] | 27.1064 | 217.9999 | 355.7507 | 594.7409 | 1183.3194 | 970.2492 | 1826.1955 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531
45% | FY39: 376.3722; FY40: 376.3722; FY41: 376.3722; FY42: 376.3722; FY43: 376.3722; FY44: 376.3722; FY45: 376.3722; FY46: 376.3722; FY47: 376.3722; FY48: 376.3722; FY49: 376.3722; FY50: 376.3722; FY51: 376.3722; FY52: 376.3722; FY53: 376.3722; FY54: 376.3722 | [12 empty] | 2.1201 |  | 147.2604 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 201.6526 | 576.6711 | 3110.2114 | 7036.1081 | 9800.165 | 12068.132 | 14940.0983 | 17261.3111 | 19979.4193 | 21465.4746 | 22794.1564 | 26247.2855 | 24129.4693 | 30006.0367 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | E @ R (MWh) | 686.1021 | 1463.636 | 5030.2175 | 10017.6555 | 13253.356 | 16169.3978 | 19165.4946 | 21879.9737 | 24885.8013 | 26253.6541 | 28174.7879 | 31887.9362 | 30644.6052 | 35727.5141 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631
Option 7 Winter POE50 W E @ R (MWh) N 1 | 141.1569 | 403.6698 | 2177.148 | 4925.2757 | 6860.1155 | 8447.6924 | 10458.0688 | 12082.9178 | 13985.5935 | 15025.8322 | 15955.9095 | 18373.0998 | 16890.6285 | 21004.2257 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 205.8306 | 439.0908 | 1509.0653 | 3005.2966 | 3976.0068 | 4850.8193 | 5749.6484 | 6563.9921 | 7465.7404 | 7876.0962 | 8452.4364 | 9566.3809 | 9193.3815 | 10718.2542 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.8537 | 20.9364 | 26.7753 | 30.9278 | 33.4161 | 35.4082 | 37.0239 | 38.5779 | 39.9234 | 40.5962 | 41.5902 | 42.7278 | 43.8882 | 45.3496 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752
98% | 6.2456 | 7.0779 | 9.9599 | 12.0388 | 13.1314 | 14.1103 | 14.7311 | 15.44 | 16.0064 | 16.3747 | 17.2547 | 17.8629 | 18.1819 | 18.7753 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 |  | 9.1603 | 10.1912 | 13.0813 | 15.1367 | 16.3683 | 17.3544 | 18.1541 | 18.9233 | 19.5893 | 19.9223 | 20.4143 | 20.9774 | 21.5518 | 22.2751 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868
97% | 6.0086 | 6.8325 | 9.6853 | 11.743 | 12.8246 | 13.7935 | 14.408 | 15.1097 | 15.6704 | 16.0349 | 16.906 | 17.508 | 17.8237 | 18.4112 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 |  | 17.7875 | 19.8284 | 25.5499 | 29.6189 | 32.0573 | 34.0093 | 35.5926 | 37.1153 | 38.4337 | 39.093 | 40.067 | 41.1818 | 42.3189 | 43.7509 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972
95% | 16.9597 | 19.3932 | 27.82 | 33.8982 | 37.093 | 39.9551 | 41.77 | 43.8427 | 45.4989 | 46.5757 | 49.1487 | 50.927 | 51.8597 | 53.5949 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 |  | 33.9759 | 37.9948 | 49.2618 | 57.2747 | 62.0762 | 65.9203 | 69.0381 | 72.0367 | 74.633 | 75.9313 | 77.8494 | 80.0445 | 82.2838 | 85.1038 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391
90% | 33.7676 | 39.2387 | 58.1843 | 71.8499 | 79.0325 | 85.4672 | 89.5478 | 94.2077 | 97.9313 | 100.3521 | 106.137 | 110.1351 | 112.2319 | 116.1333 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 |  | 113.4167 | 127.9383 | 168.649 | 197.6017 | 214.9512 | 228.8409 | 240.1063 | 250.9409 | 260.3224 | 265.0133 | 271.9439 | 279.8757 | 287.9668 | 298.1562 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292
85% | 43.6709 | 52.543 | 83.2656 | 105.426 | 117.0734 | 127.5082 | 134.1252 | 141.6819 | 147.7201 | 151.6458 | 161.0267 | 167.5101 | 170.9103 | 177.2369 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 |  | 118.3407 | 135.7404 | 184.5199 | 219.211 | 239.9991 | 256.6418 | 270.14 | 283.122 | 294.3629 | 299.9835 | 308.2877 | 317.7916 | 327.4862 | 339.6952 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58
80% | 120.2726 | 154.4301 | 272.7122 | 358.0296 | 402.8721 | 443.0459 | 468.5217 | 497.6149 | 520.8618 | 535.9757 | 572.0924 | 597.0532 | 610.1442 | 634.5015 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 |  | 112.6035 | 132.4627 | 188.1373 | 227.7321 | 251.4587 | 270.4538 | 285.86 | 300.6771 | 313.5069 | 319.922 | 329.4 | 340.2474 | 351.3124 | 365.2472 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984
75% | 100.3174 | 152.0501 | 331.1923 | 460.4083 | 528.3238 | 589.1684 | 627.7522 | 671.815 | 707.0232 | 729.9136 | 784.6135 | 822.4175 | 842.2443 | 879.1343 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 |  | 74.8261 | 91.8595 | 139.612 | 173.5728 | 193.9233 | 210.2155 | 223.4295 | 236.1383 | 247.1425 | 252.6448 | 260.7741 | 270.078 | 279.5685 | 291.5205 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656
70% | 24.9895 | 90.0079 | 363.6588 | 561.0443 | 664.7895 | 757.7333 | 816.6725 | 883.9811 | 937.7638 | 972.7304 | 1056.288 | 1114.0359 | 1144.3225 | 1200.6742 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 |  | 53.5318 | 71.7426 | 122.796 | 159.1043 | 180.8615 | 198.2799 | 212.4074 | 225.9946 | 237.7595 | 243.6421 | 252.3334 | 262.2803 | 272.4269 | 285.205 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777
65% |  | 0.73201 | 365.7907 | 726.2132 | 915.65 | 1085.3638 | 1192.9858 | 1315.8901 | 1414.0963 | 1477.9446 | 1630.5193 | 1735.9661 | 1791.2689 | 1894.1661 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 |  | 61.0527 | 109.0916 | 243.7669 | 339.5457 | 396.9397 | 442.8884 | 480.1556 | 515.9976 | 547.0326 | 562.5505 | 585.4776 | 611.717 | 638.4831 | 672.1908 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946
60% |  |  | 111.4336 | 738.9582 | 1107.0997 | 1436.9124 | 1646.0591 | 1884.9047 | 2075.7535 | 2199.8329 | 2496.3384 | 2701.258 | 2808.7305 | 3008.6955 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 |  | 1.6489 | 24.6112 | 168.3555 | 275.2981 | 339.3818 | 390.6862 | 432.2971 | 472.3169 | 506.9692 | 524.2958 | 549.8953 | 579.193 | 609.0789 | 646.7156 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259
55% |  |  |  | 96.2323 | 378.628 | 750.7007 | 993.1218 | 1269.9669 | 1491.179 | 1634.9989 | 1978.6772 | 2216.1987 | 2340.7696 | 2572.5483 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 |  |  |  | 78.4343 | 249.5839 | 353.8371 | 437.3006 | 504.9945 | 570.0998 | 626.4733 | 654.6607 | 696.3066 | 743.9691 | 792.5883 | 853.8167 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691
50% | [5 empty] | 29.6615 | 122.1993 | 300.2563 | 494.8265 | 645.0196 | 1046.5764 | 1326.0081 | 1472.5592 | 1745.2346 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 |  |  |  |  | 69.0686 | 206.397 | 351.033 | 469.1066 | 582.665 | 680.9932 | 730.1585 | 802.7984 | 885.9327 | 970.7356 | 1077.532 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191
45% | [10 empty] | 56.9726 | 202.4712 | 312.8424 | 577.9293 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | [6 empty] | 26.9353 | 108.8071 | 235.9916 | 382.1514 | 467.1756 | 606.501 | 772.1407 | 941.1051 | 1153.8901 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396
40% | [41 empty] | 0.54558 | 26.9538 | 93.4527 | 231.3516 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 352.2319 | 522.3053 | 1633.7029 | 3175.8418 | 4256.518 | 5373.4204 | 6161.8944 | 7134.711 | 7964.3311 | 8527.3987 | 9972.5509 | 11079.3518 | 11693.8891 | 12897.0355 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | E @ R (MWh) | 615.1978 | 782.3971 | 1408.9389 | 2043.6763 | 2521.6672 | 2965.9678 | 3387.1128 | 3840.5968 | 4269.2935 | 4495.5896 | 4844.1844 | 5275.1107 | 5754.2472 | 6411.8004 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5
Option 7 Summer POE50 W E @ R (MWh) N 1 | 246.5624 | 365.6137 | 1143.592 | 2223.0893 | 2979.5626 | 3761.3943 | 4313.3261 | 4994.2977 | 5575.0318 | 5969.1791 | 6980.7857 | 7755.5463 | 8185.7224 | 9027.9249 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 184.5593 | 234.7191 | 422.6817 | 613.1029 | 756.5002 | 889.7903 | 1016.1338 | 1152.179 | 1280.788 | 1348.6769 | 1453.2553 | 1582.5332 | 1726.2742 | 1923.5401 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 6.3927 | 9.039 | 16.0723 | 21.9949 | 25.188 | 27.4949 | 30.1537 | 32.142 | 34.3353 | 35.4824 | 36.4761 | 38.9414 | 37.4481 | 41.4705 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 | 46.7185 |  | 9.5576 | 12.2937 | 19.2723 | 25.4191 | 28.6233 | 31.2218 | 33.6917 | 35.7954 | 37.9878 | 38.9458 | 40.2559 | 42.6877 | 41.8869 | 45.0643 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955 | 46.8955
98% | 17.695 | 25.554 | 46.442 | 64.0311 | 73.5141 | 80.3653 | 88.2616 | 94.1665 | 100.6804 | 104.0869 | 107.0383 | 114.3596 | 109.9247 | 121.8707 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 | 137.4566 |  | 27.0942 | 35.2201 | 55.9456 | 74.2006 | 83.7166 | 91.4335 | 98.769 | 105.0167 | 111.5276 | 114.3727 | 118.2635 | 125.4856 | 123.1075 | 132.5437 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822 | 137.9822
97% | 7.2053 | 10.6627 | 19.852 | 27.59 | 31.7619 | 34.776 | 38.2498 | 40.8476 | 43.7133 | 45.2119 | 46.5103 | 49.7312 | 47.7801 | 53.0356 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 | 59.8923 |  | 11.3403 | 14.9151 | 24.033 | 32.0639 | 36.2503 | 39.6453 | 42.8724 | 45.6209 | 48.4853 | 49.7369 | 51.4486 | 54.6258 | 53.5797 | 57.7309 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235 | 60.1235
95% | 15.5414 | 24.052 | 46.6718 | 65.7193 | 75.9885 | 83.4077 | 91.9587 | 98.3532 | 105.4072 | 109.0961 | 112.2922 | 120.2205 | 115.4179 | 128.3544 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 | 145.2324 |  | 25.7199 | 34.5195 | 56.9634 | 76.7319 | 87.0369 | 95.3936 | 103.3373 | 110.103 | 117.1536 | 120.2347 | 124.448 | 132.2689 | 129.6937 | 139.9123 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017 | 145.8017
90% | 103.6024 | 190.5261 | 421.5543 | 616.0961 | 720.9809 | 796.7577 | 884.0936 | 949.4042 | 1021.4505 | 1059.1276 | 1091.7704 | 1172.7471 | 1123.6953 | 1255.8225 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 | 1428.2073 |  | 207.561 | 297.436 | 526.6677 | 728.5745 | 833.8249 | 919.1765 | 1000.3096 | 1069.4112 | 1141.4233 | 1172.892 | 1215.9248 | 1295.8038 | 1269.5018 | 1373.8693 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214 | 1434.0214
85% | 51.2159 | 245.2952 | 789.5839 | 1247.9131 | 1495.0154 | 1673.5411 | 1879.2993 | 2033.1672 | 2202.9039 | 2291.6691 | 2368.5734 | 2559.3499 | 2443.7868 | 2755.0705 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 | 3161.1989 |  | 285.4285 | 497.1685 | 1037.2249 | 1512.9055 | 1760.8691 | 1961.9526 | 2153.0972 | 2315.8967 | 2485.5528 | 2559.6911 | 2661.074 | 2849.2642 | 2787.2981 | 3033.1819 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967 | 3174.8967
80% |  | 71.542 | 1016.4181 | 1846.3213 | 2293.7529 | 2617.0119 | 2989.5813 | 3268.1921 | 3575.5368 | 3736.2652 | 3875.5169 | 4220.9587 | 4011.7069 | 4575.3528 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 | 5310.7352 |  | 119.4005 | 486.9374 | 1464.8252 | 2326.1467 | 2775.1381 | 3139.2428 | 3485.351 | 3780.1344 | 4087.3333 | 4221.5765 | 4405.1519 | 4745.9106 | 4633.7077 | 5078.933 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538 | 5335.538
75% |  |  | 642.7938 | 1613.0728 | 2136.1861 | 2514.1234 | 2949.7118 | 3275.4488 | 3634.7801 | 3822.6951 | 3985.5009 | 4389.3731 | 4144.727 | 4803.7119 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 | 5663.4822 |  |  | 85.1457 | 1167.0476 | 2174.0593 | 2698.9962 | 3124.6882 | 3529.3396 | 3873.9847 | 4233.1453 | 4390.0955 | 4604.7221 | 5003.1191 | 4871.9374 | 5392.4713 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803 | 5692.4803
70% |  |  | 110.8231 | 1163.633 | 1777.0831 | 2220.2866 | 2731.097 | 3113.0857 | 3534.4701 | 3754.8363 | 3945.7571 | 4419.3742 | 4132.48 | 4905.2654 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 | 5913.5099 |  |  |  | 640.5835 | 1821.4966 | 2437.0851 | 2936.2901 | 3410.821 | 3814.983 | 4236.1674 | 4420.2213 | 4671.912 | 5139.1083 | 4985.2728 | 5595.698 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157 | 5947.5157
65% |  |  |  | 369.7364 | 1031.4166 | 1517.0876 | 2076.8435 | 2495.4341 | 2957.1953 | 3198.6768 | 3407.8915 | 3926.8903 | 3612.5062 | 4459.3394 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 | 5564.1932 |  |  |  | 37.6543 | 1080.0858 | 1754.6596 | 2301.6981 | 2821.6983 | 3264.5868 | 3726.1288 | 3927.8186 | 4203.6261 | 4715.5889 | 4547.013 | 5215.9288 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574 | 5601.4574
60% |  |  |  |  | 139.2776 | 503.2799 | 1103.6475 | 1559.0898 | 2061.5032 | 2324.2442 | 2551.8777 | 3116.5679 | 2774.5061 | 3695.8924 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 | 4898.0148 |  |  |  |  | 165.9716 | 753.0993 | 1348.2977 | 1914.0774 | 2395.9568 | 2898.1318 | 3117.5779 | 3417.6668 | 3974.7016 | 3791.2846 | 4519.0901 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597 | 4938.5597
55% | [6 empty] | 77.2006 | 301.9799 | 707.4432 | 969.4921 | 1197.6749 | 1763.7277 | 1420.8405 | 2344.4503 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | 3549.4736 | [5 empty] | 4.0564 | 180.3574 | 572.1301 | 1041.3777 | 1544.7645 | 1764.7402 | 2065.5533 | 2623.9322 | 2440.0727 | 3169.6345 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163 | 3590.1163
50% | [9 empty] | 14.5909 | 67.2768 | 355.0439 | 154.6496 | 866.4004 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | 2273.6731 | [8 empty] | 27.1064 | 217.9999 | 355.7507 | 594.7409 | 1183.3194 | 970.2492 | 1826.1955 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531 | 2321.5531
45% | FY39: 376.3722; FY40: 376.3722; FY41: 376.3722; FY42: 376.3722; FY43: 376.3722; FY44: 376.3722; FY45: 376.3722; FY46: 376.3722; FY47: 376.3722; FY48: 376.3722; FY49: 376.3722; FY50: 376.3722; FY51: 376.3722; FY52: 376.3722; FY53: 376.3722; FY54: 376.3722 | [12 empty] | 2.1201 |  | 147.2604 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214 | 406.8214
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 201.6526 | 576.6711 | 3110.2114 | 7036.1081 | 9800.165 | 12068.132 | 14940.0983 | 17261.3111 | 19979.4193 | 21465.4746 | 22794.1564 | 26247.2855 | 24129.4693 | 30006.0367 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | 38528.1601 | E @ R (MWh) | 686.1021 | 1463.636 | 5030.2175 | 10017.6555 | 13253.356 | 16169.3978 | 19165.4946 | 21879.9737 | 24885.8013 | 26253.6541 | 28174.7879 | 31887.9362 | 30644.6052 | 35727.5141 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631 | 38833.7631
Option 8 Winter POE50 W E @ R (MWh) N 1 | 141.1569 | 403.6698 | 2177.148 | 4925.2757 | 6860.1155 | 8447.6924 | 10458.0688 | 12082.9178 | 13985.5935 | 15025.8322 | 15955.9095 | 18373.0998 | 16890.6285 | 21004.2257 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | 26969.7121 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 205.8306 | 439.0908 | 1509.0653 | 3005.2966 | 3976.0068 | 4850.8193 | 5749.6484 | 6563.9921 | 7465.7404 | 7876.0962 | 8452.4364 | 9566.3809 | 9193.3815 | 10718.2542 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289 | 11650.1289
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18.8537 | 20.9364 | 26.7753 | 30.9278 | 33.4161 | 35.4082 | 37.0239 | 38.5779 | 39.9234 | 40.5962 | 41.5902 | 42.7278 | 43.8882 | 45.3496 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752
98% | 6.2456 | 7.0779 | 9.9599 | 12.0388 | 13.1314 | 14.1103 | 14.7311 | 15.44 | 16.0064 | 16.3747 | 17.2547 | 17.8629 | 18.1819 | 18.7753 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 |  | 9.1603 | 10.1912 | 13.0813 | 15.1367 | 16.3683 | 17.3544 | 18.1541 | 18.9233 | 19.5893 | 19.9223 | 20.4143 | 20.9774 | 21.5518 | 22.2751 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868
97% | 6.0086 | 6.8325 | 9.6853 | 11.743 | 12.8246 | 13.7935 | 14.408 | 15.1097 | 15.6704 | 16.0349 | 16.906 | 17.508 | 17.8237 | 18.4112 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 |  | 17.7875 | 19.8284 | 25.5499 | 29.6189 | 32.0573 | 34.0093 | 35.5926 | 37.1153 | 38.4337 | 39.093 | 40.067 | 41.1818 | 42.3189 | 43.7509 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972
95% | 16.9597 | 19.3932 | 27.82 | 33.8982 | 37.093 | 39.9551 | 41.77 | 43.8427 | 45.4989 | 46.5757 | 49.1487 | 50.927 | 51.8597 | 53.5949 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 |  | 33.9759 | 37.9948 | 49.2618 | 57.2747 | 62.0762 | 65.9203 | 69.0381 | 72.0367 | 74.633 | 75.9313 | 77.8494 | 80.0445 | 82.2838 | 85.1038 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391
90% | 33.7676 | 39.2387 | 58.1843 | 71.8499 | 79.0325 | 85.4672 | 89.5478 | 94.2077 | 97.9313 | 100.3521 | 106.137 | 110.1351 | 112.2319 | 116.1333 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 |  | 113.4167 | 127.9383 | 168.649 | 197.6017 | 214.9512 | 228.8409 | 240.1063 | 250.9409 | 260.3224 | 265.0133 | 271.9439 | 279.8757 | 287.9668 | 298.1562 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292
85% | 43.6709 | 52.543 | 83.2656 | 105.426 | 117.0734 | 127.5082 | 134.1252 | 141.6819 | 147.7201 | 151.6458 | 161.0267 | 167.5101 | 170.9103 | 177.2369 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 |  | 118.3407 | 135.7404 | 184.5199 | 219.211 | 239.9991 | 256.6418 | 270.14 | 283.122 | 294.3629 | 299.9835 | 308.2877 | 317.7916 | 327.4862 | 339.6952 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58
80% | 120.2726 | 154.4301 | 272.7122 | 358.0296 | 402.8721 | 443.0459 | 468.5217 | 497.6149 | 520.8618 | 535.9757 | 572.0924 | 597.0532 | 610.1442 | 634.5015 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 |  | 112.6035 | 132.4627 | 188.1373 | 227.7321 | 251.4587 | 270.4538 | 285.86 | 300.6771 | 313.5069 | 319.922 | 329.4 | 340.2474 | 351.3124 | 365.2472 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984
75% | 100.3174 | 152.0501 | 331.1923 | 460.4083 | 528.3238 | 589.1684 | 627.7522 | 671.815 | 707.0232 | 729.9136 | 784.6135 | 822.4175 | 842.2443 | 879.1343 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 |  | 74.8261 | 91.8595 | 139.612 | 173.5728 | 193.9233 | 210.2155 | 223.4295 | 236.1383 | 247.1425 | 252.6448 | 260.7741 | 270.078 | 279.5685 | 291.5205 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656
70% | 24.9895 | 90.0079 | 363.6588 | 561.0443 | 664.7895 | 757.7333 | 816.6725 | 883.9811 | 937.7638 | 972.7304 | 1056.288 | 1114.0359 | 1144.3225 | 1200.6742 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 |  | 53.5318 | 71.7426 | 122.796 | 159.1043 | 180.8615 | 198.2799 | 212.4074 | 225.9946 | 237.7595 | 243.6421 | 252.3334 | 262.2803 | 272.4269 | 285.205 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777
65% |  | 0.73201 | 365.7907 | 726.2132 | 915.65 | 1085.3638 | 1192.9858 | 1315.8901 | 1414.0963 | 1477.9446 | 1630.5193 | 1735.9661 | 1791.2689 | 1894.1661 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 |  | 61.0527 | 109.0916 | 243.7669 | 339.5457 | 396.9397 | 442.8884 | 480.1556 | 515.9976 | 547.0326 | 562.5505 | 585.4776 | 611.717 | 638.4831 | 672.1908 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946
60% |  |  | 111.4336 | 738.9582 | 1107.0997 | 1436.9124 | 1646.0591 | 1884.9047 | 2075.7535 | 2199.8329 | 2496.3384 | 2701.258 | 2808.7305 | 3008.6955 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 |  | 1.6489 | 24.6112 | 168.3555 | 275.2981 | 339.3818 | 390.6862 | 432.2971 | 472.3169 | 506.9692 | 524.2958 | 549.8953 | 579.193 | 609.0789 | 646.7156 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259
55% |  |  |  | 96.2323 | 378.628 | 750.7007 | 993.1218 | 1269.9669 | 1491.179 | 1634.9989 | 1978.6772 | 2216.1987 | 2340.7696 | 2572.5483 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 |  |  |  | 78.4343 | 249.5839 | 353.8371 | 437.3006 | 504.9945 | 570.0998 | 626.4733 | 654.6607 | 696.3066 | 743.9691 | 792.5883 | 853.8167 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691
50% | [5 empty] | 29.6615 | 122.1993 | 300.2563 | 494.8265 | 645.0196 | 1046.5764 | 1326.0081 | 1472.5592 | 1745.2346 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 |  |  |  |  | 69.0686 | 206.397 | 351.033 | 469.1066 | 582.665 | 680.9932 | 730.1585 | 802.7984 | 885.9327 | 970.7356 | 1077.532 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191
45% | [10 empty] | 56.9726 | 202.4712 | 312.8424 | 577.9293 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | [6 empty] | 26.9353 | 108.8071 | 235.9916 | 382.1514 | 467.1756 | 606.501 | 772.1407 | 941.1051 | 1153.8901 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396
40% | [41 empty] | 0.54558 | 26.9538 | 93.4527 | 231.3516 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 352.2319 | 522.3053 | 1633.7029 | 3175.8418 | 4256.518 | 5373.4204 | 6161.8944 | 7134.711 | 7964.3311 | 8527.3987 | 9972.5509 | 11079.3518 | 11693.8891 | 12897.0355 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | E @ R (MWh) | 615.1978 | 782.3971 | 1408.9389 | 2043.6763 | 2521.6672 | 2965.9678 | 3387.1128 | 3840.5968 | 4269.2935 | 4495.5896 | 4844.1844 | 5275.1107 | 5754.2472 | 6411.8004 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5
Option 8 Summer POE50 W E @ R (MWh) N 1 | 246.5624 | 365.6137 | 1143.592 | 2223.0893 | 2979.5626 | 3761.3943 | 4313.3261 | 4994.2977 | 5575.0318 | 5969.1791 | 6980.7857 | 7755.5463 | 8185.7224 | 9027.9249 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 184.5593 | 234.7191 | 422.6817 | 613.1029 | 756.5002 | 889.7903 | 1016.1338 | 1152.179 | 1280.788 | 1348.6769 | 1453.2553 | 1582.5332 | 1726.2742 | 1923.5401 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 49.1893 | 51.8356 | 58.8689 | 64.7915 | 67.9845 | 70.2915 | 72.9503 | 74.9386 | 77.1319 | 78.279 | 79.2727 | 81.738 | 80.2446 | 84.2671 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 |  | 52.3542 | 55.0903 | 62.0689 | 68.2157 | 71.4199 | 74.0183 | 76.4883 | 78.592 | 80.7843 | 81.7424 | 83.0524 | 85.4842 | 84.6835 | 87.8608 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921
98% | 146.0848 | 153.9438 | 174.8318 | 192.4209 | 201.9038 | 208.7551 | 216.6514 | 222.5563 | 229.0702 | 232.4767 | 235.428 | 242.7494 | 238.3145 | 250.2605 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 |  | 155.484 | 163.6098 | 184.3354 | 202.5904 | 212.1064 | 219.8233 | 227.1588 | 233.4065 | 239.9173 | 242.7625 | 246.6532 | 253.8753 | 251.4973 | 260.9335 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372
97% | 64.2674 | 67.7249 | 76.9141 | 84.6522 | 88.824 | 91.8381 | 95.3119 | 97.9097 | 100.7754 | 102.274 | 103.5724 | 106.7933 | 104.8422 | 110.0977 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 |  | 68.4024 | 71.9773 | 81.0951 | 89.1261 | 93.3125 | 96.7074 | 99.9345 | 102.6831 | 105.5474 | 106.7991 | 108.5107 | 111.688 | 110.6418 | 114.7931 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857
95% | 158.1967 | 166.7073 | 189.3271 | 208.3746 | 218.6438 | 226.063 | 234.614 | 241.0085 | 248.0625 | 251.7514 | 254.9475 | 262.8758 | 258.0732 | 271.0097 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 |  | 168.3752 | 177.1748 | 199.6187 | 219.3872 | 229.6922 | 238.0489 | 245.9926 | 252.7583 | 259.8089 | 262.89 | 267.1033 | 274.9242 | 272.349 | 282.5676 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457
90% | 1615.7485 | 1702.6723 | 1933.7004 | 2128.2423 | 2233.1271 | 2308.9039 | 2396.2398 | 2461.5504 | 2533.5966 | 2571.2738 | 2603.9165 | 2684.8933 | 2635.8415 | 2767.9686 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 |  | 1719.7072 | 1809.5821 | 2038.8138 | 2240.7207 | 2345.971 | 2431.3227 | 2512.4557 | 2581.5574 | 2653.5695 | 2685.0381 | 2728.071 | 2807.95 | 2781.6479 | 2886.0155 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676
85% | 3806.6079 | 4011.3951 | 4555.6838 | 5014.013 | 5261.1153 | 5439.6409 | 5645.3992 | 5799.2671 | 5969.0038 | 6057.769 | 6134.6733 | 6325.4498 | 6209.8867 | 6521.1704 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 |  | 4051.5284 | 4263.2684 | 4803.3248 | 5279.0053 | 5526.969 | 5728.0525 | 5919.1971 | 6081.9965 | 6251.6527 | 6325.791 | 6427.1739 | 6615.3641 | 6553.398 | 6799.2818 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966
80% | 6892.6794 | 7263.4904 | 8249.0417 | 9078.945 | 9526.3766 | 9849.6355 | 10222.2049 | 10500.8157 | 10808.1605 | 10968.8888 | 11108.1405 | 11453.5823 | 11244.3305 | 11807.9764 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 |  | 7336.1604 | 7719.561 | 8697.4488 | 9558.7704 | 10007.7617 | 10371.8665 | 10717.9747 | 11012.758 | 11319.9569 | 11454.2002 | 11637.7756 | 11978.5342 | 11866.3313 | 12311.5567 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616
75% | 8058.556 | 8492.0887 | 9644.3432 | 10614.6221 | 11137.7355 | 11515.6728 | 11951.2611 | 12276.9981 | 12636.3294 | 12824.2444 | 12987.0502 | 13390.9224 | 13146.2763 | 13805.2613 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 |  | 8577.0505 | 9025.3023 | 10168.597 | 11175.6086 | 11700.5455 | 12126.2375 | 12530.8889 | 12875.534 | 13234.6947 | 13391.6448 | 13606.2715 | 14004.6684 | 13873.4868 | 14394.0207 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296
70% | 9450.1926 | 9958.5923 | 11309.8302 | 12447.6671 | 13061.1172 | 13504.3207 | 14015.1311 | 14397.1198 | 14818.5042 | 15038.8704 | 15229.7912 | 15703.4083 | 15416.5141 | 16189.2995 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 |  | 10058.2262 | 10583.8868 | 11924.6176 | 13105.5307 | 13721.1192 | 14220.3242 | 14694.8551 | 15099.0171 | 15520.2015 | 15704.2554 | 15955.9461 | 16423.1424 | 16269.3069 | 16879.7321 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498
65% | 10355.7039 | 10912.8181 | 12393.5307 | 13640.3944 | 14312.6249 | 14798.2959 | 15358.0518 | 15776.6424 | 16238.4036 | 16479.8851 | 16689.0998 | 17208.0986 | 16893.7145 | 17740.5476 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 |  | 11021.9989 | 11598.028 | 13067.2267 | 14361.2941 | 15035.8679 | 15582.9064 | 16102.9065 | 16545.7951 | 17007.337 | 17209.0269 | 17484.8344 | 17996.7972 | 17828.2213 | 18497.137 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657
60% | 11267.3947 | 11873.5559 | 13484.6268 | 14841.2614 | 15572.6734 | 16101.1017 | 16710.1371 | 17165.5794 | 17667.9929 | 17930.7339 | 18158.3673 | 18723.0575 | 18380.9958 | 19302.3821 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 |  | 11992.3487 | 12619.09 | 14217.6334 | 15625.6273 | 16359.589 | 16954.7874 | 17520.567 | 18002.4464 | 18504.6214 | 18724.0676 | 19024.1565 | 19581.1912 | 19397.7743 | 20125.5797 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494
55% | 11294.5848 | 11902.2087 | 13517.1674 | 14877.0758 | 15610.2528 | 16139.9562 | 16750.4614 | 17207.0028 | 17710.6286 | 17974.0037 | 18202.1864 | 18768.2393 | 18425.3521 | 19348.9619 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 |  | 12021.2882 | 12649.5419 | 14251.9428 | 15663.3344 | 16399.0673 | 16995.7021 | 17562.847 | 18045.8893 | 18549.2761 | 18769.2518 | 19070.0648 | 19628.4438 | 19444.5843 | 20174.146 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279
50% | 13305.825 | 14021.6493 | 15924.1856 | 17526.2545 | 18389.9893 | 19014.0176 | 19733.2361 | 20271.0744 | 20864.3815 | 21174.656 | 21443.4716 | 22110.3222 | 21706.3766 | 22794.4547 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 |  | 14161.9334 | 14902.061 | 16789.8034 | 18452.5232 | 19319.2689 | 20022.1471 | 20690.2843 | 21259.3424 | 21852.3679 | 22111.515 | 22465.8942 | 23123.7043 | 22907.1047 | 23766.5804 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938
45% | 16641.1386 | 17536.3955 | 19915.8324 | 21919.4849 | 22999.7283 | 23780.1792 | 24679.6811 | 25352.3369 | 26094.3658 | 26482.4155 | 26818.6139 | 27652.621 | 27147.4202 | 28508.2421 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 |  | 17711.844 | 18637.4962 | 20998.4308 | 23077.9374 | 24161.9465 | 25041.0121 | 25876.6283 | 26588.3298 | 27330.0065 | 27654.1128 | 28097.3227 | 28920.0233 | 28649.1296 | 29724.0464 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731
40% | 17620.8046 | 18568.7653 | 21088.28 | 23209.8878 | 24353.7253 | 25180.1214 | 26132.5771 | 26844.8323 | 27630.5445 | 28041.4387 | 28397.4292 | 29280.5344 | 28745.5924 | 30186.526 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 |  | 18754.5425 | 19734.688 | 22234.6112 | 24436.5385 | 25584.3634 | 26515.1798 | 27399.9888 | 28153.5883 | 28938.9275 | 29282.114 | 29751.4157 | 30622.5488 | 30335.7076 | 31473.9048 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032
35% | 7205.365 | 7592.9979 | 8623.2586 | 9490.8103 | 9958.5396 | 10296.4632 | 10685.9341 | 10977.1841 | 11298.4715 | 11466.4912 | 11612.0601 | 11973.1728 | 11754.4284 | 12343.644 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 |  | 7668.9645 | 8069.7581 | 9092.0076 | 9992.403 | 10461.7627 | 10842.3851 | 11204.1944 | 11512.3506 | 11833.4855 | 11973.8187 | 12165.722 | 12521.9391 | 12404.6462 | 12870.0691 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149
30% | 2222.5811 | 2342.1511 | 2659.9474 | 2927.5541 | 3071.8308 | 3176.0674 | 3296.2044 | 3386.0439 | 3485.1489 | 3536.9766 | 3581.879 | 3693.2686 | 3625.7942 | 3807.5448 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 |  | 2365.584 | 2489.2135 | 2804.5387 | 3082.2764 | 3227.056 | 3344.4635 | 3456.068 | 3551.1224 | 3650.1803 | 3693.4678 | 3752.6627 | 3862.5421 | 3826.3617 | 3969.927 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706
25% | 1635.9351 | 1723.9448 | 1957.8593 | 2154.8318 | 2261.0269 | 2337.7504 | 2426.1775 | 2492.3041 | 2565.2504 | 2603.3983 | 2636.4489 | 2718.4373 | 2668.7727 | 2802.5506 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 |  | 1741.1926 | 1832.1904 | 2064.286 | 2268.7154 | 2375.2807 | 2461.6987 | 2543.8454 | 2613.8104 | 2686.7222 | 2718.584 | 2762.1545 | 2843.0315 | 2816.4008 | 2922.0723 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759
20% | 1301.415 | 1371.4283 | 1557.5114 | 1714.2064 | 1798.6865 | 1859.7214 | 1930.0667 | 1982.6715 | 2040.7016 | 2071.0489 | 2097.3412 | 2162.5645 | 2123.0554 | 2229.4781 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 |  | 1385.1492 | 1457.5395 | 1642.1756 | 1804.8028 | 1889.5774 | 1958.3244 | 2023.6735 | 2079.3319 | 2137.3345 | 2162.6811 | 2197.3422 | 2261.6813 | 2240.4961 | 2324.5596 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095
15% | 1020.863 | 1075.7832 | 1221.7516 | 1344.6671 | 1410.9355 | 1458.8128 | 1513.9934 | 1555.258 | 1600.7783 | 1624.5835 | 1645.2078 | 1696.3706 | 1665.3787 | 1748.8593 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 |  | 1086.5463 | 1143.3311 | 1288.1644 | 1415.7332 | 1482.2326 | 1536.1595 | 1587.421 | 1631.0809 | 1676.5796 | 1696.4621 | 1723.6512 | 1774.1204 | 1757.5022 | 1823.4438 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491
10% | 716.8288 | 755.3926 | 857.8885 | 944.1973 | 990.7295 | 1024.348 | 1063.0946 | 1092.0698 | 1124.0332 | 1140.7487 | 1155.2307 | 1191.1561 | 1169.3942 | 1228.0126 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 |  | 762.9502 | 802.8233 | 904.5222 | 994.0984 | 1040.7929 | 1078.6592 | 1114.654 | 1145.311 | 1177.2593 | 1191.2204 | 1210.312 | 1245.7504 | 1234.0814 | 1280.3842 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708
5% | 74.1547 | 78.1441 | 88.7471 | 97.6756 | 102.4893 | 105.967 | 109.9753 | 112.9727 | 116.2793 | 118.0085 | 119.5066 | 123.223 | 120.9718 | 127.0358 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 |  | 78.9259 | 83.0507 | 93.5713 | 102.8378 | 107.6682 | 111.5854 | 115.309 | 118.4805 | 121.7854 | 123.2297 | 125.2047 | 128.8707 | 127.6636 | 132.4535 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 124904.117 | 131623.685 | 149483.1281 | 164522.0299 | 172630.0598 | 178487.9236 | 185239.3543 | 190288.1364 | 195857.6146 | 198770.2162 | 201293.6351 | 207553.4786 | 203761.5708 | 213975.5507 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | E @ R (MWh) | 132940.5564 | 139888.2644 | 157608.8341 | 173217.0768 | 181353.3711 | 187951.4123 | 194223.3331 | 199565.182 | 205132.0165 | 207564.6754 | 210891.2951 | 217066.275 | 215033.0162 | 223101.0657 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744
Option 1 Winter POE50 W E @ R (MWh) N 2 | 87432.8819 | 92136.5795 | 104638.1897 | 115165.421 | 120841.0419 | 124941.5465 | 129667.548 | 133201.6955 | 137100.3302 | 139139.1513 | 140905.5446 | 145287.435 | 142633.0996 | 149782.8855 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 39882.1669 | 41966.4793 | 47282.6502 | 51965.123 | 54406.0113 | 56385.4237 | 58266.9999 | 59869.5546 | 61539.6049 | 62269.4026 | 63267.3885 | 65119.8825 | 64509.9049 | 66930.3197 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 53.0397 | 55.1225 | 60.9613 | 65.1138 | 67.6021 | 69.5943 | 71.21 | 72.7639 | 74.1094 | 74.7822 | 75.7762 | 76.9138 | 78.0743 | 79.5357 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613
98% | 23.3386 | 24.1709 | 27.053 | 29.1318 | 30.2245 | 31.2033 | 31.8241 | 32.533 | 33.0994 | 33.4677 | 34.3477 | 34.9559 | 35.2749 | 35.8684 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 |  | 26.2533 | 27.2842 | 30.1743 | 32.2297 | 33.4614 | 34.4474 | 35.2471 | 36.0163 | 36.6823 | 37.0153 | 37.5073 | 38.0704 | 38.6448 | 39.3682 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798
97% | 23.1017 | 23.9255 | 26.7783 | 28.8361 | 29.9176 | 30.8866 | 31.501 | 32.2027 | 32.7634 | 33.1279 | 33.999 | 34.601 | 34.9168 | 35.5042 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 |  | 51.9736 | 54.0145 | 59.736 | 63.805 | 66.2433 | 68.1954 | 69.7786 | 71.3013 | 72.6198 | 73.2791 | 74.2531 | 75.3678 | 76.5049 | 77.937 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581
95% | 68.2388 | 70.6723 | 79.099 | 85.1773 | 88.372 | 91.2341 | 93.0491 | 95.1218 | 96.778 | 97.8547 | 100.4278 | 102.2061 | 103.1387 | 104.874 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 |  | 102.348 | 106.3669 | 117.6339 | 125.6468 | 130.4483 | 134.2924 | 137.4102 | 140.4088 | 143.0051 | 144.3034 | 146.2215 | 148.4166 | 150.6559 | 153.4759 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112
90% | 153.4188 | 158.8899 | 177.8355 | 191.5011 | 198.6837 | 205.1184 | 209.1989 | 213.8589 | 217.5824 | 220.0033 | 225.7882 | 229.7863 | 231.8831 | 235.7845 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 |  | 369.8121 | 384.3337 | 425.0443 | 453.9971 | 471.3466 | 485.2363 | 496.5017 | 507.3363 | 516.7178 | 521.4087 | 528.3393 | 536.2711 | 544.3621 | 554.5516 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246
85% | 248.7872 | 257.6593 | 288.3819 | 310.5423 | 322.1897 | 332.6245 | 339.2415 | 346.7982 | 352.8364 | 356.7621 | 366.143 | 372.6264 | 376.0266 | 382.3532 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 |  | 443.1082 | 460.5079 | 509.2874 | 543.9785 | 564.7666 | 581.4093 | 594.9075 | 607.8895 | 619.1304 | 624.7509 | 633.0551 | 642.5591 | 652.2537 | 664.4627 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475
80% | 957.8308 | 991.9883 | 1110.2705 | 1195.5878 | 1240.4304 | 1280.6042 | 1306.0799 | 1335.1732 | 1358.4201 | 1373.5339 | 1409.6507 | 1434.6115 | 1447.7025 | 1472.0598 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 |  | 505.7431 | 525.6023 | 581.2768 | 620.8717 | 644.5983 | 663.5934 | 678.9996 | 693.8167 | 706.6465 | 713.0616 | 722.5396 | 733.3869 | 744.452 | 758.3868 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538
75% | 1450.6665 | 1502.3991 | 1681.5413 | 1810.7574 | 1878.6729 | 1939.5174 | 1978.1012 | 2022.164 | 2057.3722 | 2080.2626 | 2134.9626 | 2172.7666 | 2192.5933 | 2229.4833 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 |  | 433.7796 | 450.813 | 498.5655 | 532.5263 | 552.8768 | 569.1691 | 582.3831 | 595.0918 | 606.096 | 611.5983 | 619.7277 | 629.0315 | 638.5221 | 650.474 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191
70% | 2215.9834 | 2295.0082 | 2568.6591 | 2766.0446 | 2869.7898 | 2962.7336 | 3021.6728 | 3088.9814 | 3142.7641 | 3177.7307 | 3261.2883 | 3319.0362 | 3349.3228 | 3405.6745 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 |  | 463.7644 | 481.9752 | 533.0286 | 569.3369 | 591.0941 | 608.5126 | 622.64 | 636.2272 | 647.9921 | 653.8747 | 662.566 | 672.5129 | 682.6595 | 695.4377 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103
65% | 4046.3465 | 4190.6445 | 4690.3262 | 5050.7487 | 5240.1855 | 5409.8993 | 5517.5213 | 5640.4256 | 5738.6318 | 5802.4801 | 5955.0548 | 6060.5016 | 6115.8044 | 6218.7016 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 |  | 1223.3785 | 1271.4174 | 1406.0926 | 1501.8715 | 1559.2654 | 1605.2142 | 1642.4813 | 1678.3234 | 1709.3584 | 1724.8763 | 1747.8034 | 1774.0427 | 1800.8088 | 1834.5166 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204
60% | 7863.4534 | 8143.8744 | 9114.9291 | 9815.3548 | 10183.4963 | 10513.309 | 10722.4557 | 10961.3013 | 11152.1501 | 11276.2295 | 11572.735 | 11777.6546 | 11885.1271 | 12085.0921 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 |  | 1365.9727 | 1419.6109 | 1569.9836 | 1676.9262 | 1741.0099 | 1792.3143 | 1833.9252 | 1873.945 | 1908.5973 | 1925.924 | 1951.5234 | 1980.8211 | 2010.707 | 2048.3437 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154
55% | 9114.4977 | 9439.5326 | 10565.0783 | 11376.9389 | 11803.6503 | 12185.9349 | 12428.356 | 12705.201 | 12926.4131 | 13070.233 | 13413.9114 | 13651.4329 | 13776.0038 | 14007.7825 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 |  | 2222.2044 | 2309.4645 | 2554.0952 | 2728.0726 | 2832.3258 | 2915.7893 | 2983.4832 | 3048.5885 | 3104.962 | 3133.1495 | 3174.7953 | 3222.4578 | 3271.077 | 3332.3054 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578
50% | 10722.7294 | 11105.1159 | 12429.2615 | 13384.3731 | 13886.3766 | 14336.1145 | 14621.3102 | 14947.0039 | 15207.2484 | 15376.4449 | 15780.7645 | 16060.1962 | 16206.7473 | 16479.4228 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 |  | 3876.0308 | 4028.2324 | 4454.9241 | 4758.3803 | 4940.2217 | 5085.8011 | 5203.8747 | 5317.4331 | 5415.7613 | 5464.9266 | 5537.5665 | 5620.7008 | 5705.5037 | 5812.3001 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872
45% | 19076.649 | 19756.9472 | 22112.715 | 23811.9398 | 24705.0469 | 25505.1688 | 26012.5564 | 26591.9932 | 27054.9902 | 27356.0054 | 28075.3244 | 28572.4571 | 28833.184 | 29318.2969 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 |  | 7722.7432 | 8025.9952 | 8876.1511 | 9480.7681 | 9843.0753 | 10133.133 | 10368.387 | 10594.6449 | 10790.5576 | 10888.5164 | 11033.2467 | 11198.8863 | 11367.8507 | 11580.6357 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852
40% | 21841.7413 | 22620.6463 | 25317.8743 | 27263.3956 | 28285.9554 | 29202.0522 | 29782.9837 | 30446.4078 | 30976.5147 | 31321.1609 | 32144.7426 | 32713.9329 | 33012.4513 | 33567.8795 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 |  | 13151.3186 | 13667.7365 | 15115.4956 | 16145.1182 | 16762.1033 | 17256.0522 | 17656.6743 | 18041.9764 | 18375.6027 | 18542.42 | 18788.8861 | 19070.9594 | 19358.6946 | 19721.0533 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938
35% | 13247.9197 | 13720.3578 | 15356.3382 | 16536.3774 | 17156.6022 | 17712.2528 | 18064.6118 | 18467.006 | 18788.5377 | 18997.5799 | 19497.1163 | 19842.3537 | 20023.4175 | 20360.3077 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 |  | 15921.911 | 16547.1229 | 18299.8818 | 19546.4153 | 20293.3809 | 20891.3902 | 21376.4114 | 21842.8853 | 22246.7967 | 22448.7575 | 22747.1467 | 23088.6444 | 23436.9969 | 23875.6938 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193
30% | 5490.4971 | 5686.2954 | 6364.3147 | 6853.3728 | 7110.4201 | 7340.7052 | 7486.7376 | 7653.5067 | 7786.7631 | 7873.399 | 8080.4279 | 8223.5089 | 8298.5494 | 8438.1709 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 |  | 24323.6426 | 25278.7685 | 27956.4296 | 29860.7384 | 31001.8655 | 31915.4345 | 32656.3934 | 33369.018 | 33986.0669 | 34294.599 | 34750.4432 | 35272.1438 | 35804.3161 | 36474.5062 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693
25% | 3277.4755 | 3394.3546 | 3799.0887 | 4091.0251 | 4244.4659 | 4381.9314 | 4469.1034 | 4568.6539 | 4648.1994 | 4699.9155 | 4823.4985 | 4908.9087 | 4953.7031 | 5037.0482 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 |  | 20684.1582 | 21496.3711 | 23773.3806 | 25392.7526 | 26363.1358 | 27140.0098 | 27770.1009 | 28376.0973 | 28900.8187 | 29163.186 | 29550.8235 | 29994.4633 | 30447.008 | 31016.9192 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015
20% | 3486.5752 | 3610.9111 | 4041.4669 | 4352.0285 | 4515.2587 | 4661.4943 | 4754.2278 | 4860.1295 | 4944.75 | 4999.7655 | 5131.233 | 5222.0923 | 5269.7445 | 5358.4069 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 |  | 5487.2123 | 5702.6808 | 6306.7389 | 6736.3352 | 6993.764 | 7199.8576 | 7367.0118 | 7527.774 | 7666.9751 | 7736.5774 | 7839.4121 | 7957.1035 | 8077.1571 | 8228.3464 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869
15% | 3611.5612 | 3740.3542 | 4186.3445 | 4508.039 | 4677.1207 | 4828.5985 | 4924.6563 | 5034.3544 | 5122.0082 | 5178.996 | 5315.1763 | 5409.2927 | 5458.6531 | 5550.4939 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 |  | 3400.2725 | 3533.7923 | 3908.1103 | 4174.3192 | 4333.8407 | 4461.5511 | 4565.1319 | 4664.7518 | 4751.0108 | 4794.1414 | 4857.8652 | 4930.7953 | 5005.1892 | 5098.877 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404
10% | 2407.9049 | 2493.774 | 2791.1252 | 3005.6058 | 3118.3361 | 3219.3296 | 3283.3734 | 3356.5115 | 3414.9522 | 3452.9471 | 3543.7415 | 3606.4909 | 3639.4005 | 3700.6327 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 |  | 972.8391 | 1011.0399 | 1118.1346 | 1194.2987 | 1239.9387 | 1276.4775 | 1306.1126 | 1334.6145 | 1359.2937 | 1371.6336 | 1389.8654 | 1410.7312 | 1432.0157 | 1458.8204 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584
5% | 191.9216 | 198.7657 | 222.4661 | 239.5612 | 248.5463 | 256.596 | 261.7006 | 267.5301 | 272.1881 | 275.2164 | 282.4532 | 287.4546 | 290.0777 | 294.9582 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 109520.6382 | 113426.2871 | 126950.9475 | 136706.3391 | 141833.7416 | 146427.3086 | 149340.263 | 152666.8581 | 155324.963 | 157053.1161 | 161182.7867 | 164036.867 | 165533.7223 | 168318.7958 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | E @ R (MWh) | 102801.5058 | 106838.2526 | 118155.1262 | 126203.5021 | 131026.3646 | 134887.4749 | 138019.0656 | 141030.9039 | 143638.8008 | 144942.7819 | 146869.3632 | 149074.2799 | 151323.4542 | 154155.9472 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242
Option 1 Summer POE50 W E @ R (MWh) N 2 | 76664.4467 | 79398.4009 | 88865.6632 | 95694.4374 | 99283.6191 | 102499.116 | 104538.1841 | 106866.8007 | 108727.4741 | 109937.1812 | 112827.9507 | 114825.8069 | 115873.6056 | 117823.1571 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 30840.4517 | 32051.4758 | 35446.5379 | 37861.0506 | 39307.9094 | 40466.2425 | 41405.7197 | 42309.2712 | 43091.6403 | 43482.8346 | 44060.809 | 44722.284 | 45397.0363 | 46246.7841 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 49.1893 | 51.8356 | 58.8689 | 64.7915 | 67.9845 | 57.428 | 60.0868 | 62.0751 | 64.2684 | 65.4155 | 66.4092 | 68.8745 | 67.3811 | 71.4036 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 | 76.6516 |  | 52.3542 | 55.0903 | 62.0689 | 68.2157 | 71.4199 | 61.1548 | 63.6248 | 65.7285 | 67.9208 | 68.8789 | 70.1889 | 72.6208 | 71.82 | 74.9974 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286 | 76.8286
98% | 146.0848 | 153.9438 | 174.8318 | 192.4209 | 201.9038 | 170.5524 | 178.4487 | 184.3536 | 190.8676 | 194.2741 | 197.2254 | 204.5468 | 200.1118 | 212.0579 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 | 227.6437 |  | 155.484 | 163.6098 | 184.3354 | 202.5904 | 212.1064 | 181.6207 | 188.9562 | 195.2038 | 201.7147 | 204.5599 | 208.4506 | 215.6727 | 213.2946 | 222.7308 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694 | 228.1694
97% | 64.2674 | 67.7249 | 76.9141 | 84.6522 | 88.824 | 75.0315 | 78.5054 | 81.1031 | 83.9688 | 85.4674 | 86.7658 | 89.9867 | 88.0357 | 93.2911 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 | 100.1478 |  | 68.4024 | 71.9773 | 81.0951 | 89.1261 | 93.3125 | 79.9008 | 83.1279 | 85.8765 | 88.7408 | 89.9925 | 91.7042 | 94.8814 | 93.8352 | 97.9865 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791 | 100.3791
95% | 158.1967 | 166.7073 | 189.3271 | 208.3746 | 218.6438 | 184.693 | 193.244 | 199.6385 | 206.6925 | 210.3814 | 213.5774 | 221.5058 | 216.7032 | 229.6396 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 | 246.5177 |  | 168.3752 | 177.1748 | 199.6187 | 219.3872 | 229.6922 | 196.6789 | 204.6226 | 211.3883 | 218.4389 | 221.52 | 225.7333 | 233.5542 | 230.979 | 241.1975 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087 | 247.087
90% | 1615.7485 | 1702.6723 | 1933.7004 | 2128.2423 | 2233.1271 | 1886.3693 | 1973.7052 | 2039.0158 | 2111.062 | 2148.7392 | 2181.3819 | 2262.3587 | 2213.3069 | 2345.4341 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 | 2517.8188 |  | 1719.7072 | 1809.5821 | 2038.8138 | 2240.7207 | 2345.971 | 2008.7881 | 2089.9211 | 2159.0228 | 2231.0349 | 2262.5035 | 2305.5364 | 2385.4154 | 2359.1133 | 2463.4809 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633 | 2523.633
85% | 3806.6079 | 4011.3951 | 4555.6838 | 5014.013 | 5261.1153 | 4444.1744 | 4649.9327 | 4803.8005 | 4973.5373 | 5062.3025 | 5139.2068 | 5329.9833 | 5214.4202 | 5525.7039 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 | 5931.8323 |  | 4051.5284 | 4263.2684 | 4803.3248 | 5279.0053 | 5526.969 | 4732.586 | 4923.7306 | 5086.53 | 5256.1862 | 5330.3245 | 5431.7074 | 5619.8975 | 5557.9315 | 5803.8153 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301 | 5945.5301
80% | 6892.6794 | 7263.4904 | 8249.0417 | 9078.945 | 9526.3766 | 8047.1301 | 8419.6995 | 8698.3103 | 9005.6551 | 9166.3834 | 9305.6351 | 9651.0769 | 9441.8251 | 10005.471 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 | 10740.8534 |  | 7336.1604 | 7719.561 | 8697.4488 | 9558.7704 | 10007.7617 | 8569.361 | 8915.4693 | 9210.2526 | 9517.4515 | 9651.6947 | 9835.2701 | 10176.0288 | 10063.8259 | 10509.0512 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562 | 10765.6562
75% | 8058.556 | 8492.0887 | 9644.3432 | 10614.6221 | 11137.7355 | 9408.2788 | 9843.8672 | 10169.6042 | 10528.9354 | 10716.8505 | 10879.6563 | 11283.5284 | 11038.8824 | 11697.8673 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 | 12557.6376 |  | 8577.0505 | 9025.3023 | 10168.597 | 11175.6086 | 11700.5455 | 10018.8436 | 10423.495 | 10768.14 | 11127.3007 | 11284.2508 | 11498.8775 | 11897.2745 | 11766.0928 | 12286.6267 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357 | 12586.6357
70% | 9450.1926 | 9958.5923 | 11309.8302 | 12447.6671 | 13061.1172 | 11032.9997 | 11543.8101 | 11925.7988 | 12347.1831 | 12567.5494 | 12758.4702 | 13232.0873 | 12945.1931 | 13717.9785 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 | 14726.223 |  | 10058.2262 | 10583.8868 | 11924.6176 | 13105.5307 | 13721.1192 | 11749.0032 | 12223.5341 | 12627.6961 | 13048.8805 | 13232.9344 | 13484.6251 | 13951.8214 | 13797.9859 | 14408.4111 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288 | 14760.2288
65% | 10355.7039 | 10912.8181 | 12393.5307 | 13640.3944 | 14312.6249 | 12090.1745 | 12649.9304 | 13068.521 | 13530.2822 | 13771.7637 | 13980.9784 | 14499.9772 | 14185.5931 | 15032.4263 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 | 16137.2801 |  | 11021.9989 | 11598.028 | 13067.2267 | 14361.2941 | 15035.8679 | 12874.7851 | 13394.7852 | 13837.6737 | 14299.2157 | 14500.9055 | 14776.713 | 15288.6758 | 15120.0999 | 15789.0157 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443 | 16174.5443
60% | 11267.3947 | 11873.5559 | 13484.6268 | 14841.2614 | 15572.6734 | 13154.5639 | 13763.5994 | 14219.0417 | 14721.4551 | 14984.1961 | 15211.8296 | 15776.5198 | 15434.458 | 16355.8443 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 | 17557.9667 |  | 11992.3487 | 12619.09 | 14217.6334 | 15625.6273 | 16359.589 | 14008.2496 | 14574.0293 | 15055.9087 | 15558.0836 | 15777.5298 | 16077.6187 | 16634.6535 | 16451.2365 | 17179.042 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116 | 17598.5116
55% | 11294.5848 | 11902.2087 | 13517.1674 | 14877.0758 | 15610.2528 | 13186.308 | 13796.8132 | 14253.3545 | 14756.9804 | 15020.3554 | 15248.5382 | 15814.5911 | 15471.7039 | 16395.3136 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 | 17600.337 |  | 12021.2882 | 12649.5419 | 14251.9428 | 15663.3344 | 16399.0673 | 14042.0538 | 14609.1988 | 15092.241 | 15595.6278 | 15815.6035 | 16116.4166 | 16674.7956 | 16490.936 | 17220.4978 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797 | 17640.9797
50% | 13305.825 | 14021.6493 | 15924.1856 | 17526.2545 | 18389.9893 | 15534.4097 | 16253.6282 | 16791.4665 | 17384.7736 | 17695.0481 | 17963.8637 | 18630.7143 | 18226.7687 | 19314.8468 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 | 20734.4501 |  | 14161.9334 | 14902.061 | 16789.8034 | 18452.5232 | 19319.2689 | 16542.5392 | 17210.6763 | 17779.7345 | 18372.76 | 18631.907 | 18986.2862 | 19644.0964 | 19427.4968 | 20286.9725 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301 | 20782.3301
45% | 16641.1386 | 17536.3955 | 19915.8324 | 21919.4849 | 22999.7283 | 19428.353 | 20327.8549 | 21000.5108 | 21742.5396 | 22130.5893 | 22466.7877 | 23300.7949 | 22795.594 | 24156.4159 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 | 25931.865 |  | 17711.844 | 18637.4962 | 20998.4308 | 23077.9374 | 24161.9465 | 20689.186 | 21524.8022 | 22236.5037 | 22978.1803 | 23302.2866 | 23745.4965 | 24568.1971 | 24297.3034 | 25372.2202 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469 | 25991.7469
40% | 17620.8046 | 18568.7653 | 21088.28 | 23209.8878 | 24353.7253 | 20572.1027 | 21524.5584 | 22236.8135 | 23022.5257 | 23433.42 | 23789.4104 | 24672.5157 | 24137.5736 | 25578.5072 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 | 27458.4772 |  | 18754.5425 | 19734.688 | 22234.6112 | 24436.5385 | 25584.3634 | 21907.161 | 22791.97 | 23545.5695 | 24330.9087 | 24674.0952 | 25143.397 | 26014.5301 | 25727.6888 | 26865.8861 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844 | 27521.8844
35% | 7205.365 | 7592.9979 | 8623.2586 | 9490.8103 | 9958.5396 | 8412.1873 | 8801.6582 | 9092.9082 | 9414.1956 | 9582.2154 | 9727.7843 | 10088.8969 | 9870.1525 | 10459.3681 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 | 11228.1111 |  | 7668.9645 | 8069.7581 | 9092.0076 | 9992.403 | 10461.7627 | 8958.1092 | 9319.9185 | 9628.0747 | 9949.2096 | 10089.5428 | 10281.4461 | 10637.6632 | 10520.3703 | 10985.7932 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391 | 11254.0391
30% | 2222.5811 | 2342.1511 | 2659.9474 | 2927.5541 | 3071.8308 | 2594.8399 | 2714.9769 | 2804.8164 | 2903.9214 | 2955.7491 | 3000.6516 | 3112.0411 | 3044.5668 | 3226.3174 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 | 3463.4454 |  | 2365.584 | 2489.2135 | 2804.5387 | 3082.2764 | 3227.056 | 2763.2361 | 2874.8405 | 2969.895 | 3068.9529 | 3112.2403 | 3171.4352 | 3281.3146 | 3245.1342 | 3388.6995 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431 | 3471.4431
25% | 1635.9351 | 1723.9448 | 1957.8593 | 2154.8318 | 2261.0269 | 1909.9369 | 1998.3639 | 2064.4905 | 2137.4369 | 2175.5847 | 2208.6353 | 2290.6238 | 2240.9591 | 2374.737 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 | 2549.2755 |  | 1741.1926 | 1832.1904 | 2064.286 | 2268.7154 | 2375.2807 | 2033.8852 | 2116.0318 | 2185.9968 | 2258.9086 | 2290.7704 | 2334.3409 | 2415.2179 | 2388.5872 | 2494.2587 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623 | 2555.1623
20% | 1301.415 | 1371.4283 | 1557.5114 | 1714.2064 | 1798.6865 | 1519.3882 | 1589.7335 | 1642.3383 | 1700.3684 | 1730.7157 | 1757.008 | 1822.2313 | 1782.7222 | 1889.1449 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 | 2027.9933 |  | 1385.1492 | 1457.5395 | 1642.1756 | 1804.8028 | 1889.5774 | 1617.9912 | 1683.3403 | 1738.9987 | 1797.0013 | 1822.348 | 1857.009 | 1921.3481 | 1900.1629 | 1984.2265 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764 | 2032.6764
15% | 1020.863 | 1075.7832 | 1221.7516 | 1344.6671 | 1410.9355 | 1191.8468 | 1247.0274 | 1288.292 | 1333.8123 | 1357.6175 | 1378.2418 | 1429.4046 | 1398.4127 | 1481.8933 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 | 1590.8096 |  | 1086.5463 | 1143.3311 | 1288.1644 | 1415.7332 | 1482.2326 | 1269.1935 | 1320.455 | 1364.1149 | 1409.6136 | 1429.4961 | 1456.6852 | 1507.1543 | 1490.5362 | 1556.4777 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831 | 1594.4831
10% | 716.8288 | 755.3926 | 857.8885 | 944.1973 | 990.7295 | 836.89 | 875.6367 | 904.6118 | 936.5752 | 953.2907 | 967.7727 | 1003.6981 | 981.9363 | 1040.5546 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 | 1117.0333 |  | 762.9502 | 802.8233 | 904.5222 | 994.0984 | 1040.7929 | 891.2013 | 927.196 | 957.8531 | 989.8013 | 1003.7624 | 1022.854 | 1058.2924 | 1046.6235 | 1092.9263 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128 | 1119.6128
5% | 74.1547 | 78.1441 | 88.7471 | 97.6756 | 102.4893 | 86.5748 | 90.5831 | 93.5805 | 96.8871 | 98.6163 | 100.1144 | 103.8308 | 101.5796 | 107.6436 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 | 115.5552 |  | 78.9259 | 83.0507 | 93.5713 | 102.8378 | 107.6682 | 92.1932 | 95.9168 | 99.0882 | 102.3932 | 103.8375 | 105.8125 | 109.4785 | 108.2714 | 113.0613 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822 | 115.822
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 124904.117 | 131623.685 | 149483.1281 | 164522.0299 | 172630.0598 | 145824.2328 | 152575.6635 | 157624.4456 | 163193.9238 | 166106.5253 | 168629.9443 | 174889.7878 | 171097.88 | 181311.8599 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | 194637.9253 | E @ R (MWh) | 132940.5564 | 139888.2644 | 157608.8341 | 173217.0768 | 181353.3711 | 155287.7215 | 161559.6423 | 166901.4912 | 172468.3256 | 174900.9846 | 178227.6043 | 184402.5842 | 182369.3254 | 190437.3749 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836 | 195087.3836
Option 2 Winter POE50 W E @ R (MWh) N 2 | 87432.8819 | 92136.5795 | 104638.1897 | 115165.421 | 120841.0419 | 102076.963 | 106802.9645 | 110337.1119 | 114235.7466 | 116274.5677 | 118040.961 | 122422.8515 | 119768.516 | 126918.3019 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | 136246.5477 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 39882.1669 | 41966.4793 | 47282.6502 | 51965.123 | 54406.0113 | 46586.3164 | 48467.8927 | 50070.4474 | 51740.4977 | 52470.2954 | 53468.2813 | 55320.7752 | 54710.7976 | 57131.2125 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151 | 58526.2151
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 53.0397 | 55.1225 | 60.9613 | 65.1138 | 67.6021 | 58.6823 | 60.298 | 61.852 | 63.1975 | 63.8703 | 64.8643 | 66.0019 | 67.1624 | 68.6238 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494 | 68.8494
98% | 23.3386 | 24.1709 | 27.053 | 29.1318 | 30.2245 | 25.8022 | 26.423 | 27.1318 | 27.6983 | 28.0665 | 28.9466 | 29.5548 | 29.8737 | 30.4672 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 | 30.2926 |  | 26.2533 | 27.2842 | 30.1743 | 32.2297 | 33.4614 | 29.0463 | 29.846 | 30.6152 | 31.2812 | 31.6142 | 32.1062 | 32.6693 | 33.2437 | 33.967 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787 | 34.0787
97% | 23.1017 | 23.9255 | 26.7783 | 28.8361 | 29.9176 | 25.5403 | 26.1547 | 26.8564 | 27.4171 | 27.7816 | 28.6527 | 29.2547 | 29.5705 | 30.1579 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 | 29.985 |  | 51.9736 | 54.0145 | 59.736 | 63.805 | 66.2433 | 57.5028 | 59.086 | 60.6087 | 61.9272 | 62.5865 | 63.5605 | 64.6752 | 65.8124 | 67.2444 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655 | 67.4655
95% | 68.2388 | 70.6723 | 79.099 | 85.1773 | 88.372 | 75.442 | 77.257 | 79.3297 | 80.9858 | 82.0626 | 84.6357 | 86.4139 | 87.3466 | 89.0819 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 | 88.5712 |  | 102.348 | 106.3669 | 117.6339 | 125.6468 | 130.4483 | 113.2362 | 116.354 | 119.3526 | 121.949 | 123.2472 | 125.1653 | 127.3605 | 129.5997 | 132.4197 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551 | 132.8551
90% | 153.4188 | 158.8899 | 177.8355 | 191.5011 | 198.6837 | 169.6135 | 173.694 | 178.354 | 182.0775 | 184.4984 | 190.2833 | 194.2814 | 196.3782 | 200.2796 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 | 199.1315 |  | 369.8121 | 384.3337 | 425.0443 | 453.9971 | 471.3466 | 409.1544 | 420.4198 | 431.2544 | 440.6359 | 445.3268 | 452.2573 | 460.1892 | 468.2802 | 478.4697 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427 | 480.0427
85% | 248.7872 | 257.6593 | 288.3819 | 310.5423 | 322.1897 | 275.049 | 281.666 | 289.2227 | 295.2609 | 299.1866 | 308.5675 | 315.0508 | 318.4511 | 324.7777 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 | 322.9159 |  | 443.1082 | 460.5079 | 509.2874 | 543.9785 | 564.7666 | 490.248 | 503.7462 | 516.7282 | 527.9691 | 533.5897 | 541.8939 | 551.3978 | 561.0925 | 573.3015 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863 | 575.1863
80% | 957.8308 | 991.9883 | 1110.2705 | 1195.5878 | 1240.4304 | 1058.9385 | 1084.4142 | 1113.5075 | 1136.7544 | 1151.8682 | 1187.9849 | 1212.9458 | 1226.0368 | 1250.3941 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 | 1243.2261 |  | 505.7431 | 525.6023 | 581.2768 | 620.8717 | 644.5983 | 559.5463 | 574.9525 | 589.7695 | 602.5993 | 609.0144 | 618.4924 | 629.3398 | 640.4048 | 654.3396 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908 | 656.4908
75% | 1450.6665 | 1502.3991 | 1681.5413 | 1810.7574 | 1878.6729 | 1603.7973 | 1642.3812 | 1686.4439 | 1721.6521 | 1744.5425 | 1799.2425 | 1837.0465 | 1856.8732 | 1893.7632 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 | 1882.9071 |  | 433.7796 | 450.813 | 498.5655 | 532.5263 | 552.8768 | 479.927 | 493.141 | 505.8497 | 516.854 | 522.3562 | 530.4856 | 539.7894 | 549.28 | 561.232 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771 | 563.0771
70% | 2215.9834 | 2295.0082 | 2568.6591 | 2766.0446 | 2869.7898 | 2449.9003 | 2508.8395 | 2576.1481 | 2629.9308 | 2664.8974 | 2748.4549 | 2806.2029 | 2836.4895 | 2892.8412 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 | 2876.2578 |  | 463.7644 | 481.9752 | 533.0286 | 569.3369 | 591.0941 | 513.1017 | 527.2291 | 540.8163 | 552.5812 | 558.4638 | 567.1551 | 577.1021 | 587.2487 | 600.0268 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995 | 601.9995
65% | 4046.3465 | 4190.6445 | 4690.3262 | 5050.7487 | 5240.1855 | 4473.4748 | 4581.0967 | 4704.001 | 4802.2073 | 4866.0556 | 5018.6302 | 5124.077 | 5179.3798 | 5282.277 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 | 5251.996 |  | 1223.3785 | 1271.4174 | 1406.0926 | 1501.8715 | 1559.2654 | 1353.5269 | 1390.7941 | 1426.6362 | 1457.6712 | 1473.189 | 1496.1161 | 1522.3555 | 1549.1216 | 1582.8293 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331 | 1588.0331
60% | 7863.4534 | 8143.8744 | 9114.9291 | 9815.3548 | 10183.4963 | 8693.5116 | 8902.6583 | 9141.5039 | 9332.3527 | 9456.4321 | 9752.9376 | 9957.8572 | 10065.3296 | 10265.2947 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 | 10206.4482 |  | 1365.9727 | 1419.6109 | 1569.9836 | 1676.9262 | 1741.0099 | 1511.291 | 1552.9019 | 1592.9216 | 1627.574 | 1644.9006 | 1670.5 | 1699.7978 | 1729.6837 | 1767.3203 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307 | 1773.1307
55% | 9114.4977 | 9439.5326 | 10565.0783 | 11376.9389 | 11803.6503 | 10076.6149 | 10319.036 | 10595.881 | 10817.0931 | 10960.913 | 11304.5914 | 11542.1129 | 11666.6838 | 11898.4624 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 | 11830.2537 |  | 2222.2044 | 2309.4645 | 2554.0952 | 2728.0726 | 2832.3258 | 2458.6124 | 2526.3063 | 2591.4115 | 2647.785 | 2675.9725 | 2717.6183 | 2765.2808 | 2813.9 | 2875.1285 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808 | 2884.5808
50% | 10722.7294 | 11105.1159 | 12429.2615 | 13384.3731 | 13886.3766 | 11854.6099 | 12139.8056 | 12465.4993 | 12725.7438 | 12894.9404 | 13299.26 | 13578.6916 | 13725.2427 | 13997.9182 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 | 13917.6742 |  | 3876.0308 | 4028.2324 | 4454.9241 | 4758.3803 | 4940.2217 | 4288.3802 | 4406.4538 | 4520.0122 | 4618.3405 | 4667.5058 | 4740.1457 | 4823.2799 | 4908.0828 | 5014.8792 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663 | 5031.3663
45% | 19076.649 | 19756.9472 | 22112.715 | 23811.9398 | 24705.0469 | 21090.3608 | 21597.7483 | 22177.1851 | 22640.1822 | 22941.1973 | 23660.5163 | 24157.649 | 24418.376 | 24903.4888 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 | 24760.7279 |  | 7722.7432 | 8025.9952 | 8876.1511 | 9480.7681 | 9843.0753 | 8544.323 | 8779.5771 | 9005.835 | 9201.7476 | 9299.7064 | 9444.4367 | 9610.0764 | 9779.0408 | 9991.8258 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753 | 10024.6753
40% | 21841.7413 | 22620.6463 | 25317.8743 | 27263.3956 | 28285.9554 | 24147.3334 | 24728.265 | 25391.6891 | 25921.796 | 26266.4422 | 27090.0239 | 27659.2142 | 27957.7326 | 28513.1608 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 | 28349.7072 |  | 13151.3186 | 13667.7365 | 15115.4956 | 16145.1182 | 16762.1033 | 14550.4144 | 14951.0364 | 15336.3386 | 15669.9649 | 15836.7822 | 16083.2483 | 16365.3216 | 16653.0568 | 17015.4154 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559 | 17071.3559
35% | 13247.9197 | 13720.3578 | 15356.3382 | 16536.3774 | 17156.6022 | 14646.3568 | 14998.7158 | 15401.1099 | 15722.6417 | 15931.6839 | 16431.2202 | 16776.4577 | 16957.5215 | 17294.4117 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 | 17195.2703 |  | 15921.911 | 16547.1229 | 18299.8818 | 19546.4153 | 20293.3809 | 17615.7548 | 18100.776 | 18567.2499 | 18971.1613 | 19173.1221 | 19471.5113 | 19813.009 | 20161.3615 | 20600.0584 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839 | 20667.7839
30% | 5490.4971 | 5686.2954 | 6364.3147 | 6853.3728 | 7110.4201 | 6070.0684 | 6216.1009 | 6382.87 | 6516.1263 | 6602.7622 | 6809.7912 | 6952.8722 | 7027.9127 | 7167.5342 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 | 7126.4458 |  | 24323.6426 | 25278.7685 | 27956.4296 | 29860.7384 | 31001.8655 | 26911.3 | 27652.2589 | 28364.8835 | 28981.9323 | 29290.4645 | 29746.3087 | 30268.0093 | 30800.1816 | 31470.3716 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348 | 31573.8348
25% | 3277.4755 | 3394.3546 | 3799.0887 | 4091.0251 | 4244.4659 | 3623.4425 | 3710.6146 | 3810.165 | 3889.7105 | 3941.4266 | 4065.0097 | 4150.4199 | 4195.2142 | 4278.5593 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 | 4254.0322 |  | 20684.1582 | 21496.3711 | 23773.3806 | 25392.7526 | 26363.1358 | 22884.6311 | 23514.7222 | 24120.7186 | 24645.44 | 24907.8073 | 25295.4448 | 25739.0846 | 26191.6293 | 26761.5405 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228 | 26849.5228
20% | 3486.5752 | 3610.9111 | 4041.4669 | 4352.0285 | 4515.2587 | 3854.6146 | 3947.3481 | 4053.2499 | 4137.8703 | 4192.8858 | 4324.3533 | 4415.2126 | 4462.8648 | 4551.5273 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 | 4525.4353 |  | 5487.2123 | 5702.6808 | 6306.7389 | 6736.3352 | 6993.764 | 6070.9663 | 6238.1205 | 6398.8827 | 6538.0838 | 6607.6861 | 6710.5208 | 6828.2122 | 6948.2658 | 7099.4551 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956 | 7122.7956
15% | 3611.5612 | 3740.3542 | 4186.3445 | 4508.039 | 4677.1207 | 3992.794 | 4088.8518 | 4198.5498 | 4286.2037 | 4343.1914 | 4479.3718 | 4573.4882 | 4622.8486 | 4714.6894 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 | 4687.6621 |  | 3400.2725 | 3533.7923 | 3908.1103 | 4174.3192 | 4333.8407 | 3762.0086 | 3865.5894 | 3965.2093 | 4051.4684 | 4094.599 | 4158.3227 | 4231.2528 | 4305.6467 | 4399.3345 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979 | 4413.7979
10% | 2407.9049 | 2493.774 | 2791.1252 | 3005.6058 | 3118.3361 | 2662.0809 | 2726.1247 | 2799.2628 | 2857.7035 | 2895.6984 | 2986.4927 | 3049.2421 | 3082.1518 | 3143.384 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 | 3125.3644 |  | 972.8391 | 1011.0399 | 1118.1346 | 1194.2987 | 1239.9387 | 1076.334 | 1105.9692 | 1134.471 | 1159.1503 | 1171.4902 | 1189.722 | 1210.5877 | 1231.8723 | 1258.6769 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815 | 1262.815
5% | 191.9216 | 198.7657 | 222.4661 | 239.5612 | 248.5463 | 212.1806 | 217.2852 | 223.1147 | 227.7727 | 230.8011 | 238.0378 | 243.0392 | 245.6623 | 250.5428 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 | 249.1065 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 109520.6382 | 113426.2871 | 126950.9475 | 136706.3391 | 141833.7416 | 121081.5262 | 123994.4806 | 127321.0757 | 129979.1807 | 131707.3337 | 135837.0043 | 138691.0846 | 140187.94 | 142973.0134 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | 142153.411 | E @ R (MWh) | 102801.5058 | 106838.2526 | 118155.1262 | 126203.5021 | 131026.3646 | 113737.9878 | 116869.5785 | 119881.4168 | 122489.3137 | 123793.2947 | 125719.8761 | 127924.7928 | 130173.9671 | 133006.46 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371 | 133443.7371
Option 2 Summer POE50 W E @ R (MWh) N 2 | 76664.4467 | 79398.4009 | 88865.6632 | 95694.4374 | 99283.6191 | 84757.0684 | 86796.1364 | 89124.753 | 90985.4265 | 92195.1336 | 95085.903 | 97083.7592 | 98131.558 | 100081.1094 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | 99507.3877 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 30840.4517 | 32051.4758 | 35446.5379 | 37861.0506 | 39307.9094 | 34121.3963 | 35060.8736 | 35964.425 | 36746.7941 | 37137.9884 | 37715.9628 | 38377.4378 | 39052.1901 | 39901.938 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211 | 40033.1211
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 49.1893 | 51.8356 | 58.8689 | 51.928 | 55.121 | 44.5645 | 47.2233 | 49.2116 | 51.4049 | 52.552 | 53.5457 | 56.011 | 54.5176 | 58.5401 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 |  | 52.3542 | 55.0903 | 62.0689 | 55.3522 | 58.5564 | 48.2913 | 50.7613 | 52.865 | 55.0574 | 56.0154 | 57.3255 | 59.7573 | 58.9565 | 62.1339 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651
98% | 146.0848 | 153.9438 | 174.8318 | 154.2182 | 163.7012 | 132.3498 | 140.2461 | 146.151 | 152.6649 | 156.0714 | 159.0228 | 166.3441 | 161.9092 | 173.8552 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 |  | 155.484 | 163.6098 | 184.3354 | 164.3878 | 173.9038 | 143.418 | 150.7535 | 157.0012 | 163.512 | 166.3572 | 170.2479 | 177.47 | 175.092 | 184.5282 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667
97% | 64.2674 | 67.7249 | 76.9141 | 67.8456 | 72.0174 | 58.2249 | 61.6988 | 64.2965 | 67.1622 | 68.6609 | 69.9593 | 73.1802 | 71.2291 | 76.4845 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 |  | 68.4024 | 71.9773 | 81.0951 | 72.3195 | 76.5059 | 63.0942 | 66.3213 | 69.0699 | 71.9342 | 73.1859 | 74.8976 | 78.0748 | 77.0286 | 81.1799 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725
95% | 158.1967 | 166.7073 | 189.3271 | 167.0045 | 177.2737 | 143.3229 | 151.8739 | 158.2684 | 165.3224 | 169.0114 | 172.2074 | 180.1358 | 175.3331 | 188.2696 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 |  | 168.3752 | 177.1748 | 199.6187 | 178.0172 | 188.3222 | 155.3089 | 163.2525 | 170.0182 | 177.0689 | 180.1499 | 184.3633 | 192.1841 | 189.6089 | 199.8275 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169
90% | 1615.7485 | 1702.6723 | 1933.7004 | 1705.7077 | 1810.5925 | 1463.8347 | 1551.1706 | 1616.4812 | 1688.5275 | 1726.2046 | 1758.8473 | 1839.8241 | 1790.7723 | 1922.8995 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 |  | 1719.7072 | 1809.5821 | 2038.8138 | 1818.1861 | 1923.4364 | 1586.2535 | 1667.3865 | 1736.4882 | 1808.5003 | 1839.969 | 1883.0018 | 1962.8808 | 1936.5787 | 2040.9463 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984
85% | 3806.6079 | 4011.3951 | 4555.6838 | 4018.5465 | 4265.6488 | 3448.7079 | 3654.4661 | 3808.334 | 3978.0708 | 4066.836 | 4143.7403 | 4334.5168 | 4218.9537 | 4530.2374 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 |  | 4051.5284 | 4263.2684 | 4803.3248 | 4283.5388 | 4531.5025 | 3737.1195 | 3928.264 | 4091.0635 | 4260.7197 | 4334.858 | 4436.2409 | 4624.431 | 4562.465 | 4808.3488 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636
80% | 6892.6794 | 7263.4904 | 8249.0417 | 7276.4395 | 7723.8711 | 6244.6247 | 6617.1941 | 6895.8049 | 7203.1496 | 7363.878 | 7503.1297 | 7848.5714 | 7639.3197 | 8202.9656 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 |  | 7336.1604 | 7719.561 | 8697.4488 | 7756.2649 | 8205.2563 | 6766.8556 | 7112.9638 | 7407.7472 | 7714.946 | 7849.1893 | 8032.7647 | 8373.5234 | 8261.3205 | 8706.5458 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508
75% | 8058.556 | 8492.0887 | 9644.3432 | 8507.2281 | 9030.3415 | 7300.8848 | 7736.4732 | 8062.2102 | 8421.5414 | 8609.4565 | 8772.2623 | 9176.1345 | 8931.4884 | 9590.4733 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 |  | 8577.0505 | 9025.3023 | 10168.597 | 9068.2146 | 9593.1515 | 7911.4496 | 8316.101 | 8660.7461 | 9019.9067 | 9176.8569 | 9391.4835 | 9789.8805 | 9658.6988 | 10179.2327 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417
70% | 9450.1926 | 9958.5923 | 11309.8302 | 9976.3461 | 10589.7962 | 8561.6787 | 9072.4891 | 9454.4778 | 9875.8621 | 10096.2283 | 10287.1491 | 10760.7663 | 10473.8721 | 11246.6575 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 |  | 10058.2262 | 10583.8868 | 11924.6176 | 10634.2097 | 11249.7982 | 9277.6822 | 9752.2131 | 10156.3751 | 10577.5595 | 10761.6134 | 11013.304 | 11480.5004 | 11326.6649 | 11937.0901 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078
65% | 10355.7039 | 10912.8181 | 12393.5307 | 10932.2731 | 11604.5035 | 9382.0531 | 9941.809 | 10360.3997 | 10822.1608 | 11063.6423 | 11272.8571 | 11791.8559 | 11477.4717 | 12324.3049 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 |  | 11021.9989 | 11598.028 | 13067.2267 | 11653.1727 | 12327.7466 | 10166.6637 | 10686.6638 | 11129.5523 | 11591.0943 | 11792.7842 | 12068.5916 | 12580.5545 | 12411.9785 | 13080.8943 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229
60% | 11267.3947 | 11873.5559 | 13484.6268 | 11894.7236 | 12626.1357 | 10208.0262 | 10817.0616 | 11272.5039 | 11774.9174 | 12037.6584 | 12265.2918 | 12829.982 | 12487.9202 | 13409.3066 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 |  | 11992.3487 | 12619.09 | 14217.6334 | 12679.0895 | 13413.0512 | 11061.7119 | 11627.4915 | 12109.3709 | 12611.5459 | 12830.992 | 13131.0809 | 13688.1157 | 13504.6988 | 14232.5042 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739
55% | 11294.5848 | 11902.2087 | 13517.1674 | 11923.4275 | 12656.6046 | 10232.6598 | 10843.1649 | 11299.7063 | 11803.3322 | 12066.7072 | 12294.89 | 12860.9428 | 12518.0556 | 13441.6654 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 |  | 12021.2882 | 12649.5419 | 14251.9428 | 12709.6862 | 13445.4191 | 11088.4056 | 11655.5506 | 12138.5928 | 12641.9796 | 12861.9553 | 13162.7684 | 13721.1473 | 13537.2878 | 14266.8496 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315
50% | 13305.825 | 14021.6493 | 15924.1856 | 14046.6466 | 14910.3813 | 12054.8018 | 12774.0203 | 13311.8585 | 13905.1657 | 14215.4402 | 14484.2558 | 15151.1064 | 14747.1608 | 15835.2389 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 |  | 14161.9334 | 14902.061 | 16789.8034 | 14972.9153 | 15839.661 | 13062.9313 | 13731.0684 | 14300.1266 | 14893.1521 | 15152.2991 | 15506.6783 | 16164.4885 | 15947.8889 | 16807.3646 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222
45% | 16641.1386 | 17536.3955 | 19915.8324 | 17567.6587 | 18647.9022 | 15076.5268 | 15976.0287 | 16648.6846 | 17390.7134 | 17778.7631 | 18114.9615 | 18948.9687 | 18443.7678 | 19804.5897 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 |  | 17711.844 | 18637.4962 | 20998.4308 | 18726.1112 | 19810.1203 | 16337.3598 | 17172.976 | 17884.6775 | 18626.3541 | 18950.4604 | 19393.6703 | 20216.3709 | 19945.4772 | 21020.394 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207
40% | 17620.8046 | 18568.7653 | 21088.28 | 18601.8691 | 19745.7066 | 15964.0839 | 16916.5396 | 17628.7948 | 18414.507 | 18825.4012 | 19181.3917 | 20064.4969 | 19529.5548 | 20970.4885 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 |  | 18754.5425 | 19734.688 | 22234.6112 | 19828.5198 | 20976.3446 | 17299.1422 | 18183.9513 | 18937.5507 | 19722.89 | 20066.0765 | 20535.3782 | 21406.5113 | 21119.6701 | 22257.8673 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657
35% | 7205.365 | 7592.9979 | 8623.2586 | 7606.5344 | 8074.2637 | 6527.9114 | 6917.3824 | 7208.6323 | 7529.9197 | 7697.9395 | 7843.5084 | 8204.621 | 7985.8766 | 8575.0922 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 |  | 7668.9645 | 8069.7581 | 9092.0076 | 8108.1271 | 8577.4869 | 7073.8333 | 7435.6427 | 7743.7988 | 8064.9337 | 8205.2669 | 8397.1702 | 8753.3873 | 8636.0944 | 9101.5173 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632
30% | 2222.5811 | 2342.1511 | 2659.9474 | 2346.3267 | 2490.6034 | 2013.6125 | 2133.7494 | 2223.589 | 2322.6939 | 2374.5216 | 2419.4241 | 2530.8136 | 2463.3393 | 2645.0899 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 |  | 2365.584 | 2489.2135 | 2804.5387 | 2501.0489 | 2645.8286 | 2182.0086 | 2293.613 | 2388.6675 | 2487.7254 | 2531.0129 | 2590.2077 | 2700.0872 | 2663.9068 | 2807.472 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157
25% | 1635.9351 | 1723.9448 | 1957.8593 | 1727.0182 | 1833.2133 | 1482.1233 | 1570.5503 | 1636.6769 | 1709.6233 | 1747.7712 | 1780.8217 | 1862.8102 | 1813.1456 | 1946.9234 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 |  | 1741.1926 | 1832.1904 | 2064.286 | 1840.9018 | 1947.4671 | 1606.0716 | 1688.2182 | 1758.1833 | 1831.095 | 1862.9568 | 1906.5273 | 1987.4043 | 1960.7736 | 2066.4451 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487
20% | 1301.415 | 1371.4283 | 1557.5114 | 1373.8732 | 1458.3533 | 1179.055 | 1249.4003 | 1302.0051 | 1360.0352 | 1390.3826 | 1416.6748 | 1481.8981 | 1442.389 | 1548.8117 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 |  | 1385.1492 | 1457.5395 | 1642.1756 | 1464.4696 | 1549.2442 | 1277.6581 | 1343.0072 | 1398.6655 | 1456.6681 | 1482.0148 | 1516.6759 | 1581.0149 | 1559.8297 | 1643.8933 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432
15% | 1020.863 | 1075.7832 | 1221.7516 | 1077.7011 | 1143.9694 | 924.8808 | 980.0614 | 1021.3259 | 1066.8463 | 1090.6515 | 1111.2758 | 1162.4386 | 1131.4467 | 1214.9273 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 |  | 1086.5463 | 1143.3311 | 1288.1644 | 1148.7672 | 1215.2666 | 1002.2275 | 1053.489 | 1097.1489 | 1142.6476 | 1162.5301 | 1189.7191 | 1240.1883 | 1223.5701 | 1289.5117 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517
10% | 716.8288 | 755.3926 | 857.8885 | 756.7393 | 803.2715 | 649.432 | 688.1787 | 717.1538 | 749.1172 | 765.8327 | 780.3147 | 816.2402 | 794.4783 | 853.0967 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 |  | 762.9502 | 802.8233 | 904.5222 | 806.6404 | 853.3349 | 703.7433 | 739.738 | 770.3951 | 802.3433 | 816.3044 | 835.396 | 870.8344 | 859.1655 | 905.4683 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548
5% | 74.1547 | 78.1441 | 88.7471 | 78.2834 | 83.0971 | 67.1826 | 71.1909 | 74.1883 | 77.4949 | 79.2241 | 80.7222 | 84.4386 | 82.1874 | 88.2514 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 |  | 78.9259 | 83.0507 | 93.5713 | 83.4456 | 88.276 | 72.801 | 76.5246 | 79.696 | 83.001 | 84.4453 | 86.4203 | 90.0863 | 88.8792 | 93.6691 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 124904.117 | 131623.685 | 149483.1281 | 131858.3391 | 139966.369 | 113160.542 | 119911.9727 | 124960.7548 | 130530.233 | 133442.8345 | 135966.2535 | 142226.097 | 138434.1892 | 148648.1691 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | E @ R (MWh) | 132940.5564 | 139888.2644 | 157608.8341 | 140553.386 | 148689.6803 | 122624.0307 | 128895.9515 | 134237.8004 | 139804.6348 | 142237.2938 | 145563.9135 | 151738.8934 | 149705.6346 | 157773.6841 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927
Option 3 Winter POE50 W E @ R (MWh) N 2 | 87432.8819 | 92136.5795 | 104638.1897 | 92300.8374 | 97976.4583 | 79212.3794 | 83938.3809 | 87472.5283 | 91371.1631 | 93409.9842 | 95176.3774 | 99558.2679 | 96903.9325 | 104053.7184 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 39882.1669 | 41966.4793 | 47282.6502 | 42166.0158 | 44606.9041 | 36787.2092 | 38668.7855 | 40271.3401 | 41941.3905 | 42671.1881 | 43669.1741 | 45521.668 | 44911.6904 | 47332.1052 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 53.0397 | 55.1225 | 60.9613 | 54.2019 | 56.6902 | 47.7704 | 49.3861 | 50.9401 | 52.2856 | 52.9584 | 53.9524 | 55.09 | 56.2504 | 57.7118 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374
98% | 23.3386 | 24.1709 | 27.053 | 23.7307 | 24.8233 | 20.4011 | 21.0218 | 21.7307 | 22.2972 | 22.6654 | 23.5454 | 24.1536 | 24.4726 | 25.0661 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 |  | 26.2533 | 27.2842 | 30.1743 | 26.8286 | 28.0602 | 23.6451 | 24.4449 | 25.214 | 25.88 | 26.2131 | 26.7051 | 27.2682 | 27.8425 | 28.5659 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776
97% | 23.1017 | 23.9255 | 26.7783 | 23.4898 | 24.5713 | 20.194 | 20.8084 | 21.5101 | 22.0708 | 22.4353 | 23.3064 | 23.9084 | 24.2242 | 24.8116 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 |  | 51.9736 | 54.0145 | 59.736 | 53.1124 | 55.5507 | 46.8102 | 48.3934 | 49.9161 | 51.2346 | 51.8939 | 52.8679 | 53.9826 | 55.1198 | 56.5518 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729
95% | 68.2388 | 70.6723 | 79.099 | 69.3852 | 72.5799 | 59.6499 | 61.4648 | 63.5375 | 65.1937 | 66.2705 | 68.8435 | 70.6218 | 71.5544 | 73.2897 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 |  | 102.348 | 106.3669 | 117.6339 | 104.5906 | 109.3922 | 92.1801 | 95.2978 | 98.2964 | 100.8928 | 102.191 | 104.1091 | 106.3043 | 108.5435 | 111.3635 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989
90% | 153.4188 | 158.8899 | 177.8355 | 155.9962 | 163.1788 | 134.1086 | 138.1891 | 142.8491 | 146.5726 | 148.9935 | 154.7784 | 158.7765 | 160.8733 | 164.7747 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 |  | 369.8121 | 384.3337 | 425.0443 | 377.9152 | 395.2646 | 333.0725 | 344.3379 | 355.1725 | 364.554 | 369.2448 | 376.1754 | 384.1072 | 392.1983 | 402.3877 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608
85% | 248.7872 | 257.6593 | 288.3819 | 252.9668 | 264.6142 | 217.4734 | 224.0905 | 231.6472 | 237.6854 | 241.611 | 250.992 | 257.4753 | 260.8756 | 267.2022 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 |  | 443.1082 | 460.5079 | 509.2874 | 452.8173 | 473.6054 | 399.0868 | 412.585 | 425.567 | 436.8079 | 442.4285 | 450.7327 | 460.2366 | 469.9313 | 482.1402 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251
80% | 957.8308 | 991.9883 | 1110.2705 | 973.9221 | 1018.7647 | 837.2727 | 862.7485 | 891.8418 | 915.0887 | 930.2025 | 966.3192 | 991.28 | 1004.371 | 1028.7284 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 |  | 505.7431 | 525.6023 | 581.2768 | 516.8245 | 540.5511 | 455.4991 | 470.9053 | 485.7223 | 498.5522 | 504.9672 | 514.4453 | 525.2926 | 536.3577 | 550.2924 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436
75% | 1450.6665 | 1502.3991 | 1681.5413 | 1475.0373 | 1542.9528 | 1268.0773 | 1306.6611 | 1350.7238 | 1385.932 | 1408.8225 | 1463.5224 | 1501.3264 | 1521.1532 | 1558.0431 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 |  | 433.7796 | 450.813 | 498.5655 | 443.2843 | 463.6347 | 390.685 | 403.899 | 416.6077 | 427.6119 | 433.1142 | 441.2436 | 450.5474 | 460.038 | 471.9899 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351
70% | 2215.9834 | 2295.0082 | 2568.6591 | 2253.2113 | 2356.9565 | 1937.067 | 1996.0062 | 2063.3148 | 2117.0975 | 2152.064 | 2235.6216 | 2293.3696 | 2323.6562 | 2380.0079 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 |  | 463.7644 | 481.9752 | 533.0286 | 473.926 | 495.6832 | 417.6909 | 431.8183 | 445.4055 | 457.1704 | 463.053 | 471.7443 | 481.6912 | 491.8378 | 504.616 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886
65% | 4046.3465 | 4190.6445 | 4690.3262 | 4114.3241 | 4303.761 | 3537.0502 | 3644.6721 | 3767.5764 | 3865.7827 | 3929.631 | 4082.2057 | 4187.6524 | 4242.9552 | 4345.8525 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 |  | 1223.3785 | 1271.4174 | 1406.0926 | 1250.1842 | 1307.5782 | 1101.8397 | 1139.1068 | 1174.9489 | 1205.9839 | 1221.5018 | 1244.4289 | 1270.6683 | 1297.4343 | 1331.1421 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459
60% | 7863.4534 | 8143.8744 | 9114.9291 | 7995.5573 | 8363.6988 | 6873.7141 | 7082.8608 | 7321.7064 | 7512.5553 | 7636.6346 | 7933.1401 | 8138.0597 | 8245.5322 | 8445.4972 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 |  | 1365.9727 | 1419.6109 | 1569.9836 | 1395.9029 | 1459.9865 | 1230.2676 | 1271.8786 | 1311.8983 | 1346.5507 | 1363.8773 | 1389.4767 | 1418.7745 | 1448.6603 | 1486.297 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073
55% | 9114.4977 | 9439.5326 | 10565.0783 | 9267.6189 | 9694.3302 | 7967.2948 | 8209.716 | 8486.561 | 8707.7731 | 8851.593 | 9195.2713 | 9432.7929 | 9557.3638 | 9789.1424 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 |  | 2222.2044 | 2309.4645 | 2554.0952 | 2270.8956 | 2375.1488 | 2001.4354 | 2069.1293 | 2134.2345 | 2190.608 | 2218.7955 | 2260.4413 | 2308.1038 | 2356.723 | 2417.9515 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039
50% | 10722.7294 | 11105.1159 | 12429.2615 | 10902.8685 | 11404.872 | 9373.1053 | 9658.3011 | 9983.9947 | 10244.2392 | 10413.4358 | 10817.7554 | 11097.187 | 11243.7382 | 11516.4136 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 |  | 3876.0308 | 4028.2324 | 4454.9241 | 3960.9595 | 4142.8008 | 3490.9594 | 3609.033 | 3722.5914 | 3820.9196 | 3870.085 | 3942.7248 | 4025.8591 | 4110.662 | 4217.4584 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455
45% | 19076.649 | 19756.9472 | 22112.715 | 19397.1318 | 20290.2389 | 16675.5528 | 17182.9403 | 17762.3771 | 18225.3742 | 18526.3893 | 19245.7083 | 19742.841 | 20003.568 | 20488.6808 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 |  | 7722.7432 | 8025.9952 | 8876.1511 | 7891.9581 | 8254.2653 | 6955.513 | 7190.7671 | 7417.025 | 7612.9377 | 7710.8964 | 7855.6268 | 8021.2664 | 8190.2308 | 8403.0158 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653
40% | 21841.7413 | 22620.6463 | 25317.8743 | 22208.6769 | 23231.2367 | 19092.6147 | 19673.5463 | 20336.9704 | 20867.0772 | 21211.7234 | 22035.3052 | 22604.4954 | 22903.0139 | 23458.4421 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 |  | 13151.3186 | 13667.7365 | 15115.4956 | 13439.4804 | 14056.4655 | 11844.7766 | 12245.3986 | 12630.7008 | 12964.3271 | 13131.1444 | 13377.6105 | 13659.6838 | 13947.4189 | 14309.7776 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181
35% | 13247.9197 | 13720.3578 | 15356.3382 | 13470.4814 | 14090.7062 | 11580.4607 | 11932.8198 | 12335.2139 | 12656.7456 | 12865.7878 | 13365.3242 | 13710.5617 | 13891.6254 | 14228.5156 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 |  | 15921.911 | 16547.1229 | 18299.8818 | 16270.7799 | 17017.7455 | 14340.1194 | 14825.1406 | 15291.6145 | 15695.5259 | 15897.4867 | 16195.8759 | 16537.3736 | 16885.7261 | 17324.423 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485
30% | 5490.4971 | 5686.2954 | 6364.3147 | 5582.736 | 5839.7834 | 4799.4317 | 4945.4642 | 5112.2333 | 5245.4896 | 5332.1255 | 5539.1545 | 5682.2355 | 5757.2759 | 5896.8975 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 |  | 24323.6426 | 25278.7685 | 27956.4296 | 24856.6039 | 25997.731 | 21907.1654 | 22648.1244 | 23360.7489 | 23977.7978 | 24286.3299 | 24742.1742 | 25263.8748 | 25796.0471 | 26466.2371 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003
25% | 3277.4755 | 3394.3546 | 3799.0887 | 3332.5363 | 3485.9771 | 2864.9537 | 2952.1257 | 3051.6762 | 3131.2217 | 3182.9378 | 3306.5209 | 3391.931 | 3436.7254 | 3520.0705 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 |  | 20684.1582 | 21496.3711 | 23773.3806 | 21137.3739 | 22107.7571 | 18629.2524 | 19259.3435 | 19865.3399 | 20390.0613 | 20652.4286 | 21040.0661 | 21483.7059 | 21936.2506 | 22506.1619 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441
20% | 3486.5752 | 3610.9111 | 4041.4669 | 3545.1488 | 3708.379 | 3047.7349 | 3140.4685 | 3246.3702 | 3330.9906 | 3386.0061 | 3517.4737 | 3608.3329 | 3655.9851 | 3744.6476 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 |  | 5487.2123 | 5702.6808 | 6306.7389 | 5607.4439 | 5864.8727 | 4942.075 | 5109.2292 | 5269.9914 | 5409.1926 | 5478.7948 | 5581.6295 | 5699.3209 | 5819.3745 | 5970.5638 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043
15% | 3611.5612 | 3740.3542 | 4186.3445 | 3672.2345 | 3841.3161 | 3156.9894 | 3253.0473 | 3362.7453 | 3450.3992 | 3507.3869 | 3643.5673 | 3737.6836 | 3787.0441 | 3878.8849 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 |  | 3400.2725 | 3533.7923 | 3908.1103 | 3474.7767 | 3634.2982 | 3062.4662 | 3166.047 | 3265.6668 | 3351.9259 | 3395.0565 | 3458.7803 | 3531.7103 | 3606.1042 | 3699.792 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554
10% | 2407.9049 | 2493.774 | 2791.1252 | 2448.3571 | 2561.0874 | 2104.8322 | 2168.876 | 2242.0141 | 2300.4548 | 2338.4497 | 2429.244 | 2491.9934 | 2524.9031 | 2586.1353 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 |  | 972.8391 | 1011.0399 | 1118.1346 | 994.1552 | 1039.7953 | 876.1906 | 905.8257 | 934.3276 | 959.0068 | 971.3467 | 989.5785 | 1010.4443 | 1031.7288 | 1058.5335 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716
5% | 191.9216 | 198.7657 | 222.4661 | 195.1458 | 204.131 | 167.7652 | 172.8698 | 178.6993 | 183.3573 | 186.3857 | 193.6224 | 198.6238 | 201.2469 | 206.1274 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 109520.6382 | 113426.2871 | 126950.9475 | 111360.5567 | 116487.9592 | 95735.7439 | 98648.6982 | 101975.2934 | 104633.3983 | 106361.5513 | 110491.2219 | 113345.3023 | 114842.1576 | 117627.2311 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | E @ R (MWh) | 102801.5058 | 106838.2526 | 118155.1262 | 105054.015 | 109876.8775 | 92588.5007 | 95720.0914 | 98731.9297 | 101339.8266 | 102643.8076 | 104570.389 | 106775.3057 | 109024.48 | 111856.9729 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25
Option 3 Summer POE50 W E @ R (MWh) N 2 | 76664.4467 | 79398.4009 | 88865.6632 | 77952.3897 | 81541.5715 | 67015.0207 | 69054.0888 | 71382.7053 | 73243.3788 | 74453.0859 | 77343.8554 | 79341.7116 | 80389.5103 | 82339.0618 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 30840.4517 | 32051.4758 | 35446.5379 | 31516.2045 | 32963.0633 | 27776.5502 | 28716.0274 | 29619.5789 | 30401.948 | 30793.1423 | 31371.1167 | 32032.5917 | 32707.344 | 33557.0919 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 49.1893 | 51.8356 | 58.8689 | 24.4913 | 27.6844 | 29.9913 | 32.6502 | 34.6385 | 36.8318 | 37.9788 | 38.9726 | 41.4378 | 39.9445 | 43.967 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 | 49.215 |  | 52.3542 | 55.0903 | 62.0689 | 27.9156 | 31.1198 | 33.7182 | 36.1882 | 38.2919 | 40.4842 | 41.4422 | 42.7523 | 45.1841 | 44.3834 | 47.5607 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392 | 49.392
98% | 146.0848 | 153.9438 | 174.8318 | 71.5205 | 81.0035 | 87.8547 | 95.751 | 101.6559 | 108.1698 | 111.5764 | 114.5277 | 121.849 | 117.4141 | 129.3601 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 | 144.946 |  | 155.484 | 163.6098 | 184.3354 | 81.69 | 91.206 | 98.9229 | 106.2584 | 112.5061 | 119.017 | 121.8621 | 125.7529 | 132.975 | 130.5969 | 140.0331 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716 | 145.4716
97% | 64.2674 | 67.7249 | 76.9141 | 30.9187 | 35.0905 | 38.1046 | 41.5784 | 44.1762 | 47.0419 | 48.5405 | 49.8389 | 53.0598 | 51.1087 | 56.3642 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 | 63.2209 |  | 68.4024 | 71.9773 | 81.0951 | 35.3926 | 39.579 | 42.9739 | 46.201 | 48.9496 | 51.8139 | 53.0656 | 54.7772 | 57.9545 | 56.9083 | 61.0596 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522 | 63.4522
95% | 158.1967 | 166.7073 | 189.3271 | 74.0408 | 84.31 | 91.7293 | 100.2803 | 106.6748 | 113.7288 | 117.4177 | 120.6137 | 128.5421 | 123.7395 | 136.6759 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 | 153.554 |  | 168.3752 | 177.1748 | 199.6187 | 85.0535 | 95.3585 | 103.7152 | 111.6589 | 118.4246 | 125.4752 | 128.5563 | 132.7696 | 140.5905 | 138.0153 | 148.2338 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233 | 154.1233
90% | 1615.7485 | 1702.6723 | 1933.7004 | 704.3047 | 809.1894 | 884.9662 | 972.3021 | 1037.6127 | 1109.659 | 1147.3362 | 1179.9789 | 1260.9557 | 1211.9039 | 1344.031 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 | 1516.4158 |  | 1719.7072 | 1809.5821 | 2038.8138 | 816.783 | 922.0334 | 1007.3851 | 1088.5181 | 1157.6198 | 1229.6318 | 1261.1005 | 1304.1334 | 1384.0123 | 1357.7103 | 1462.0779 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23 | 1522.23
85% | 3806.6079 | 4011.3951 | 4555.6838 | 1467.6023 | 1714.7045 | 1893.2302 | 2098.9884 | 2252.8563 | 2422.5931 | 2511.3582 | 2588.2626 | 2779.0391 | 2663.476 | 2974.7597 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 | 3380.8881 |  | 4051.5284 | 4263.2684 | 4803.3248 | 1732.5946 | 1980.5583 | 2181.6418 | 2372.7863 | 2535.5858 | 2705.242 | 2779.3803 | 2880.7632 | 3068.9533 | 3006.9873 | 3252.8711 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859 | 3394.5859
80% | 6892.6794 | 7263.4904 | 8249.0417 | 2268.2244 | 2715.656 | 3038.915 | 3411.4843 | 3690.0951 | 3997.4399 | 4158.1682 | 4297.42 | 4642.8617 | 4433.6099 | 4997.2558 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 | 5732.6383 |  | 7336.1604 | 7719.561 | 8697.4488 | 2748.0498 | 3197.0411 | 3561.1459 | 3907.2541 | 4202.0374 | 4509.2363 | 4643.4796 | 4827.055 | 5167.8136 | 5055.6107 | 5500.8361 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411 | 5757.4411
75% | 8058.556 | 8492.0887 | 9644.3432 | 2138.1631 | 2661.2765 | 3039.2138 | 3474.8022 | 3800.5392 | 4159.8704 | 4347.7855 | 4510.5913 | 4914.4635 | 4669.8174 | 5328.8023 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 | 6188.5726 |  | 8577.0505 | 9025.3023 | 10168.597 | 2699.1496 | 3224.0866 | 3649.7786 | 4054.43 | 4399.075 | 4758.2357 | 4915.1859 | 5129.8125 | 5528.2095 | 5397.0278 | 5917.5617 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707 | 6217.5707
70% | 9450.1926 | 9958.5923 | 11309.8302 | 1821.8683 | 2435.3184 | 2878.5219 | 3389.3323 | 3771.321 | 4192.7054 | 4413.0716 | 4603.9924 | 5077.6095 | 4790.7154 | 5563.5008 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 | 6571.7452 |  | 10058.2262 | 10583.8868 | 11924.6176 | 2479.7319 | 3095.3205 | 3594.5255 | 4069.0563 | 4473.2184 | 4894.4027 | 5078.4566 | 5330.1473 | 5797.3436 | 5643.5081 | 6253.9334 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751 | 6605.751
65% | 10355.7039 | 10912.8181 | 12393.5307 | 1133.9233 | 1806.1538 | 2291.8248 | 2851.5807 | 3270.1713 | 3731.9324 | 3973.414 | 4182.6287 | 4701.6275 | 4387.2433 | 5234.0765 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 | 6338.9303 |  | 11021.9989 | 11598.028 | 13067.2267 | 1854.8229 | 2529.3968 | 3076.4353 | 3596.4354 | 4039.324 | 4500.8659 | 4702.5558 | 4978.3633 | 5490.3261 | 5321.7502 | 5990.6659 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945 | 6376.1945
60% | 11267.3947 | 11873.5559 | 13484.6268 | 229.8603 | 876.5623 | 1404.9906 | 2014.026 | 2469.4683 | 2971.8818 | 3234.6228 | 3462.2563 | 4026.9464 | 3684.8847 | 4606.271 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 | 5808.3934 |  | 11992.3487 | 12619.09 | 14217.6334 | 929.5162 | 1663.4779 | 2258.6763 | 2824.456 | 3306.3354 | 3808.5103 | 4027.9565 | 4328.0454 | 4885.0801 | 4701.6632 | 5429.4687 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383 | 5848.9383
55% | 11294.5848 | 11902.2087 | 13517.1674 |  | 28.1361 | 244.9016 | 737.8797 | 1194.421 | 1698.0469 | 1961.4219 | 2189.6047 | 2755.6576 | 2412.7704 | 3336.3801 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 | 4541.4035 |  | 12021.2882 | 12649.5419 | 14251.9428 | 40.4064 | 423.8675 | 983.1203 | 1550.2653 | 2033.3075 | 2536.6943 | 2756.6701 | 3057.4831 | 3615.8621 | 3432.0025 | 4161.5643 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462 | 4582.0462
50% | 13305.825 | 14021.6493 | 15924.1856 |  |  |  | 0.040808 | 85.8772 | 360.7682 | 574.6793 | 796.8311 | 1449.7931 | 1045.8475 | 2133.9256 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 | 3553.5289 |  | 14161.9334 | 14902.061 | 16789.8034 |  |  | 26.0266 | 261.4151 | 641.0448 | 1191.8388 | 1450.9858 | 1805.365 | 2463.1752 | 2246.5756 | 3106.0513 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089 | 3601.4089
45% | 16641.1386 | 17536.3955 | 19915.8324 | [8 empty] | 51.7105 | 0.049848 | 349.9883 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 | 1724.3382 |  | 17711.844 | 18637.4962 | 20998.4308 | [5 empty] | 7.5973 | 52.0041 | 174.775 | 582.2274 | 423.1869 | 1190.2274 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201 | 1784.2201
40% | 17620.8046 | 18568.7653 | 21088.28 | [11 empty] | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 | 3.1593 |  | 18754.5425 | 19734.688 | 22234.6112 | [11 empty] | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914 | 6.4914
35% | FY25: 7205.365; FY26: 7592.9979; FY27: 8623.2586 |  | 7668.9645 | 8069.7581 | 9092.0076
30% | FY25: 2222.5811; FY26: 2342.1511; FY27: 2659.9474 |  | 2365.584 | 2489.2135 | 2804.5387
25% | FY25: 1635.9351; FY26: 1723.9448; FY27: 1957.8593 |  | 1741.1926 | 1832.1904 | 2064.286
20% | FY25: 1301.415; FY26: 1371.4283; FY27: 1557.5114 |  | 1385.1492 | 1457.5395 | 1642.1756
15% | FY25: 1020.863; FY26: 1075.7832; FY27: 1221.7516 |  | 1086.5463 | 1143.3311 | 1288.1644
10% | FY25: 716.8288; FY26: 755.3926; FY27: 857.8885 |  | 762.9502 | 802.8233 | 904.5222
5% | FY25: 74.1547; FY26: 78.1441; FY27: 88.7471 |  | 78.9259 | 83.0507 | 93.5713
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 124904.117 | 131623.685 | 149483.1281 | 9964.9177 | 13275.0855 | 15924.2439 | 19220.6964 | 21859.5076 | 24950.6694 | 26637.371 | 28135.5187 | 32005.5532 | 29632.5252 | 36235.3582 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | 45770.9493 | E @ R (MWh) | 132940.5564 | 139888.2644 | 157608.8341 | 13531.1062 | 17293.0453 | 20618.0655 | 24024.9231 | 27105.7202 | 30479.0455 | 32012.7013 | 34171.9951 | 38359.7074 | 36955.9265 | 42662.1449 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171 | 46109.3171
Option 4 Winter POE50 W E @ R (MWh) N 2 | 87432.8819 | 92136.5795 | 104638.1897 | 6975.4424 | 9292.5599 | 11146.9708 | 13454.4875 | 15301.6553 | 17465.4686 | 18646.1597 | 19694.8631 | 22403.8872 | 20742.7676 | 25364.7508 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | 32039.6645 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 39882.1669 | 41966.4793 | 47282.6502 | 4059.3319 | 5187.9136 | 6185.4197 | 7207.4769 | 8131.7161 | 9143.7136 | 9603.8104 | 10251.5985 | 11507.9122 | 11086.7779 | 12798.6435 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951 | 13832.7951
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 53.0397 | 55.1225 | 60.9613 | 30.9278 | 33.4161 | 35.4082 | 37.0239 | 38.5779 | 39.9234 | 40.5962 | 41.5902 | 42.7278 | 43.8882 | 45.3496 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752 | 45.5752
98% | 23.3386 | 24.1709 | 27.053 | 12.0388 | 13.1314 | 14.1103 | 14.7311 | 15.44 | 16.0064 | 16.3747 | 17.2547 | 17.8629 | 18.1819 | 18.7753 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 | 18.6007 |  | 26.2533 | 27.2842 | 30.1743 | 15.1367 | 16.3683 | 17.3544 | 18.1541 | 18.9233 | 19.5893 | 19.9223 | 20.4143 | 20.9774 | 21.5518 | 22.2751 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868 | 22.3868
97% | 23.1017 | 23.9255 | 26.7783 | 11.743 | 12.8246 | 13.7935 | 14.408 | 15.1097 | 15.6704 | 16.0349 | 16.906 | 17.508 | 17.8237 | 18.4112 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 | 18.2383 |  | 51.9736 | 54.0145 | 59.736 | 29.6189 | 32.0573 | 34.0093 | 35.5926 | 37.1153 | 38.4337 | 39.093 | 40.067 | 41.1818 | 42.3189 | 43.7509 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972 | 43.972
95% | 68.2388 | 70.6723 | 79.099 | 33.8982 | 37.093 | 39.9551 | 41.77 | 43.8427 | 45.4989 | 46.5757 | 49.1487 | 50.927 | 51.8597 | 53.5949 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 | 53.0843 |  | 102.348 | 106.3669 | 117.6339 | 57.2747 | 62.0762 | 65.9203 | 69.0381 | 72.0367 | 74.633 | 75.9313 | 77.8494 | 80.0445 | 82.2838 | 85.1038 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391 | 85.5391
90% | 153.4188 | 158.8899 | 177.8355 | 71.8499 | 79.0325 | 85.4672 | 89.5478 | 94.2077 | 97.9313 | 100.3521 | 106.137 | 110.1351 | 112.2319 | 116.1333 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 | 114.9852 |  | 369.8121 | 384.3337 | 425.0443 | 197.6017 | 214.9512 | 228.8409 | 240.1063 | 250.9409 | 260.3224 | 265.0133 | 271.9439 | 279.8757 | 287.9668 | 298.1562 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292 | 299.7292
85% | 248.7872 | 257.6593 | 288.3819 | 105.426 | 117.0734 | 127.5082 | 134.1252 | 141.6819 | 147.7201 | 151.6458 | 161.0267 | 167.5101 | 170.9103 | 177.2369 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 | 175.3751 |  | 443.1082 | 460.5079 | 509.2874 | 219.211 | 239.9991 | 256.6418 | 270.14 | 283.122 | 294.3629 | 299.9835 | 308.2877 | 317.7916 | 327.4862 | 339.6952 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58 | 341.58
80% | 957.8308 | 991.9883 | 1110.2705 | 358.0296 | 402.8721 | 443.0459 | 468.5217 | 497.6149 | 520.8618 | 535.9757 | 572.0924 | 597.0532 | 610.1442 | 634.5015 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 | 627.3336 |  | 505.7431 | 525.6023 | 581.2768 | 227.7321 | 251.4587 | 270.4538 | 285.86 | 300.6771 | 313.5069 | 319.922 | 329.4 | 340.2474 | 351.3124 | 365.2472 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984 | 367.3984
75% | 1450.6665 | 1502.3991 | 1681.5413 | 460.4083 | 528.3238 | 589.1684 | 627.7522 | 671.815 | 707.0232 | 729.9136 | 784.6135 | 822.4175 | 842.2443 | 879.1343 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 | 868.2781 |  | 433.7796 | 450.813 | 498.5655 | 173.5728 | 193.9233 | 210.2155 | 223.4295 | 236.1383 | 247.1425 | 252.6448 | 260.7741 | 270.078 | 279.5685 | 291.5205 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656 | 293.3656
70% | 2215.9834 | 2295.0082 | 2568.6591 | 561.0443 | 664.7895 | 757.7333 | 816.6725 | 883.9811 | 937.7638 | 972.7304 | 1056.288 | 1114.0359 | 1144.3225 | 1200.6742 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 | 1184.0908 |  | 463.7644 | 481.9752 | 533.0286 | 159.1043 | 180.8615 | 198.2799 | 212.4074 | 225.9946 | 237.7595 | 243.6421 | 252.3334 | 262.2803 | 272.4269 | 285.205 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777 | 287.1777
65% | 4046.3465 | 4190.6445 | 4690.3262 | 726.2132 | 915.65 | 1085.3638 | 1192.9858 | 1315.8901 | 1414.0963 | 1477.9446 | 1630.5193 | 1735.9661 | 1791.2689 | 1894.1661 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 | 1863.8851 |  | 1223.3785 | 1271.4174 | 1406.0926 | 339.5457 | 396.9397 | 442.8884 | 480.1556 | 515.9976 | 547.0326 | 562.5505 | 585.4776 | 611.717 | 638.4831 | 672.1908 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946 | 677.3946
60% | 7863.4534 | 8143.8744 | 9114.9291 | 738.9582 | 1107.0997 | 1436.9124 | 1646.0591 | 1884.9047 | 2075.7535 | 2199.8329 | 2496.3384 | 2701.258 | 2808.7305 | 3008.6955 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 | 2949.849 |  | 1365.9727 | 1419.6109 | 1569.9836 | 275.2981 | 339.3818 | 390.6862 | 432.2971 | 472.3169 | 506.9692 | 524.2958 | 549.8953 | 579.193 | 609.0789 | 646.7156 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259 | 652.5259
55% | 9114.4977 | 9439.5326 | 10565.0783 | 96.2323 | 378.628 | 750.7007 | 993.1218 | 1269.9669 | 1491.179 | 1634.9989 | 1978.6772 | 2216.1987 | 2340.7696 | 2572.5483 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 | 2504.3396 |  | 2222.2044 | 2309.4645 | 2554.0952 | 249.5839 | 353.8371 | 437.3006 | 504.9945 | 570.0998 | 626.4733 | 654.6607 | 696.3066 | 743.9691 | 792.5883 | 853.8167 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691 | 863.2691
50% | 10722.7294 | 11105.1159 | 12429.2615 |  |  | 29.6615 | 122.1993 | 300.2563 | 494.8265 | 645.0196 | 1046.5764 | 1326.0081 | 1472.5592 | 1745.2346 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 | 1664.9906 |  | 3876.0308 | 4028.2324 | 4454.9241 | 69.0686 | 206.397 | 351.033 | 469.1066 | 582.665 | 680.9932 | 730.1585 | 802.7984 | 885.9327 | 970.7356 | 1077.532 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191 | 1094.0191
45% | 19076.649 | 19756.9472 | 22112.715 | [7 empty] | 56.9726 | 202.4712 | 312.8424 | 577.9293 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 | 492.0171 |  | 7722.7432 | 8025.9952 | 8876.1511 |  |  | 26.9353 | 108.8071 | 235.9916 | 382.1514 | 467.1756 | 606.501 | 772.1407 | 941.1051 | 1153.8901 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396 | 1186.7396
40% | FY25: 21841.7413; FY26: 22620.6463; FY27: 25317.8743 |  | 13151.3186 | 13667.7365 | 15115.4956 | [7 empty] | 0.54558 | 26.9538 | 93.4527 | 231.3516 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276 | 257.8276
35% | FY25: 13247.9197; FY26: 13720.3578; FY27: 15356.3382 |  | 15921.911 | 16547.1229 | 18299.8818
30% | FY25: 5490.4971; FY26: 5686.2954; FY27: 6364.3147 |  | 24323.6426 | 25278.7685 | 27956.4296
25% | FY25: 3277.4755; FY26: 3394.3546; FY27: 3799.0887 |  | 20684.1582 | 21496.3711 | 23773.3806
20% | FY25: 3486.5752; FY26: 3610.9111; FY27: 4041.4669 |  | 5487.2123 | 5702.6808 | 6306.7389
15% | FY25: 3611.5612; FY26: 3740.3542; FY27: 4186.3445 |  | 3400.2725 | 3533.7923 | 3908.1103
10% | FY25: 2407.9049; FY26: 2493.774; FY27: 2791.1252 |  | 972.8391 | 1011.0399 | 1118.1346
5% | FY25: 191.9216; FY26: 198.7657; FY27: 222.4661 |  | 0 | 0 | 0
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 109520.6382 | 113426.2871 | 126950.9475 | 3175.8418 | 4256.518 | 5373.4204 | 6161.8944 | 7134.711 | 7964.3311 | 8527.3987 | 9972.5509 | 11079.3518 | 11693.8891 | 12897.0355 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | 12535.0674 | E @ R (MWh) | 102801.5058 | 106838.2526 | 118155.1262 | 2043.6763 | 2521.6672 | 2965.9678 | 3387.1128 | 3840.5968 | 4269.2935 | 4495.5896 | 4844.1844 | 5275.1107 | 5754.2472 | 6411.8004 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5 | 6518.5
Option 4 Summer POE50 W E @ R (MWh) N 2 | 76664.4467 | 79398.4009 | 88865.6632 | 2223.0893 | 2979.5626 | 3761.3943 | 4313.3261 | 4994.2977 | 5575.0318 | 5969.1791 | 6980.7857 | 7755.5463 | 8185.7224 | 9027.9249 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | 8774.5472 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 30840.4517 | 32051.4758 | 35446.5379 | 613.1029 | 756.5002 | 889.7903 | 1016.1338 | 1152.179 | 1280.788 | 1348.6769 | 1453.2553 | 1582.5332 | 1726.2742 | 1923.5401 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55 | 1955.55
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 49.1893 | 51.8356 | 58.8689 | 51.928 | 55.121 | 44.5645 | 47.2233 | 49.2116 | 51.4049 | 52.552 | 53.5457 | 56.011 | 54.5176 | 58.5401 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 | 63.7881 |  | 52.3542 | 55.0903 | 62.0689 | 55.3522 | 58.5564 | 48.2913 | 50.7613 | 52.865 | 55.0574 | 56.0154 | 57.3255 | 59.7573 | 58.9565 | 62.1339 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651 | 63.9651
98% | 146.0848 | 153.9438 | 174.8318 | 154.2182 | 163.7012 | 132.3498 | 140.2461 | 146.151 | 152.6649 | 156.0714 | 159.0228 | 166.3441 | 161.9092 | 173.8552 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 | 189.441 |  | 155.484 | 163.6098 | 184.3354 | 164.3878 | 173.9038 | 143.418 | 150.7535 | 157.0012 | 163.512 | 166.3572 | 170.2479 | 177.47 | 175.092 | 184.5282 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667 | 189.9667
97% | 64.2674 | 67.7249 | 76.9141 | 67.8456 | 72.0174 | 58.2249 | 61.6988 | 64.2965 | 67.1622 | 68.6609 | 69.9593 | 73.1802 | 71.2291 | 76.4845 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 | 83.3412 |  | 68.4024 | 71.9773 | 81.0951 | 72.3195 | 76.5059 | 63.0942 | 66.3213 | 69.0699 | 71.9342 | 73.1859 | 74.8976 | 78.0748 | 77.0286 | 81.1799 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725 | 83.5725
95% | 158.1967 | 166.7073 | 189.3271 | 167.0045 | 177.2737 | 143.3229 | 151.8739 | 158.2684 | 165.3224 | 169.0114 | 172.2074 | 180.1358 | 175.3331 | 188.2696 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 | 205.1477 |  | 168.3752 | 177.1748 | 199.6187 | 178.0172 | 188.3222 | 155.3089 | 163.2525 | 170.0182 | 177.0689 | 180.1499 | 184.3633 | 192.1841 | 189.6089 | 199.8275 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169 | 205.7169
90% | 1615.7485 | 1702.6723 | 1933.7004 | 1705.7077 | 1810.5925 | 1463.8347 | 1551.1706 | 1616.4812 | 1688.5275 | 1726.2046 | 1758.8473 | 1839.8241 | 1790.7723 | 1922.8995 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 | 2095.2843 |  | 1719.7072 | 1809.5821 | 2038.8138 | 1818.1861 | 1923.4364 | 1586.2535 | 1667.3865 | 1736.4882 | 1808.5003 | 1839.969 | 1883.0018 | 1962.8808 | 1936.5787 | 2040.9463 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984 | 2101.0984
85% | 3806.6079 | 4011.3951 | 4555.6838 | 4018.5465 | 4265.6488 | 3448.7079 | 3654.4661 | 3808.334 | 3978.0708 | 4066.836 | 4143.7403 | 4334.5168 | 4218.9537 | 4530.2374 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 | 4936.3658 |  | 4051.5284 | 4263.2684 | 4803.3248 | 4283.5388 | 4531.5025 | 3737.1195 | 3928.264 | 4091.0635 | 4260.7197 | 4334.858 | 4436.2409 | 4624.431 | 4562.465 | 4808.3488 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636 | 4950.0636
80% | 6892.6794 | 7263.4904 | 8249.0417 | 7276.4395 | 7723.8711 | 6244.6247 | 6617.1941 | 6895.8049 | 7203.1496 | 7363.878 | 7503.1297 | 7848.5714 | 7639.3197 | 8202.9656 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 | 8938.348 |  | 7336.1604 | 7719.561 | 8697.4488 | 7756.2649 | 8205.2563 | 6766.8556 | 7112.9638 | 7407.7472 | 7714.946 | 7849.1893 | 8032.7647 | 8373.5234 | 8261.3205 | 8706.5458 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508 | 8963.1508
75% | 8058.556 | 8492.0887 | 9644.3432 | 8507.2281 | 9030.3415 | 7300.8848 | 7736.4732 | 8062.2102 | 8421.5414 | 8609.4565 | 8772.2623 | 9176.1345 | 8931.4884 | 9590.4733 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 | 10450.2436 |  | 8577.0505 | 9025.3023 | 10168.597 | 9068.2146 | 9593.1515 | 7911.4496 | 8316.101 | 8660.7461 | 9019.9067 | 9176.8569 | 9391.4835 | 9789.8805 | 9658.6988 | 10179.2327 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417 | 10479.2417
70% | 9450.1926 | 9958.5923 | 11309.8302 | 9976.3461 | 10589.7962 | 8561.6787 | 9072.4891 | 9454.4778 | 9875.8621 | 10096.2283 | 10287.1491 | 10760.7663 | 10473.8721 | 11246.6575 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 | 12254.902 |  | 10058.2262 | 10583.8868 | 11924.6176 | 10634.2097 | 11249.7982 | 9277.6822 | 9752.2131 | 10156.3751 | 10577.5595 | 10761.6134 | 11013.304 | 11480.5004 | 11326.6649 | 11937.0901 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078 | 12288.9078
65% | 10355.7039 | 10912.8181 | 12393.5307 | 10932.2731 | 11604.5035 | 9382.0531 | 9941.809 | 10360.3997 | 10822.1608 | 11063.6423 | 11272.8571 | 11791.8559 | 11477.4717 | 12324.3049 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 | 13429.1587 |  | 11021.9989 | 11598.028 | 13067.2267 | 11653.1727 | 12327.7466 | 10166.6637 | 10686.6638 | 11129.5523 | 11591.0943 | 11792.7842 | 12068.5916 | 12580.5545 | 12411.9785 | 13080.8943 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229 | 13466.4229
60% | 11267.3947 | 11873.5559 | 13484.6268 | 11894.7236 | 12626.1357 | 10208.0262 | 10817.0616 | 11272.5039 | 11774.9174 | 12037.6584 | 12265.2918 | 12829.982 | 12487.9202 | 13409.3066 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 | 14611.429 |  | 11992.3487 | 12619.09 | 14217.6334 | 12679.0895 | 13413.0512 | 11061.7119 | 11627.4915 | 12109.3709 | 12611.5459 | 12830.992 | 13131.0809 | 13688.1157 | 13504.6988 | 14232.5042 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739 | 14651.9739
55% | 11294.5848 | 11902.2087 | 13517.1674 | 11923.4275 | 12656.6046 | 10232.6598 | 10843.1649 | 11299.7063 | 11803.3322 | 12066.7072 | 12294.89 | 12860.9428 | 12518.0556 | 13441.6654 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 | 14646.6887 |  | 12021.2882 | 12649.5419 | 14251.9428 | 12709.6862 | 13445.4191 | 11088.4056 | 11655.5506 | 12138.5928 | 12641.9796 | 12861.9553 | 13162.7684 | 13721.1473 | 13537.2878 | 14266.8496 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315 | 14687.3315
50% | 13305.825 | 14021.6493 | 15924.1856 | 14046.6466 | 14910.3813 | 12054.8018 | 12774.0203 | 13311.8585 | 13905.1657 | 14215.4402 | 14484.2558 | 15151.1064 | 14747.1608 | 15835.2389 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 | 17254.8421 |  | 14161.9334 | 14902.061 | 16789.8034 | 14972.9153 | 15839.661 | 13062.9313 | 13731.0684 | 14300.1266 | 14893.1521 | 15152.2991 | 15506.6783 | 16164.4885 | 15947.8889 | 16807.3646 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222 | 17302.7222
45% | 16641.1386 | 17536.3955 | 19915.8324 | 17567.6587 | 18647.9022 | 15076.5268 | 15976.0287 | 16648.6846 | 17390.7134 | 17778.7631 | 18114.9615 | 18948.9687 | 18443.7678 | 19804.5897 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 | 21580.0388 |  | 17711.844 | 18637.4962 | 20998.4308 | 18726.1112 | 19810.1203 | 16337.3598 | 17172.976 | 17884.6775 | 18626.3541 | 18950.4604 | 19393.6703 | 20216.3709 | 19945.4772 | 21020.394 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207 | 21639.9207
40% | 17620.8046 | 18568.7653 | 21088.28 | 18601.8691 | 19745.7066 | 15964.0839 | 16916.5396 | 17628.7948 | 18414.507 | 18825.4012 | 19181.3917 | 20064.4969 | 19529.5548 | 20970.4885 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 | 22850.4585 |  | 18754.5425 | 19734.688 | 22234.6112 | 19828.5198 | 20976.3446 | 17299.1422 | 18183.9513 | 18937.5507 | 19722.89 | 20066.0765 | 20535.3782 | 21406.5113 | 21119.6701 | 22257.8673 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657 | 22913.8657
35% | 7205.365 | 7592.9979 | 8623.2586 | 7606.5344 | 8074.2637 | 6527.9114 | 6917.3824 | 7208.6323 | 7529.9197 | 7697.9395 | 7843.5084 | 8204.621 | 7985.8766 | 8575.0922 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 | 9343.8352 |  | 7668.9645 | 8069.7581 | 9092.0076 | 8108.1271 | 8577.4869 | 7073.8333 | 7435.6427 | 7743.7988 | 8064.9337 | 8205.2669 | 8397.1702 | 8753.3873 | 8636.0944 | 9101.5173 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632 | 9369.7632
30% | 2222.5811 | 2342.1511 | 2659.9474 | 2346.3267 | 2490.6034 | 2013.6125 | 2133.7494 | 2223.589 | 2322.6939 | 2374.5216 | 2419.4241 | 2530.8136 | 2463.3393 | 2645.0899 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 | 2882.2179 |  | 2365.584 | 2489.2135 | 2804.5387 | 2501.0489 | 2645.8286 | 2182.0086 | 2293.613 | 2388.6675 | 2487.7254 | 2531.0129 | 2590.2077 | 2700.0872 | 2663.9068 | 2807.472 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157 | 2890.2157
25% | 1635.9351 | 1723.9448 | 1957.8593 | 1727.0182 | 1833.2133 | 1482.1233 | 1570.5503 | 1636.6769 | 1709.6233 | 1747.7712 | 1780.8217 | 1862.8102 | 1813.1456 | 1946.9234 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 | 2121.462 |  | 1741.1926 | 1832.1904 | 2064.286 | 1840.9018 | 1947.4671 | 1606.0716 | 1688.2182 | 1758.1833 | 1831.095 | 1862.9568 | 1906.5273 | 1987.4043 | 1960.7736 | 2066.4451 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487 | 2127.3487
20% | 1301.415 | 1371.4283 | 1557.5114 | 1373.8732 | 1458.3533 | 1179.055 | 1249.4003 | 1302.0051 | 1360.0352 | 1390.3826 | 1416.6748 | 1481.8981 | 1442.389 | 1548.8117 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 | 1687.6601 |  | 1385.1492 | 1457.5395 | 1642.1756 | 1464.4696 | 1549.2442 | 1277.6581 | 1343.0072 | 1398.6655 | 1456.6681 | 1482.0148 | 1516.6759 | 1581.0149 | 1559.8297 | 1643.8933 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432 | 1692.3432
15% | 1020.863 | 1075.7832 | 1221.7516 | 1077.7011 | 1143.9694 | 924.8808 | 980.0614 | 1021.3259 | 1066.8463 | 1090.6515 | 1111.2758 | 1162.4386 | 1131.4467 | 1214.9273 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 | 1323.8435 |  | 1086.5463 | 1143.3311 | 1288.1644 | 1148.7672 | 1215.2666 | 1002.2275 | 1053.489 | 1097.1489 | 1142.6476 | 1162.5301 | 1189.7191 | 1240.1883 | 1223.5701 | 1289.5117 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517 | 1327.517
10% | 716.8288 | 755.3926 | 857.8885 | 756.7393 | 803.2715 | 649.432 | 688.1787 | 717.1538 | 749.1172 | 765.8327 | 780.3147 | 816.2402 | 794.4783 | 853.0967 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 | 929.5754 |  | 762.9502 | 802.8233 | 904.5222 | 806.6404 | 853.3349 | 703.7433 | 739.738 | 770.3951 | 802.3433 | 816.3044 | 835.396 | 870.8344 | 859.1655 | 905.4683 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548 | 932.1548
5% | 74.1547 | 78.1441 | 88.7471 | 78.2834 | 83.0971 | 67.1826 | 71.1909 | 74.1883 | 77.4949 | 79.2241 | 80.7222 | 84.4386 | 82.1874 | 88.2514 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 | 96.163 |  | 78.9259 | 83.0507 | 93.5713 | 83.4456 | 88.276 | 72.801 | 76.5246 | 79.696 | 83.001 | 84.4453 | 86.4203 | 90.0863 | 88.8792 | 93.6691 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298 | 96.4298
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 124904.117 | 131623.685 | 149483.1281 | 131858.3391 | 139966.369 | 113160.542 | 119911.9727 | 124960.7548 | 130530.233 | 133442.8345 | 135966.2535 | 142226.097 | 138434.1892 | 148648.1691 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | 161974.2345 | E @ R (MWh) | 132940.5564 | 139888.2644 | 157608.8341 | 140553.386 | 148689.6803 | 122624.0307 | 128895.9515 | 134237.8004 | 139804.6348 | 142237.2938 | 145563.9135 | 151738.8934 | 149705.6346 | 157773.6841 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927 | 162423.6927
Option 5 Winter POE50 W E @ R (MWh) N 2 | 87432.8819 | 92136.5795 | 104638.1897 | 92300.8374 | 97976.4583 | 79212.3794 | 83938.3809 | 87472.5283 | 91371.1631 | 93409.9842 | 95176.3774 | 99558.2679 | 96903.9325 | 104053.7184 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | 113381.9642 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 39882.1669 | 41966.4793 | 47282.6502 | 42166.0158 | 44606.9041 | 36787.2092 | 38668.7855 | 40271.3401 | 41941.3905 | 42671.1881 | 43669.1741 | 45521.668 | 44911.6904 | 47332.1052 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078 | 48727.1078
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 53.0397 | 55.1225 | 60.9613 | 54.2019 | 56.6902 | 47.7704 | 49.3861 | 50.9401 | 52.2856 | 52.9584 | 53.9524 | 55.09 | 56.2504 | 57.7118 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374 | 57.9374
98% | 23.3386 | 24.1709 | 27.053 | 23.7307 | 24.8233 | 20.4011 | 21.0218 | 21.7307 | 22.2972 | 22.6654 | 23.5454 | 24.1536 | 24.4726 | 25.0661 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 | 24.8915 |  | 26.2533 | 27.2842 | 30.1743 | 26.8286 | 28.0602 | 23.6451 | 24.4449 | 25.214 | 25.88 | 26.2131 | 26.7051 | 27.2682 | 27.8425 | 28.5659 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776 | 28.6776
97% | 23.1017 | 23.9255 | 26.7783 | 23.4898 | 24.5713 | 20.194 | 20.8084 | 21.5101 | 22.0708 | 22.4353 | 23.3064 | 23.9084 | 24.2242 | 24.8116 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 | 24.6387 |  | 51.9736 | 54.0145 | 59.736 | 53.1124 | 55.5507 | 46.8102 | 48.3934 | 49.9161 | 51.2346 | 51.8939 | 52.8679 | 53.9826 | 55.1198 | 56.5518 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729 | 56.7729
95% | 68.2388 | 70.6723 | 79.099 | 69.3852 | 72.5799 | 59.6499 | 61.4648 | 63.5375 | 65.1937 | 66.2705 | 68.8435 | 70.6218 | 71.5544 | 73.2897 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 | 72.7791 |  | 102.348 | 106.3669 | 117.6339 | 104.5906 | 109.3922 | 92.1801 | 95.2978 | 98.2964 | 100.8928 | 102.191 | 104.1091 | 106.3043 | 108.5435 | 111.3635 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989 | 111.7989
90% | 153.4188 | 158.8899 | 177.8355 | 155.9962 | 163.1788 | 134.1086 | 138.1891 | 142.8491 | 146.5726 | 148.9935 | 154.7784 | 158.7765 | 160.8733 | 164.7747 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 | 163.6266 |  | 369.8121 | 384.3337 | 425.0443 | 377.9152 | 395.2646 | 333.0725 | 344.3379 | 355.1725 | 364.554 | 369.2448 | 376.1754 | 384.1072 | 392.1983 | 402.3877 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608 | 403.9608
85% | 248.7872 | 257.6593 | 288.3819 | 252.9668 | 264.6142 | 217.4734 | 224.0905 | 231.6472 | 237.6854 | 241.611 | 250.992 | 257.4753 | 260.8756 | 267.2022 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 | 265.3404 |  | 443.1082 | 460.5079 | 509.2874 | 452.8173 | 473.6054 | 399.0868 | 412.585 | 425.567 | 436.8079 | 442.4285 | 450.7327 | 460.2366 | 469.9313 | 482.1402 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251 | 484.0251
80% | 957.8308 | 991.9883 | 1110.2705 | 973.9221 | 1018.7647 | 837.2727 | 862.7485 | 891.8418 | 915.0887 | 930.2025 | 966.3192 | 991.28 | 1004.371 | 1028.7284 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 | 1021.5604 |  | 505.7431 | 525.6023 | 581.2768 | 516.8245 | 540.5511 | 455.4991 | 470.9053 | 485.7223 | 498.5522 | 504.9672 | 514.4453 | 525.2926 | 536.3577 | 550.2924 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436 | 552.4436
75% | 1450.6665 | 1502.3991 | 1681.5413 | 1475.0373 | 1542.9528 | 1268.0773 | 1306.6611 | 1350.7238 | 1385.932 | 1408.8225 | 1463.5224 | 1501.3264 | 1521.1532 | 1558.0431 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 | 1547.187 |  | 433.7796 | 450.813 | 498.5655 | 443.2843 | 463.6347 | 390.685 | 403.899 | 416.6077 | 427.6119 | 433.1142 | 441.2436 | 450.5474 | 460.038 | 471.9899 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351 | 473.8351
70% | 2215.9834 | 2295.0082 | 2568.6591 | 2253.2113 | 2356.9565 | 1937.067 | 1996.0062 | 2063.3148 | 2117.0975 | 2152.064 | 2235.6216 | 2293.3696 | 2323.6562 | 2380.0079 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 | 2363.4245 |  | 463.7644 | 481.9752 | 533.0286 | 473.926 | 495.6832 | 417.6909 | 431.8183 | 445.4055 | 457.1704 | 463.053 | 471.7443 | 481.6912 | 491.8378 | 504.616 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886 | 506.5886
65% | 4046.3465 | 4190.6445 | 4690.3262 | 4114.3241 | 4303.761 | 3537.0502 | 3644.6721 | 3767.5764 | 3865.7827 | 3929.631 | 4082.2057 | 4187.6524 | 4242.9552 | 4345.8525 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 | 4315.5715 |  | 1223.3785 | 1271.4174 | 1406.0926 | 1250.1842 | 1307.5782 | 1101.8397 | 1139.1068 | 1174.9489 | 1205.9839 | 1221.5018 | 1244.4289 | 1270.6683 | 1297.4343 | 1331.1421 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459 | 1336.3459
60% | 7863.4534 | 8143.8744 | 9114.9291 | 7995.5573 | 8363.6988 | 6873.7141 | 7082.8608 | 7321.7064 | 7512.5553 | 7636.6346 | 7933.1401 | 8138.0597 | 8245.5322 | 8445.4972 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 | 8386.6507 |  | 1365.9727 | 1419.6109 | 1569.9836 | 1395.9029 | 1459.9865 | 1230.2676 | 1271.8786 | 1311.8983 | 1346.5507 | 1363.8773 | 1389.4767 | 1418.7745 | 1448.6603 | 1486.297 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073 | 1492.1073
55% | 9114.4977 | 9439.5326 | 10565.0783 | 9267.6189 | 9694.3302 | 7967.2948 | 8209.716 | 8486.561 | 8707.7731 | 8851.593 | 9195.2713 | 9432.7929 | 9557.3638 | 9789.1424 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 | 9720.9337 |  | 2222.2044 | 2309.4645 | 2554.0952 | 2270.8956 | 2375.1488 | 2001.4354 | 2069.1293 | 2134.2345 | 2190.608 | 2218.7955 | 2260.4413 | 2308.1038 | 2356.723 | 2417.9515 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039 | 2427.4039
50% | 10722.7294 | 11105.1159 | 12429.2615 | 10902.8685 | 11404.872 | 9373.1053 | 9658.3011 | 9983.9947 | 10244.2392 | 10413.4358 | 10817.7554 | 11097.187 | 11243.7382 | 11516.4136 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 | 11436.1696 |  | 3876.0308 | 4028.2324 | 4454.9241 | 3960.9595 | 4142.8008 | 3490.9594 | 3609.033 | 3722.5914 | 3820.9196 | 3870.085 | 3942.7248 | 4025.8591 | 4110.662 | 4217.4584 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455 | 4233.9455
45% | 19076.649 | 19756.9472 | 22112.715 | 19397.1318 | 20290.2389 | 16675.5528 | 17182.9403 | 17762.3771 | 18225.3742 | 18526.3893 | 19245.7083 | 19742.841 | 20003.568 | 20488.6808 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 | 20345.9199 |  | 7722.7432 | 8025.9952 | 8876.1511 | 7891.9581 | 8254.2653 | 6955.513 | 7190.7671 | 7417.025 | 7612.9377 | 7710.8964 | 7855.6268 | 8021.2664 | 8190.2308 | 8403.0158 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653 | 8435.8653
40% | 21841.7413 | 22620.6463 | 25317.8743 | 22208.6769 | 23231.2367 | 19092.6147 | 19673.5463 | 20336.9704 | 20867.0772 | 21211.7234 | 22035.3052 | 22604.4954 | 22903.0139 | 23458.4421 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 | 23294.9885 |  | 13151.3186 | 13667.7365 | 15115.4956 | 13439.4804 | 14056.4655 | 11844.7766 | 12245.3986 | 12630.7008 | 12964.3271 | 13131.1444 | 13377.6105 | 13659.6838 | 13947.4189 | 14309.7776 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181 | 14365.7181
35% | 13247.9197 | 13720.3578 | 15356.3382 | 13470.4814 | 14090.7062 | 11580.4607 | 11932.8198 | 12335.2139 | 12656.7456 | 12865.7878 | 13365.3242 | 13710.5617 | 13891.6254 | 14228.5156 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 | 14129.3743 |  | 15921.911 | 16547.1229 | 18299.8818 | 16270.7799 | 17017.7455 | 14340.1194 | 14825.1406 | 15291.6145 | 15695.5259 | 15897.4867 | 16195.8759 | 16537.3736 | 16885.7261 | 17324.423 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485 | 17392.1485
30% | 5490.4971 | 5686.2954 | 6364.3147 | 5582.736 | 5839.7834 | 4799.4317 | 4945.4642 | 5112.2333 | 5245.4896 | 5332.1255 | 5539.1545 | 5682.2355 | 5757.2759 | 5896.8975 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 | 5855.8091 |  | 24323.6426 | 25278.7685 | 27956.4296 | 24856.6039 | 25997.731 | 21907.1654 | 22648.1244 | 23360.7489 | 23977.7978 | 24286.3299 | 24742.1742 | 25263.8748 | 25796.0471 | 26466.2371 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003 | 26569.7003
25% | 3277.4755 | 3394.3546 | 3799.0887 | 3332.5363 | 3485.9771 | 2864.9537 | 2952.1257 | 3051.6762 | 3131.2217 | 3182.9378 | 3306.5209 | 3391.931 | 3436.7254 | 3520.0705 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 | 3495.5434 |  | 20684.1582 | 21496.3711 | 23773.3806 | 21137.3739 | 22107.7571 | 18629.2524 | 19259.3435 | 19865.3399 | 20390.0613 | 20652.4286 | 21040.0661 | 21483.7059 | 21936.2506 | 22506.1619 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441 | 22594.1441
20% | 3486.5752 | 3610.9111 | 4041.4669 | 3545.1488 | 3708.379 | 3047.7349 | 3140.4685 | 3246.3702 | 3330.9906 | 3386.0061 | 3517.4737 | 3608.3329 | 3655.9851 | 3744.6476 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 | 3718.5556 |  | 5487.2123 | 5702.6808 | 6306.7389 | 5607.4439 | 5864.8727 | 4942.075 | 5109.2292 | 5269.9914 | 5409.1926 | 5478.7948 | 5581.6295 | 5699.3209 | 5819.3745 | 5970.5638 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043 | 5993.9043
15% | 3611.5612 | 3740.3542 | 4186.3445 | 3672.2345 | 3841.3161 | 3156.9894 | 3253.0473 | 3362.7453 | 3450.3992 | 3507.3869 | 3643.5673 | 3737.6836 | 3787.0441 | 3878.8849 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 | 3851.8576 |  | 3400.2725 | 3533.7923 | 3908.1103 | 3474.7767 | 3634.2982 | 3062.4662 | 3166.047 | 3265.6668 | 3351.9259 | 3395.0565 | 3458.7803 | 3531.7103 | 3606.1042 | 3699.792 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554 | 3714.2554
10% | 2407.9049 | 2493.774 | 2791.1252 | 2448.3571 | 2561.0874 | 2104.8322 | 2168.876 | 2242.0141 | 2300.4548 | 2338.4497 | 2429.244 | 2491.9934 | 2524.9031 | 2586.1353 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 | 2568.1156 |  | 972.8391 | 1011.0399 | 1118.1346 | 994.1552 | 1039.7953 | 876.1906 | 905.8257 | 934.3276 | 959.0068 | 971.3467 | 989.5785 | 1010.4443 | 1031.7288 | 1058.5335 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716 | 1062.6716
5% | 191.9216 | 198.7657 | 222.4661 | 195.1458 | 204.131 | 167.7652 | 172.8698 | 178.6993 | 183.3573 | 186.3857 | 193.6224 | 198.6238 | 201.2469 | 206.1274 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 | 204.6911 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 109520.6382 | 113426.2871 | 126950.9475 | 111360.5567 | 116487.9592 | 95735.7439 | 98648.6982 | 101975.2934 | 104633.3983 | 106361.5513 | 110491.2219 | 113345.3023 | 114842.1576 | 117627.2311 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | 116807.6286 | E @ R (MWh) | 102801.5058 | 106838.2526 | 118155.1262 | 105054.015 | 109876.8775 | 92588.5007 | 95720.0914 | 98731.9297 | 101339.8266 | 102643.8076 | 104570.389 | 106775.3057 | 109024.48 | 111856.9729 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25 | 112294.25
Option 5 Summer POE50 W E @ R (MWh) N 2 | 76664.4467 | 79398.4009 | 88865.6632 | 77952.3897 | 81541.5715 | 67015.0207 | 69054.0888 | 71382.7053 | 73243.3788 | 74453.0859 | 77343.8554 | 79341.7116 | 80389.5103 | 82339.0618 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | 81765.34 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 30840.4517 | 32051.4758 | 35446.5379 | 31516.2045 | 32963.0633 | 27776.5502 | 28716.0274 | 29619.5789 | 30401.948 | 30793.1423 | 31371.1167 | 32032.5917 | 32707.344 | 33557.0919 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275 | 33688.275
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 44.8129 | 47.0825 | 53.6371 | 59.2202 | 62.211 | 64.3561 | 66.8847 | 68.7479 | 70.8327 | 71.9273 | 72.8415 | 75.2154 | 73.6294 | 77.5338 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 | 82.7657 |  | 47.9778 | 50.3372 | 56.8372 | 62.6444 | 65.6464 | 68.083 | 70.4227 | 72.4013 | 74.4851 | 75.3907 | 76.6213 | 78.9617 | 78.0683 | 81.1275 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427 | 82.9427
98% | 133.0877 | 139.8278 | 159.2942 | 175.875 | 184.7574 | 191.1279 | 198.6375 | 204.1708 | 210.3624 | 213.6133 | 216.3284 | 223.3784 | 218.6683 | 230.2636 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 | 245.8015 |  | 142.4869 | 149.4938 | 168.7978 | 186.0445 | 194.96 | 202.1961 | 209.1449 | 215.021 | 221.2095 | 223.8991 | 227.5536 | 234.5043 | 231.8511 | 240.9366 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272 | 246.3272
97% | 58.5496 | 61.5148 | 70.0787 | 77.3731 | 81.2808 | 84.0833 | 87.387 | 89.8213 | 92.5452 | 93.9754 | 95.1699 | 98.2714 | 96.1993 | 101.3004 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 | 108.136 |  | 62.6846 | 65.7672 | 74.2596 | 81.847 | 85.7692 | 88.9526 | 92.0096 | 94.5947 | 97.3172 | 98.5004 | 100.1082 | 103.166 | 101.9988 | 105.9958 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673 | 108.3673
95% | 144.122 | 151.421 | 172.5013 | 190.4568 | 200.0757 | 206.9743 | 215.1065 | 221.0987 | 227.8036 | 231.324 | 234.2643 | 241.8987 | 236.7982 | 249.3548 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 | 266.181 |  | 154.3005 | 161.8884 | 182.7929 | 201.4695 | 211.1242 | 218.9603 | 226.4852 | 232.8485 | 239.5501 | 242.4626 | 246.4201 | 253.9471 | 251.074 | 260.9127 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503 | 266.7503
90% | 1471.9961 | 1546.5443 | 1761.8495 | 1945.239 | 2043.4816 | 2113.9409 | 2196.9997 | 2258.2007 | 2326.6818 | 2362.6375 | 2392.6678 | 2470.6429 | 2418.5479 | 2546.7958 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 | 2718.6508 |  | 1575.9548 | 1653.4542 | 1866.9629 | 2057.7173 | 2156.3256 | 2236.3597 | 2313.2156 | 2378.2077 | 2446.6546 | 2476.4018 | 2516.8222 | 2593.6996 | 2564.3544 | 2664.8427 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649 | 2724.4649
85% | 3467.9357 | 3643.567 | 4150.8133 | 4582.8679 | 4814.3219 | 4980.3196 | 5176.0013 | 5320.1872 | 5481.5246 | 5566.2341 | 5636.9837 | 5820.6885 | 5697.9559 | 6000.1003 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 | 6404.9804 |  | 3712.8562 | 3895.4403 | 4398.4542 | 4847.8603 | 5080.1756 | 5268.7312 | 5449.7992 | 5602.9166 | 5764.1735 | 5834.2562 | 5929.4843 | 6110.6027 | 6041.4672 | 6278.2117 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782 | 6418.6782
80% | 6279.4408 | 6597.4587 | 7515.9369 | 8298.2644 | 8717.3614 | 9017.9359 | 9372.2595 | 9633.3389 | 9925.4749 | 10078.8597 | 10206.9669 | 10539.6037 | 10317.3701 | 10864.4674 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 | 11597.5894 |  | 6722.9218 | 7053.5293 | 7964.3439 | 8778.0899 | 9198.7466 | 9540.1668 | 9868.0293 | 10145.2812 | 10437.2713 | 10564.171 | 10736.6019 | 11064.5556 | 10939.3709 | 11368.0477 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922 | 11622.3922
75% | 7341.5899 | 7713.3997 | 8787.2358 | 9701.8917 | 10191.8778 | 10543.2935 | 10957.5499 | 11262.7902 | 11604.3401 | 11783.6695 | 11933.4457 | 12322.3471 | 12062.5233 | 12702.1605 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 | 13559.288 |  | 7860.0844 | 8246.6133 | 9311.4896 | 10262.8782 | 10754.6878 | 11153.8583 | 11537.1777 | 11861.326 | 12202.7054 | 12351.0699 | 12552.6669 | 12936.0931 | 12789.7337 | 13290.9199 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861 | 13588.2861
70% | 8609.4132 | 9045.431 | 10304.7084 | 11377.3168 | 11951.9188 | 12364.0207 | 12849.8153 | 13207.7677 | 13608.3001 | 13818.5979 | 13994.239 | 14450.3 | 14145.6071 | 14895.7037 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 | 15900.849 |  | 9217.4468 | 9670.7256 | 10919.4959 | 12035.1804 | 12611.9208 | 13080.0243 | 13529.5394 | 13909.665 | 14309.9974 | 14483.983 | 14720.3939 | 15170.0342 | 14998.3999 | 15586.1363 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548 | 15934.8548
65% | 9434.3615 | 9912.1583 | 11292.0988 | 12467.4839 | 13097.1439 | 13548.7331 | 14081.0763 | 14473.3274 | 14912.2385 | 15142.687 | 15335.1579 | 15834.9184 | 15501.03 | 16323.0003 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 | 17424.4579 |  | 10100.6565 | 10597.3682 | 11965.7949 | 13188.3835 | 13820.3869 | 14333.3437 | 14825.931 | 15242.4801 | 15681.172 | 15871.8288 | 16130.8925 | 16623.617 | 16435.5368 | 17079.5897 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222 | 17461.7222
60% | 10264.9397 | 10784.8005 | 12286.2276 | 13565.0907 | 14250.1844 | 14741.5305 | 15320.7398 | 15747.5237 | 16225.0755 | 16475.8121 | 16685.2277 | 17228.9858 | 16865.7027 | 17760.0373 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 | 18958.4646 |  | 10989.8936 | 11530.3346 | 13019.2342 | 14349.4565 | 15037.0999 | 15595.2162 | 16131.1697 | 16584.3907 | 17061.7041 | 17269.1458 | 17551.0168 | 18087.1195 | 17882.4813 | 18583.235 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095 | 18999.0095
55% | 10289.7106 | 10810.8259 | 12315.8763 | 13597.8255 | 14284.5724 | 14777.1042 | 15357.7112 | 15785.525 | 16264.2293 | 16515.5709 | 16725.4919 | 17270.5622 | 16906.4024 | 17802.8951 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 | 19004.2144 |  | 11016.414 | 11558.1591 | 13050.6517 | 14384.0841 | 15073.3869 | 15632.85 | 16170.0968 | 16624.4115 | 17102.8767 | 17310.819 | 17593.3703 | 18130.7667 | 17925.6346 | 18628.0793 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572 | 19044.8572
50% | 12122.0117 | 12735.9227 | 14508.9791 | 16019.2065 | 16828.2433 | 17408.4808 | 18092.4773 | 18596.4724 | 19160.4201 | 19456.5184 | 19703.8203 | 20345.9519 | 19916.9458 | 20973.078 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 | 22388.3177 |  | 12978.1201 | 13616.3344 | 15374.5969 | 16945.4752 | 17757.523 | 18416.6103 | 19049.5254 | 19584.7405 | 20148.4065 | 20393.3773 | 20726.2428 | 21359.3341 | 21117.6738 | 21945.2038 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977 | 22436.1977
45% | 15160.584 | 15928.3814 | 18145.8822 | 20034.6718 | 21046.5063 | 21772.1894 | 22627.6403 | 23257.9698 | 23963.2798 | 24333.5998 | 24642.8917 | 25445.9837 | 24909.4404 | 26230.3088 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 | 28000.3005 |  | 16231.2893 | 17029.4821 | 19228.4806 | 21193.1242 | 22208.7245 | 23033.0224 | 23824.5875 | 24493.9627 | 25198.9204 | 25505.2971 | 25921.6005 | 26713.386 | 26411.1498 | 27446.1131 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824 | 28060.1824
40% | 16053.0895 | 16866.0872 | 19214.1326 | 21214.1155 | 22285.5169 | 23053.921 | 23959.7324 | 24627.1694 | 25374.0011 | 25766.1219 | 26093.6219 | 26943.9921 | 26375.8624 | 27774.4905 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 | 29648.6818 |  | 17186.8274 | 18032.0099 | 20360.4638 | 22440.7662 | 23516.1549 | 24388.9794 | 25227.1441 | 25935.9254 | 26682.3841 | 27006.7972 | 27447.6084 | 28286.0065 | 27965.9776 | 29061.8693 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089 | 29712.089
35% | 6564.3069 | 6896.7517 | 7856.8966 | 8674.7143 | 9112.8236 | 9427.0336 | 9797.431 | 10070.3543 | 10375.743 | 10536.0861 | 10670.0048 | 11017.7317 | 10785.4165 | 11357.3328 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 | 12123.7128 |  | 7027.9064 | 7373.5119 | 8325.6455 | 9176.3069 | 9616.0467 | 9972.9554 | 10315.6913 | 10605.5208 | 10910.757 | 11043.4135 | 11223.6667 | 11566.498 | 11435.6343 | 11883.7579 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408 | 12149.6408
30% | 2024.8391 | 2127.3857 | 2423.5539 | 2675.8195 | 2810.9596 | 2907.8814 | 3022.135 | 3106.3214 | 3200.5222 | 3249.9819 | 3291.2908 | 3398.5513 | 3326.8909 | 3503.3053 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 | 3739.7044 |  | 2167.8419 | 2274.4481 | 2568.1451 | 2830.5418 | 2966.1848 | 3076.2776 | 3181.9986 | 3271.3999 | 3365.5537 | 3406.4732 | 3462.0744 | 3567.8249 | 3527.4584 | 3665.6875 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022 | 3747.7022
25% | 1490.3867 | 1565.8663 | 1783.8614 | 1969.5421 | 2069.0121 | 2140.3516 | 2224.4482 | 2286.4138 | 2355.7505 | 2392.1554 | 2422.5608 | 2501.5102 | 2448.7644 | 2578.6146 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 | 2752.6166 |  | 1595.6442 | 1674.1118 | 1890.2881 | 2083.4257 | 2183.266 | 2264.2999 | 2342.1161 | 2407.9201 | 2477.2222 | 2507.3411 | 2548.2665 | 2626.1043 | 2596.3924 | 2698.1362 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033 | 2758.5033
20% | 1185.6287 | 1245.674 | 1419.093 | 1566.8052 | 1645.9354 | 1702.6872 | 1769.5875 | 1818.8822 | 1874.0407 | 1903.0015 | 1927.1896 | 1989.9951 | 1948.0349 | 2051.333 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 | 2189.7546 |  | 1269.3629 | 1331.7853 | 1503.7572 | 1657.4016 | 1736.8263 | 1801.2902 | 1863.1943 | 1915.5426 | 1970.6736 | 1994.6337 | 2027.1906 | 2089.1119 | 2065.4756 | 2146.4146 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377 | 2194.4377
15% | 930.0373 | 977.1384 | 1113.1727 | 1229.0419 | 1291.1136 | 1335.6312 | 1388.1094 | 1426.7775 | 1470.0452 | 1492.7628 | 1511.7365 | 1561.0028 | 1528.0882 | 1609.1178 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 | 1717.6993 |  | 995.7205 | 1044.6863 | 1179.5855 | 1300.108 | 1362.4107 | 1412.9779 | 1461.5371 | 1502.6004 | 1545.8465 | 1564.6414 | 1590.1799 | 1638.7525 | 1620.2116 | 1683.7022 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728 | 1721.3728
10% | 653.0528 | 686.1262 | 781.6467 | 863.0076 | 906.5931 | 937.8524 | 974.7015 | 1001.8534 | 1032.2352 | 1048.1869 | 1061.5099 | 1096.1037 | 1072.9917 | 1129.889 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 | 1206.1327 |  | 699.1742 | 733.5569 | 828.2803 | 912.9088 | 956.6564 | 992.1637 | 1026.2609 | 1055.0947 | 1085.4612 | 1098.6586 | 1116.5912 | 1150.6979 | 1137.6789 | 1182.2607 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121 | 1208.7121
5% | 67.5572 | 70.9786 | 80.86 | 89.2766 | 93.7855 | 97.0192 | 100.8312 | 103.64 | 106.7829 | 108.4331 | 109.8114 | 113.39 | 110.9991 | 116.8851 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 | 124.7723 |  | 72.3284 | 75.8852 | 85.6842 | 94.4388 | 98.9645 | 102.6376 | 106.1649 | 109.1477 | 112.2891 | 113.6543 | 115.5094 | 119.0377 | 117.6909 | 122.3028 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392 | 125.0392
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 113791.4537 | 119554.3436 | 136198.336 | 150375.106 | 157969.6764 | 163416.4678 | 169837.2625 | 174568.3536 | 179862.2295 | 182641.7565 | 184963.2222 | 190991.0249 | 186963.8689 | 196877.968 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | 210163.0714 | E @ R (MWh) | 121827.8931 | 127818.9231 | 144324.042 | 159070.1529 | 166692.9877 | 172879.9564 | 178821.2413 | 183845.3992 | 189136.6314 | 191436.2158 | 194560.8823 | 200503.8213 | 198235.3142 | 206003.483 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296 | 210612.5296
Option 6 Winter POE50 W E @ R (MWh) N 2 | 79654.0176 | 83688.0405 | 95338.8352 | 105262.5742 | 110578.7735 | 114391.5274 | 118886.0837 | 122197.8475 | 125903.5606 | 127849.2296 | 129474.2556 | 133693.7175 | 130874.7082 | 137814.5776 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | 147114.1499 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 36548.3679 | 38345.6769 | 43297.2126 | 47721.0459 | 50007.8963 | 51863.9869 | 53646.3724 | 55153.6198 | 56740.9894 | 57430.8647 | 58368.2647 | 60151.1464 | 59470.5943 | 61801.0449 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589 | 63183.7589
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49.3273 | 51.0905 | 56.5233 | 60.3878 | 62.7046 | 64.5593 | 66.0646 | 67.5124 | 68.7659 | 69.3942 | 70.3207 | 71.3808 | 72.4627 | 73.8239 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358 | 74.0358
98% | 21.5011 | 22.1752 | 24.8563 | 26.7925 | 27.8003 | 28.7112 | 29.2773 | 29.9336 | 30.4545 | 30.8007 | 31.6474 | 32.2172 | 32.4973 | 33.0412 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 | 32.8598 |  | 24.4158 | 25.2885 | 27.9776 | 29.8904 | 31.0372 | 31.9553 | 32.7003 | 33.417 | 34.0374 | 34.3484 | 34.807 | 35.3317 | 35.8672 | 36.541 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459 | 36.6459
97% | 21.2828 | 21.95 | 24.6039 | 26.5205 | 27.518 | 28.4197 | 28.98 | 29.6297 | 30.1453 | 30.488 | 31.3261 | 31.8901 | 32.1674 | 32.7057 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 | 32.5262 |  | 48.3358 | 50.0635 | 55.3871 | 59.1739 | 61.4442 | 63.2617 | 64.7367 | 66.1554 | 67.3836 | 67.9993 | 68.9073 | 69.946 | 71.0062 | 72.34 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477 | 72.5477
95% | 62.8661 | 64.837 | 72.6762 | 78.3376 | 81.2841 | 83.9474 | 85.6026 | 87.5216 | 89.0446 | 90.057 | 92.5324 | 94.1985 | 95.0174 | 96.6077 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 | 96.0773 |  | 95.1844 | 98.5866 | 109.07 | 116.5271 | 120.9977 | 124.5768 | 127.4815 | 130.2752 | 132.6939 | 133.9064 | 135.6943 | 137.7399 | 139.8275 | 142.4542 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631 | 142.8631
90% | 141.3395 | 145.7707 | 163.3952 | 176.1236 | 182.7481 | 188.736 | 192.4571 | 196.7718 | 200.1957 | 202.4719 | 208.0373 | 211.7831 | 213.6243 | 217.1997 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 | 216.007 |  | 343.9279 | 356.2212 | 394.1007 | 421.0454 | 437.1989 | 450.1311 | 460.6264 | 470.721 | 479.4606 | 483.8415 | 490.3016 | 497.693 | 505.2361 | 514.727 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046 | 516.2046
85% | 229.1992 | 236.385 | 264.9652 | 285.6059 | 296.3482 | 306.0584 | 312.0926 | 319.0893 | 324.6417 | 328.3328 | 337.3578 | 343.4321 | 346.4177 | 352.2157 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 | 350.2817 |  | 412.0938 | 426.8235 | 472.2108 | 504.4958 | 523.8509 | 539.3463 | 551.9217 | 564.0171 | 574.4888 | 579.738 | 587.4785 | 596.3348 | 605.373 | 616.745 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155 | 618.5155
80% | 882.4169 | 910.0821 | 1020.1158 | 1099.5825 | 1140.9406 | 1178.3247 | 1201.5566 | 1228.494 | 1249.8706 | 1264.0813 | 1298.8275 | 1322.2137 | 1333.7082 | 1356.0304 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 | 1348.5845 |  | 470.3447 | 487.1565 | 538.9594 | 575.808 | 597.899 | 615.5847 | 629.9377 | 643.7428 | 655.6947 | 661.6859 | 670.5206 | 680.6288 | 690.9445 | 703.924 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447 | 705.9447
75% | 1336.4496 | 1378.3494 | 1544.9992 | 1665.3541 | 1727.9923 | 1784.6118 | 1819.7973 | 1860.5948 | 1892.9703 | 1914.493 | 1967.1173 | 2002.5363 | 2019.9452 | 2053.7529 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 | 2042.4758 |  | 403.4182 | 417.8378 | 462.2695 | 493.8748 | 512.8225 | 527.9916 | 540.3023 | 552.143 | 562.3943 | 567.5329 | 575.1106 | 583.7804 | 592.6283 | 603.7609 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941 | 605.4941
70% | 2041.51 | 2105.5146 | 2360.0824 | 2543.9321 | 2639.6158 | 2726.1056 | 2779.8537 | 2842.1744 | 2891.63 | 2924.5072 | 3004.8941 | 3058.9989 | 3085.592 | 3137.2355 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 | 3120.009 |  | 431.3042 | 446.7206 | 494.2236 | 528.0136 | 548.271 | 564.4887 | 577.6504 | 590.3096 | 601.2694 | 606.7633 | 614.8647 | 624.1339 | 633.5933 | 645.4955 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485 | 647.3485
65% | 3727.7612 | 3844.6325 | 4309.4689 | 4645.1752 | 4819.8918 | 4977.8207 | 5075.9638 | 5189.7603 | 5280.0654 | 5340.0986 | 5486.8836 | 5585.6781 | 5634.2366 | 5728.5367 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 | 5697.0813 |  | 1137.7508 | 1178.4181 | 1303.7278 | 1392.8636 | 1446.3011 | 1489.0824 | 1523.8018 | 1557.196 | 1586.1073 | 1600.5998 | 1621.9708 | 1646.4222 | 1671.3756 | 1702.7726 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608 | 1707.6608
60% | 7244.3318 | 7471.4532 | 8374.7914 | 9027.1849 | 9366.72 | 9673.6306 | 9864.3565 | 10085.5026 | 10260.9967 | 10377.6621 | 10662.9161 | 10854.908 | 10949.274 | 11132.5317 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 | 11071.4031 |  | 1270.3645 | 1315.7718 | 1455.6874 | 1555.2126 | 1614.8787 | 1662.6464 | 1701.4127 | 1738.6992 | 1770.9804 | 1787.1621 | 1811.024 | 1838.3254 | 1866.1873 | 1901.244 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019 | 1906.7019
55% | 8396.8763 | 8660.1319 | 9707.1875 | 10463.3744 | 10856.9281 | 11212.6669 | 11433.7366 | 11690.0661 | 11893.4807 | 12028.707 | 12359.3439 | 12581.8809 | 12691.2602 | 12903.6735 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 | 12832.8196 |  | 2066.6661 | 2140.5361 | 2368.1548 | 2530.0653 | 2627.1319 | 2704.8419 | 2767.908 | 2828.5667 | 2881.0828 | 2907.4076 | 2946.2269 | 2990.6416 | 3035.9681 | 3092.9993 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784 | 3101.8784
50% | 9878.4854 | 10188.1918 | 11419.998 | 12309.6122 | 12772.6075 | 13191.1157 | 13451.1926 | 13752.7508 | 13992.0574 | 14151.1441 | 14540.1211 | 14801.9243 | 14930.6033 | 15180.4964 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 | 15097.1404 |  | 3604.7366 | 3733.5828 | 4130.6016 | 4413.0105 | 4582.3168 | 4717.8606 | 4827.8624 | 4933.665 | 5025.2649 | 5071.1815 | 5138.8911 | 5216.3605 | 5295.4203 | 5394.8957 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828 | 5410.3828
45% | 17574.667 | 18125.6611 | 20317.1492 | 21899.8487 | 22723.5568 | 23468.1184 | 23930.8174 | 24467.3152 | 24893.062 | 25176.0909 | 25868.114 | 26333.8841 | 26562.8151 | 27007.3962 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 | 26859.0988 |  | 7182.2069 | 7438.9246 | 8229.9592 | 8792.6409 | 9129.9727 | 9400.0352 | 9619.2066 | 9830.0116 | 10012.5185 | 10104.0044 | 10238.9114 | 10393.2642 | 10550.7858 | 10748.9841 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412 | 10779.8412
40% | 20122.0524 | 20752.9111 | 23262.0476 | 25074.1537 | 26017.2554 | 26869.7386 | 27399.5041 | 28013.7654 | 28501.2227 | 28825.2755 | 29617.6049 | 30150.8868 | 30413.0005 | 30922.022 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 | 30752.2295 |  | 12230.8212 | 12667.9944 | 14015.0738 | 14973.2833 | 15547.737 | 16007.6354 | 16380.8698 | 16739.8566 | 17050.6539 | 17206.4482 | 17436.1859 | 17699.0385 | 17967.2873 | 18304.8059 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534 | 18357.3534
35% | 12204.8572 | 12587.4991 | 14109.3943 | 15208.5116 | 15780.5418 | 16297.6081 | 16618.9328 | 16991.5077 | 17287.1707 | 17483.7222 | 17964.3027 | 18287.7602 | 18446.743 | 18755.4857 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 | 18652.4995 |  | 14807.4921 | 15336.7648 | 16967.6338 | 18127.7096 | 18823.1836 | 19379.969 | 19831.8328 | 20266.4475 | 20642.7205 | 20831.3361 | 21109.4726 | 21427.7005 | 21752.4613 | 22161.0851 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028 | 22224.7028
30% | 5058.208 | 5216.7909 | 5847.5285 | 6303.0491 | 6540.1226 | 6754.4167 | 6887.5872 | 7041.998 | 7164.5332 | 7245.9924 | 7445.1653 | 7579.2198 | 7645.1089 | 7773.0649 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 | 7730.3831 |  | 22621.1631 | 23429.7243 | 25921.1762 | 27693.4049 | 28755.8692 | 29606.4611 | 30296.766 | 30960.7198 | 31535.5459 | 31823.6908 | 32248.5955 | 32734.747 | 33230.8788 | 33855.1266 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143 | 33952.3143
25% | 3019.4266 | 3114.0904 | 3490.6004 | 3762.5171 | 3904.0348 | 4031.9546 | 4111.4489 | 4203.6223 | 4276.768 | 4325.3939 | 4444.2874 | 4524.3093 | 4563.6409 | 4640.0225 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 | 4614.5441 |  | 19236.4164 | 19923.9947 | 22042.657 | 23549.7117 | 24453.2021 | 25176.5222 | 25763.5386 | 26328.1466 | 26816.963 | 27061.9935 | 27423.3207 | 27836.7306 | 28258.6275 | 28789.4707 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165 | 28872.1165
20% | 3212.063 | 3312.7664 | 3713.2973 | 4002.562 | 4153.1084 | 4289.1894 | 4373.7554 | 4471.8093 | 4549.6216 | 4601.3498 | 4727.8286 | 4812.9558 | 4854.7968 | 4936.0514 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 | 4908.9475 |  | 5103.147 | 5285.5517 | 5847.6026 | 6247.4027 | 6487.0859 | 6678.9724 | 6834.6994 | 6984.4819 | 7114.1579 | 7179.161 | 7275.016 | 7384.6877 | 7496.611 | 7637.4361 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608 | 7659.3608
15% | 3327.2083 | 3431.5217 | 3846.4108 | 4146.0449 | 4301.9881 | 4442.9473 | 4530.5447 | 4632.1137 | 4712.7154 | 4766.298 | 4897.3107 | 4985.4896 | 5028.8304 | 5112.9978 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 | 5084.9224 |  | 3162.278 | 3275.3091 | 3623.5964 | 3871.3414 | 4019.8663 | 4138.773 | 4235.2728 | 4328.0888 | 4408.4454 | 4448.726 | 4508.1247 | 4576.0852 | 4645.4409 | 4732.7063 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925 | 4746.2925
10% | 2218.3208 | 2287.8687 | 2564.4841 | 2764.2566 | 2868.2272 | 2962.2078 | 3020.6109 | 3088.329 | 3142.0679 | 3177.7926 | 3265.1415 | 3323.9323 | 3352.8285 | 3408.9447 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 | 3390.2263 |  | 904.7474 | 937.0863 | 1036.7334 | 1107.6148 | 1150.1087 | 1184.1287 | 1211.7378 | 1238.2931 | 1261.2836 | 1272.8081 | 1289.8025 | 1309.2464 | 1329.0895 | 1354.0567 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438 | 1357.9438
5% | 176.8108 | 182.3541 | 204.4017 | 220.3245 | 228.6115 | 236.1022 | 240.7572 | 246.1546 | 250.4379 | 253.2853 | 260.2474 | 264.9333 | 267.2365 | 271.7092 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 | 270.2173 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 100897.6339 | 104060.937 | 116642.4538 | 125728.8639 | 130457.8414 | 134732.4318 | 137388.8252 | 140468.9042 | 142913.1523 | 144538.0445 | 148511.0071 | 151185.0325 | 152499.3441 | 155051.7216 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | 154200.3341 | E @ R (MWh) | 95606.1423 | 99023.4475 | 109553.3261 | 117043.4783 | 121533.8798 | 125128.8238 | 128046.3303 | 130852.4662 | 133281.9128 | 134499.729 | 136295.5472 | 138350.2192 | 140447.0721 | 143085.3946 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149 | 143496.149
Option 6 Summer POE50 W E @ R (MWh) N 2 | 70628.3437 | 72842.6559 | 81649.7177 | 88010.2047 | 91320.489 | 94312.7022 | 96172.1776 | 98328.233 | 100039.2066 | 101176.6312 | 103957.7049 | 105829.5228 | 106749.5409 | 108536.2051 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | 107940.2339 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 28681.8427 | 29707.0342 | 32865.9978 | 35113.0435 | 36460.1639 | 37538.6471 | 38413.8991 | 39255.7399 | 39984.5738 | 40349.9187 | 40888.6642 | 41505.0658 | 42134.1216 | 42925.6184 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447 | 43048.8447
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 49.1893 | 51.8356 | 58.8689 | 64.7915 | 67.9845 | 70.2915 | 72.9503 | 74.9386 | 77.1319 | 78.279 | 79.2727 | 81.738 | 80.2446 | 84.2671 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 |  | 52.3542 | 55.0903 | 62.0689 | 68.2157 | 71.4199 | 74.0183 | 76.4883 | 78.592 | 80.7843 | 81.7424 | 83.0524 | 85.4842 | 84.6835 | 87.8608 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921
98% | 146.0848 | 153.9438 | 174.8318 | 192.4209 | 201.9038 | 208.7551 | 216.6514 | 222.5563 | 229.0702 | 232.4767 | 235.428 | 242.7494 | 238.3145 | 250.2605 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 |  | 155.484 | 163.6098 | 184.3354 | 202.5904 | 212.1064 | 219.8233 | 227.1588 | 233.4065 | 239.9173 | 242.7625 | 246.6532 | 253.8753 | 251.4973 | 260.9335 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372
97% | 64.2674 | 67.7249 | 76.9141 | 84.6522 | 88.824 | 91.8381 | 95.3119 | 97.9097 | 100.7754 | 102.274 | 103.5724 | 106.7933 | 104.8422 | 110.0977 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 |  | 68.4024 | 71.9773 | 81.0951 | 89.1261 | 93.3125 | 96.7074 | 99.9345 | 102.6831 | 105.5474 | 106.7991 | 108.5107 | 111.688 | 110.6418 | 114.7931 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857
95% | 158.1967 | 166.7073 | 189.3271 | 208.3746 | 218.6438 | 226.063 | 234.614 | 241.0085 | 248.0625 | 251.7514 | 254.9475 | 262.8758 | 258.0732 | 271.0097 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 |  | 168.3752 | 177.1748 | 199.6187 | 219.3872 | 229.6922 | 238.0489 | 245.9926 | 252.7583 | 259.8089 | 262.89 | 267.1033 | 274.9242 | 272.349 | 282.5676 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457
90% | 1615.7485 | 1702.6723 | 1933.7004 | 2128.2423 | 2233.1271 | 2308.9039 | 2396.2398 | 2461.5504 | 2533.5966 | 2571.2738 | 2603.9165 | 2684.8933 | 2635.8415 | 2767.9686 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 |  | 1719.7072 | 1809.5821 | 2038.8138 | 2240.7207 | 2345.971 | 2431.3227 | 2512.4557 | 2581.5574 | 2653.5695 | 2685.0381 | 2728.071 | 2807.95 | 2781.6479 | 2886.0155 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676
85% | 3806.6079 | 4011.3951 | 4555.6838 | 5014.013 | 5261.1153 | 5439.6409 | 5645.3992 | 5799.2671 | 5969.0038 | 6057.769 | 6134.6733 | 6325.4498 | 6209.8867 | 6521.1704 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 |  | 4051.5284 | 4263.2684 | 4803.3248 | 5279.0053 | 5526.969 | 5728.0525 | 5919.1971 | 6081.9965 | 6251.6527 | 6325.791 | 6427.1739 | 6615.3641 | 6553.398 | 6799.2818 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966
80% | 6892.6794 | 7263.4904 | 8249.0417 | 9078.945 | 9526.3766 | 9849.6355 | 10222.2049 | 10500.8157 | 10808.1605 | 10968.8888 | 11108.1405 | 11453.5823 | 11244.3305 | 11807.9764 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 |  | 7336.1604 | 7719.561 | 8697.4488 | 9558.7704 | 10007.7617 | 10371.8665 | 10717.9747 | 11012.758 | 11319.9569 | 11454.2002 | 11637.7756 | 11978.5342 | 11866.3313 | 12311.5567 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616
75% | 8058.556 | 8492.0887 | 9644.3432 | 10614.6221 | 11137.7355 | 11515.6728 | 11951.2611 | 12276.9981 | 12636.3294 | 12824.2444 | 12987.0502 | 13390.9224 | 13146.2763 | 13805.2613 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 |  | 8577.0505 | 9025.3023 | 10168.597 | 11175.6086 | 11700.5455 | 12126.2375 | 12530.8889 | 12875.534 | 13234.6947 | 13391.6448 | 13606.2715 | 14004.6684 | 13873.4868 | 14394.0207 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296
70% | 9450.1926 | 9958.5923 | 11309.8302 | 12447.6671 | 13061.1172 | 13504.3207 | 14015.1311 | 14397.1198 | 14818.5042 | 15038.8704 | 15229.7912 | 15703.4083 | 15416.5141 | 16189.2995 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 |  | 10058.2262 | 10583.8868 | 11924.6176 | 13105.5307 | 13721.1192 | 14220.3242 | 14694.8551 | 15099.0171 | 15520.2015 | 15704.2554 | 15955.9461 | 16423.1424 | 16269.3069 | 16879.7321 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498
65% | 10355.7039 | 10912.8181 | 12393.5307 | 13640.3944 | 14312.6249 | 14798.2959 | 15358.0518 | 15776.6424 | 16238.4036 | 16479.8851 | 16689.0998 | 17208.0986 | 16893.7145 | 17740.5476 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 |  | 11021.9989 | 11598.028 | 13067.2267 | 14361.2941 | 15035.8679 | 15582.9064 | 16102.9065 | 16545.7951 | 17007.337 | 17209.0269 | 17484.8344 | 17996.7972 | 17828.2213 | 18497.137 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657
60% | 11267.3947 | 11873.5559 | 13484.6268 | 14841.2614 | 15572.6734 | 16101.1017 | 16710.1371 | 17165.5794 | 17667.9929 | 17930.7339 | 18158.3673 | 18723.0575 | 18380.9958 | 19302.3821 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 |  | 11992.3487 | 12619.09 | 14217.6334 | 15625.6273 | 16359.589 | 16954.7874 | 17520.567 | 18002.4464 | 18504.6214 | 18724.0676 | 19024.1565 | 19581.1912 | 19397.7743 | 20125.5797 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494
55% | 11294.5848 | 11902.2087 | 13517.1674 | 14877.0758 | 15610.2528 | 16139.9562 | 16750.4614 | 17207.0028 | 17710.6286 | 17974.0037 | 18202.1864 | 18768.2393 | 18425.3521 | 19348.9619 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 |  | 12021.2882 | 12649.5419 | 14251.9428 | 15663.3344 | 16399.0673 | 16995.7021 | 17562.847 | 18045.8893 | 18549.2761 | 18769.2518 | 19070.0648 | 19628.4438 | 19444.5843 | 20174.146 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279
50% | 13305.825 | 14021.6493 | 15924.1856 | 17526.2545 | 18389.9893 | 19014.0176 | 19733.2361 | 20271.0744 | 20864.3815 | 21174.656 | 21443.4716 | 22110.3222 | 21706.3766 | 22794.4547 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 |  | 14161.9334 | 14902.061 | 16789.8034 | 18452.5232 | 19319.2689 | 20022.1471 | 20690.2843 | 21259.3424 | 21852.3679 | 22111.515 | 22465.8942 | 23123.7043 | 22907.1047 | 23766.5804 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938
45% | 16641.1386 | 17536.3955 | 19915.8324 | 21919.4849 | 22999.7283 | 23780.1792 | 24679.6811 | 25352.3369 | 26094.3658 | 26482.4155 | 26818.6139 | 27652.621 | 27147.4202 | 28508.2421 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 |  | 17711.844 | 18637.4962 | 20998.4308 | 23077.9374 | 24161.9465 | 25041.0121 | 25876.6283 | 26588.3298 | 27330.0065 | 27654.1128 | 28097.3227 | 28920.0233 | 28649.1296 | 29724.0464 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731
40% | 17620.8046 | 18568.7653 | 21088.28 | 23209.8878 | 24353.7253 | 25180.1214 | 26132.5771 | 26844.8323 | 27630.5445 | 28041.4387 | 28397.4292 | 29280.5344 | 28745.5924 | 30186.526 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 |  | 18754.5425 | 19734.688 | 22234.6112 | 24436.5385 | 25584.3634 | 26515.1798 | 27399.9888 | 28153.5883 | 28938.9275 | 29282.114 | 29751.4157 | 30622.5488 | 30335.7076 | 31473.9048 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032
35% | 7205.365 | 7592.9979 | 8623.2586 | 9490.8103 | 9958.5396 | 10296.4632 | 10685.9341 | 10977.1841 | 11298.4715 | 11466.4912 | 11612.0601 | 11973.1728 | 11754.4284 | 12343.644 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 |  | 7668.9645 | 8069.7581 | 9092.0076 | 9992.403 | 10461.7627 | 10842.3851 | 11204.1944 | 11512.3506 | 11833.4855 | 11973.8187 | 12165.722 | 12521.9391 | 12404.6462 | 12870.0691 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149
30% | 2222.5811 | 2342.1511 | 2659.9474 | 2927.5541 | 3071.8308 | 3176.0674 | 3296.2044 | 3386.0439 | 3485.1489 | 3536.9766 | 3581.879 | 3693.2686 | 3625.7942 | 3807.5448 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 |  | 2365.584 | 2489.2135 | 2804.5387 | 3082.2764 | 3227.056 | 3344.4635 | 3456.068 | 3551.1224 | 3650.1803 | 3693.4678 | 3752.6627 | 3862.5421 | 3826.3617 | 3969.927 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706
25% | 1635.9351 | 1723.9448 | 1957.8593 | 2154.8318 | 2261.0269 | 2337.7504 | 2426.1775 | 2492.3041 | 2565.2504 | 2603.3983 | 2636.4489 | 2718.4373 | 2668.7727 | 2802.5506 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 |  | 1741.1926 | 1832.1904 | 2064.286 | 2268.7154 | 2375.2807 | 2461.6987 | 2543.8454 | 2613.8104 | 2686.7222 | 2718.584 | 2762.1545 | 2843.0315 | 2816.4008 | 2922.0723 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759
20% | 1301.415 | 1371.4283 | 1557.5114 | 1714.2064 | 1798.6865 | 1859.7214 | 1930.0667 | 1982.6715 | 2040.7016 | 2071.0489 | 2097.3412 | 2162.5645 | 2123.0554 | 2229.4781 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 |  | 1385.1492 | 1457.5395 | 1642.1756 | 1804.8028 | 1889.5774 | 1958.3244 | 2023.6735 | 2079.3319 | 2137.3345 | 2162.6811 | 2197.3422 | 2261.6813 | 2240.4961 | 2324.5596 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095
15% | 1020.863 | 1075.7832 | 1221.7516 | 1344.6671 | 1410.9355 | 1458.8128 | 1513.9934 | 1555.258 | 1600.7783 | 1624.5835 | 1645.2078 | 1696.3706 | 1665.3787 | 1748.8593 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 |  | 1086.5463 | 1143.3311 | 1288.1644 | 1415.7332 | 1482.2326 | 1536.1595 | 1587.421 | 1631.0809 | 1676.5796 | 1696.4621 | 1723.6512 | 1774.1204 | 1757.5022 | 1823.4438 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491
10% | 716.8288 | 755.3926 | 857.8885 | 944.1973 | 990.7295 | 1024.348 | 1063.0946 | 1092.0698 | 1124.0332 | 1140.7487 | 1155.2307 | 1191.1561 | 1169.3942 | 1228.0126 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 |  | 762.9502 | 802.8233 | 904.5222 | 994.0984 | 1040.7929 | 1078.6592 | 1114.654 | 1145.311 | 1177.2593 | 1191.2204 | 1210.312 | 1245.7504 | 1234.0814 | 1280.3842 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708
5% | 74.1547 | 78.1441 | 88.7471 | 97.6756 | 102.4893 | 105.967 | 109.9753 | 112.9727 | 116.2793 | 118.0085 | 119.5066 | 123.223 | 120.9718 | 127.0358 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 |  | 78.9259 | 83.0507 | 93.5713 | 102.8378 | 107.6682 | 111.5854 | 115.309 | 118.4805 | 121.7854 | 123.2297 | 125.2047 | 128.8707 | 127.6636 | 132.4535 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 124904.117 | 131623.685 | 149483.1281 | 164522.0299 | 172630.0598 | 178487.9236 | 185239.3543 | 190288.1364 | 195857.6146 | 198770.2162 | 201293.6351 | 207553.4786 | 203761.5708 | 213975.5507 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | E @ R (MWh) | 132940.5564 | 139888.2644 | 157608.8341 | 173217.0768 | 181353.3711 | 187951.4123 | 194223.3331 | 199565.182 | 205132.0165 | 207564.6754 | 210891.2951 | 217066.275 | 215033.0162 | 223101.0657 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744
Option 7 Winter POE50 W E @ R (MWh) N 2 | 87432.8819 | 92136.5795 | 104638.1897 | 115165.421 | 120841.0419 | 124941.5465 | 129667.548 | 133201.6955 | 137100.3302 | 139139.1513 | 140905.5446 | 145287.435 | 142633.0996 | 149782.8855 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 39882.1669 | 41966.4793 | 47282.6502 | 51965.123 | 54406.0113 | 56385.4237 | 58266.9999 | 59869.5546 | 61539.6049 | 62269.4026 | 63267.3885 | 65119.8825 | 64509.9049 | 66930.3197 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 53.0397 | 55.1225 | 60.9613 | 65.1138 | 67.6021 | 69.5943 | 71.21 | 72.7639 | 74.1094 | 74.7822 | 75.7762 | 76.9138 | 78.0743 | 79.5357 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613
98% | 23.3386 | 24.1709 | 27.053 | 29.1318 | 30.2245 | 31.2033 | 31.8241 | 32.533 | 33.0994 | 33.4677 | 34.3477 | 34.9559 | 35.2749 | 35.8684 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 |  | 26.2533 | 27.2842 | 30.1743 | 32.2297 | 33.4614 | 34.4474 | 35.2471 | 36.0163 | 36.6823 | 37.0153 | 37.5073 | 38.0704 | 38.6448 | 39.3682 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798
97% | 23.1017 | 23.9255 | 26.7783 | 28.8361 | 29.9176 | 30.8866 | 31.501 | 32.2027 | 32.7634 | 33.1279 | 33.999 | 34.601 | 34.9168 | 35.5042 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 |  | 51.9736 | 54.0145 | 59.736 | 63.805 | 66.2433 | 68.1954 | 69.7786 | 71.3013 | 72.6198 | 73.2791 | 74.2531 | 75.3678 | 76.5049 | 77.937 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581
95% | 68.2388 | 70.6723 | 79.099 | 85.1773 | 88.372 | 91.2341 | 93.0491 | 95.1218 | 96.778 | 97.8547 | 100.4278 | 102.2061 | 103.1387 | 104.874 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 |  | 102.348 | 106.3669 | 117.6339 | 125.6468 | 130.4483 | 134.2924 | 137.4102 | 140.4088 | 143.0051 | 144.3034 | 146.2215 | 148.4166 | 150.6559 | 153.4759 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112
90% | 153.4188 | 158.8899 | 177.8355 | 191.5011 | 198.6837 | 205.1184 | 209.1989 | 213.8589 | 217.5824 | 220.0033 | 225.7882 | 229.7863 | 231.8831 | 235.7845 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 |  | 369.8121 | 384.3337 | 425.0443 | 453.9971 | 471.3466 | 485.2363 | 496.5017 | 507.3363 | 516.7178 | 521.4087 | 528.3393 | 536.2711 | 544.3621 | 554.5516 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246
85% | 248.7872 | 257.6593 | 288.3819 | 310.5423 | 322.1897 | 332.6245 | 339.2415 | 346.7982 | 352.8364 | 356.7621 | 366.143 | 372.6264 | 376.0266 | 382.3532 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 |  | 443.1082 | 460.5079 | 509.2874 | 543.9785 | 564.7666 | 581.4093 | 594.9075 | 607.8895 | 619.1304 | 624.7509 | 633.0551 | 642.5591 | 652.2537 | 664.4627 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475
80% | 957.8308 | 991.9883 | 1110.2705 | 1195.5878 | 1240.4304 | 1280.6042 | 1306.0799 | 1335.1732 | 1358.4201 | 1373.5339 | 1409.6507 | 1434.6115 | 1447.7025 | 1472.0598 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 |  | 505.7431 | 525.6023 | 581.2768 | 620.8717 | 644.5983 | 663.5934 | 678.9996 | 693.8167 | 706.6465 | 713.0616 | 722.5396 | 733.3869 | 744.452 | 758.3868 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538
75% | 1450.6665 | 1502.3991 | 1681.5413 | 1810.7574 | 1878.6729 | 1939.5174 | 1978.1012 | 2022.164 | 2057.3722 | 2080.2626 | 2134.9626 | 2172.7666 | 2192.5933 | 2229.4833 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 |  | 433.7796 | 450.813 | 498.5655 | 532.5263 | 552.8768 | 569.1691 | 582.3831 | 595.0918 | 606.096 | 611.5983 | 619.7277 | 629.0315 | 638.5221 | 650.474 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191
70% | 2215.9834 | 2295.0082 | 2568.6591 | 2766.0446 | 2869.7898 | 2962.7336 | 3021.6728 | 3088.9814 | 3142.7641 | 3177.7307 | 3261.2883 | 3319.0362 | 3349.3228 | 3405.6745 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 |  | 463.7644 | 481.9752 | 533.0286 | 569.3369 | 591.0941 | 608.5126 | 622.64 | 636.2272 | 647.9921 | 653.8747 | 662.566 | 672.5129 | 682.6595 | 695.4377 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103
65% | 4046.3465 | 4190.6445 | 4690.3262 | 5050.7487 | 5240.1855 | 5409.8993 | 5517.5213 | 5640.4256 | 5738.6318 | 5802.4801 | 5955.0548 | 6060.5016 | 6115.8044 | 6218.7016 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 |  | 1223.3785 | 1271.4174 | 1406.0926 | 1501.8715 | 1559.2654 | 1605.2142 | 1642.4813 | 1678.3234 | 1709.3584 | 1724.8763 | 1747.8034 | 1774.0427 | 1800.8088 | 1834.5166 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204
60% | 7863.4534 | 8143.8744 | 9114.9291 | 9815.3548 | 10183.4963 | 10513.309 | 10722.4557 | 10961.3013 | 11152.1501 | 11276.2295 | 11572.735 | 11777.6546 | 11885.1271 | 12085.0921 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 |  | 1365.9727 | 1419.6109 | 1569.9836 | 1676.9262 | 1741.0099 | 1792.3143 | 1833.9252 | 1873.945 | 1908.5973 | 1925.924 | 1951.5234 | 1980.8211 | 2010.707 | 2048.3437 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154
55% | 9114.4977 | 9439.5326 | 10565.0783 | 11376.9389 | 11803.6503 | 12185.9349 | 12428.356 | 12705.201 | 12926.4131 | 13070.233 | 13413.9114 | 13651.4329 | 13776.0038 | 14007.7825 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 |  | 2222.2044 | 2309.4645 | 2554.0952 | 2728.0726 | 2832.3258 | 2915.7893 | 2983.4832 | 3048.5885 | 3104.962 | 3133.1495 | 3174.7953 | 3222.4578 | 3271.077 | 3332.3054 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578
50% | 10722.7294 | 11105.1159 | 12429.2615 | 13384.3731 | 13886.3766 | 14336.1145 | 14621.3102 | 14947.0039 | 15207.2484 | 15376.4449 | 15780.7645 | 16060.1962 | 16206.7473 | 16479.4228 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 |  | 3876.0308 | 4028.2324 | 4454.9241 | 4758.3803 | 4940.2217 | 5085.8011 | 5203.8747 | 5317.4331 | 5415.7613 | 5464.9266 | 5537.5665 | 5620.7008 | 5705.5037 | 5812.3001 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872
45% | 19076.649 | 19756.9472 | 22112.715 | 23811.9398 | 24705.0469 | 25505.1688 | 26012.5564 | 26591.9932 | 27054.9902 | 27356.0054 | 28075.3244 | 28572.4571 | 28833.184 | 29318.2969 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 |  | 7722.7432 | 8025.9952 | 8876.1511 | 9480.7681 | 9843.0753 | 10133.133 | 10368.387 | 10594.6449 | 10790.5576 | 10888.5164 | 11033.2467 | 11198.8863 | 11367.8507 | 11580.6357 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852
40% | 21841.7413 | 22620.6463 | 25317.8743 | 27263.3956 | 28285.9554 | 29202.0522 | 29782.9837 | 30446.4078 | 30976.5147 | 31321.1609 | 32144.7426 | 32713.9329 | 33012.4513 | 33567.8795 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 |  | 13151.3186 | 13667.7365 | 15115.4956 | 16145.1182 | 16762.1033 | 17256.0522 | 17656.6743 | 18041.9764 | 18375.6027 | 18542.42 | 18788.8861 | 19070.9594 | 19358.6946 | 19721.0533 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938
35% | 13247.9197 | 13720.3578 | 15356.3382 | 16536.3774 | 17156.6022 | 17712.2528 | 18064.6118 | 18467.006 | 18788.5377 | 18997.5799 | 19497.1163 | 19842.3537 | 20023.4175 | 20360.3077 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 |  | 15921.911 | 16547.1229 | 18299.8818 | 19546.4153 | 20293.3809 | 20891.3902 | 21376.4114 | 21842.8853 | 22246.7967 | 22448.7575 | 22747.1467 | 23088.6444 | 23436.9969 | 23875.6938 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193
30% | 5490.4971 | 5686.2954 | 6364.3147 | 6853.3728 | 7110.4201 | 7340.7052 | 7486.7376 | 7653.5067 | 7786.7631 | 7873.399 | 8080.4279 | 8223.5089 | 8298.5494 | 8438.1709 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 |  | 24323.6426 | 25278.7685 | 27956.4296 | 29860.7384 | 31001.8655 | 31915.4345 | 32656.3934 | 33369.018 | 33986.0669 | 34294.599 | 34750.4432 | 35272.1438 | 35804.3161 | 36474.5062 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693
25% | 3277.4755 | 3394.3546 | 3799.0887 | 4091.0251 | 4244.4659 | 4381.9314 | 4469.1034 | 4568.6539 | 4648.1994 | 4699.9155 | 4823.4985 | 4908.9087 | 4953.7031 | 5037.0482 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 |  | 20684.1582 | 21496.3711 | 23773.3806 | 25392.7526 | 26363.1358 | 27140.0098 | 27770.1009 | 28376.0973 | 28900.8187 | 29163.186 | 29550.8235 | 29994.4633 | 30447.008 | 31016.9192 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015
20% | 3486.5752 | 3610.9111 | 4041.4669 | 4352.0285 | 4515.2587 | 4661.4943 | 4754.2278 | 4860.1295 | 4944.75 | 4999.7655 | 5131.233 | 5222.0923 | 5269.7445 | 5358.4069 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 |  | 5487.2123 | 5702.6808 | 6306.7389 | 6736.3352 | 6993.764 | 7199.8576 | 7367.0118 | 7527.774 | 7666.9751 | 7736.5774 | 7839.4121 | 7957.1035 | 8077.1571 | 8228.3464 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869
15% | 3611.5612 | 3740.3542 | 4186.3445 | 4508.039 | 4677.1207 | 4828.5985 | 4924.6563 | 5034.3544 | 5122.0082 | 5178.996 | 5315.1763 | 5409.2927 | 5458.6531 | 5550.4939 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 |  | 3400.2725 | 3533.7923 | 3908.1103 | 4174.3192 | 4333.8407 | 4461.5511 | 4565.1319 | 4664.7518 | 4751.0108 | 4794.1414 | 4857.8652 | 4930.7953 | 5005.1892 | 5098.877 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404
10% | 2407.9049 | 2493.774 | 2791.1252 | 3005.6058 | 3118.3361 | 3219.3296 | 3283.3734 | 3356.5115 | 3414.9522 | 3452.9471 | 3543.7415 | 3606.4909 | 3639.4005 | 3700.6327 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 |  | 972.8391 | 1011.0399 | 1118.1346 | 1194.2987 | 1239.9387 | 1276.4775 | 1306.1126 | 1334.6145 | 1359.2937 | 1371.6336 | 1389.8654 | 1410.7312 | 1432.0157 | 1458.8204 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584
5% | 191.9216 | 198.7657 | 222.4661 | 239.5612 | 248.5463 | 256.596 | 261.7006 | 267.5301 | 272.1881 | 275.2164 | 282.4532 | 287.4546 | 290.0777 | 294.9582 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 109520.6382 | 113426.2871 | 126950.9475 | 136706.3391 | 141833.7416 | 146427.3086 | 149340.263 | 152666.8581 | 155324.963 | 157053.1161 | 161182.7867 | 164036.867 | 165533.7223 | 168318.7958 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | E @ R (MWh) | 102801.5058 | 106838.2526 | 118155.1262 | 126203.5021 | 131026.3646 | 134887.4749 | 138019.0656 | 141030.9039 | 143638.8008 | 144942.7819 | 146869.3632 | 149074.2799 | 151323.4542 | 154155.9472 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242
Option 7 Summer POE50 W E @ R (MWh) N 2 | 76664.4467 | 79398.4009 | 88865.6632 | 95694.4374 | 99283.6191 | 102499.116 | 104538.1841 | 106866.8007 | 108727.4741 | 109937.1812 | 112827.9507 | 114825.8069 | 115873.6056 | 117823.1571 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 30840.4517 | 32051.4758 | 35446.5379 | 37861.0506 | 39307.9094 | 40466.2425 | 41405.7197 | 42309.2712 | 43091.6403 | 43482.8346 | 44060.809 | 44722.284 | 45397.0363 | 46246.7841 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 49.1893 | 51.8356 | 58.8689 | 64.7915 | 67.9845 | 70.2915 | 72.9503 | 74.9386 | 77.1319 | 78.279 | 79.2727 | 81.738 | 80.2446 | 84.2671 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 | 89.5151 |  | 52.3542 | 55.0903 | 62.0689 | 68.2157 | 71.4199 | 74.0183 | 76.4883 | 78.592 | 80.7843 | 81.7424 | 83.0524 | 85.4842 | 84.6835 | 87.8608 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921 | 89.6921
98% | 146.0848 | 153.9438 | 174.8318 | 192.4209 | 201.9038 | 208.7551 | 216.6514 | 222.5563 | 229.0702 | 232.4767 | 235.428 | 242.7494 | 238.3145 | 250.2605 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 | 265.8463 |  | 155.484 | 163.6098 | 184.3354 | 202.5904 | 212.1064 | 219.8233 | 227.1588 | 233.4065 | 239.9173 | 242.7625 | 246.6532 | 253.8753 | 251.4973 | 260.9335 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372 | 266.372
97% | 64.2674 | 67.7249 | 76.9141 | 84.6522 | 88.824 | 91.8381 | 95.3119 | 97.9097 | 100.7754 | 102.274 | 103.5724 | 106.7933 | 104.8422 | 110.0977 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 | 116.9544 |  | 68.4024 | 71.9773 | 81.0951 | 89.1261 | 93.3125 | 96.7074 | 99.9345 | 102.6831 | 105.5474 | 106.7991 | 108.5107 | 111.688 | 110.6418 | 114.7931 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857 | 117.1857
95% | 158.1967 | 166.7073 | 189.3271 | 208.3746 | 218.6438 | 226.063 | 234.614 | 241.0085 | 248.0625 | 251.7514 | 254.9475 | 262.8758 | 258.0732 | 271.0097 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 | 287.8877 |  | 168.3752 | 177.1748 | 199.6187 | 219.3872 | 229.6922 | 238.0489 | 245.9926 | 252.7583 | 259.8089 | 262.89 | 267.1033 | 274.9242 | 272.349 | 282.5676 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457 | 288.457
90% | 1615.7485 | 1702.6723 | 1933.7004 | 2128.2423 | 2233.1271 | 2308.9039 | 2396.2398 | 2461.5504 | 2533.5966 | 2571.2738 | 2603.9165 | 2684.8933 | 2635.8415 | 2767.9686 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 | 2940.3534 |  | 1719.7072 | 1809.5821 | 2038.8138 | 2240.7207 | 2345.971 | 2431.3227 | 2512.4557 | 2581.5574 | 2653.5695 | 2685.0381 | 2728.071 | 2807.95 | 2781.6479 | 2886.0155 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676 | 2946.1676
85% | 3806.6079 | 4011.3951 | 4555.6838 | 5014.013 | 5261.1153 | 5439.6409 | 5645.3992 | 5799.2671 | 5969.0038 | 6057.769 | 6134.6733 | 6325.4498 | 6209.8867 | 6521.1704 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 | 6927.2988 |  | 4051.5284 | 4263.2684 | 4803.3248 | 5279.0053 | 5526.969 | 5728.0525 | 5919.1971 | 6081.9965 | 6251.6527 | 6325.791 | 6427.1739 | 6615.3641 | 6553.398 | 6799.2818 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966 | 6940.9966
80% | 6892.6794 | 7263.4904 | 8249.0417 | 9078.945 | 9526.3766 | 9849.6355 | 10222.2049 | 10500.8157 | 10808.1605 | 10968.8888 | 11108.1405 | 11453.5823 | 11244.3305 | 11807.9764 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 | 12543.3588 |  | 7336.1604 | 7719.561 | 8697.4488 | 9558.7704 | 10007.7617 | 10371.8665 | 10717.9747 | 11012.758 | 11319.9569 | 11454.2002 | 11637.7756 | 11978.5342 | 11866.3313 | 12311.5567 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616 | 12568.1616
75% | 8058.556 | 8492.0887 | 9644.3432 | 10614.6221 | 11137.7355 | 11515.6728 | 11951.2611 | 12276.9981 | 12636.3294 | 12824.2444 | 12987.0502 | 13390.9224 | 13146.2763 | 13805.2613 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 | 14665.0315 |  | 8577.0505 | 9025.3023 | 10168.597 | 11175.6086 | 11700.5455 | 12126.2375 | 12530.8889 | 12875.534 | 13234.6947 | 13391.6448 | 13606.2715 | 14004.6684 | 13873.4868 | 14394.0207 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296 | 14694.0296
70% | 9450.1926 | 9958.5923 | 11309.8302 | 12447.6671 | 13061.1172 | 13504.3207 | 14015.1311 | 14397.1198 | 14818.5042 | 15038.8704 | 15229.7912 | 15703.4083 | 15416.5141 | 16189.2995 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 | 17197.544 |  | 10058.2262 | 10583.8868 | 11924.6176 | 13105.5307 | 13721.1192 | 14220.3242 | 14694.8551 | 15099.0171 | 15520.2015 | 15704.2554 | 15955.9461 | 16423.1424 | 16269.3069 | 16879.7321 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498 | 17231.5498
65% | 10355.7039 | 10912.8181 | 12393.5307 | 13640.3944 | 14312.6249 | 14798.2959 | 15358.0518 | 15776.6424 | 16238.4036 | 16479.8851 | 16689.0998 | 17208.0986 | 16893.7145 | 17740.5476 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 | 18845.4014 |  | 11021.9989 | 11598.028 | 13067.2267 | 14361.2941 | 15035.8679 | 15582.9064 | 16102.9065 | 16545.7951 | 17007.337 | 17209.0269 | 17484.8344 | 17996.7972 | 17828.2213 | 18497.137 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657 | 18882.6657
60% | 11267.3947 | 11873.5559 | 13484.6268 | 14841.2614 | 15572.6734 | 16101.1017 | 16710.1371 | 17165.5794 | 17667.9929 | 17930.7339 | 18158.3673 | 18723.0575 | 18380.9958 | 19302.3821 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 | 20504.5045 |  | 11992.3487 | 12619.09 | 14217.6334 | 15625.6273 | 16359.589 | 16954.7874 | 17520.567 | 18002.4464 | 18504.6214 | 18724.0676 | 19024.1565 | 19581.1912 | 19397.7743 | 20125.5797 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494 | 20545.0494
55% | 11294.5848 | 11902.2087 | 13517.1674 | 14877.0758 | 15610.2528 | 16139.9562 | 16750.4614 | 17207.0028 | 17710.6286 | 17974.0037 | 18202.1864 | 18768.2393 | 18425.3521 | 19348.9619 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 | 20553.9852 |  | 12021.2882 | 12649.5419 | 14251.9428 | 15663.3344 | 16399.0673 | 16995.7021 | 17562.847 | 18045.8893 | 18549.2761 | 18769.2518 | 19070.0648 | 19628.4438 | 19444.5843 | 20174.146 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279 | 20594.6279
50% | 13305.825 | 14021.6493 | 15924.1856 | 17526.2545 | 18389.9893 | 19014.0176 | 19733.2361 | 20271.0744 | 20864.3815 | 21174.656 | 21443.4716 | 22110.3222 | 21706.3766 | 22794.4547 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 | 24214.058 |  | 14161.9334 | 14902.061 | 16789.8034 | 18452.5232 | 19319.2689 | 20022.1471 | 20690.2843 | 21259.3424 | 21852.3679 | 22111.515 | 22465.8942 | 23123.7043 | 22907.1047 | 23766.5804 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938 | 24261.938
45% | 16641.1386 | 17536.3955 | 19915.8324 | 21919.4849 | 22999.7283 | 23780.1792 | 24679.6811 | 25352.3369 | 26094.3658 | 26482.4155 | 26818.6139 | 27652.621 | 27147.4202 | 28508.2421 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 | 30283.6912 |  | 17711.844 | 18637.4962 | 20998.4308 | 23077.9374 | 24161.9465 | 25041.0121 | 25876.6283 | 26588.3298 | 27330.0065 | 27654.1128 | 28097.3227 | 28920.0233 | 28649.1296 | 29724.0464 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731 | 30343.5731
40% | 17620.8046 | 18568.7653 | 21088.28 | 23209.8878 | 24353.7253 | 25180.1214 | 26132.5771 | 26844.8323 | 27630.5445 | 28041.4387 | 28397.4292 | 29280.5344 | 28745.5924 | 30186.526 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 | 32066.496 |  | 18754.5425 | 19734.688 | 22234.6112 | 24436.5385 | 25584.3634 | 26515.1798 | 27399.9888 | 28153.5883 | 28938.9275 | 29282.114 | 29751.4157 | 30622.5488 | 30335.7076 | 31473.9048 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032 | 32129.9032
35% | 7205.365 | 7592.9979 | 8623.2586 | 9490.8103 | 9958.5396 | 10296.4632 | 10685.9341 | 10977.1841 | 11298.4715 | 11466.4912 | 11612.0601 | 11973.1728 | 11754.4284 | 12343.644 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 | 13112.387 |  | 7668.9645 | 8069.7581 | 9092.0076 | 9992.403 | 10461.7627 | 10842.3851 | 11204.1944 | 11512.3506 | 11833.4855 | 11973.8187 | 12165.722 | 12521.9391 | 12404.6462 | 12870.0691 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149 | 13138.3149
30% | 2222.5811 | 2342.1511 | 2659.9474 | 2927.5541 | 3071.8308 | 3176.0674 | 3296.2044 | 3386.0439 | 3485.1489 | 3536.9766 | 3581.879 | 3693.2686 | 3625.7942 | 3807.5448 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 | 4044.6728 |  | 2365.584 | 2489.2135 | 2804.5387 | 3082.2764 | 3227.056 | 3344.4635 | 3456.068 | 3551.1224 | 3650.1803 | 3693.4678 | 3752.6627 | 3862.5421 | 3826.3617 | 3969.927 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706 | 4052.6706
25% | 1635.9351 | 1723.9448 | 1957.8593 | 2154.8318 | 2261.0269 | 2337.7504 | 2426.1775 | 2492.3041 | 2565.2504 | 2603.3983 | 2636.4489 | 2718.4373 | 2668.7727 | 2802.5506 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 | 2977.0891 |  | 1741.1926 | 1832.1904 | 2064.286 | 2268.7154 | 2375.2807 | 2461.6987 | 2543.8454 | 2613.8104 | 2686.7222 | 2718.584 | 2762.1545 | 2843.0315 | 2816.4008 | 2922.0723 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759 | 2982.9759
20% | 1301.415 | 1371.4283 | 1557.5114 | 1714.2064 | 1798.6865 | 1859.7214 | 1930.0667 | 1982.6715 | 2040.7016 | 2071.0489 | 2097.3412 | 2162.5645 | 2123.0554 | 2229.4781 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 | 2368.3265 |  | 1385.1492 | 1457.5395 | 1642.1756 | 1804.8028 | 1889.5774 | 1958.3244 | 2023.6735 | 2079.3319 | 2137.3345 | 2162.6811 | 2197.3422 | 2261.6813 | 2240.4961 | 2324.5596 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095 | 2373.0095
15% | 1020.863 | 1075.7832 | 1221.7516 | 1344.6671 | 1410.9355 | 1458.8128 | 1513.9934 | 1555.258 | 1600.7783 | 1624.5835 | 1645.2078 | 1696.3706 | 1665.3787 | 1748.8593 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 | 1857.7756 |  | 1086.5463 | 1143.3311 | 1288.1644 | 1415.7332 | 1482.2326 | 1536.1595 | 1587.421 | 1631.0809 | 1676.5796 | 1696.4621 | 1723.6512 | 1774.1204 | 1757.5022 | 1823.4438 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491 | 1861.4491
10% | 716.8288 | 755.3926 | 857.8885 | 944.1973 | 990.7295 | 1024.348 | 1063.0946 | 1092.0698 | 1124.0332 | 1140.7487 | 1155.2307 | 1191.1561 | 1169.3942 | 1228.0126 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 | 1304.4913 |  | 762.9502 | 802.8233 | 904.5222 | 994.0984 | 1040.7929 | 1078.6592 | 1114.654 | 1145.311 | 1177.2593 | 1191.2204 | 1210.312 | 1245.7504 | 1234.0814 | 1280.3842 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708 | 1307.0708
5% | 74.1547 | 78.1441 | 88.7471 | 97.6756 | 102.4893 | 105.967 | 109.9753 | 112.9727 | 116.2793 | 118.0085 | 119.5066 | 123.223 | 120.9718 | 127.0358 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 | 134.9474 |  | 78.9259 | 83.0507 | 93.5713 | 102.8378 | 107.6682 | 111.5854 | 115.309 | 118.4805 | 121.7854 | 123.2297 | 125.2047 | 128.8707 | 127.6636 | 132.4535 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142 | 135.2142
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 124904.117 | 131623.685 | 149483.1281 | 164522.0299 | 172630.0598 | 178487.9236 | 185239.3543 | 190288.1364 | 195857.6146 | 198770.2162 | 201293.6351 | 207553.4786 | 203761.5708 | 213975.5507 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | 227301.6161 | E @ R (MWh) | 132940.5564 | 139888.2644 | 157608.8341 | 173217.0768 | 181353.3711 | 187951.4123 | 194223.3331 | 199565.182 | 205132.0165 | 207564.6754 | 210891.2951 | 217066.275 | 215033.0162 | 223101.0657 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744 | 227751.0744
Option 8 Winter POE50 W E @ R (MWh) N 2 | 87432.8819 | 92136.5795 | 104638.1897 | 115165.421 | 120841.0419 | 124941.5465 | 129667.548 | 133201.6955 | 137100.3302 | 139139.1513 | 140905.5446 | 145287.435 | 142633.0996 | 149782.8855 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | 159111.1313 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 39882.1669 | 41966.4793 | 47282.6502 | 51965.123 | 54406.0113 | 56385.4237 | 58266.9999 | 59869.5546 | 61539.6049 | 62269.4026 | 63267.3885 | 65119.8825 | 64509.9049 | 66930.3197 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223 | 68325.3223
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 53.0397 | 55.1225 | 60.9613 | 65.1138 | 67.6021 | 69.5943 | 71.21 | 72.7639 | 74.1094 | 74.7822 | 75.7762 | 76.9138 | 78.0743 | 79.5357 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613 | 79.7613
98% | 23.3386 | 24.1709 | 27.053 | 29.1318 | 30.2245 | 31.2033 | 31.8241 | 32.533 | 33.0994 | 33.4677 | 34.3477 | 34.9559 | 35.2749 | 35.8684 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 | 35.6937 |  | 26.2533 | 27.2842 | 30.1743 | 32.2297 | 33.4614 | 34.4474 | 35.2471 | 36.0163 | 36.6823 | 37.0153 | 37.5073 | 38.0704 | 38.6448 | 39.3682 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798 | 39.4798
97% | 23.1017 | 23.9255 | 26.7783 | 28.8361 | 29.9176 | 30.8866 | 31.501 | 32.2027 | 32.7634 | 33.1279 | 33.999 | 34.601 | 34.9168 | 35.5042 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 | 35.3313 |  | 51.9736 | 54.0145 | 59.736 | 63.805 | 66.2433 | 68.1954 | 69.7786 | 71.3013 | 72.6198 | 73.2791 | 74.2531 | 75.3678 | 76.5049 | 77.937 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581 | 78.1581
95% | 68.2388 | 70.6723 | 79.099 | 85.1773 | 88.372 | 91.2341 | 93.0491 | 95.1218 | 96.778 | 97.8547 | 100.4278 | 102.2061 | 103.1387 | 104.874 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 | 104.3634 |  | 102.348 | 106.3669 | 117.6339 | 125.6468 | 130.4483 | 134.2924 | 137.4102 | 140.4088 | 143.0051 | 144.3034 | 146.2215 | 148.4166 | 150.6559 | 153.4759 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112 | 153.9112
90% | 153.4188 | 158.8899 | 177.8355 | 191.5011 | 198.6837 | 205.1184 | 209.1989 | 213.8589 | 217.5824 | 220.0033 | 225.7882 | 229.7863 | 231.8831 | 235.7845 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 | 234.6364 |  | 369.8121 | 384.3337 | 425.0443 | 453.9971 | 471.3466 | 485.2363 | 496.5017 | 507.3363 | 516.7178 | 521.4087 | 528.3393 | 536.2711 | 544.3621 | 554.5516 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246 | 556.1246
85% | 248.7872 | 257.6593 | 288.3819 | 310.5423 | 322.1897 | 332.6245 | 339.2415 | 346.7982 | 352.8364 | 356.7621 | 366.143 | 372.6264 | 376.0266 | 382.3532 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 | 380.4914 |  | 443.1082 | 460.5079 | 509.2874 | 543.9785 | 564.7666 | 581.4093 | 594.9075 | 607.8895 | 619.1304 | 624.7509 | 633.0551 | 642.5591 | 652.2537 | 664.4627 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475 | 666.3475
80% | 957.8308 | 991.9883 | 1110.2705 | 1195.5878 | 1240.4304 | 1280.6042 | 1306.0799 | 1335.1732 | 1358.4201 | 1373.5339 | 1409.6507 | 1434.6115 | 1447.7025 | 1472.0598 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 | 1464.8918 |  | 505.7431 | 525.6023 | 581.2768 | 620.8717 | 644.5983 | 663.5934 | 678.9996 | 693.8167 | 706.6465 | 713.0616 | 722.5396 | 733.3869 | 744.452 | 758.3868 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538 | 760.538
75% | 1450.6665 | 1502.3991 | 1681.5413 | 1810.7574 | 1878.6729 | 1939.5174 | 1978.1012 | 2022.164 | 2057.3722 | 2080.2626 | 2134.9626 | 2172.7666 | 2192.5933 | 2229.4833 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 | 2218.6272 |  | 433.7796 | 450.813 | 498.5655 | 532.5263 | 552.8768 | 569.1691 | 582.3831 | 595.0918 | 606.096 | 611.5983 | 619.7277 | 629.0315 | 638.5221 | 650.474 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191 | 652.3191
70% | 2215.9834 | 2295.0082 | 2568.6591 | 2766.0446 | 2869.7898 | 2962.7336 | 3021.6728 | 3088.9814 | 3142.7641 | 3177.7307 | 3261.2883 | 3319.0362 | 3349.3228 | 3405.6745 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 | 3389.0911 |  | 463.7644 | 481.9752 | 533.0286 | 569.3369 | 591.0941 | 608.5126 | 622.64 | 636.2272 | 647.9921 | 653.8747 | 662.566 | 672.5129 | 682.6595 | 695.4377 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103 | 697.4103
65% | 4046.3465 | 4190.6445 | 4690.3262 | 5050.7487 | 5240.1855 | 5409.8993 | 5517.5213 | 5640.4256 | 5738.6318 | 5802.4801 | 5955.0548 | 6060.5016 | 6115.8044 | 6218.7016 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 | 6188.4206 |  | 1223.3785 | 1271.4174 | 1406.0926 | 1501.8715 | 1559.2654 | 1605.2142 | 1642.4813 | 1678.3234 | 1709.3584 | 1724.8763 | 1747.8034 | 1774.0427 | 1800.8088 | 1834.5166 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204 | 1839.7204
60% | 7863.4534 | 8143.8744 | 9114.9291 | 9815.3548 | 10183.4963 | 10513.309 | 10722.4557 | 10961.3013 | 11152.1501 | 11276.2295 | 11572.735 | 11777.6546 | 11885.1271 | 12085.0921 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 | 12026.2456 |  | 1365.9727 | 1419.6109 | 1569.9836 | 1676.9262 | 1741.0099 | 1792.3143 | 1833.9252 | 1873.945 | 1908.5973 | 1925.924 | 1951.5234 | 1980.8211 | 2010.707 | 2048.3437 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154 | 2054.154
55% | 9114.4977 | 9439.5326 | 10565.0783 | 11376.9389 | 11803.6503 | 12185.9349 | 12428.356 | 12705.201 | 12926.4131 | 13070.233 | 13413.9114 | 13651.4329 | 13776.0038 | 14007.7825 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 | 13939.5737 |  | 2222.2044 | 2309.4645 | 2554.0952 | 2728.0726 | 2832.3258 | 2915.7893 | 2983.4832 | 3048.5885 | 3104.962 | 3133.1495 | 3174.7953 | 3222.4578 | 3271.077 | 3332.3054 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578 | 3341.7578
50% | 10722.7294 | 11105.1159 | 12429.2615 | 13384.3731 | 13886.3766 | 14336.1145 | 14621.3102 | 14947.0039 | 15207.2484 | 15376.4449 | 15780.7645 | 16060.1962 | 16206.7473 | 16479.4228 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 | 16399.1788 |  | 3876.0308 | 4028.2324 | 4454.9241 | 4758.3803 | 4940.2217 | 5085.8011 | 5203.8747 | 5317.4331 | 5415.7613 | 5464.9266 | 5537.5665 | 5620.7008 | 5705.5037 | 5812.3001 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872 | 5828.7872
45% | 19076.649 | 19756.9472 | 22112.715 | 23811.9398 | 24705.0469 | 25505.1688 | 26012.5564 | 26591.9932 | 27054.9902 | 27356.0054 | 28075.3244 | 28572.4571 | 28833.184 | 29318.2969 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 | 29175.5359 |  | 7722.7432 | 8025.9952 | 8876.1511 | 9480.7681 | 9843.0753 | 10133.133 | 10368.387 | 10594.6449 | 10790.5576 | 10888.5164 | 11033.2467 | 11198.8863 | 11367.8507 | 11580.6357 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852 | 11613.4852
40% | 21841.7413 | 22620.6463 | 25317.8743 | 27263.3956 | 28285.9554 | 29202.0522 | 29782.9837 | 30446.4078 | 30976.5147 | 31321.1609 | 32144.7426 | 32713.9329 | 33012.4513 | 33567.8795 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 | 33404.4259 |  | 13151.3186 | 13667.7365 | 15115.4956 | 16145.1182 | 16762.1033 | 17256.0522 | 17656.6743 | 18041.9764 | 18375.6027 | 18542.42 | 18788.8861 | 19070.9594 | 19358.6946 | 19721.0533 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938 | 19776.9938
35% | 13247.9197 | 13720.3578 | 15356.3382 | 16536.3774 | 17156.6022 | 17712.2528 | 18064.6118 | 18467.006 | 18788.5377 | 18997.5799 | 19497.1163 | 19842.3537 | 20023.4175 | 20360.3077 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 | 20261.1663 |  | 15921.911 | 16547.1229 | 18299.8818 | 19546.4153 | 20293.3809 | 20891.3902 | 21376.4114 | 21842.8853 | 22246.7967 | 22448.7575 | 22747.1467 | 23088.6444 | 23436.9969 | 23875.6938 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193 | 23943.4193
30% | 5490.4971 | 5686.2954 | 6364.3147 | 6853.3728 | 7110.4201 | 7340.7052 | 7486.7376 | 7653.5067 | 7786.7631 | 7873.399 | 8080.4279 | 8223.5089 | 8298.5494 | 8438.1709 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 | 8397.0825 |  | 24323.6426 | 25278.7685 | 27956.4296 | 29860.7384 | 31001.8655 | 31915.4345 | 32656.3934 | 33369.018 | 33986.0669 | 34294.599 | 34750.4432 | 35272.1438 | 35804.3161 | 36474.5062 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693 | 36577.9693
25% | 3277.4755 | 3394.3546 | 3799.0887 | 4091.0251 | 4244.4659 | 4381.9314 | 4469.1034 | 4568.6539 | 4648.1994 | 4699.9155 | 4823.4985 | 4908.9087 | 4953.7031 | 5037.0482 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 | 5012.521 |  | 20684.1582 | 21496.3711 | 23773.3806 | 25392.7526 | 26363.1358 | 27140.0098 | 27770.1009 | 28376.0973 | 28900.8187 | 29163.186 | 29550.8235 | 29994.4633 | 30447.008 | 31016.9192 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015 | 31104.9015
20% | 3486.5752 | 3610.9111 | 4041.4669 | 4352.0285 | 4515.2587 | 4661.4943 | 4754.2278 | 4860.1295 | 4944.75 | 4999.7655 | 5131.233 | 5222.0923 | 5269.7445 | 5358.4069 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 | 5332.315 |  | 5487.2123 | 5702.6808 | 6306.7389 | 6736.3352 | 6993.764 | 7199.8576 | 7367.0118 | 7527.774 | 7666.9751 | 7736.5774 | 7839.4121 | 7957.1035 | 8077.1571 | 8228.3464 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869 | 8251.6869
15% | 3611.5612 | 3740.3542 | 4186.3445 | 4508.039 | 4677.1207 | 4828.5985 | 4924.6563 | 5034.3544 | 5122.0082 | 5178.996 | 5315.1763 | 5409.2927 | 5458.6531 | 5550.4939 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 | 5523.4666 |  | 3400.2725 | 3533.7923 | 3908.1103 | 4174.3192 | 4333.8407 | 4461.5511 | 4565.1319 | 4664.7518 | 4751.0108 | 4794.1414 | 4857.8652 | 4930.7953 | 5005.1892 | 5098.877 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404 | 5113.3404
10% | 2407.9049 | 2493.774 | 2791.1252 | 3005.6058 | 3118.3361 | 3219.3296 | 3283.3734 | 3356.5115 | 3414.9522 | 3452.9471 | 3543.7415 | 3606.4909 | 3639.4005 | 3700.6327 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 | 3682.6131 |  | 972.8391 | 1011.0399 | 1118.1346 | 1194.2987 | 1239.9387 | 1276.4775 | 1306.1126 | 1334.6145 | 1359.2937 | 1371.6336 | 1389.8654 | 1410.7312 | 1432.0157 | 1458.8204 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584 | 1462.9584
5% | 191.9216 | 198.7657 | 222.4661 | 239.5612 | 248.5463 | 256.596 | 261.7006 | 267.5301 | 272.1881 | 275.2164 | 282.4532 | 287.4546 | 290.0777 | 294.9582 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 | 293.5219 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 109520.6382 | 113426.2871 | 126950.9475 | 136706.3391 | 141833.7416 | 146427.3086 | 149340.263 | 152666.8581 | 155324.963 | 157053.1161 | 161182.7867 | 164036.867 | 165533.7223 | 168318.7958 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | 167499.1934 | E @ R (MWh) | 102801.5058 | 106838.2526 | 118155.1262 | 126203.5021 | 131026.3646 | 134887.4749 | 138019.0656 | 141030.9039 | 143638.8008 | 144942.7819 | 146869.3632 | 149074.2799 | 151323.4542 | 154155.9472 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242 | 154593.2242
Option 8 Summer POE50 W E @ R (MWh) N 2 | 76664.4467 | 79398.4009 | 88865.6632 | 95694.4374 | 99283.6191 | 102499.116 | 104538.1841 | 106866.8007 | 108727.4741 | 109937.1812 | 112827.9507 | 114825.8069 | 115873.6056 | 117823.1571 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | 117249.4354 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 30840.4517 | 32051.4758 | 35446.5379 | 37861.0506 | 39307.9094 | 40466.2425 | 41405.7197 | 42309.2712 | 43091.6403 | 43482.8346 | 44060.809 | 44722.284 | 45397.0363 | 46246.7841 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673 | 46377.9673

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-OFR-TRNFMR-9000014181 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 2 Pof | DS-OFR-TRNFMR-9000016122 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.3818% | 0.3818% | 0.4219% | 0.4644% | 0.5094% | 0.5569% | 0.607% | 0.6597% | 0.715% | 0.7729% | 0.8336% | 0.8971% | 0.9634% | 1.032% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104%
N-1 Risk |  | 0.1473% | 0.1473% | 0.1628% | 0.1792% | 0.1965% | 0.2149% | 0.2342% | 0.2545% | 0.2758% | 0.2982% | 0.3216% | 0.3461% | 0.3717% | 0.3983% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261%
N-2 Risk |  | 8.542e-05% | 8.542e-05% | 0.0001043% | 0.0001264% | 0.0001521% | 0.0001818% | 0.0002159% | 0.000255% | 0.0002995% | 0.0003501% | 0.0004073% | 0.0004716% | 0.0005439% | 0.0006247% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148%
N Risk |  | 99.85% | 99.85% | 99.84% | 99.82% | 99.8% | 99.78% | 99.77% | 99.75% | 99.72% | 99.7% | 99.68% | 99.65% | 99.63% | 99.6% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0.30492 | 1.5891 | 3.6944 | 5.1726 | 7.966 | 14.5973 | 18.2119 | 36.5871 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097
Weighted Energy @ Risk (MWh) under N-1 Conditions | 1.4221 | 2.5788 | 10.1708 | 22.816 | 33.8316 | 45.5805 | 59.4887 | 74.4299 | 92.0129 | 106.1954 | 124.7847 | 152.2557 | 158.5456 | 200.8032 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.24502 | 0.25606 | 0.35153 | 0.46323 | 0.58148 | 0.71805 | 0.87762 | 1.0623 | 1.2772 | 1.5112 | 1.7894 | 2.1221 | 2.4395 | 2.8928 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926
Total EUE (MWh) - Option 1 | 1.6672 | 2.8349 | 10.5223 | 23.2792 | 34.4131 | 46.2985 | 60.6713 | 77.0813 | 96.9845 | 112.8792 | 134.54 | 168.9751 | 179.1971 | 240.2831 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858
Cost of EUE ($) - Option 1 | 72084.1724 | 122573.7157 | 454963.6626 | 1006544.8989 | 1487950.2733 | 2001852.8529 | 2623301.6632 | 3332836.3755 | 4193412.8475 | 4880664.3188 | 5817234.9665 | 7306137.3129 | 7748115.5231 | 10389350.9022 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459
Hours at Risk pA. (Hrs) (N) | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 2.0261 | 4.2951 | 9.9675 | 9.9675 | 12.6423 | 48.3061 | 23.9882 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517 | 133.9517
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 1.4221 | 2.5788 | 10.1708 | 22.816 | 33.8316 | 10.3417 | 15.9508 | 22.3967 | 30.7045 | 37.1251 | 45.941 | 60.81 | 61.4865 | 86.2218 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081 | 115.5081
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.24502 | 0.25606 | 0.35153 | 0.46323 | 0.58148 | 0.59273 | 0.72876 | 0.88645 | 1.0707 | 1.2698 | 1.5086 | 1.7969 | 2.0646 | 2.4621 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998 | 2.8998
Total EUE (MWh) - Option 2 | 1.6672 | 2.8349 | 10.5223 | 23.2792 | 34.4131 | 10.9344 | 16.6795 | 23.2831 | 31.7752 | 38.3949 | 47.4496 | 62.6069 | 63.5511 | 88.6839 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079 | 118.4079
Cost of EUE ($) - Option 2 | 72084.1724 | 122573.7157 | 454963.6626 | 1006544.8989 | 1487950.2733 | 472781.004 | 721188.9122 | 1006714.7215 | 1373895.5683 | 1660116.5429 | 2051624.9678 | 2706992.9811 | 2747818.6701 | 3834511.7233 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786 | 5119715.2786
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 1.4221 | 2.5788 | 10.1708 | 3.0064 | 6.2538 | 0.46724 | 0.97258 | 1.909 | 3.5616 | 4.9526 | 7.1132 | 11.9048 | 11.0915 | 20.6019 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.24502 | 0.25606 | 0.35153 | 0.37609 | 0.47663 | 0.46741 | 0.5799 | 0.71064 | 0.86417 | 1.0284 | 1.2278 | 1.4718 | 1.6896 | 2.0315 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407
Total EUE (MWh) - Option 3 | 1.6672 | 2.8349 | 10.5223 | 3.3825 | 6.7305 | 0.93465 | 1.5525 | 2.6197 | 4.4258 | 5.981 | 8.341 | 13.3765 | 12.7811 | 22.6334 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612
Cost of EUE ($) - Option 3 | 72084.1724 | 122573.7157 | 454963.6626 | 146251.053 | 291011.6468 | 40412.3527 | 67126.0056 | 113269.3225 | 191362.4076 | 258607.7449 | 360647.8459 | 578373.0967 | 552629.8186 | 978622.5531 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 1.4221 | 2.5788 | 10.1708 | 0 | 0 | 0.0012902 | 0.0056752 | 0.014276 | 0.026934 | 0.036712 | 0.054047 | 0.091297 | 0.12296 | 0.22438 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044 | 0.50044
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.24502 | 0.25606 | 0.35153 | 0.020529 | 0.032441 | 0.046844 | 0.065715 | 0.088369 | 0.11738 | 0.14584 | 0.18349 | 0.2393 | 0.26731 | 0.36037 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253 | 0.47253
Total EUE (MWh) - Option 4 | 1.6672 | 2.8349 | 10.5223 | 0.020529 | 0.032441 | 0.048134 | 0.071391 | 0.10265 | 0.14432 | 0.18255 | 0.23754 | 0.33059 | 0.39026 | 0.58475 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297 | 0.97297
Cost of EUE ($) - Option 4 | 72084.1724 | 122573.7157 | 454963.6626 | 887.6305 | 1402.684 | 2081.2184 | 3086.7802 | 4438.1685 | 6239.9566 | 7892.9845 | 10270.7585 | 14294.2254 | 16874.2532 | 25283.3181 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064 | 42069.1064
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 1.4221 | 2.5788 | 10.1708 | 3.0064 | 6.2538 | 0.46724 | 0.97258 | 1.909 | 3.5616 | 4.9526 | 7.1132 | 11.9048 | 11.0915 | 20.6019 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542 | 34.9542
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.24502 | 0.25606 | 0.35153 | 0.37609 | 0.47663 | 0.46741 | 0.5799 | 0.71064 | 0.86417 | 1.0284 | 1.2278 | 1.4718 | 1.6896 | 2.0315 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407 | 2.407
Total EUE (MWh) - Option 5 | 1.6672 | 2.8349 | 10.5223 | 3.3825 | 6.7305 | 0.93465 | 1.5525 | 2.6197 | 4.4258 | 5.981 | 8.341 | 13.3765 | 12.7811 | 22.6334 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612 | 37.3612
Cost of EUE ($) - Option 5 | 72084.1724 | 122573.7157 | 454963.6626 | 146251.053 | 291011.6468 | 40412.3527 | 67126.0056 | 113269.3225 | 191362.4076 | 258607.7449 | 360647.8459 | 578373.0967 | 552629.8186 | 978622.5531 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881 | 1615420.7881
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0095557 | 0.39354 | 1.2432 | 3.1613 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643 | 3.5643
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.44842 | 0.77295 | 4.1363 | 11.4059 | 18.2785 | 25.8687 | 35.2708 | 45.455 | 57.8125 | 67.6223 | 80.5742 | 100.7294 | 102.9748 | 134.6805 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839 | 171.3839
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.22499 | 0.2343 | 0.32228 | 0.42549 | 0.53442 | 0.66023 | 0.80743 | 0.97765 | 1.1761 | 1.392 | 1.649 | 1.9572 | 2.2467 | 2.6674 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134 | 3.134
Total EUE (MWh) - Option 6 | 0.67341 | 1.0072 | 4.4585 | 11.8314 | 18.8129 | 26.5289 | 36.0783 | 46.4327 | 58.9886 | 69.0143 | 82.2327 | 103.0801 | 106.4647 | 140.5093 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822 | 178.0822
Cost of EUE ($) - Option 6 | 29116.7224 | 43551.2243 | 192777.8275 | 511565.735 | 813432.6065 | 1147055.3854 | 1559950.6819 | 2007654.8348 | 2550544.7755 | 2984037.8661 | 3555573.5315 | 4456972.3424 | 4603316.8292 | 6075333.1023 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226 | 7699911.8226
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0.30492 | 1.5891 | 3.6944 | 5.1726 | 7.966 | 14.5973 | 18.2119 | 36.5871 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097
Weighted Energy @ Risk (MWh) under N-1 Conditions | 1.4221 | 2.5788 | 10.1708 | 22.816 | 33.8316 | 45.5805 | 59.4887 | 74.4299 | 92.0129 | 106.1954 | 124.7847 | 152.2557 | 158.5456 | 200.8032 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.24502 | 0.25606 | 0.35153 | 0.46323 | 0.58148 | 0.71805 | 0.87762 | 1.0623 | 1.2772 | 1.5112 | 1.7894 | 2.1221 | 2.4395 | 2.8928 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926
Total EUE (MWh) - Option 7 | 1.6672 | 2.8349 | 10.5223 | 23.2792 | 34.4131 | 46.2985 | 60.6713 | 77.0813 | 96.9845 | 112.8792 | 134.54 | 168.9751 | 179.1971 | 240.2831 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858
Cost of EUE ($) - Option 7 | 72084.1724 | 122573.7157 | 454963.6626 | 1006544.8989 | 1487950.2733 | 2001852.8529 | 2623301.6632 | 3332836.3755 | 4193412.8475 | 4880664.3188 | 5817234.9665 | 7306137.3129 | 7748115.5231 | 10389350.9022 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0.30492 | 1.5891 | 3.6944 | 5.1726 | 7.966 | 14.5973 | 18.2119 | 36.5871 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097 | 97.7097
Weighted Energy @ Risk (MWh) under N-1 Conditions | 1.4221 | 2.5788 | 10.1708 | 22.816 | 33.8316 | 45.5805 | 59.4887 | 74.4299 | 92.0129 | 106.1954 | 124.7847 | 152.2557 | 158.5456 | 200.8032 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557 | 246.7557
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.24502 | 0.25606 | 0.35153 | 0.46323 | 0.58148 | 0.71805 | 0.87762 | 1.0623 | 1.2772 | 1.5112 | 1.7894 | 2.1221 | 2.4395 | 2.8928 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926 | 3.3926
Total EUE (MWh) - Option 8 | 1.6672 | 2.8349 | 10.5223 | 23.2792 | 34.4131 | 46.2985 | 60.6713 | 77.0813 | 96.9845 | 112.8792 | 134.54 | 168.9751 | 179.1971 | 240.2831 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858 | 347.858
Cost of EUE ($) - Option 8 | 72084.1724 | 122573.7157 | 454963.6626 | 1006544.8989 | 1487950.2733 | 2001852.8529 | 2623301.6632 | 3332836.3755 | 4193412.8475 | 4880664.3188 | 5817234.9665 | 7306137.3129 | 7748115.5231 | 10389350.9022 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459 | 15040670.2459