## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 105212961.6203 | 61.5% | 30.2784
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 59818974.1027 | 34.97% | 12.0256
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 2268426.58 | 1.326% | 0.44409
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 3766583.5488 | 2.202% | 0.4899
[5 empty] | 171066945.8518 |  | 43.238
Customer No. and Vol per Feeder | [6 empty] | 43237.9539 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 59818974.1027 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 49.6582 | E@R MWh | 49.6582
RESIDENTL | 105212961.6203 | [14 empty] | cost of EUE ($) | 2147118.6735 | cost of EUE ($M) | 2.1471
FARM | 3766583.5488
INDUSTRIAL | 2268426.58
Forecast (FCT)
Forecast | 2031
Summer POE50 | 80.4506
Summer POE10 | 88.8048
Winter POE50 | 77.5373
Winter POE10 | 81.1629
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 3.06 |  | Summer POE50 | 77.3906 |  |  | 100% | 0 | 77.3906 | 100% |  | 0% |  | 0%
|  |  | Summer POE10 | 85.7448 |  |  | 99% | 0 | 76.6167 | 99% |  | 0% | 0 | 0% | 0
Embedded Generation |  |  | Winter POE50 | 74.4773 |  |  | 98% | 0.37816 | 75.8428 | 98% |  | 0% | 11.7343 | 0% | 28.8274
|  |  | Winter POE10 | 78.1029 |  |  | 97% | 0.75633 | 75.0689 | 97% |  | 0% | 11.4417 | 0% | 28.5347
Year | 2031 | [5 empty] | 95% | 1.8908 | 73.5211 | 95% |  | 0% | 33.008 | 0% | 84.2871
Capacity | 0 | [5 empty] | 90% | 4.538 | 69.6515 | 90% |  | 0% | 69.8485 | 0% | 189.4997
[7 empty] | 85% | 9.0759 | 65.782 | 85% |  | 0% | 102.1805 | 0% | 307.2968
Demand Mangement | [6 empty] | 80% | 27.606 | 61.9125 | 80% |  | 0% | 345.5345 | 0% | 1183.0927
[7 empty] | 75% | 57.481 | 58.043 | 75% |  | 0% | 441.4841 | 0% | 1791.8331
Year | 2031 | [5 empty] | 70% | 106.2642 | 54.1734 | 70% |  | 0% | 532.1363 | 0% | 2737.1366
Capacity | 0 | [5 empty] | 65% | 201.9397 | 50.3039 | 65% |  | 0% | 673.4277 | 0% | 4997.9632
[7 empty] | 60% | 402.745 | 46.4344 | 60% |  | 0% | 636.3776 | 0% | 9712.7743
LDC | [6 empty] | 55% | 655.7369 | 42.5648 | 55% |  | 0% | 49.8086 | 0% | 11258.0382
[7 empty] | 50% | 981.7145 | 38.6953 | 50% |  | 0% |  | 0% | 13244.4926
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 1622.7029 | 34.8258 | 45% |  | 0% |  | 0% | 23563.0806
100% | 0% | 0 |  |  |  |  | 40% | 2442.9413 | 30.9562 | 40% |  | 0% |  | 0% | 26978.4652
99% | 0% | 0 |  |  |  |  | 35% | 3006.7842 | 27.0867 | 35% |  | 0% |  | 0% | 16363.5553
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3276.4154 | 23.2172 | 30% |  | 0% |  | 0% | 6781.748
97% | 0.01722% | 0.75633 |  |  |  |  | 25% | 3466.632 | 19.3477 | 25% |  | 0% |  | 0% | 4048.2697
95% | 0.04305% | 1.8908 |  |  |  |  | 20% | 3713.9514 | 15.4781 | 20% |  | 0% |  | 0% | 4306.5453
90% | 0.1033% | 4.538 |  |  |  |  | 15% | 4043.3325 | 11.6086 | 15% |  | 0% |  | 0% | 4460.9254
85% | 0.2066% | 9.0759 |  |  |  |  | 10% | 4350.7801 | 7.7391 | 10% |  | 0% |  | 0% | 2974.1942
80% | 0.6286% | 27.606 |  |  |  |  | 5% | 4391.6218 | 3.8695 | 5% |  | 0% |  | 0% | 237.0575
75% | 1.309% | 57.481 |  |  |  |  | 9.992e-14% | 4391.6218 | 7.7329e-14 | 9.992e-14% |  | 0% |  | 0% | 0
70% | 2.419% | 106.2642 | [7 empty] | Total E@R | 0 | Total E@R | 2906.9819 | Total E@R | 135277.6178
65% | 4.598% | 201.9397 | [7 empty] | Total WE@R | 0 | Total WE@R | 9.5068 | Total WE@R | 0.61183
60% | 9.17% | 402.745 |  |  |  |  | MD Weighted LDC
55% | 14.93% | 655.7369
50% | 22.35% | 981.7145 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 36.95% | 1622.7029 |  |  |  |  | 100% | 0 | 85.7448 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 55.62% | 2442.9413 |  |  |  |  | 99% | 0.75633 | 84.8874
35% | 68.46% | 3006.7842 |  |  |  |  | 98% | 1.1345 | 84.0299 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 74.6% | 3276.4154 |  |  |  |  | 97% | 1.8908 | 83.1725 | 100% |  | 0% |  | 0%
25% | 78.93% | 3466.632 |  |  |  |  | 95% | 3.4035 | 81.4576 | 99% |  | 0% | 30.3409 | 0% | 64.527
20% | 84.56% | 3713.9514 |  |  |  |  | 90% | 9.0759 | 77.1703 | 98% |  | 0% | 14.8462 | 0% | 31.9392
15% | 92.06% | 4043.3325 |  |  |  |  | 85% | 16.2611 | 72.8831 | 97% |  | 0% | 29.0439 | 0% | 63.23
10% | 99.06% | 4350.7801 |  |  |  |  | 80% | 24.9588 | 68.5959 | 95% |  | 0% | 56.1423 | 0% | 124.5144
5% | 99.99% | 4391.6218 |  |  |  |  | 75% | 32.9003 | 64.3086 | 90% |  | 0% | 193.5102 | 0% | 449.9056
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 41.9762 | 60.0214 | 85% |  | 0% | 214.3085 | 0% | 539.076
[7 empty] | 65% | 67.6914 | 55.7341 | 80% |  | 0% | 222.1367 | 0% | 615.2763
[7 empty] | 60% | 98.7009 | 51.4469 | 75% |  | 0% | 168.7735 | 0% | 527.7271
[7 empty] | 55% | 153.5347 | 47.1596 | 70% |  | 0% | 153.9733 | 0% | 564.2059
LDC | [6 empty] | 50% | 258.2862 | 42.8724 | 65% |  | 0% | 326.0105 | 0% | 1488.3362
[7 empty] | 45% | 488.9664 | 38.5852 | 60% |  | 0% | 260.1852 | 0% | 1661.8133
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 928.0152 | 34.2979 | 55% |  | 0% | 224.9978 | 0% | 2703.4866
100% | 0% | 0 |  |  |  |  | 35% | 1530.4309 | 30.0107 | 50% |  | 0% | 46.9146 | 0% | 4715.4967
99% | 0.01722% | 0.75633 |  |  |  |  | 30% | 2592.3162 | 25.7234 | 45% |  | 0% |  | 0% | 9395.3251
98% | 0.02583% | 1.1345 |  |  |  |  | 25% | 3659.4958 | 21.4362 | 40% |  | 0% |  | 0% | 15999.6145
97% | 0.04305% | 1.8908 |  |  |  |  | 20% | 4005.5161 | 17.149 | 35% |  | 0% |  | 0% | 19370.2583
95% | 0.07749% | 3.4035 |  |  |  |  | 15% | 4281.1979 | 12.8617 | 30% |  | 0% |  | 0% | 29591.6263
90% | 0.2066% | 9.0759 |  |  |  |  | 10% | 4391.6218 | 8.5745 | 25% |  | 0% |  | 0% | 25163.9071
85% | 0.3702% | 16.2611 |  |  |  |  | 5% | 4391.6218 | 4.2872 | 20% |  | 0% |  | 0% | 6675.6258
80% | 0.5683% | 24.9588 |  |  |  |  | 9.992e-14% | 4391.6218 | 8.5676e-14 | 15% |  | 0% |  | 0% | 4136.6992
75% | 0.7491% | 32.9003 | [7 empty] | 10% |  | 0% |  | 0% | 1183.5353
70% | 0.9557% | 41.9762 | [7 empty] | 5% |  | 0% |  | 0% | 0
65% | 1.541% | 67.6914 | [7 empty] | 9.992e-14% |  | 0% |  | 0% | 0
60% | 2.247% | 98.7009 | [7 empty] | Total E@R | 0 | Total E@R | 1941.1838 | Total E@R | 125066.1259
55% | 3.496% | 153.5347 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 2.7207 | Total WE@R | 0.24242
50% | 5.881% | 258.2862
45% | 11.13% | 488.9664 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 21.13% | 928.0152 |  |  |  |  | 100% | 0 | 74.4773
35% | 34.85% | 1530.4309 |  |  |  |  | 99% | 0.8916 | 73.7326 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 59.02% | 2592.3162 |  |  |  |  | 98% | 3.5664 | 72.9878
25% | 83.32% | 3659.4958 |  |  |  |  | 97% | 4.7552 | 72.243 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 91.2% | 4005.5161 |  |  |  |  | 95% | 7.7272 | 70.7535 | 100% |  | 0% |  | 0%
15% | 97.48% | 4281.1979 |  |  |  |  | 90% | 39.2302 | 67.0296 | 99% |  | 0% | 23.2751 | 0% | 66.0717
10% | 99.99% | 4391.6218 |  |  |  |  | 85% | 117.6906 | 63.3057 | 98% |  | 0% | 67.8331 | 0% | 196.2229
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 268.3703 | 59.5819 | 97% |  | 0% | 29.2627 | 0% | 86.3248
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 455.9026 | 55.858 | 95% |  | 0% | 69.8365 | 0% | 212.4918
[7 empty] | 70% | 690.9866 | 52.1341 | 90% |  | 0% | 658.1473 | 0% | 2170.2935
[7 empty] | 65% | 967.6784 | 48.4103 | 85% |  | 0% | 1346.9832 | 0% | 5113.0831
[7 empty] | 60% | 1292.8136 | 44.6864 | 80% |  | 0% | 2025.7089 | 0% | 9258.3326
LDC | [6 empty] | 55% | 1647.0743 | 40.9625 | 75% |  | 0% | 1822.8033 | 0% | 10824.3526
[7 empty] | 50% | 2104.1657 | 37.2387 | 70% |  | 0% | 1409.582 | 0% | 12693.6161
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 2736.0097 | 33.5148 | 65% |  | 0% | 628.7018 | 0% | 13909.9101
100% | 0% | 0 |  |  |  |  | 40% | 3483.7613 | 29.7909 | 60% |  | 0% | 7.3484 | 0% | 15134.5046
99% | 0.0203% | 0.8916 |  |  |  |  | 35% | 3830.2948 | 26.0671 | 55% |  | 0% |  | 0% | 15171.0266
98% | 0.0812% | 3.5664 |  |  |  |  | 30% | 3953.6322 | 22.3432 | 50% |  | 0% |  | 0% | 17872.5495
97% | 0.1083% | 4.7552 |  |  |  |  | 25% | 4060.9208 | 18.6193 | 45% |  | 0% |  | 0% | 22352.5842
95% | 0.1759% | 7.7272 |  |  |  |  | 20% | 4165.2375 | 14.8955 | 40% |  | 0% |  | 0% | 23668.4837
90% | 0.8932% | 39.2302 |  |  |  |  | 15% | 4270.4458 | 11.1716 | 35% |  | 0% |  | 0% | 9678.3358
85% | 2.68% | 117.6906 |  |  |  |  | 10% | 4373.8709 | 7.4477 | 30% |  | 0% |  | 0% | 2985.3986
80% | 6.11% | 268.3703 |  |  |  |  | 5% | 4391.7028 | 3.7239 | 25% |  | 0% |  | 0% | 2197.4083
75% | 10.38% | 455.9026 |  |  |  |  | 9.992e-14% | 4391.7028 | 7.4418e-14 | 20% |  | 0% |  | 0% | 1748.0768
70% | 15.73% | 690.9866 | [7 empty] | 15% |  | 0% |  | 0% | 1371.2359
65% | 22.03% | 967.6784 | [7 empty] | 10% |  | 0% |  | 0% | 962.8533
60% | 29.44% | 1292.8136 | [7 empty] | 5% |  | 0% |  | 0% | 99.6055
55% | 37.5% | 1647.0743 | [7 empty] | 9.992e-14% |  | 0% |  | 0% | 0
50% | 47.91% | 2104.1657 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 8089.4822 | Total E@R | 167772.7617
45% | 62.3% | 2736.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 22.4771 | Total WE@R | 0.6447
40% | 79.32% | 3483.7613 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 87.21% | 3830.2948 |  |  |  |  | 100% | 0 | 78.1029 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 90.02% | 3953.6322 |  |  |  |  | 99% | 0.8916 | 77.3219
25% | 92.46% | 4060.9208 |  |  |  |  | 98% | 3.5664 | 76.5409 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 94.84% | 4165.2375 |  |  |  |  | 97% | 4.7552 | 75.7598 | 100% |  | 100% |  | 100%
15% | 97.23% | 4270.4458 |  |  |  |  | 95% | 7.7272 | 74.1978 | 99% |  | 99% | 26.4915 | 99% | 69.2881
10% | 99.59% | 4373.8709 |  |  |  |  | 90% | 39.2302 | 70.2926 | 98% |  | 98% | 77.3853 | 98% | 205.7751
5% | 99.99% | 4391.7028 |  |  |  |  | 85% | 117.6906 | 66.3875 | 97% |  | 97% | 33.465 | 97% | 90.5271
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 268.3703 | 62.4824 | 95% |  | 95% | 80.1807 | 95% | 222.836
[7 empty] | 75% | 455.9026 | 58.5772 | 90% |  | 90% | 763.7982 | 90% | 2275.9443
[7 empty] | 70% | 690.9866 | 54.6721 | 85% |  | 85% | 1595.8904 | 85% | 5361.9903
[7 empty] | 65% | 967.6784 | 50.7669 | 80% |  | 80% | 2476.4087 | 80% | 9709.0324
LDC | [6 empty] | 60% | 1292.8136 | 46.8618 | 75% |  | 75% | 2349.7376 | 75% | 11351.2869
[7 empty] | 55% | 1647.0743 | 42.9566 | 70% |  | 70% | 2027.5129 | 70% | 13311.547
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 2104.1657 | 39.0515 | 65% |  | 65% | 1305.8425 | 65% | 14587.0508
100% | 0% | 0 |  |  |  |  | 45% | 2736.0097 | 35.1463 | 60% |  | 60% | 318.7033 | 60% | 15871.259
99% | 0.0203% | 0.8916 |  |  |  |  | 40% | 3483.7613 | 31.2412 | 55% |  | 55% |  | 55% | 15909.559
98% | 0.0812% | 3.5664 |  |  |  |  | 35% | 3830.2948 | 27.336 | 50% |  | 50% |  | 50% | 18742.5932
97% | 0.1083% | 4.7552 |  |  |  |  | 30% | 3953.6322 | 23.4309 | 45% |  | 45% |  | 45% | 23440.718
95% | 0.1759% | 7.7272 |  |  |  |  | 25% | 4060.9208 | 19.5257 | 40% |  | 40% |  | 40% | 24820.6761
90% | 0.8932% | 39.2302 |  |  |  |  | 20% | 4165.2375 | 15.6206 | 35% |  | 35% |  | 35% | 10149.4816
85% | 2.68% | 117.6906 |  |  |  |  | 15% | 4270.4458 | 11.7154 | 30% |  | 30% |  | 30% | 3130.7292
80% | 6.11% | 268.3703 |  |  |  |  | 10% | 4373.8709 | 7.8103 | 25% |  | 25% |  | 25% | 2304.3791
75% | 10.38% | 455.9026 |  |  |  |  | 5% | 4391.7028 | 3.9051 | 20% |  | 20% |  | 20% | 1833.1739
70% | 15.73% | 690.9866 |  |  |  |  | 9.992e-14% | 4391.7028 | 7.8041e-14 | 15% |  | 15% |  | 15% | 1437.9883
65% | 22.03% | 967.6784 | [7 empty] | 10% |  | 10% |  | 10% | 1009.7254
60% | 29.44% | 1292.8136 | [7 empty] | 5% |  | 5% |  | 5% | 104.4544
55% | 37.5% | 1647.0743 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0 | 9.992e-14% | 0
50% | 47.91% | 2104.1657 | [7 empty] | Total E@R | 0 | Total E@R | 11055.4161 | Total E@R | 175940.0151
45% | 62.3% | 2736.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 13.1649 | Total WE@R | 0.28975
40% | 79.32% | 3483.7613
35% | 87.21% | 3830.2948
30% | 90.02% | 3953.6322
25% | 92.46% | 4060.9208
20% | 94.84% | 4165.2375
15% | 97.23% | 4270.4458
10% | 99.59% | 4373.8709
5% | 99.99% | 4391.7028
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 93.2 |  |  | Year | 2031
SCR (N-1) | 45.2 |  |  | SCR (N) | 93.2
SCR (N-2) | 0 |  |  | SCR (N-1) | 45.2
WCR (N) | 93.2 |  |  | SCR (N-2) | 0
WCR (N-1) | 48 |  |  | WCR (N) | 93.2
WCR (N-2) | 0 |  |  | WCR (N-1) | 48
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.046016 | 0.064327 | 0.2653 | 0.69775 | 1.114 | 1.576 | 2.1471 | 2.7711 | 3.5258 | 4.1288 | 4.9221 | 6.1427 | 6.3566 | 8.3111 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858
Total EUE (MWh) | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 25.7643 | 36.4498 | 49.6582 | 64.0905 | 81.5439 | 95.4911 | 113.8383 | 142.0667 | 147.015 | 192.2187 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137
Residual Values
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.046016 | 0.064327 | 0.2653 | 0.69775 | 0.12285 | 0.21534 | 0.3633 | 0.55109 | 0.81266 | 1.0195 | 1.305 | 1.8344 | 1.8239 | 2.7644 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853 | 3.9853
Total EUE (MWh) | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 2.8413 | 4.9804 | 8.4024 | 12.7456 | 18.795 | 23.5796 | 30.1811 | 42.4247 | 42.1834 | 63.9336 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.046016 | 0.064327 | 0.2653 | 0.2329 | 0.0486 | 0.069722 | 0.10547 | 0.16282 | 0.25794 | 0.34198 | 0.46837 | 0.73147 | 0.71106 | 1.2237 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992
Total EUE (MWh) | 1.0642 | 1.4877 | 6.1358 | 5.3865 | 1.124 | 1.6125 | 2.4393 | 3.7656 | 5.9656 | 7.9092 | 10.8325 | 16.9173 | 16.4453 | 28.3014 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.046016 | 0.064327 | 0.2653 | 0.00097812 | 0.0016572 | 0.0025004 | 0.003649 | 0.0050396 | 0.00686 | 0.0086181 | 0.010988 | 0.01473 | 0.016562 | 0.023352 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218 | 0.031218
Total EUE (MWh) | 1.0642 | 1.4877 | 6.1358 | 0.022622 | 0.038328 | 0.057828 | 0.084394 | 0.11655 | 0.15866 | 0.19932 | 0.25412 | 0.34068 | 0.38305 | 0.54007 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.046016 | 0.064327 | 0.2653 | 0.2329 | 0.0486 | 0.069722 | 0.10547 | 0.16282 | 0.25794 | 0.34198 | 0.46837 | 0.73147 | 0.71106 | 1.2237 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992 | 1.9992
Total EUE (MWh) | 1.0642 | 1.4877 | 6.1358 | 5.3865 | 1.124 | 1.6125 | 2.4393 | 3.7656 | 5.9656 | 7.9092 | 10.8325 | 16.9173 | 16.4453 | 28.3014 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.046016 | 0.064327 | 0.2653 | 0.69775 | 1.114 | 1.576 | 2.1471 | 2.7711 | 3.5258 | 4.1288 | 4.9221 | 6.1427 | 6.3566 | 8.3111 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858
Total EUE (MWh) | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 25.7643 | 36.4498 | 49.6582 | 64.0905 | 81.5439 | 95.4911 | 113.8383 | 142.0667 | 147.015 | 192.2187 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.046016 | 0.064327 | 0.2653 | 0.69775 | 1.114 | 1.576 | 2.1471 | 2.7711 | 3.5258 | 4.1288 | 4.9221 | 6.1427 | 6.3566 | 8.3111 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858
Total EUE (MWh) | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 25.7643 | 36.4498 | 49.6582 | 64.0905 | 81.5439 | 95.4911 | 113.8383 | 142.0667 | 147.015 | 192.2187 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.046016 | 0.064327 | 0.2653 | 0.69775 | 1.114 | 1.576 | 2.1471 | 2.7711 | 3.5258 | 4.1288 | 4.9221 | 6.1427 | 6.3566 | 8.3111 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858 | 10.4858
Total EUE (MWh) | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 25.7643 | 36.4498 | 49.6582 | 64.0905 | 81.5439 | 95.4911 | 113.8383 | 142.0667 | 147.015 | 192.2187 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137

## Key Model Assumption & Inputs
Select ZSS & Region | OFR | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Base | 100% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | High | 150%
Option 2 - 1B New PHS ZSS + Three new feeders | 1B New PHS ZSS + Three new feeders
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N |  |  |  | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Added Capacity (MVA) Option 4 N-1 |  |  |  | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Added Capacity (MVA) Option 4 N-2 |  |  |  | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Transfers (MVA) Option 3 |  |  |  | 7.25 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Transfers (MVA) Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Transfers (MVA) Option 5 |  |  |  | 7.25 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | OFR
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 56.9594 | 61.9907 | 68.9791 | 74.0072 | 76.6284 | 78.9811 | 80.4506 | 82.1352 | 83.4813 | 84.3346 | 86.446 | 87.894 | 88.627 | 90.0391 | 89.5765
Summer POE10 | 10 |  |  | 64.073 | 69.589 | 76.597 | 81.5678 | 84.5283 | 86.8984 | 88.8048 | 90.6365 | 92.2256 | 92.9929 | 94.1573 | 95.4952 | 96.8516 | 98.5806 | 98.8168
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 50.4065 | 56.1183 | 63.2802 | 69.3039 | 72.5305 | 74.8582 | 77.5373 | 79.5294 | 81.7407 | 82.8706 | 83.8526 | 86.3425 | 84.7668 | 88.8524 | 94.1939
Winter POE10 | 10 |  |  | 53.6497 | 59.4536 | 66.5595 | 72.8129 | 76.0509 | 78.6773 | 81.1629 | 83.2732 | 85.4834 | 86.4197 | 87.7259 | 90.1815 | 89.3155 | 92.5351 | 94.3753
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | OFR | 0 | 3.3 | 3.25 | 3.2 | 3.15 | 3.11 | 3.06 | 3.01 | 2.97 | 2.92 | 2.88 | 2.84 | 2.79 | 2.75 | 2.71
|  | PowerFactor | 1

## Load Duration Curves
Station
OFR
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.0203% | 0.8916 | 0.01722% | 0.75633 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.0812% | 3.5664 | 0.02583% | 1.1345 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.1083% | 4.7552 | 0.04305% | 1.8908 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.1759% | 7.7272 | 0.07749% | 3.4035 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.8932% | 39.2302 | 0.2066% | 9.0759 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 2.68% | 117.6906 | 0.3702% | 16.2611 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 6.11% | 268.3703 | 0.5683% | 24.9588 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 10.38% | 455.9026 | 0.7491% | 32.9003 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 15.73% | 690.9866 | 0.9557% | 41.9762 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 22.03% | 967.6784 | 1.541% | 67.6914 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 29.44% | 1292.8136 | 2.247% | 98.7009 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 37.5% | 1647.0743 | 3.496% | 153.5347 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 47.91% | 2104.1657 | 5.881% | 258.2862 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 62.3% | 2736.0097 | 11.13% | 488.9664 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 79.32% | 3483.7613 | 21.13% | 928.0152 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 87.21% | 3830.2948 | 34.85% | 1530.4309 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 90.02% | 3953.6322 | 59.02% | 2592.3162 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 92.46% | 4060.9208 | 83.32% | 3659.4958 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 94.84% | 4165.2375 | 91.2% | 4005.5161 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 97.23% | 4270.4458 | 97.48% | 4281.1979 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.59% | 4373.8709 | 99.99% | 4391.6218 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.0203% | 0.8916 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.0812% | 3.5664 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.1083% | 4.7552 | 0.01722% | 0.75633 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.1759% | 7.7272 | 0.04305% | 1.8908 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.8932% | 39.2302 | 0.1033% | 4.538 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 2.68% | 117.6906 | 0.2066% | 9.0759 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 6.11% | 268.3703 | 0.6286% | 27.606 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 10.38% | 455.9026 | 1.309% | 57.481 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 15.73% | 690.9866 | 2.419% | 106.2642 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 22.03% | 967.6784 | 4.598% | 201.9397 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 29.44% | 1292.8136 | 9.17% | 402.745 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 37.5% | 1647.0743 | 14.93% | 655.7369 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 47.91% | 2104.1657 | 22.35% | 981.7145 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 62.3% | 2736.0097 | 36.95% | 1622.7029 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 79.32% | 3483.7613 | 55.62% | 2442.9413 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 87.21% | 3830.2948 | 68.46% | 3006.7842 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 90.02% | 3953.6322 | 74.6% | 3276.4154 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 92.46% | 4060.9208 | 78.93% | 3466.632 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 94.84% | 4165.2375 | 84.56% | 3713.9514 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 97.23% | 4270.4458 | 92.06% | 4043.3325 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.59% | 4373.8709 | 99.06% | 4350.7801 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 1 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 3 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 93.2 | 93.2 | 93.2 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4
SCR N Rating (MVA) - Option 4 | 93.2 | 93.2 | 93.2 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4
Capacity Added (MVA) | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 5 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 6 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 7 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 8 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 1 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 3 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 48 | 48 | 48 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N-1 Rating (MVA) - Option 4 | 45.2 | 45.2 | 45.2 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4
Capacity Added (MVA) | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 5 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 6 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 7 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 8 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 50.4065 | 56.1183 | 63.2802 | 69.3039 | 72.5305 | 74.8582 | 77.5373 | 79.5294 | 81.7407 | 82.8706 | 83.8526 | 86.3425 | 84.7668 | 88.8524 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939 | 94.1939
Maximum Demand (MVA) - P10 | 53.6497 | 59.4536 | 66.5595 | 72.8129 | 76.0509 | 78.6773 | 81.1629 | 83.2732 | 85.4834 | 86.4197 | 87.7259 | 90.1815 | 89.3155 | 92.5351 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753 | 94.3753
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 3.3 | 3.25 | 3.2 | 3.15 | 3.11 | 3.06 | 3.01 | 2.97 | 2.92 | 2.88 | 2.84 | 2.79 | 2.75 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 56.9594 | 61.9907 | 68.9791 | 74.0072 | 76.6284 | 78.9811 | 80.4506 | 82.1352 | 83.4813 | 84.3346 | 86.446 | 87.894 | 88.627 | 90.0391 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765 | 89.5765
Maximum Demand (MVA) - P10 | 64.073 | 69.589 | 76.597 | 81.5678 | 84.5283 | 86.8984 | 88.8048 | 90.6365 | 92.2256 | 92.9929 | 94.1573 | 95.4952 | 96.8516 | 98.5806 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168 | 98.8168
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 3.3 | 3.25 | 3.2 | 3.15 | 3.11 | 3.06 | 3.01 | 2.97 | 2.92 | 2.88 | 2.84 | 2.79 | 2.75 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068
Option 2 - 1B New PHS ZSS + Three new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 54.8805 | 57.2482 | 59.9773 | 62.0194 | 64.2707 | 65.4506 | 66.4726 | 69.0025 | 67.4768 | 71.6024 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 58.4009 | 61.0673 | 63.6029 | 65.7632 | 68.0134 | 68.9997 | 70.3459 | 72.8415 | 72.0255 | 75.2851 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 58.9784 | 61.3711 | 62.8906 | 64.6252 | 66.0113 | 66.9146 | 69.066 | 70.554 | 71.337 | 72.7891 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 64.073 | 66.289 | 73.347 | 78.3678 | 66.8783 | 69.2884 | 71.2448 | 73.1265 | 74.7556 | 75.5729 | 76.7773 | 78.1552 | 79.5616 | 81.3306 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 7.25 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 50.4065 | 52.8183 | 60.0302 | 58.8539 | 47.6305 | 49.9982 | 52.7273 | 54.7694 | 57.0207 | 58.2006 | 59.2226 | 61.7525 | 60.2268 | 64.3524 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 53.6497 | 56.1536 | 63.3095 | 62.3629 | 51.1509 | 53.8173 | 56.3529 | 58.5132 | 60.7634 | 61.7497 | 63.0959 | 65.5915 | 64.7755 | 68.0351 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 56.9594 | 58.6907 | 65.7291 | 63.5572 | 51.7284 | 54.1211 | 55.6406 | 57.3752 | 58.7613 | 59.6646 | 61.816 | 63.304 | 64.087 | 65.5391 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 64.073 | 66.289 | 73.347 | 71.1178 | 59.6283 | 62.0384 | 63.9948 | 65.8765 | 67.5056 | 68.3229 | 69.5273 | 70.9052 | 72.3116 | 74.0806 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 7.25 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 50.4065 | 52.8183 | 60.0302 | 58.8539 | 47.6305 | 49.9982 | 52.7273 | 54.7694 | 57.0207 | 58.2006 | 59.2226 | 61.7525 | 60.2268 | 64.3524 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 53.6497 | 56.1536 | 63.3095 | 62.3629 | 51.1509 | 53.8173 | 56.3529 | 58.5132 | 60.7634 | 61.7497 | 63.0959 | 65.5915 | 64.7755 | 68.0351 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 56.9594 | 58.6907 | 65.7291 | 63.5572 | 51.7284 | 54.1211 | 55.6406 | 57.3752 | 58.7613 | 59.6646 | 61.816 | 63.304 | 64.087 | 65.5391 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 64.073 | 66.289 | 73.347 | 71.1178 | 59.6283 | 62.0384 | 63.9948 | 65.8765 | 67.5056 | 68.3229 | 69.5273 | 70.9052 | 72.3116 | 74.0806 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 100% | 0 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
99% | 0.8916 | 49.9025 | 52.2901 | 59.4299 | 65.4429 | 68.6867 | 71.0307 | 73.7326 | 75.7542 | 77.9829 | 79.1511 | 80.1629 | 82.6675 | 81.157 | 85.2413 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 99% | 0.8916 | 53.1132 | 55.592 | 62.6764 | 68.9168 | 72.1719 | 74.8116 | 77.3219 | 79.4606 | 81.6883 | 82.6647 | 83.9974 | 86.4681 | 85.6602 | 88.8872 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486
98% | 3.5664 | 49.3984 | 51.7619 | 58.8296 | 64.7818 | 67.9929 | 70.3132 | 72.9878 | 74.989 | 77.1952 | 78.3516 | 79.3532 | 81.8324 | 80.3372 | 84.3803 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 98% | 3.5664 | 52.5767 | 55.0305 | 62.0433 | 68.2206 | 71.4429 | 74.0559 | 76.5409 | 78.658 | 80.8632 | 81.8297 | 83.1489 | 85.5946 | 84.795 | 87.9894 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832
97% | 4.7552 | 48.8943 | 51.2337 | 58.2293 | 64.1208 | 67.2991 | 69.5957 | 72.243 | 74.2238 | 76.4075 | 77.5521 | 78.5434 | 80.9974 | 79.5174 | 83.5193 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 97% | 4.7552 | 52.0402 | 54.469 | 61.4102 | 67.5245 | 70.7139 | 73.3003 | 75.7598 | 77.8554 | 80.038 | 80.9947 | 82.3005 | 84.7212 | 83.9297 | 87.0915 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153
95% | 7.7272 | 47.8862 | 50.1774 | 57.0287 | 62.7987 | 65.9115 | 68.1608 | 70.7535 | 72.6934 | 74.8321 | 75.9531 | 76.924 | 79.3274 | 77.8779 | 81.7972 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 95% | 7.7272 | 50.9672 | 53.3459 | 60.144 | 66.1322 | 69.2559 | 71.7889 | 74.1978 | 76.2501 | 78.3878 | 79.3247 | 80.6036 | 82.9744 | 82.1992 | 85.2958 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082
90% | 39.2302 | 45.3659 | 47.5365 | 54.0272 | 59.4935 | 62.4425 | 64.5734 | 67.0296 | 68.8674 | 70.8936 | 71.9556 | 72.8753 | 75.1522 | 73.7791 | 77.4921 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 90% | 39.2302 | 48.2848 | 50.5382 | 56.9785 | 62.6516 | 65.6108 | 68.0106 | 70.2926 | 72.2369 | 74.2621 | 75.1497 | 76.3613 | 78.6073 | 77.8729 | 80.8066 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987
85% | 117.6906 | 42.8456 | 44.8955 | 51.0257 | 56.1883 | 58.9735 | 60.986 | 63.3057 | 65.0415 | 66.9551 | 67.958 | 68.8267 | 70.9771 | 69.6802 | 73.187 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 85% | 117.6906 | 45.6023 | 47.7305 | 53.813 | 59.171 | 61.9658 | 64.2322 | 66.3875 | 68.2238 | 70.1364 | 70.9748 | 72.119 | 74.2403 | 73.5467 | 76.3173 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155
80% | 268.3703 | 40.3252 | 42.2546 | 48.0242 | 52.8831 | 55.5044 | 57.3985 | 59.5819 | 61.2155 | 63.0165 | 63.9605 | 64.7781 | 66.802 | 65.5814 | 68.8819 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 80% | 268.3703 | 42.9198 | 44.9228 | 50.6476 | 55.6903 | 58.3207 | 60.4538 | 62.4824 | 64.2106 | 66.0108 | 66.7998 | 67.8767 | 69.8732 | 69.2204 | 71.8281 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322
75% | 455.9026 | 37.8049 | 39.6137 | 45.0227 | 49.5779 | 52.0354 | 53.8111 | 55.858 | 57.3895 | 59.078 | 59.963 | 60.7295 | 62.6269 | 61.4826 | 64.5768 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 75% | 455.9026 | 40.2373 | 42.1152 | 47.4821 | 52.2097 | 54.6757 | 56.6755 | 58.5772 | 60.1974 | 61.8851 | 62.6248 | 63.6344 | 65.5061 | 64.8941 | 67.3388 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749
70% | 690.9866 | 35.2846 | 36.9728 | 42.0212 | 46.2727 | 48.5664 | 50.2237 | 52.1341 | 53.5636 | 55.1395 | 55.9654 | 56.6808 | 58.4517 | 57.3837 | 60.2717 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 70% | 690.9866 | 37.5548 | 39.3075 | 44.3166 | 48.729 | 51.0307 | 52.8971 | 54.6721 | 56.1843 | 57.7594 | 58.4498 | 59.3921 | 61.139 | 60.5678 | 62.8495 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657
65% | 967.6784 | 32.7642 | 34.3319 | 39.0196 | 42.9675 | 45.0973 | 46.6363 | 48.4103 | 49.7376 | 51.2009 | 51.9679 | 52.6322 | 54.2766 | 53.2849 | 55.9665 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 65% | 967.6784 | 34.8723 | 36.4998 | 41.1511 | 45.2484 | 47.3856 | 49.1187 | 50.7669 | 52.1711 | 53.6337 | 54.2748 | 55.1498 | 56.772 | 56.2416 | 58.3603 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824
60% | 1292.8136 | 30.2439 | 31.691 | 36.0181 | 39.6623 | 41.6283 | 43.0489 | 44.6864 | 45.9116 | 47.2624 | 47.9704 | 48.5836 | 50.1015 | 49.1861 | 51.6614 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 60% | 1292.8136 | 32.1898 | 33.6921 | 37.9857 | 41.7677 | 43.7406 | 45.3404 | 46.8618 | 48.1579 | 49.5081 | 50.0998 | 50.9075 | 52.4049 | 51.9153 | 53.871 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992
55% | 1647.0743 | 27.7236 | 29.0501 | 33.0166 | 36.3571 | 38.1593 | 39.4615 | 40.9625 | 42.0857 | 43.3239 | 43.9728 | 44.5349 | 45.9264 | 45.0872 | 47.3563 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 55% | 1647.0743 | 29.5074 | 30.8845 | 34.8202 | 38.2871 | 40.0955 | 41.562 | 42.9566 | 44.1448 | 45.3824 | 45.9248 | 46.6652 | 48.0378 | 47.589 | 49.3818 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159
50% | 2104.1657 | 25.2033 | 26.4091 | 30.0151 | 33.0519 | 34.6903 | 35.8741 | 37.2387 | 38.2597 | 39.3853 | 39.9753 | 40.4863 | 41.7512 | 40.9884 | 43.0512 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 50% | 2104.1657 | 26.8249 | 28.0768 | 31.6547 | 34.8064 | 36.4505 | 37.7836 | 39.0515 | 40.1316 | 41.2567 | 41.7499 | 42.4229 | 43.6707 | 43.2627 | 44.8925 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326
45% | 2736.0097 | 22.6829 | 23.7682 | 27.0136 | 29.7468 | 31.2212 | 32.2867 | 33.5148 | 34.4337 | 35.4468 | 35.9778 | 36.4377 | 37.5761 | 36.8895 | 38.7461 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 45% | 2736.0097 | 24.1424 | 25.2691 | 28.4893 | 31.3258 | 32.8054 | 34.0053 | 35.1463 | 36.1185 | 37.1311 | 37.5749 | 38.1806 | 39.3037 | 38.9365 | 40.4033 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494
40% | 3483.7613 | 20.1626 | 21.1273 | 24.0121 | 26.4416 | 27.7522 | 28.6993 | 29.7909 | 30.6078 | 31.5083 | 31.9802 | 32.389 | 33.401 | 32.7907 | 34.4409 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 40% | 3483.7613 | 21.4599 | 22.4614 | 25.3238 | 27.8452 | 29.1604 | 30.2269 | 31.2412 | 32.1053 | 33.0054 | 33.3999 | 33.9383 | 34.9366 | 34.6102 | 35.914 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661
35% | 3830.2948 | 17.6423 | 18.4864 | 21.0106 | 23.1364 | 24.2832 | 25.1119 | 26.0671 | 26.7818 | 27.5697 | 27.9827 | 28.3404 | 29.2259 | 28.6919 | 30.1358 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 35% | 3830.2948 | 18.7774 | 19.6537 | 22.1583 | 24.3645 | 25.5153 | 26.4485 | 27.336 | 28.0921 | 28.8797 | 29.2249 | 29.696 | 30.5695 | 30.2839 | 31.4248 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828
30% | 3953.6322 | 15.122 | 15.8455 | 18.0091 | 19.8312 | 20.8142 | 21.5245 | 22.3432 | 22.9558 | 23.6312 | 23.9852 | 24.2918 | 25.0507 | 24.593 | 25.8307 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 30% | 3953.6322 | 16.0949 | 16.8461 | 18.9928 | 20.8839 | 21.8703 | 22.6702 | 23.4309 | 24.079 | 24.754 | 25.0499 | 25.4538 | 26.2024 | 25.9576 | 26.9355 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996
25% | 4060.9208 | 12.6016 | 13.2046 | 15.0076 | 16.526 | 17.3451 | 17.937 | 18.6193 | 19.1298 | 19.6927 | 19.9877 | 20.2432 | 20.8756 | 20.4942 | 21.5256 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 25% | 4060.9208 | 13.4124 | 14.0384 | 15.8274 | 17.4032 | 18.2252 | 18.8918 | 19.5257 | 20.0658 | 20.6284 | 20.8749 | 21.2115 | 21.8354 | 21.6314 | 22.4463 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163
20% | 4165.2375 | 10.0813 | 10.5637 | 12.006 | 13.2208 | 13.8761 | 14.3496 | 14.8955 | 15.3039 | 15.7541 | 15.9901 | 16.1945 | 16.7005 | 16.3954 | 17.2205 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 20% | 4165.2375 | 10.7299 | 11.2307 | 12.6619 | 13.9226 | 14.5802 | 15.1135 | 15.6206 | 16.0526 | 16.5027 | 16.6999 | 16.9692 | 17.4683 | 17.3051 | 17.957 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331
15% | 4270.4458 | 7.561 | 7.9227 | 9.0045 | 9.9156 | 10.4071 | 10.7622 | 11.1716 | 11.4779 | 11.8156 | 11.9926 | 12.1459 | 12.5254 | 12.2965 | 12.9154 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 15% | 4270.4458 | 8.0475 | 8.423 | 9.4964 | 10.4419 | 10.9351 | 11.3351 | 11.7154 | 12.0395 | 12.377 | 12.525 | 12.7269 | 13.1012 | 12.9788 | 13.4678 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498
10% | 4373.8709 | 5.0407 | 5.2818 | 6.003 | 6.6104 | 6.9381 | 7.1748 | 7.4477 | 7.6519 | 7.8771 | 7.9951 | 8.0973 | 8.3502 | 8.1977 | 8.6102 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 10% | 4373.8709 | 5.365 | 5.6154 | 6.3309 | 6.9613 | 7.2901 | 7.5567 | 7.8103 | 8.0263 | 8.2513 | 8.35 | 8.4846 | 8.7341 | 8.6525 | 8.9785 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665
5% | 4391.7028 | 2.5203 | 2.6409 | 3.0015 | 3.3052 | 3.469 | 3.5874 | 3.7239 | 3.826 | 3.9385 | 3.9975 | 4.0486 | 4.1751 | 4.0988 | 4.3051 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 5% | 4391.7028 | 2.6825 | 2.8077 | 3.1655 | 3.4806 | 3.645 | 3.7784 | 3.9051 | 4.0132 | 4.1257 | 4.175 | 4.2423 | 4.3671 | 4.3263 | 4.4893 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833
9.992e-14% | 4391.7028 | 5.0366e-14 | 5.2776e-14 | 5.9982e-14 | 6.6051e-14 | 6.9325e-14 | 7.1691e-14 | 7.4418e-14 | 7.6458e-14 | 7.8708e-14 | 7.9887e-14 | 8.0908e-14 | 8.3436e-14 | 8.1911e-14 | 8.6034e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.992e-14% | 4391.7028 | 5.3607e-14 | 5.6109e-14 | 6.3259e-14 | 6.9557e-14 | 7.2843e-14 | 7.5507e-14 | 7.8041e-14 | 8.0199e-14 | 8.2447e-14 | 8.3433e-14 | 8.4778e-14 | 8.7272e-14 | 8.6456e-14 | 8.9713e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 100% | 0 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068
99% | 0 | 56.3898 | 58.1038 | 65.0718 | 70.0992 | 72.7437 | 75.1124 | 76.6167 | 78.334 | 79.7062 | 80.6005 | 82.7304 | 84.2035 | 84.9787 | 86.4162 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 99% | 0.75633 | 63.4323 | 65.6261 | 72.6135 | 77.5841 | 80.5645 | 82.9506 | 84.8874 | 86.7503 | 88.363 | 89.1721 | 90.3645 | 91.7286 | 93.121 | 94.8723 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457
98% | 0.37816 | 55.8202 | 57.5169 | 64.4145 | 69.3911 | 72.0089 | 74.3537 | 75.8428 | 77.5427 | 78.9011 | 79.7863 | 81.8947 | 83.3529 | 84.1203 | 85.5433 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 98% | 1.1345 | 62.7915 | 64.9632 | 71.88 | 76.8005 | 79.7507 | 82.1127 | 84.0299 | 85.874 | 87.4705 | 88.2714 | 89.4517 | 90.8021 | 92.1803 | 93.914 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847
97% | 0.75633 | 55.2506 | 56.93 | 63.7572 | 68.683 | 71.2741 | 73.595 | 75.0689 | 76.7515 | 78.096 | 78.9722 | 81.059 | 82.5024 | 83.2619 | 84.6705 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 97% | 1.8908 | 62.1508 | 64.3003 | 71.1466 | 76.0168 | 78.9369 | 81.2748 | 83.1725 | 84.9977 | 86.5779 | 87.3707 | 88.539 | 89.8755 | 91.2397 | 92.9557 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236
95% | 1.8908 | 54.1115 | 55.7561 | 62.4427 | 67.2669 | 69.8045 | 72.0775 | 73.5211 | 75.169 | 76.4857 | 77.3439 | 79.3877 | 80.8013 | 81.5452 | 82.9247 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 95% | 3.4035 | 60.8693 | 62.9745 | 69.6796 | 74.4494 | 77.3094 | 79.599 | 81.4576 | 83.2452 | 84.7928 | 85.5692 | 86.7134 | 88.0224 | 89.3585 | 91.0391 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015
90% | 4.538 | 51.2635 | 52.8216 | 59.1562 | 63.7265 | 66.1306 | 68.284 | 69.6515 | 71.2127 | 72.4602 | 73.2732 | 75.2094 | 76.5486 | 77.2533 | 78.5602 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 90% | 9.0759 | 57.6657 | 59.6601 | 66.0123 | 70.531 | 73.2405 | 75.4096 | 77.1703 | 78.8639 | 80.33 | 81.0656 | 82.1496 | 83.3897 | 84.6554 | 86.2476 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961
85% | 9.0759 | 48.4155 | 49.8871 | 55.8697 | 60.1862 | 62.4567 | 64.4904 | 65.782 | 67.2565 | 68.4346 | 69.2024 | 71.0311 | 72.2959 | 72.9615 | 74.1958 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 85% | 16.2611 | 54.462 | 56.3456 | 62.3449 | 66.6126 | 69.1716 | 71.2202 | 72.8831 | 74.4826 | 75.8673 | 76.5619 | 77.5857 | 78.7569 | 79.9523 | 81.456 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908
80% | 27.606 | 45.5675 | 46.9525 | 52.5833 | 56.6458 | 58.7827 | 60.6969 | 61.9125 | 63.3002 | 64.409 | 65.1317 | 66.8528 | 68.0432 | 68.6696 | 69.8313 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 80% | 24.9588 | 51.2584 | 53.0312 | 58.6776 | 62.6943 | 65.1026 | 67.0308 | 68.5959 | 70.1012 | 71.4045 | 72.0583 | 73.0218 | 74.1241 | 75.2493 | 76.6645 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854
75% | 57.481 | 42.7196 | 44.018 | 49.2968 | 53.1054 | 55.1088 | 56.9033 | 58.043 | 59.3439 | 60.3835 | 61.061 | 62.6745 | 63.7905 | 64.3778 | 65.4668 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 75% | 32.9003 | 48.0547 | 49.7167 | 55.0102 | 58.7759 | 61.0337 | 62.8413 | 64.3086 | 65.7199 | 66.9417 | 67.5547 | 68.458 | 69.4914 | 70.5462 | 71.873 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801
70% | 106.2642 | 39.8716 | 41.0835 | 46.0104 | 49.5651 | 51.4349 | 53.1098 | 54.1734 | 55.3877 | 56.3579 | 56.9902 | 58.4962 | 59.5378 | 60.0859 | 61.1024 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 70% | 41.9762 | 44.8511 | 46.4023 | 51.3429 | 54.8575 | 56.9648 | 58.6519 | 60.0214 | 61.3386 | 62.4789 | 63.051 | 63.8941 | 64.8586 | 65.8431 | 67.0814 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748
65% | 201.9397 | 37.0236 | 38.1489 | 42.7239 | 46.0247 | 47.761 | 49.3162 | 50.3039 | 51.4314 | 52.3323 | 52.9195 | 54.3179 | 55.2851 | 55.7941 | 56.7379 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 65% | 67.6914 | 41.6474 | 43.0878 | 47.6755 | 50.9391 | 52.8959 | 54.4625 | 55.7341 | 56.9573 | 58.0161 | 58.5474 | 59.3302 | 60.2259 | 61.14 | 62.2899 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694
60% | 402.745 | 34.1757 | 35.2144 | 39.4375 | 42.4843 | 44.0871 | 45.5227 | 46.4344 | 47.4751 | 48.3068 | 48.8488 | 50.1396 | 51.0324 | 51.5022 | 52.3735 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 60% | 98.7009 | 38.4438 | 39.7734 | 44.0082 | 47.0207 | 48.827 | 50.2731 | 51.4469 | 52.5759 | 53.5534 | 54.0437 | 54.7664 | 55.5931 | 56.4369 | 57.4984 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641
55% | 655.7369 | 31.3277 | 32.2799 | 36.151 | 38.944 | 40.4131 | 41.7291 | 42.5648 | 43.5189 | 44.2812 | 44.778 | 45.9613 | 46.7797 | 47.2104 | 48.009 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 55% | 153.5347 | 35.2401 | 36.4589 | 40.3408 | 43.1023 | 44.7581 | 46.0836 | 47.1596 | 48.1946 | 49.0906 | 49.5401 | 50.2025 | 50.9604 | 51.7339 | 52.7068 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587
50% | 981.7145 | 28.4797 | 29.3453 | 32.8646 | 35.4036 | 36.7392 | 37.9355 | 38.6953 | 39.5626 | 40.2557 | 40.7073 | 41.783 | 42.527 | 42.9185 | 43.6446 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 50% | 258.2862 | 32.0365 | 33.1445 | 36.6735 | 39.1839 | 40.6891 | 41.8942 | 42.8724 | 43.8133 | 44.6278 | 45.0364 | 45.6386 | 46.3276 | 47.0308 | 47.9153 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534
45% | 1622.7029 | 25.6317 | 26.4108 | 29.5781 | 31.8633 | 33.0653 | 34.142 | 34.8258 | 35.6064 | 36.2301 | 36.6366 | 37.6047 | 38.2743 | 38.6267 | 39.2801 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 45% | 488.9664 | 28.8328 | 29.83 | 33.0061 | 35.2655 | 36.6202 | 37.7048 | 38.5852 | 39.4319 | 40.165 | 40.5328 | 41.0748 | 41.6948 | 42.3277 | 43.1238 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481
40% | 2442.9413 | 22.7838 | 23.4763 | 26.2916 | 28.3229 | 29.3914 | 30.3484 | 30.9562 | 31.6501 | 32.2045 | 32.5659 | 33.4264 | 34.0216 | 34.3348 | 34.9157 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 40% | 928.0152 | 25.6292 | 26.5156 | 29.3388 | 31.3471 | 32.5513 | 33.5154 | 34.2979 | 35.0506 | 35.7022 | 36.0292 | 36.5109 | 37.0621 | 37.6246 | 38.3322 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427
35% | 3006.7842 | 19.9358 | 20.5417 | 23.0052 | 24.7825 | 25.7175 | 26.5549 | 27.0867 | 27.6938 | 28.179 | 28.4951 | 29.2481 | 29.7689 | 30.043 | 30.5512 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 35% | 1530.4309 | 22.4255 | 23.2011 | 25.6714 | 27.4287 | 28.4824 | 29.326 | 30.0107 | 30.6693 | 31.2395 | 31.5255 | 31.9471 | 32.4293 | 32.9215 | 33.5407 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374
30% | 3276.4154 | 17.0878 | 17.6072 | 19.7187 | 21.2422 | 22.0435 | 22.7613 | 23.2172 | 23.7376 | 24.1534 | 24.4244 | 25.0698 | 25.5162 | 25.7511 | 26.1867 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 30% | 2592.3162 | 19.2219 | 19.8867 | 22.0041 | 23.5103 | 24.4135 | 25.1365 | 25.7234 | 26.288 | 26.7767 | 27.0219 | 27.3832 | 27.7966 | 28.2185 | 28.7492 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832
25% | 3466.632 | 14.2399 | 14.6727 | 16.4323 | 17.7018 | 18.3696 | 18.9678 | 19.3477 | 19.7813 | 20.1278 | 20.3537 | 20.8915 | 21.2635 | 21.4593 | 21.8223 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 25% | 3659.4958 | 16.0182 | 16.5722 | 18.3367 | 19.592 | 20.3446 | 20.9471 | 21.4362 | 21.9066 | 22.3139 | 22.5182 | 22.8193 | 23.1638 | 23.5154 | 23.9577 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267
20% | 3713.9514 | 11.3919 | 11.7381 | 13.1458 | 14.1614 | 14.6957 | 15.1742 | 15.4781 | 15.825 | 16.1023 | 16.2829 | 16.7132 | 17.0108 | 17.1674 | 17.4578 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 20% | 4005.5161 | 12.8146 | 13.2578 | 14.6694 | 15.6736 | 16.2757 | 16.7577 | 17.149 | 17.5253 | 17.8511 | 18.0146 | 18.2555 | 18.531 | 18.8123 | 19.1661 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214
15% | 4043.3325 | 8.5439 | 8.8036 | 9.8594 | 10.6211 | 11.0218 | 11.3807 | 11.6086 | 11.8688 | 12.0767 | 12.2122 | 12.5349 | 12.7581 | 12.8756 | 13.0934 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 15% | 4281.1979 | 9.6109 | 9.9433 | 11.002 | 11.7552 | 12.2067 | 12.5683 | 12.8617 | 13.144 | 13.3883 | 13.5109 | 13.6916 | 13.8983 | 14.1092 | 14.3746 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416
10% | 4350.7801 | 5.6959 | 5.8691 | 6.5729 | 7.0807 | 7.3478 | 7.5871 | 7.7391 | 7.9125 | 8.0511 | 8.1415 | 8.3566 | 8.5054 | 8.5837 | 8.7289 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 10% | 4391.6218 | 6.4073 | 6.6289 | 7.3347 | 7.8368 | 8.1378 | 8.3788 | 8.5745 | 8.7627 | 8.9256 | 9.0073 | 9.1277 | 9.2655 | 9.4062 | 9.5831 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107
5% | 4391.6218 | 2.848 | 2.9345 | 3.2865 | 3.5404 | 3.6739 | 3.7936 | 3.8695 | 3.9563 | 4.0256 | 4.0707 | 4.1783 | 4.2527 | 4.2919 | 4.3645 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 5% | 4391.6218 | 3.2036 | 3.3144 | 3.6673 | 3.9184 | 4.0689 | 4.1894 | 4.2872 | 4.3813 | 4.4628 | 4.5036 | 4.5639 | 4.6328 | 4.7031 | 4.7915 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053
9.992e-14% | 4391.6218 | 5.6914e-14 | 5.8644e-14 | 6.5677e-14 | 7.0751e-14 | 7.342e-14 | 7.581e-14 | 7.7329e-14 | 7.9062e-14 | 8.0447e-14 | 8.135e-14 | 8.3499e-14 | 8.4986e-14 | 8.5768e-14 | 8.7219e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 9.992e-14% | 4391.6218 | 6.4022e-14 | 6.6236e-14 | 7.3288e-14 | 7.8305e-14 | 8.1313e-14 | 8.3721e-14 | 8.5676e-14 | 8.7557e-14 | 8.9184e-14 | 9.0001e-14 | 9.1204e-14 | 9.2581e-14 | 9.3986e-14 | 9.5754e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 54.8805 | 57.2482 | 59.9773 | 62.0194 | 64.2707 | 65.4506 | 66.4726 | 69.0025 | 67.4768 | 71.6024 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 76.9839 | 100% | 0 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 58.4009 | 61.0673 | 63.6029 | 65.7632 | 68.0134 | 68.9997 | 70.3459 | 72.8415 | 72.0255 | 75.2851 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653 | 77.1653
99% | 0.8916 | 49.9025 | 52.2901 | 59.4299 | 65.4429 | 54.3317 | 56.6757 | 59.3776 | 61.3992 | 63.6279 | 64.7961 | 65.8079 | 68.3125 | 66.802 | 70.8863 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 76.214 | 99% | 0.8916 | 53.1132 | 55.592 | 62.6764 | 68.9168 | 57.8169 | 60.4566 | 62.9669 | 65.1056 | 67.3333 | 68.3097 | 69.6424 | 72.1131 | 71.3052 | 74.5322 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936 | 76.3936
98% | 3.5664 | 49.3984 | 51.7619 | 58.8296 | 64.7818 | 53.7829 | 56.1032 | 58.7778 | 60.779 | 62.9852 | 64.1416 | 65.1432 | 67.6224 | 66.1272 | 70.1703 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 75.4442 | 98% | 3.5664 | 52.5767 | 55.0305 | 62.0433 | 68.2206 | 57.2329 | 59.8459 | 62.3309 | 64.448 | 66.6532 | 67.6197 | 68.9389 | 71.3846 | 70.585 | 73.7794 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622 | 75.622
97% | 4.7552 | 48.8943 | 51.2337 | 58.2293 | 64.1208 | 53.2341 | 55.5307 | 58.178 | 60.1588 | 62.3425 | 63.4871 | 64.4784 | 66.9324 | 65.4524 | 69.4543 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 74.6744 | 97% | 4.7552 | 52.0402 | 54.469 | 61.4102 | 67.5245 | 56.6489 | 59.2353 | 61.6948 | 63.7904 | 65.973 | 66.9297 | 68.2355 | 70.6562 | 69.8647 | 73.0265 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503 | 74.8503
95% | 7.7272 | 47.8862 | 50.1774 | 57.0287 | 62.7987 | 52.1365 | 54.3858 | 56.9785 | 58.9184 | 61.0571 | 62.1781 | 63.149 | 65.5524 | 64.1029 | 68.0222 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 73.1347 | 95% | 7.7272 | 50.9672 | 53.3459 | 60.144 | 66.1322 | 55.4809 | 58.0139 | 60.4228 | 62.4751 | 64.6128 | 65.5497 | 66.8286 | 69.1994 | 68.4242 | 71.5208 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307 | 73.307
90% | 39.2302 | 45.3659 | 47.5365 | 54.0272 | 59.4935 | 49.3925 | 51.5234 | 53.9796 | 55.8174 | 57.8436 | 58.9056 | 59.8253 | 62.1022 | 60.7291 | 64.4421 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 69.2855 | 90% | 39.2302 | 48.2848 | 50.5382 | 56.9785 | 62.6516 | 52.5608 | 54.9606 | 57.2426 | 59.1869 | 61.2121 | 62.0997 | 63.3113 | 65.5573 | 64.8229 | 67.7566 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487 | 69.4487
85% | 117.6906 | 42.8456 | 44.8955 | 51.0257 | 56.1883 | 46.6485 | 48.661 | 50.9807 | 52.7165 | 54.6301 | 55.633 | 56.5017 | 58.6521 | 57.3552 | 60.862 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 65.4363 | 85% | 117.6906 | 45.6023 | 47.7305 | 53.813 | 59.171 | 49.6408 | 51.9072 | 54.0625 | 55.8988 | 57.8114 | 58.6498 | 59.794 | 61.9153 | 61.2217 | 63.9923 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905 | 65.5905
80% | 268.3703 | 40.3252 | 42.2546 | 48.0242 | 52.8831 | 43.9044 | 45.7985 | 47.9819 | 49.6155 | 51.4165 | 52.3605 | 53.1781 | 55.202 | 53.9814 | 57.2819 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 61.5871 | 80% | 268.3703 | 42.9198 | 44.9228 | 50.6476 | 55.6903 | 46.7207 | 48.8538 | 50.8824 | 52.6106 | 54.4108 | 55.1998 | 56.2767 | 58.2732 | 57.6204 | 60.2281 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322 | 61.7322
75% | 455.9026 | 37.8049 | 39.6137 | 45.0227 | 49.5779 | 41.1604 | 42.9361 | 44.983 | 46.5145 | 48.203 | 49.088 | 49.8545 | 51.7519 | 50.6076 | 53.7018 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 57.7379 | 75% | 455.9026 | 40.2373 | 42.1152 | 47.4821 | 52.2097 | 43.8007 | 45.8005 | 47.7022 | 49.3224 | 51.0101 | 51.7498 | 52.7594 | 54.6311 | 54.0191 | 56.4638 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874 | 57.874
70% | 690.9866 | 35.2846 | 36.9728 | 42.0212 | 46.2727 | 38.4164 | 40.0737 | 41.9841 | 43.4136 | 44.9895 | 45.8154 | 46.5308 | 48.3017 | 47.2337 | 50.1217 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 53.8887 | 70% | 690.9866 | 37.5548 | 39.3075 | 44.3166 | 48.729 | 40.8807 | 42.7471 | 44.5221 | 46.0343 | 47.6094 | 48.2998 | 49.2421 | 50.989 | 50.4178 | 52.6995 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157 | 54.0157
65% | 967.6784 | 32.7642 | 34.3319 | 39.0196 | 42.9675 | 35.6723 | 37.2113 | 38.9853 | 40.3126 | 41.7759 | 42.5429 | 43.2072 | 44.8516 | 43.8599 | 46.5415 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 50.0395 | 65% | 967.6784 | 34.8723 | 36.4998 | 41.1511 | 45.2484 | 37.9606 | 39.6937 | 41.3419 | 42.7461 | 44.2087 | 44.8498 | 45.7248 | 47.347 | 46.8166 | 48.9353 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574 | 50.1574
60% | 1292.8136 | 30.2439 | 31.691 | 36.0181 | 39.6623 | 32.9283 | 34.3489 | 35.9864 | 37.2116 | 38.5624 | 39.2704 | 39.8836 | 41.4015 | 40.4861 | 42.9614 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 46.1903 | 60% | 1292.8136 | 32.1898 | 33.6921 | 37.9857 | 41.7677 | 35.0406 | 36.6404 | 38.1618 | 39.4579 | 40.8081 | 41.3998 | 42.2075 | 43.7049 | 43.2153 | 45.171 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992 | 46.2992
55% | 1647.0743 | 27.7236 | 29.0501 | 33.0166 | 36.3571 | 30.1843 | 31.4865 | 32.9875 | 34.1107 | 35.3489 | 35.9978 | 36.5599 | 37.9514 | 37.1122 | 39.3813 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 42.3411 | 55% | 1647.0743 | 29.5074 | 30.8845 | 34.8202 | 38.2871 | 32.1205 | 33.587 | 34.9816 | 36.1698 | 37.4074 | 37.9498 | 38.6902 | 40.0628 | 39.614 | 41.4068 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409 | 42.4409
50% | 2104.1657 | 25.2033 | 26.4091 | 30.0151 | 33.0519 | 27.4403 | 28.6241 | 29.9887 | 31.0097 | 32.1353 | 32.7253 | 33.2363 | 34.5012 | 33.7384 | 35.8012 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 38.4919 | 50% | 2104.1657 | 26.8249 | 28.0768 | 31.6547 | 34.8064 | 29.2005 | 30.5336 | 31.8015 | 32.8816 | 34.0067 | 34.4999 | 35.1729 | 36.4207 | 36.0127 | 37.6425 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826 | 38.5826
45% | 2736.0097 | 22.6829 | 23.7682 | 27.0136 | 29.7468 | 24.6962 | 25.7617 | 26.9898 | 27.9087 | 28.9218 | 29.4528 | 29.9127 | 31.0511 | 30.3645 | 32.2211 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 34.6427 | 45% | 2736.0097 | 24.1424 | 25.2691 | 28.4893 | 31.3258 | 26.2804 | 27.4803 | 28.6213 | 29.5935 | 30.6061 | 31.0499 | 31.6556 | 32.7787 | 32.4115 | 33.8783 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244 | 34.7244
40% | 3483.7613 | 20.1626 | 21.1273 | 24.0121 | 26.4416 | 21.9522 | 22.8993 | 23.9909 | 24.8078 | 25.7083 | 26.1802 | 26.589 | 27.601 | 26.9907 | 28.6409 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 30.7936 | 40% | 3483.7613 | 21.4599 | 22.4614 | 25.3238 | 27.8452 | 23.3604 | 24.4269 | 25.4412 | 26.3053 | 27.2054 | 27.5999 | 28.1383 | 29.1366 | 28.8102 | 30.114 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661 | 30.8661
35% | 3830.2948 | 17.6423 | 18.4864 | 21.0106 | 23.1364 | 19.2082 | 20.0369 | 20.9921 | 21.7068 | 22.4947 | 22.9077 | 23.2654 | 24.1509 | 23.6169 | 25.0608 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 26.9444 | 35% | 3830.2948 | 18.7774 | 19.6537 | 22.1583 | 24.3645 | 20.4403 | 21.3735 | 22.261 | 23.0171 | 23.8047 | 24.1499 | 24.621 | 25.4945 | 25.2089 | 26.3498 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078 | 27.0078
30% | 3953.6322 | 15.122 | 15.8455 | 18.0091 | 19.8312 | 16.4642 | 17.1745 | 17.9932 | 18.6058 | 19.2812 | 19.6352 | 19.9418 | 20.7007 | 20.243 | 21.4807 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 23.0952 | 30% | 3953.6322 | 16.0949 | 16.8461 | 18.9928 | 20.8839 | 17.5203 | 18.3202 | 19.0809 | 19.729 | 20.404 | 20.6999 | 21.1038 | 21.8524 | 21.6076 | 22.5855 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496 | 23.1496
25% | 4060.9208 | 12.6016 | 13.2046 | 15.0076 | 16.526 | 13.7201 | 14.312 | 14.9943 | 15.5048 | 16.0677 | 16.3627 | 16.6182 | 17.2506 | 16.8692 | 17.9006 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 19.246 | 25% | 4060.9208 | 13.4124 | 14.0384 | 15.8274 | 17.4032 | 14.6002 | 15.2668 | 15.9007 | 16.4408 | 17.0034 | 17.2499 | 17.5865 | 18.2104 | 18.0064 | 18.8213 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913 | 19.2913
20% | 4165.2375 | 10.0813 | 10.5637 | 12.006 | 13.2208 | 10.9761 | 11.4496 | 11.9955 | 12.4039 | 12.8541 | 13.0901 | 13.2945 | 13.8005 | 13.4954 | 14.3205 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 15.3968 | 20% | 4165.2375 | 10.7299 | 11.2307 | 12.6619 | 13.9226 | 11.6802 | 12.2135 | 12.7206 | 13.1526 | 13.6027 | 13.7999 | 14.0692 | 14.5683 | 14.4051 | 15.057 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331 | 15.4331
15% | 4270.4458 | 7.561 | 7.9227 | 9.0045 | 9.9156 | 8.2321 | 8.5872 | 8.9966 | 9.3029 | 9.6406 | 9.8176 | 9.9709 | 10.3504 | 10.1215 | 10.7404 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 11.5476 | 15% | 4270.4458 | 8.0475 | 8.423 | 9.4964 | 10.4419 | 8.7601 | 9.1601 | 9.5404 | 9.8645 | 10.202 | 10.35 | 10.5519 | 10.9262 | 10.8038 | 11.2928 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748 | 11.5748
10% | 4373.8709 | 5.0407 | 5.2818 | 6.003 | 6.6104 | 5.4881 | 5.7248 | 5.9977 | 6.2019 | 6.4271 | 6.5451 | 6.6473 | 6.9002 | 6.7477 | 7.1602 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 7.6984 | 10% | 4373.8709 | 5.365 | 5.6154 | 6.3309 | 6.9613 | 5.8401 | 6.1067 | 6.3603 | 6.5763 | 6.8013 | 6.9 | 7.0346 | 7.2841 | 7.2025 | 7.5285 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165 | 7.7165
5% | 4391.7028 | 2.5203 | 2.6409 | 3.0015 | 3.3052 | 2.744 | 2.8624 | 2.9989 | 3.101 | 3.2135 | 3.2725 | 3.3236 | 3.4501 | 3.3738 | 3.5801 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 3.8492 | 5% | 4391.7028 | 2.6825 | 2.8077 | 3.1655 | 3.4806 | 2.92 | 3.0534 | 3.1801 | 3.2882 | 3.4007 | 3.45 | 3.5173 | 3.6421 | 3.6013 | 3.7643 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583 | 3.8583
9.992e-14% | 4391.7028 | 5.0366e-14 | 5.2776e-14 | 5.9982e-14 | 6.6051e-14 | 5.4837e-14 | 5.7202e-14 | 5.9929e-14 | 6.197e-14 | 6.4219e-14 | 6.5398e-14 | 6.6419e-14 | 6.8947e-14 | 6.7423e-14 | 7.1545e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 7.6922e-14 | 9.992e-14% | 4391.7028 | 5.3607e-14 | 5.6109e-14 | 6.3259e-14 | 6.9557e-14 | 5.8354e-14 | 6.1018e-14 | 6.3552e-14 | 6.5711e-14 | 6.7959e-14 | 6.8945e-14 | 7.029e-14 | 7.2783e-14 | 7.1968e-14 | 7.5225e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14 | 7.7104e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 58.9784 | 61.3711 | 62.8906 | 64.6252 | 66.0113 | 66.9146 | 69.066 | 70.554 | 71.337 | 72.7891 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 72.3665 | 100% | 0 | 64.073 | 66.289 | 73.347 | 78.3678 | 66.8783 | 69.2884 | 71.2448 | 73.1265 | 74.7556 | 75.5729 | 76.7773 | 78.1552 | 79.5616 | 81.3306 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068 | 81.6068
99% | 0 | 56.3898 | 58.1038 | 65.0718 | 70.0992 | 58.3887 | 60.7574 | 62.2617 | 63.979 | 65.3512 | 66.2455 | 68.3754 | 69.8485 | 70.6237 | 72.0612 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 71.6428 | 99% | 0.75633 | 63.4323 | 65.6261 | 72.6135 | 77.5841 | 66.2095 | 68.5956 | 70.5324 | 72.3953 | 74.008 | 74.8171 | 76.0095 | 77.3736 | 78.766 | 80.5173 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907 | 80.7907
98% | 0.37816 | 55.8202 | 57.5169 | 64.4145 | 69.3911 | 57.7989 | 60.1437 | 61.6328 | 63.3327 | 64.6911 | 65.5763 | 67.6847 | 69.1429 | 69.9103 | 71.3333 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 98% | 1.1345 | 62.7915 | 64.9632 | 71.88 | 76.8005 | 65.5407 | 67.9027 | 69.8199 | 71.664 | 73.2605 | 74.0614 | 75.2417 | 76.5921 | 77.9703 | 79.704 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747 | 79.9747
97% | 0.75633 | 55.2506 | 56.93 | 63.7572 | 68.683 | 57.2091 | 59.53 | 61.0039 | 62.6865 | 64.031 | 64.9072 | 66.994 | 68.4374 | 69.1969 | 70.6055 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 70.1955 | 97% | 1.8908 | 62.1508 | 64.3003 | 71.1466 | 76.0168 | 64.8719 | 67.2098 | 69.1075 | 70.9327 | 72.5129 | 73.3057 | 74.474 | 75.8105 | 77.1747 | 78.8907 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586 | 79.1586
95% | 1.8908 | 54.1115 | 55.7561 | 62.4427 | 67.2669 | 56.0295 | 58.3025 | 59.7461 | 61.394 | 62.7107 | 63.5689 | 65.6127 | 67.0263 | 67.7702 | 69.1497 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 68.7482 | 95% | 3.4035 | 60.8693 | 62.9745 | 69.6796 | 74.4494 | 63.5344 | 65.824 | 67.6826 | 69.4702 | 71.0178 | 71.7942 | 72.9384 | 74.2474 | 75.5835 | 77.2641 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265 | 77.5265
90% | 4.538 | 51.2635 | 52.8216 | 59.1562 | 63.7265 | 53.0806 | 55.234 | 56.6015 | 58.1627 | 59.4102 | 60.2232 | 62.1594 | 63.4986 | 64.2033 | 65.5102 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 65.1299 | 90% | 9.0759 | 57.6657 | 59.6601 | 66.0123 | 70.531 | 60.1905 | 62.3596 | 64.1203 | 65.8139 | 67.28 | 68.0156 | 69.0996 | 70.3397 | 71.6054 | 73.1976 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461 | 73.4461
85% | 9.0759 | 48.4155 | 49.8871 | 55.8697 | 60.1862 | 50.1317 | 52.1654 | 53.457 | 54.9315 | 56.1096 | 56.8774 | 58.7061 | 59.9709 | 60.6365 | 61.8708 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 61.5115 | 85% | 16.2611 | 54.462 | 56.3456 | 62.3449 | 66.6126 | 56.8466 | 58.8952 | 60.5581 | 62.1576 | 63.5423 | 64.2369 | 65.2607 | 66.4319 | 67.6273 | 69.131 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658 | 69.3658
80% | 27.606 | 45.5675 | 46.9525 | 52.5833 | 56.6458 | 47.1827 | 49.0969 | 50.3125 | 51.7002 | 52.809 | 53.5317 | 55.2528 | 56.4432 | 57.0696 | 58.2313 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 57.8932 | 80% | 24.9588 | 51.2584 | 53.0312 | 58.6776 | 62.6943 | 53.5026 | 55.4308 | 56.9959 | 58.5012 | 59.8045 | 60.4583 | 61.4218 | 62.5241 | 63.6493 | 65.0645 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854 | 65.2854
75% | 57.481 | 42.7196 | 44.018 | 49.2968 | 53.1054 | 44.2338 | 46.0283 | 47.168 | 48.4689 | 49.5085 | 50.186 | 51.7995 | 52.9155 | 53.5028 | 54.5918 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 54.2749 | 75% | 32.9003 | 48.0547 | 49.7167 | 55.0102 | 58.7759 | 50.1587 | 51.9663 | 53.4336 | 54.8449 | 56.0667 | 56.6797 | 57.583 | 58.6164 | 59.6712 | 60.998 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051 | 61.2051
70% | 106.2642 | 39.8716 | 41.0835 | 46.0104 | 49.5651 | 41.2849 | 42.9598 | 44.0234 | 45.2377 | 46.2079 | 46.8402 | 48.3462 | 49.3878 | 49.9359 | 50.9524 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 50.6566 | 70% | 41.9762 | 44.8511 | 46.4023 | 51.3429 | 54.8575 | 46.8148 | 48.5019 | 49.8714 | 51.1886 | 52.3289 | 52.901 | 53.7441 | 54.7086 | 55.6931 | 56.9314 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248 | 57.1248
65% | 201.9397 | 37.0236 | 38.1489 | 42.7239 | 46.0247 | 38.336 | 39.8912 | 40.8789 | 42.0064 | 42.9073 | 43.4945 | 44.8929 | 45.8601 | 46.3691 | 47.3129 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 47.0382 | 65% | 67.6914 | 41.6474 | 43.0878 | 47.6755 | 50.9391 | 43.4709 | 45.0375 | 46.3091 | 47.5323 | 48.5911 | 49.1224 | 49.9052 | 50.8009 | 51.715 | 52.8649 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444 | 53.0444
60% | 402.745 | 34.1757 | 35.2144 | 39.4375 | 42.4843 | 35.3871 | 36.8227 | 37.7344 | 38.7751 | 39.6068 | 40.1488 | 41.4396 | 42.3324 | 42.8022 | 43.6735 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 43.4199 | 60% | 98.7009 | 38.4438 | 39.7734 | 44.0082 | 47.0207 | 40.127 | 41.5731 | 42.7469 | 43.8759 | 44.8534 | 45.3437 | 46.0664 | 46.8931 | 47.7369 | 48.7984 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641 | 48.9641
55% | 655.7369 | 31.3277 | 32.2799 | 36.151 | 38.944 | 32.4381 | 33.7541 | 34.5898 | 35.5439 | 36.3062 | 36.803 | 37.9863 | 38.8047 | 39.2354 | 40.034 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 39.8016 | 55% | 153.5347 | 35.2401 | 36.4589 | 40.3408 | 43.1023 | 36.7831 | 38.1086 | 39.1846 | 40.2196 | 41.1156 | 41.5651 | 42.2275 | 42.9854 | 43.7589 | 44.7318 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837 | 44.8837
50% | 981.7145 | 28.4797 | 29.3453 | 32.8646 | 35.4036 | 29.4892 | 30.6855 | 31.4453 | 32.3126 | 33.0057 | 33.4573 | 34.533 | 35.277 | 35.6685 | 36.3946 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 36.1833 | 50% | 258.2862 | 32.0365 | 33.1445 | 36.6735 | 39.1839 | 33.4391 | 34.6442 | 35.6224 | 36.5633 | 37.3778 | 37.7864 | 38.3886 | 39.0776 | 39.7808 | 40.6653 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034 | 40.8034
45% | 1622.7029 | 25.6317 | 26.4108 | 29.5781 | 31.8633 | 26.5403 | 27.617 | 28.3008 | 29.0814 | 29.7051 | 30.1116 | 31.0797 | 31.7493 | 32.1017 | 32.7551 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 32.5649 | 45% | 488.9664 | 28.8328 | 29.83 | 33.0061 | 35.2655 | 30.0952 | 31.1798 | 32.0602 | 32.9069 | 33.64 | 34.0078 | 34.5498 | 35.1698 | 35.8027 | 36.5988 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231 | 36.7231
40% | 2442.9413 | 22.7838 | 23.4763 | 26.2916 | 28.3229 | 23.5914 | 24.5484 | 25.1562 | 25.8501 | 26.4045 | 26.7659 | 27.6264 | 28.2216 | 28.5348 | 29.1157 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 28.9466 | 40% | 928.0152 | 25.6292 | 26.5156 | 29.3388 | 31.3471 | 26.7513 | 27.7154 | 28.4979 | 29.2506 | 29.9022 | 30.2292 | 30.7109 | 31.2621 | 31.8246 | 32.5322 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427 | 32.6427
35% | 3006.7842 | 19.9358 | 20.5417 | 23.0052 | 24.7825 | 20.6425 | 21.4799 | 22.0117 | 22.6188 | 23.104 | 23.4201 | 24.1731 | 24.6939 | 24.968 | 25.4762 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 25.3283 | 35% | 1530.4309 | 22.4255 | 23.2011 | 25.6714 | 27.4287 | 23.4074 | 24.251 | 24.9357 | 25.5943 | 26.1645 | 26.4505 | 26.8721 | 27.3543 | 27.8465 | 28.4657 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624 | 28.5624
30% | 3276.4154 | 17.0878 | 17.6072 | 19.7187 | 21.2422 | 17.6935 | 18.4113 | 18.8672 | 19.3876 | 19.8034 | 20.0744 | 20.7198 | 21.1662 | 21.4011 | 21.8367 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 21.71 | 30% | 2592.3162 | 19.2219 | 19.8867 | 22.0041 | 23.5103 | 20.0635 | 20.7865 | 21.3734 | 21.938 | 22.4267 | 22.6719 | 23.0332 | 23.4466 | 23.8685 | 24.3992 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482 | 24.482
25% | 3466.632 | 14.2399 | 14.6727 | 16.4323 | 17.7018 | 14.7446 | 15.3428 | 15.7227 | 16.1563 | 16.5028 | 16.7287 | 17.2665 | 17.6385 | 17.8343 | 18.1973 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 18.0916 | 25% | 3659.4958 | 16.0182 | 16.5722 | 18.3367 | 19.592 | 16.7196 | 17.3221 | 17.8112 | 18.2816 | 18.6889 | 18.8932 | 19.1943 | 19.5388 | 19.8904 | 20.3327 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017 | 20.4017
20% | 3713.9514 | 11.3919 | 11.7381 | 13.1458 | 14.1614 | 11.7957 | 12.2742 | 12.5781 | 12.925 | 13.2023 | 13.3829 | 13.8132 | 14.1108 | 14.2674 | 14.5578 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 14.4733 | 20% | 4005.5161 | 12.8146 | 13.2578 | 14.6694 | 15.6736 | 13.3757 | 13.8577 | 14.249 | 14.6253 | 14.9511 | 15.1146 | 15.3555 | 15.631 | 15.9123 | 16.2661 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214 | 16.3214
15% | 4043.3325 | 8.5439 | 8.8036 | 9.8594 | 10.6211 | 8.8468 | 9.2057 | 9.4336 | 9.6938 | 9.9017 | 10.0372 | 10.3599 | 10.5831 | 10.7006 | 10.9184 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 10.855 | 15% | 4281.1979 | 9.6109 | 9.9433 | 11.002 | 11.7552 | 10.0317 | 10.3933 | 10.6867 | 10.969 | 11.2133 | 11.3359 | 11.5166 | 11.7233 | 11.9342 | 12.1996 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241 | 12.241
10% | 4350.7801 | 5.6959 | 5.8691 | 6.5729 | 7.0807 | 5.8978 | 6.1371 | 6.2891 | 6.4625 | 6.6011 | 6.6915 | 6.9066 | 7.0554 | 7.1337 | 7.2789 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 7.2367 | 10% | 4391.6218 | 6.4073 | 6.6289 | 7.3347 | 7.8368 | 6.6878 | 6.9288 | 7.1245 | 7.3127 | 7.4756 | 7.5573 | 7.6777 | 7.8155 | 7.9562 | 8.1331 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607 | 8.1607
5% | 4391.6218 | 2.848 | 2.9345 | 3.2865 | 3.5404 | 2.9489 | 3.0686 | 3.1445 | 3.2313 | 3.3006 | 3.3457 | 3.4533 | 3.5277 | 3.5669 | 3.6395 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 3.6183 | 5% | 4391.6218 | 3.2036 | 3.3144 | 3.6673 | 3.9184 | 3.3439 | 3.4644 | 3.5622 | 3.6563 | 3.7378 | 3.7786 | 3.8389 | 3.9078 | 3.9781 | 4.0665 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803 | 4.0803
9.992e-14% | 4391.6218 | 5.6914e-14 | 5.8644e-14 | 6.5677e-14 | 7.0751e-14 | 5.8931e-14 | 6.1322e-14 | 6.284e-14 | 6.4574e-14 | 6.5959e-14 | 6.6861e-14 | 6.9011e-14 | 7.0498e-14 | 7.128e-14 | 7.2731e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 7.2309e-14 | 9.992e-14% | 4391.6218 | 6.4022e-14 | 6.6236e-14 | 7.3288e-14 | 7.8305e-14 | 6.6825e-14 | 6.9233e-14 | 7.1188e-14 | 7.3068e-14 | 7.4696e-14 | 7.5512e-14 | 7.6716e-14 | 7.8093e-14 | 7.9498e-14 | 8.1266e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14 | 8.1542e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 50.4065 | 52.8183 | 60.0302 | 58.8539 | 47.6305 | 49.9982 | 52.7273 | 54.7694 | 57.0207 | 58.2006 | 59.2226 | 61.7525 | 60.2268 | 64.3524 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 100% | 0 | 53.6497 | 56.1536 | 63.3095 | 62.3629 | 51.1509 | 53.8173 | 56.3529 | 58.5132 | 60.7634 | 61.7497 | 63.0959 | 65.5915 | 64.7755 | 68.0351 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153
99% | 0.8916 | 49.9025 | 52.2901 | 59.4299 | 58.2654 | 47.1542 | 49.4982 | 52.2001 | 54.2217 | 56.4504 | 57.6186 | 58.6304 | 61.135 | 59.6245 | 63.7088 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 99% | 0.8916 | 53.1132 | 55.592 | 62.6764 | 61.7393 | 50.6394 | 53.2791 | 55.7894 | 57.9281 | 60.1558 | 61.1322 | 62.4649 | 64.9356 | 64.1277 | 67.3547 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161
98% | 3.5664 | 49.3984 | 51.7619 | 58.8296 | 57.6768 | 46.6779 | 48.9982 | 51.6728 | 53.674 | 55.8802 | 57.0366 | 58.0382 | 60.5174 | 59.0222 | 63.0653 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 98% | 3.5664 | 52.5767 | 55.0305 | 62.0433 | 61.1156 | 50.1279 | 52.7409 | 55.2259 | 57.343 | 59.5482 | 60.5147 | 61.8339 | 64.2796 | 63.48 | 66.6744 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517
97% | 4.7552 | 48.8943 | 51.2337 | 58.2293 | 57.0883 | 46.2016 | 48.4982 | 51.1455 | 53.1263 | 55.31 | 56.4546 | 57.4459 | 59.8999 | 58.4199 | 62.4218 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 97% | 4.7552 | 52.0402 | 54.469 | 61.4102 | 60.492 | 49.6164 | 52.2028 | 54.6623 | 56.7579 | 58.9405 | 59.8972 | 61.203 | 63.6237 | 62.8322 | 65.994 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178
95% | 7.7272 | 47.8862 | 50.1774 | 57.0287 | 55.9112 | 45.249 | 47.4983 | 50.091 | 52.0309 | 54.1696 | 55.2906 | 56.2615 | 58.6649 | 57.2154 | 61.1347 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 95% | 7.7272 | 50.9672 | 53.3459 | 60.144 | 59.2447 | 48.5934 | 51.1264 | 53.5353 | 55.5876 | 57.7253 | 58.6622 | 59.9411 | 62.3119 | 61.5367 | 64.6333 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195
90% | 39.2302 | 45.3659 | 47.5365 | 54.0272 | 52.9685 | 42.8675 | 44.9984 | 47.4546 | 49.2924 | 51.3186 | 52.3806 | 53.3003 | 55.5772 | 54.2041 | 57.9171 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 90% | 39.2302 | 48.2848 | 50.5382 | 56.9785 | 56.1266 | 46.0358 | 48.4356 | 50.7176 | 52.6619 | 54.6871 | 55.5747 | 56.7863 | 59.0323 | 58.2979 | 61.2316 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237
85% | 117.6906 | 42.8456 | 44.8955 | 51.0257 | 50.0258 | 40.486 | 42.4985 | 44.8182 | 46.554 | 48.4676 | 49.4705 | 50.3392 | 52.4896 | 51.1927 | 54.6995 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 85% | 117.6906 | 45.6023 | 47.7305 | 53.813 | 53.0085 | 43.4783 | 45.7447 | 47.9 | 49.7363 | 51.6489 | 52.4873 | 53.6315 | 55.7528 | 55.0592 | 57.8298 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428
80% | 268.3703 | 40.3252 | 42.2546 | 48.0242 | 47.0831 | 38.1044 | 39.9985 | 42.1819 | 43.8155 | 45.6165 | 46.5605 | 47.3781 | 49.402 | 48.1814 | 51.4819 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 80% | 268.3703 | 42.9198 | 44.9228 | 50.6476 | 49.8903 | 40.9207 | 43.0538 | 45.0824 | 46.8106 | 48.6108 | 49.3998 | 50.4767 | 52.4732 | 51.8204 | 54.4281 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322
75% | 455.9026 | 37.8049 | 39.6137 | 45.0227 | 44.1404 | 35.7229 | 37.4986 | 39.5455 | 41.077 | 42.7655 | 43.6505 | 44.417 | 46.3144 | 45.1701 | 48.2643 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 75% | 455.9026 | 40.2373 | 42.1152 | 47.4821 | 46.7722 | 38.3632 | 40.363 | 42.2647 | 43.8849 | 45.5726 | 46.3123 | 47.3219 | 49.1936 | 48.5816 | 51.0263 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365
70% | 690.9866 | 35.2846 | 36.9728 | 42.0212 | 41.1977 | 33.3414 | 34.9987 | 36.9091 | 38.3386 | 39.9145 | 40.7404 | 41.4558 | 43.2267 | 42.1587 | 45.0467 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 70% | 690.9866 | 37.5548 | 39.3075 | 44.3166 | 43.654 | 35.8057 | 37.6721 | 39.4471 | 40.9593 | 42.5344 | 43.2248 | 44.1671 | 45.914 | 45.3428 | 47.6245 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407
65% | 967.6784 | 32.7642 | 34.3319 | 39.0196 | 38.255 | 30.9598 | 32.4988 | 34.2728 | 35.6001 | 37.0634 | 37.8304 | 38.4947 | 40.1391 | 39.1474 | 41.829 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 65% | 967.6784 | 34.8723 | 36.4998 | 41.1511 | 40.5359 | 33.2481 | 34.9812 | 36.6294 | 38.0336 | 39.4962 | 40.1373 | 41.0123 | 42.6345 | 42.1041 | 44.2228 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449
60% | 1292.8136 | 30.2439 | 31.691 | 36.0181 | 35.3123 | 28.5783 | 29.9989 | 31.6364 | 32.8616 | 34.2124 | 34.9204 | 35.5336 | 37.0515 | 36.1361 | 38.6114 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 60% | 1292.8136 | 32.1898 | 33.6921 | 37.9857 | 37.4177 | 30.6906 | 32.2904 | 33.8118 | 35.1079 | 36.4581 | 37.0498 | 37.8575 | 39.3549 | 38.8653 | 40.821 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492
55% | 1647.0743 | 27.7236 | 29.0501 | 33.0166 | 32.3696 | 26.1968 | 27.499 | 29 | 30.1232 | 31.3614 | 32.0103 | 32.5724 | 33.9639 | 33.1247 | 35.3938 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 55% | 1647.0743 | 29.5074 | 30.8845 | 34.8202 | 34.2996 | 28.133 | 29.5995 | 30.9941 | 32.1823 | 33.4199 | 33.9623 | 34.7027 | 36.0753 | 35.6265 | 37.4193 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534
50% | 2104.1657 | 25.2033 | 26.4091 | 30.0151 | 29.4269 | 23.8153 | 24.9991 | 26.3637 | 27.3847 | 28.5103 | 29.1003 | 29.6113 | 30.8762 | 30.1134 | 32.1762 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 50% | 2104.1657 | 26.8249 | 28.0768 | 31.6547 | 31.1814 | 25.5755 | 26.9086 | 28.1765 | 29.2566 | 30.3817 | 30.8749 | 31.5479 | 32.7957 | 32.3877 | 34.0175 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576
45% | 2736.0097 | 22.6829 | 23.7682 | 27.0136 | 26.4843 | 21.4337 | 22.4992 | 23.7273 | 24.6462 | 25.6593 | 26.1903 | 26.6502 | 27.7886 | 27.102 | 28.9586 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 45% | 2736.0097 | 24.1424 | 25.2691 | 28.4893 | 28.0633 | 23.0179 | 24.2178 | 25.3588 | 26.331 | 27.3436 | 27.7874 | 28.3931 | 29.5162 | 29.149 | 30.6158 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619
40% | 3483.7613 | 20.1626 | 21.1273 | 24.0121 | 23.5416 | 19.0522 | 19.9993 | 21.0909 | 21.9078 | 22.8083 | 23.2802 | 23.689 | 24.701 | 24.0907 | 25.7409 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 40% | 3483.7613 | 21.4599 | 22.4614 | 25.3238 | 24.9452 | 20.4604 | 21.5269 | 22.5412 | 23.4053 | 24.3054 | 24.6999 | 25.2383 | 26.2366 | 25.9102 | 27.214 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661
35% | 3830.2948 | 17.6423 | 18.4864 | 21.0106 | 20.5989 | 16.6707 | 17.4994 | 18.4546 | 19.1693 | 19.9572 | 20.3702 | 20.7279 | 21.6134 | 21.0794 | 22.5233 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 35% | 3830.2948 | 18.7774 | 19.6537 | 22.1583 | 21.827 | 17.9028 | 18.836 | 19.7235 | 20.4796 | 21.2672 | 21.6124 | 22.0835 | 22.957 | 22.6714 | 23.8123 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703
30% | 3953.6322 | 15.122 | 15.8455 | 18.0091 | 17.6562 | 14.2892 | 14.9995 | 15.8182 | 16.4308 | 17.1062 | 17.4602 | 17.7668 | 18.5257 | 18.068 | 19.3057 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 30% | 3953.6322 | 16.0949 | 16.8461 | 18.9928 | 18.7089 | 15.3453 | 16.1452 | 16.9059 | 17.554 | 18.229 | 18.5249 | 18.9288 | 19.6774 | 19.4326 | 20.4105 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746
25% | 4060.9208 | 12.6016 | 13.2046 | 15.0076 | 14.7135 | 11.9076 | 12.4995 | 13.1818 | 13.6923 | 14.2552 | 14.5502 | 14.8057 | 15.4381 | 15.0567 | 16.0881 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 25% | 4060.9208 | 13.4124 | 14.0384 | 15.8274 | 15.5907 | 12.7877 | 13.4543 | 14.0882 | 14.6283 | 15.1909 | 15.4374 | 15.774 | 16.3979 | 16.1939 | 17.0088 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788
20% | 4165.2375 | 10.0813 | 10.5637 | 12.006 | 11.7708 | 9.5261 | 9.9996 | 10.5455 | 10.9539 | 11.4041 | 11.6401 | 11.8445 | 12.3505 | 12.0454 | 12.8705 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 20% | 4165.2375 | 10.7299 | 11.2307 | 12.6619 | 12.4726 | 10.2302 | 10.7635 | 11.2706 | 11.7026 | 12.1527 | 12.3499 | 12.6192 | 13.1183 | 12.9551 | 13.607 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831
15% | 4270.4458 | 7.561 | 7.9227 | 9.0045 | 8.8281 | 7.1446 | 7.4997 | 7.9091 | 8.2154 | 8.5531 | 8.7301 | 8.8834 | 9.2629 | 9.034 | 9.6529 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 15% | 4270.4458 | 8.0475 | 8.423 | 9.4964 | 9.3544 | 7.6726 | 8.0726 | 8.4529 | 8.777 | 9.1145 | 9.2625 | 9.4644 | 9.8387 | 9.7163 | 10.2053 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873
10% | 4373.8709 | 5.0407 | 5.2818 | 6.003 | 5.8854 | 4.7631 | 4.9998 | 5.2727 | 5.4769 | 5.7021 | 5.8201 | 5.9223 | 6.1752 | 6.0227 | 6.4352 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 10% | 4373.8709 | 5.365 | 5.6154 | 6.3309 | 6.2363 | 5.1151 | 5.3817 | 5.6353 | 5.8513 | 6.0763 | 6.175 | 6.3096 | 6.5591 | 6.4775 | 6.8035 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915
5% | 4391.7028 | 2.5203 | 2.6409 | 3.0015 | 2.9427 | 2.3815 | 2.4999 | 2.6364 | 2.7385 | 2.851 | 2.91 | 2.9611 | 3.0876 | 3.0113 | 3.2176 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 5% | 4391.7028 | 2.6825 | 2.8077 | 3.1655 | 3.1181 | 2.5575 | 2.6909 | 2.8176 | 2.9257 | 3.0382 | 3.0875 | 3.1548 | 3.2796 | 3.2388 | 3.4018 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958
9.992e-14% | 4391.7028 | 5.0366e-14 | 5.2776e-14 | 5.9982e-14 | 5.8807e-14 | 4.7592e-14 | 4.9958e-14 | 5.2685e-14 | 5.4726e-14 | 5.6975e-14 | 5.8154e-14 | 5.9175e-14 | 6.1703e-14 | 6.0179e-14 | 6.4301e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 9.992e-14% | 4391.7028 | 5.3607e-14 | 5.6109e-14 | 6.3259e-14 | 6.2313e-14 | 5.111e-14 | 5.3774e-14 | 5.6308e-14 | 5.8466e-14 | 6.0715e-14 | 6.17e-14 | 6.3045e-14 | 6.5539e-14 | 6.4724e-14 | 6.7981e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.9594 | 58.6907 | 65.7291 | 63.5572 | 51.7284 | 54.1211 | 55.6406 | 57.3752 | 58.7613 | 59.6646 | 61.816 | 63.304 | 64.087 | 65.5391 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 100% | 0 | 64.073 | 66.289 | 73.347 | 71.1178 | 59.6283 | 62.0384 | 63.9948 | 65.8765 | 67.5056 | 68.3229 | 69.5273 | 70.9052 | 72.3116 | 74.0806 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568
99% | 0 | 56.3898 | 58.1038 | 65.0718 | 62.9217 | 51.2112 | 53.5799 | 55.0842 | 56.8015 | 58.1737 | 59.068 | 61.1979 | 62.671 | 63.4462 | 64.8837 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 99% | 0.75633 | 63.4323 | 65.6261 | 72.6135 | 70.4066 | 59.032 | 61.4181 | 63.3549 | 65.2178 | 66.8305 | 67.6396 | 68.832 | 70.1961 | 71.5885 | 73.3398 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132
98% | 0.37816 | 55.8202 | 57.5169 | 64.4145 | 62.2861 | 50.6939 | 53.0387 | 54.5278 | 56.2277 | 57.5861 | 58.4713 | 60.5797 | 62.0379 | 62.8053 | 64.2283 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 98% | 1.1345 | 62.7915 | 64.9632 | 71.88 | 69.6955 | 58.4357 | 60.7977 | 62.7149 | 64.559 | 66.1555 | 66.9564 | 68.1367 | 69.4871 | 70.8653 | 72.599 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697
97% | 0.75633 | 55.2506 | 56.93 | 63.7572 | 61.6505 | 50.1766 | 52.4975 | 53.9714 | 55.654 | 56.9985 | 57.8747 | 59.9615 | 61.4049 | 62.1644 | 63.573 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 97% | 1.8908 | 62.1508 | 64.3003 | 71.1466 | 68.9843 | 57.8394 | 60.1773 | 62.075 | 63.9002 | 65.4804 | 66.2732 | 67.4415 | 68.778 | 70.1422 | 71.8582 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261
95% | 1.8908 | 54.1115 | 55.7561 | 62.4427 | 60.3794 | 49.142 | 51.415 | 52.8586 | 54.5065 | 55.8232 | 56.6814 | 58.7252 | 60.1388 | 60.8827 | 62.2622 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 95% | 3.4035 | 60.8693 | 62.9745 | 69.6796 | 67.5619 | 56.6469 | 58.9365 | 60.7951 | 62.5827 | 64.1303 | 64.9067 | 66.0509 | 67.3599 | 68.696 | 70.3766 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639
90% | 4.538 | 51.2635 | 52.8216 | 59.1562 | 57.2015 | 46.5556 | 48.709 | 50.0765 | 51.6377 | 52.8852 | 53.6982 | 55.6344 | 56.9736 | 57.6783 | 58.9852 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 90% | 9.0759 | 57.6657 | 59.6601 | 66.0123 | 64.006 | 53.6655 | 55.8346 | 57.5953 | 59.2889 | 60.755 | 61.4906 | 62.5746 | 63.8147 | 65.0804 | 66.6726 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211
85% | 9.0759 | 48.4155 | 49.8871 | 55.8697 | 54.0237 | 43.9692 | 46.0029 | 47.2945 | 48.769 | 49.9471 | 50.7149 | 52.5436 | 53.8084 | 54.474 | 55.7083 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 85% | 16.2611 | 54.462 | 56.3456 | 62.3449 | 60.4501 | 50.6841 | 52.7327 | 54.3956 | 55.9951 | 57.3798 | 58.0744 | 59.0982 | 60.2694 | 61.4648 | 62.9685 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033
80% | 27.606 | 45.5675 | 46.9525 | 52.5833 | 50.8458 | 41.3827 | 43.2969 | 44.5125 | 45.9002 | 47.009 | 47.7317 | 49.4528 | 50.6432 | 51.2696 | 52.4313 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 80% | 24.9588 | 51.2584 | 53.0312 | 58.6776 | 56.8943 | 47.7026 | 49.6308 | 51.1959 | 52.7012 | 54.0045 | 54.6583 | 55.6218 | 56.7241 | 57.8493 | 59.2645 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854
75% | 57.481 | 42.7196 | 44.018 | 49.2968 | 47.6679 | 38.7963 | 40.5908 | 41.7305 | 43.0314 | 44.071 | 44.7485 | 46.362 | 47.478 | 48.0653 | 49.1543 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 75% | 32.9003 | 48.0547 | 49.7167 | 55.0102 | 53.3384 | 44.7212 | 46.5288 | 47.9961 | 49.4074 | 50.6292 | 51.2422 | 52.1455 | 53.1789 | 54.2337 | 55.5605 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676
70% | 106.2642 | 39.8716 | 41.0835 | 46.0104 | 44.4901 | 36.2099 | 37.8848 | 38.9484 | 40.1627 | 41.1329 | 41.7652 | 43.2712 | 44.3128 | 44.8609 | 45.8774 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 70% | 41.9762 | 44.8511 | 46.4023 | 51.3429 | 49.7825 | 41.7398 | 43.4269 | 44.7964 | 46.1136 | 47.2539 | 47.826 | 48.6691 | 49.6336 | 50.6181 | 51.8564 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498
65% | 201.9397 | 37.0236 | 38.1489 | 42.7239 | 41.3122 | 33.6235 | 35.1787 | 36.1664 | 37.2939 | 38.1948 | 38.782 | 40.1804 | 41.1476 | 41.6566 | 42.6004 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 65% | 67.6914 | 41.6474 | 43.0878 | 47.6755 | 46.2266 | 38.7584 | 40.325 | 41.5966 | 42.8198 | 43.8786 | 44.4099 | 45.1927 | 46.0884 | 47.0025 | 48.1524 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319
60% | 402.745 | 34.1757 | 35.2144 | 39.4375 | 38.1343 | 31.0371 | 32.4727 | 33.3844 | 34.4251 | 35.2568 | 35.7988 | 37.0896 | 37.9824 | 38.4522 | 39.3235 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 60% | 98.7009 | 38.4438 | 39.7734 | 44.0082 | 42.6707 | 35.777 | 37.2231 | 38.3969 | 39.5259 | 40.5034 | 40.9937 | 41.7164 | 42.5431 | 43.3869 | 44.4484 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141
55% | 655.7369 | 31.3277 | 32.2799 | 36.151 | 34.9565 | 28.4506 | 29.7666 | 30.6023 | 31.5564 | 32.3187 | 32.8155 | 33.9988 | 34.8172 | 35.2479 | 36.0465 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 55% | 153.5347 | 35.2401 | 36.4589 | 40.3408 | 39.1148 | 32.7956 | 34.1211 | 35.1971 | 36.2321 | 37.1281 | 37.5776 | 38.24 | 38.9979 | 39.7714 | 40.7443 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962
50% | 981.7145 | 28.4797 | 29.3453 | 32.8646 | 31.7786 | 25.8642 | 27.0605 | 27.8203 | 28.6876 | 29.3807 | 29.8323 | 30.908 | 31.652 | 32.0435 | 32.7696 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 50% | 258.2862 | 32.0365 | 33.1445 | 36.6735 | 35.5589 | 29.8141 | 31.0192 | 31.9974 | 32.9383 | 33.7528 | 34.1614 | 34.7636 | 35.4526 | 36.1558 | 37.0403 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784
45% | 1622.7029 | 25.6317 | 26.4108 | 29.5781 | 28.6008 | 23.2778 | 24.3545 | 25.0383 | 25.8189 | 26.4426 | 26.8491 | 27.8172 | 28.4868 | 28.8392 | 29.4926 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 45% | 488.9664 | 28.8328 | 29.83 | 33.0061 | 32.003 | 26.8327 | 27.9173 | 28.7977 | 29.6444 | 30.3775 | 30.7453 | 31.2873 | 31.9073 | 32.5402 | 33.3363 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606
40% | 2442.9413 | 22.7838 | 23.4763 | 26.2916 | 25.4229 | 20.6914 | 21.6484 | 22.2562 | 22.9501 | 23.5045 | 23.8659 | 24.7264 | 25.3216 | 25.6348 | 26.2157 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 40% | 928.0152 | 25.6292 | 26.5156 | 29.3388 | 28.4471 | 23.8513 | 24.8154 | 25.5979 | 26.3506 | 27.0022 | 27.3292 | 27.8109 | 28.3621 | 28.9246 | 29.6322 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427
35% | 3006.7842 | 19.9358 | 20.5417 | 23.0052 | 22.245 | 18.105 | 18.9424 | 19.4742 | 20.0813 | 20.5665 | 20.8826 | 21.6356 | 22.1564 | 22.4305 | 22.9387 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 35% | 1530.4309 | 22.4255 | 23.2011 | 25.6714 | 24.8912 | 20.8699 | 21.7135 | 22.3982 | 23.0568 | 23.627 | 23.913 | 24.3346 | 24.8168 | 25.309 | 25.9282 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249
30% | 3276.4154 | 17.0878 | 17.6072 | 19.7187 | 19.0672 | 15.5185 | 16.2363 | 16.6922 | 17.2126 | 17.6284 | 17.8994 | 18.5448 | 18.9912 | 19.2261 | 19.6617 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 30% | 2592.3162 | 19.2219 | 19.8867 | 22.0041 | 21.3353 | 17.8885 | 18.6115 | 19.1984 | 19.763 | 20.2517 | 20.4969 | 20.8582 | 21.2716 | 21.6935 | 22.2242 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307
25% | 3466.632 | 14.2399 | 14.6727 | 16.4323 | 15.8893 | 12.9321 | 13.5303 | 13.9102 | 14.3438 | 14.6903 | 14.9162 | 15.454 | 15.826 | 16.0218 | 16.3848 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 25% | 3659.4958 | 16.0182 | 16.5722 | 18.3367 | 17.7795 | 14.9071 | 15.5096 | 15.9987 | 16.4691 | 16.8764 | 17.0807 | 17.3818 | 17.7263 | 18.0779 | 18.5202 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892
20% | 3713.9514 | 11.3919 | 11.7381 | 13.1458 | 12.7114 | 10.3457 | 10.8242 | 11.1281 | 11.475 | 11.7523 | 11.9329 | 12.3632 | 12.6608 | 12.8174 | 13.1078 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 20% | 4005.5161 | 12.8146 | 13.2578 | 14.6694 | 14.2236 | 11.9257 | 12.4077 | 12.799 | 13.1753 | 13.5011 | 13.6646 | 13.9055 | 14.181 | 14.4623 | 14.8161 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714
15% | 4043.3325 | 8.5439 | 8.8036 | 9.8594 | 9.5336 | 7.7593 | 8.1182 | 8.3461 | 8.6063 | 8.8142 | 8.9497 | 9.2724 | 9.4956 | 9.6131 | 9.8309 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 15% | 4281.1979 | 9.6109 | 9.9433 | 11.002 | 10.6677 | 8.9442 | 9.3058 | 9.5992 | 9.8815 | 10.1258 | 10.2484 | 10.4291 | 10.6358 | 10.8467 | 11.1121 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535
10% | 4350.7801 | 5.6959 | 5.8691 | 6.5729 | 6.3557 | 5.1728 | 5.4121 | 5.5641 | 5.7375 | 5.8761 | 5.9665 | 6.1816 | 6.3304 | 6.4087 | 6.5539 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 10% | 4391.6218 | 6.4073 | 6.6289 | 7.3347 | 7.1118 | 5.9628 | 6.2038 | 6.3995 | 6.5877 | 6.7506 | 6.8323 | 6.9527 | 7.0905 | 7.2312 | 7.4081 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357
5% | 4391.6218 | 2.848 | 2.9345 | 3.2865 | 3.1779 | 2.5864 | 2.7061 | 2.782 | 2.8688 | 2.9381 | 2.9832 | 3.0908 | 3.1652 | 3.2044 | 3.277 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 5% | 4391.6218 | 3.2036 | 3.3144 | 3.6673 | 3.5559 | 2.9814 | 3.1019 | 3.1997 | 3.2938 | 3.3753 | 3.4161 | 3.4764 | 3.5453 | 3.6156 | 3.704 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178
9.992e-14% | 4391.6218 | 5.6914e-14 | 5.8644e-14 | 6.5677e-14 | 6.3506e-14 | 5.1687e-14 | 5.4078e-14 | 5.5596e-14 | 5.7329e-14 | 5.8714e-14 | 5.9617e-14 | 6.1767e-14 | 6.3253e-14 | 6.4036e-14 | 6.5487e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 9.992e-14% | 4391.6218 | 6.4022e-14 | 6.6236e-14 | 7.3288e-14 | 7.1061e-14 | 5.9581e-14 | 6.1989e-14 | 6.3944e-14 | 6.5824e-14 | 6.7452e-14 | 6.8268e-14 | 6.9472e-14 | 7.0849e-14 | 7.2254e-14 | 7.4021e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 100% | 0 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
99% | 0.8916 | 49.9025 | 52.2901 | 59.4299 | 65.4429 | 68.6867 | 71.0307 | 73.7326 | 75.7542 | 77.9829 | 79.1511 | 80.1629 | 82.6675 | 81.157 | 85.2413 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 99% | 0.8916 | 53.1132 | 55.592 | 62.6764 | 68.9168 | 72.1719 | 74.8116 | 77.3219 | 79.4606 | 81.6883 | 82.6647 | 83.9974 | 86.4681 | 85.6602 | 88.8872 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486
98% | 3.5664 | 49.3984 | 51.7619 | 58.8296 | 64.7818 | 67.9929 | 70.3132 | 72.9878 | 74.989 | 77.1952 | 78.3516 | 79.3532 | 81.8324 | 80.3372 | 84.3803 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 98% | 3.5664 | 52.5767 | 55.0305 | 62.0433 | 68.2206 | 71.4429 | 74.0559 | 76.5409 | 78.658 | 80.8632 | 81.8297 | 83.1489 | 85.5946 | 84.795 | 87.9894 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832
97% | 4.7552 | 48.8943 | 51.2337 | 58.2293 | 64.1208 | 67.2991 | 69.5957 | 72.243 | 74.2238 | 76.4075 | 77.5521 | 78.5434 | 80.9974 | 79.5174 | 83.5193 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 97% | 4.7552 | 52.0402 | 54.469 | 61.4102 | 67.5245 | 70.7139 | 73.3003 | 75.7598 | 77.8554 | 80.038 | 80.9947 | 82.3005 | 84.7212 | 83.9297 | 87.0915 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153
95% | 7.7272 | 47.8862 | 50.1774 | 57.0287 | 62.7987 | 65.9115 | 68.1608 | 70.7535 | 72.6934 | 74.8321 | 75.9531 | 76.924 | 79.3274 | 77.8779 | 81.7972 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 95% | 7.7272 | 50.9672 | 53.3459 | 60.144 | 66.1322 | 69.2559 | 71.7889 | 74.1978 | 76.2501 | 78.3878 | 79.3247 | 80.6036 | 82.9744 | 82.1992 | 85.2958 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082
90% | 39.2302 | 45.3659 | 47.5365 | 54.0272 | 59.4935 | 62.4425 | 64.5734 | 67.0296 | 68.8674 | 70.8936 | 71.9556 | 72.8753 | 75.1522 | 73.7791 | 77.4921 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 90% | 39.2302 | 48.2848 | 50.5382 | 56.9785 | 62.6516 | 65.6108 | 68.0106 | 70.2926 | 72.2369 | 74.2621 | 75.1497 | 76.3613 | 78.6073 | 77.8729 | 80.8066 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987
85% | 117.6906 | 42.8456 | 44.8955 | 51.0257 | 56.1883 | 58.9735 | 60.986 | 63.3057 | 65.0415 | 66.9551 | 67.958 | 68.8267 | 70.9771 | 69.6802 | 73.187 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 85% | 117.6906 | 45.6023 | 47.7305 | 53.813 | 59.171 | 61.9658 | 64.2322 | 66.3875 | 68.2238 | 70.1364 | 70.9748 | 72.119 | 74.2403 | 73.5467 | 76.3173 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155
80% | 268.3703 | 40.3252 | 42.2546 | 48.0242 | 52.8831 | 55.5044 | 57.3985 | 59.5819 | 61.2155 | 63.0165 | 63.9605 | 64.7781 | 66.802 | 65.5814 | 68.8819 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 80% | 268.3703 | 42.9198 | 44.9228 | 50.6476 | 55.6903 | 58.3207 | 60.4538 | 62.4824 | 64.2106 | 66.0108 | 66.7998 | 67.8767 | 69.8732 | 69.2204 | 71.8281 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322
75% | 455.9026 | 37.8049 | 39.6137 | 45.0227 | 49.5779 | 52.0354 | 53.8111 | 55.858 | 57.3895 | 59.078 | 59.963 | 60.7295 | 62.6269 | 61.4826 | 64.5768 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 75% | 455.9026 | 40.2373 | 42.1152 | 47.4821 | 52.2097 | 54.6757 | 56.6755 | 58.5772 | 60.1974 | 61.8851 | 62.6248 | 63.6344 | 65.5061 | 64.8941 | 67.3388 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749
70% | 690.9866 | 35.2846 | 36.9728 | 42.0212 | 46.2727 | 48.5664 | 50.2237 | 52.1341 | 53.5636 | 55.1395 | 55.9654 | 56.6808 | 58.4517 | 57.3837 | 60.2717 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 70% | 690.9866 | 37.5548 | 39.3075 | 44.3166 | 48.729 | 51.0307 | 52.8971 | 54.6721 | 56.1843 | 57.7594 | 58.4498 | 59.3921 | 61.139 | 60.5678 | 62.8495 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657
65% | 967.6784 | 32.7642 | 34.3319 | 39.0196 | 42.9675 | 45.0973 | 46.6363 | 48.4103 | 49.7376 | 51.2009 | 51.9679 | 52.6322 | 54.2766 | 53.2849 | 55.9665 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 65% | 967.6784 | 34.8723 | 36.4998 | 41.1511 | 45.2484 | 47.3856 | 49.1187 | 50.7669 | 52.1711 | 53.6337 | 54.2748 | 55.1498 | 56.772 | 56.2416 | 58.3603 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824
60% | 1292.8136 | 30.2439 | 31.691 | 36.0181 | 39.6623 | 41.6283 | 43.0489 | 44.6864 | 45.9116 | 47.2624 | 47.9704 | 48.5836 | 50.1015 | 49.1861 | 51.6614 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 60% | 1292.8136 | 32.1898 | 33.6921 | 37.9857 | 41.7677 | 43.7406 | 45.3404 | 46.8618 | 48.1579 | 49.5081 | 50.0998 | 50.9075 | 52.4049 | 51.9153 | 53.871 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992
55% | 1647.0743 | 27.7236 | 29.0501 | 33.0166 | 36.3571 | 38.1593 | 39.4615 | 40.9625 | 42.0857 | 43.3239 | 43.9728 | 44.5349 | 45.9264 | 45.0872 | 47.3563 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 55% | 1647.0743 | 29.5074 | 30.8845 | 34.8202 | 38.2871 | 40.0955 | 41.562 | 42.9566 | 44.1448 | 45.3824 | 45.9248 | 46.6652 | 48.0378 | 47.589 | 49.3818 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159
50% | 2104.1657 | 25.2033 | 26.4091 | 30.0151 | 33.0519 | 34.6903 | 35.8741 | 37.2387 | 38.2597 | 39.3853 | 39.9753 | 40.4863 | 41.7512 | 40.9884 | 43.0512 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 50% | 2104.1657 | 26.8249 | 28.0768 | 31.6547 | 34.8064 | 36.4505 | 37.7836 | 39.0515 | 40.1316 | 41.2567 | 41.7499 | 42.4229 | 43.6707 | 43.2627 | 44.8925 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326
45% | 2736.0097 | 22.6829 | 23.7682 | 27.0136 | 29.7468 | 31.2212 | 32.2867 | 33.5148 | 34.4337 | 35.4468 | 35.9778 | 36.4377 | 37.5761 | 36.8895 | 38.7461 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 45% | 2736.0097 | 24.1424 | 25.2691 | 28.4893 | 31.3258 | 32.8054 | 34.0053 | 35.1463 | 36.1185 | 37.1311 | 37.5749 | 38.1806 | 39.3037 | 38.9365 | 40.4033 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494
40% | 3483.7613 | 20.1626 | 21.1273 | 24.0121 | 26.4416 | 27.7522 | 28.6993 | 29.7909 | 30.6078 | 31.5083 | 31.9802 | 32.389 | 33.401 | 32.7907 | 34.4409 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 40% | 3483.7613 | 21.4599 | 22.4614 | 25.3238 | 27.8452 | 29.1604 | 30.2269 | 31.2412 | 32.1053 | 33.0054 | 33.3999 | 33.9383 | 34.9366 | 34.6102 | 35.914 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661
35% | 3830.2948 | 17.6423 | 18.4864 | 21.0106 | 23.1364 | 24.2832 | 25.1119 | 26.0671 | 26.7818 | 27.5697 | 27.9827 | 28.3404 | 29.2259 | 28.6919 | 30.1358 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 35% | 3830.2948 | 18.7774 | 19.6537 | 22.1583 | 24.3645 | 25.5153 | 26.4485 | 27.336 | 28.0921 | 28.8797 | 29.2249 | 29.696 | 30.5695 | 30.2839 | 31.4248 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828
30% | 3953.6322 | 15.122 | 15.8455 | 18.0091 | 19.8312 | 20.8142 | 21.5245 | 22.3432 | 22.9558 | 23.6312 | 23.9852 | 24.2918 | 25.0507 | 24.593 | 25.8307 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 30% | 3953.6322 | 16.0949 | 16.8461 | 18.9928 | 20.8839 | 21.8703 | 22.6702 | 23.4309 | 24.079 | 24.754 | 25.0499 | 25.4538 | 26.2024 | 25.9576 | 26.9355 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996
25% | 4060.9208 | 12.6016 | 13.2046 | 15.0076 | 16.526 | 17.3451 | 17.937 | 18.6193 | 19.1298 | 19.6927 | 19.9877 | 20.2432 | 20.8756 | 20.4942 | 21.5256 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 25% | 4060.9208 | 13.4124 | 14.0384 | 15.8274 | 17.4032 | 18.2252 | 18.8918 | 19.5257 | 20.0658 | 20.6284 | 20.8749 | 21.2115 | 21.8354 | 21.6314 | 22.4463 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163
20% | 4165.2375 | 10.0813 | 10.5637 | 12.006 | 13.2208 | 13.8761 | 14.3496 | 14.8955 | 15.3039 | 15.7541 | 15.9901 | 16.1945 | 16.7005 | 16.3954 | 17.2205 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 20% | 4165.2375 | 10.7299 | 11.2307 | 12.6619 | 13.9226 | 14.5802 | 15.1135 | 15.6206 | 16.0526 | 16.5027 | 16.6999 | 16.9692 | 17.4683 | 17.3051 | 17.957 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331
15% | 4270.4458 | 7.561 | 7.9227 | 9.0045 | 9.9156 | 10.4071 | 10.7622 | 11.1716 | 11.4779 | 11.8156 | 11.9926 | 12.1459 | 12.5254 | 12.2965 | 12.9154 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 15% | 4270.4458 | 8.0475 | 8.423 | 9.4964 | 10.4419 | 10.9351 | 11.3351 | 11.7154 | 12.0395 | 12.377 | 12.525 | 12.7269 | 13.1012 | 12.9788 | 13.4678 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498
10% | 4373.8709 | 5.0407 | 5.2818 | 6.003 | 6.6104 | 6.9381 | 7.1748 | 7.4477 | 7.6519 | 7.8771 | 7.9951 | 8.0973 | 8.3502 | 8.1977 | 8.6102 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 10% | 4373.8709 | 5.365 | 5.6154 | 6.3309 | 6.9613 | 7.2901 | 7.5567 | 7.8103 | 8.0263 | 8.2513 | 8.35 | 8.4846 | 8.7341 | 8.6525 | 8.9785 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665
5% | 4391.7028 | 2.5203 | 2.6409 | 3.0015 | 3.3052 | 3.469 | 3.5874 | 3.7239 | 3.826 | 3.9385 | 3.9975 | 4.0486 | 4.1751 | 4.0988 | 4.3051 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 5% | 4391.7028 | 2.6825 | 2.8077 | 3.1655 | 3.4806 | 3.645 | 3.7784 | 3.9051 | 4.0132 | 4.1257 | 4.175 | 4.2423 | 4.3671 | 4.3263 | 4.4893 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833
9.992e-14% | 4391.7028 | 5.0366e-14 | 5.2776e-14 | 5.9982e-14 | 6.6051e-14 | 6.9325e-14 | 7.1691e-14 | 7.4418e-14 | 7.6458e-14 | 7.8708e-14 | 7.9887e-14 | 8.0908e-14 | 8.3436e-14 | 8.1911e-14 | 8.6034e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.992e-14% | 4391.7028 | 5.3607e-14 | 5.6109e-14 | 6.3259e-14 | 6.9557e-14 | 7.2843e-14 | 7.5507e-14 | 7.8041e-14 | 8.0199e-14 | 8.2447e-14 | 8.3433e-14 | 8.4778e-14 | 8.7272e-14 | 8.6456e-14 | 8.9713e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 100% | 0 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068
99% | 0 | 56.3898 | 58.1038 | 65.0718 | 70.0992 | 72.7437 | 75.1124 | 76.6167 | 78.334 | 79.7062 | 80.6005 | 82.7304 | 84.2035 | 84.9787 | 86.4162 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 99% | 0.75633 | 63.4323 | 65.6261 | 72.6135 | 77.5841 | 80.5645 | 82.9506 | 84.8874 | 86.7503 | 88.363 | 89.1721 | 90.3645 | 91.7286 | 93.121 | 94.8723 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457
98% | 0.37816 | 55.8202 | 57.5169 | 64.4145 | 69.3911 | 72.0089 | 74.3537 | 75.8428 | 77.5427 | 78.9011 | 79.7863 | 81.8947 | 83.3529 | 84.1203 | 85.5433 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 98% | 1.1345 | 62.7915 | 64.9632 | 71.88 | 76.8005 | 79.7507 | 82.1127 | 84.0299 | 85.874 | 87.4705 | 88.2714 | 89.4517 | 90.8021 | 92.1803 | 93.914 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847
97% | 0.75633 | 55.2506 | 56.93 | 63.7572 | 68.683 | 71.2741 | 73.595 | 75.0689 | 76.7515 | 78.096 | 78.9722 | 81.059 | 82.5024 | 83.2619 | 84.6705 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 97% | 1.8908 | 62.1508 | 64.3003 | 71.1466 | 76.0168 | 78.9369 | 81.2748 | 83.1725 | 84.9977 | 86.5779 | 87.3707 | 88.539 | 89.8755 | 91.2397 | 92.9557 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236
95% | 1.8908 | 54.1115 | 55.7561 | 62.4427 | 67.2669 | 69.8045 | 72.0775 | 73.5211 | 75.169 | 76.4857 | 77.3439 | 79.3877 | 80.8013 | 81.5452 | 82.9247 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 95% | 3.4035 | 60.8693 | 62.9745 | 69.6796 | 74.4494 | 77.3094 | 79.599 | 81.4576 | 83.2452 | 84.7928 | 85.5692 | 86.7134 | 88.0224 | 89.3585 | 91.0391 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015
90% | 4.538 | 51.2635 | 52.8216 | 59.1562 | 63.7265 | 66.1306 | 68.284 | 69.6515 | 71.2127 | 72.4602 | 73.2732 | 75.2094 | 76.5486 | 77.2533 | 78.5602 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 90% | 9.0759 | 57.6657 | 59.6601 | 66.0123 | 70.531 | 73.2405 | 75.4096 | 77.1703 | 78.8639 | 80.33 | 81.0656 | 82.1496 | 83.3897 | 84.6554 | 86.2476 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961
85% | 9.0759 | 48.4155 | 49.8871 | 55.8697 | 60.1862 | 62.4567 | 64.4904 | 65.782 | 67.2565 | 68.4346 | 69.2024 | 71.0311 | 72.2959 | 72.9615 | 74.1958 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 85% | 16.2611 | 54.462 | 56.3456 | 62.3449 | 66.6126 | 69.1716 | 71.2202 | 72.8831 | 74.4826 | 75.8673 | 76.5619 | 77.5857 | 78.7569 | 79.9523 | 81.456 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908
80% | 27.606 | 45.5675 | 46.9525 | 52.5833 | 56.6458 | 58.7827 | 60.6969 | 61.9125 | 63.3002 | 64.409 | 65.1317 | 66.8528 | 68.0432 | 68.6696 | 69.8313 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 80% | 24.9588 | 51.2584 | 53.0312 | 58.6776 | 62.6943 | 65.1026 | 67.0308 | 68.5959 | 70.1012 | 71.4045 | 72.0583 | 73.0218 | 74.1241 | 75.2493 | 76.6645 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854
75% | 57.481 | 42.7196 | 44.018 | 49.2968 | 53.1054 | 55.1088 | 56.9033 | 58.043 | 59.3439 | 60.3835 | 61.061 | 62.6745 | 63.7905 | 64.3778 | 65.4668 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 75% | 32.9003 | 48.0547 | 49.7167 | 55.0102 | 58.7759 | 61.0337 | 62.8413 | 64.3086 | 65.7199 | 66.9417 | 67.5547 | 68.458 | 69.4914 | 70.5462 | 71.873 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801
70% | 106.2642 | 39.8716 | 41.0835 | 46.0104 | 49.5651 | 51.4349 | 53.1098 | 54.1734 | 55.3877 | 56.3579 | 56.9902 | 58.4962 | 59.5378 | 60.0859 | 61.1024 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 70% | 41.9762 | 44.8511 | 46.4023 | 51.3429 | 54.8575 | 56.9648 | 58.6519 | 60.0214 | 61.3386 | 62.4789 | 63.051 | 63.8941 | 64.8586 | 65.8431 | 67.0814 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748
65% | 201.9397 | 37.0236 | 38.1489 | 42.7239 | 46.0247 | 47.761 | 49.3162 | 50.3039 | 51.4314 | 52.3323 | 52.9195 | 54.3179 | 55.2851 | 55.7941 | 56.7379 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 65% | 67.6914 | 41.6474 | 43.0878 | 47.6755 | 50.9391 | 52.8959 | 54.4625 | 55.7341 | 56.9573 | 58.0161 | 58.5474 | 59.3302 | 60.2259 | 61.14 | 62.2899 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694
60% | 402.745 | 34.1757 | 35.2144 | 39.4375 | 42.4843 | 44.0871 | 45.5227 | 46.4344 | 47.4751 | 48.3068 | 48.8488 | 50.1396 | 51.0324 | 51.5022 | 52.3735 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 60% | 98.7009 | 38.4438 | 39.7734 | 44.0082 | 47.0207 | 48.827 | 50.2731 | 51.4469 | 52.5759 | 53.5534 | 54.0437 | 54.7664 | 55.5931 | 56.4369 | 57.4984 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641
55% | 655.7369 | 31.3277 | 32.2799 | 36.151 | 38.944 | 40.4131 | 41.7291 | 42.5648 | 43.5189 | 44.2812 | 44.778 | 45.9613 | 46.7797 | 47.2104 | 48.009 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 55% | 153.5347 | 35.2401 | 36.4589 | 40.3408 | 43.1023 | 44.7581 | 46.0836 | 47.1596 | 48.1946 | 49.0906 | 49.5401 | 50.2025 | 50.9604 | 51.7339 | 52.7068 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587
50% | 981.7145 | 28.4797 | 29.3453 | 32.8646 | 35.4036 | 36.7392 | 37.9355 | 38.6953 | 39.5626 | 40.2557 | 40.7073 | 41.783 | 42.527 | 42.9185 | 43.6446 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 50% | 258.2862 | 32.0365 | 33.1445 | 36.6735 | 39.1839 | 40.6891 | 41.8942 | 42.8724 | 43.8133 | 44.6278 | 45.0364 | 45.6386 | 46.3276 | 47.0308 | 47.9153 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534
45% | 1622.7029 | 25.6317 | 26.4108 | 29.5781 | 31.8633 | 33.0653 | 34.142 | 34.8258 | 35.6064 | 36.2301 | 36.6366 | 37.6047 | 38.2743 | 38.6267 | 39.2801 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 45% | 488.9664 | 28.8328 | 29.83 | 33.0061 | 35.2655 | 36.6202 | 37.7048 | 38.5852 | 39.4319 | 40.165 | 40.5328 | 41.0748 | 41.6948 | 42.3277 | 43.1238 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481
40% | 2442.9413 | 22.7838 | 23.4763 | 26.2916 | 28.3229 | 29.3914 | 30.3484 | 30.9562 | 31.6501 | 32.2045 | 32.5659 | 33.4264 | 34.0216 | 34.3348 | 34.9157 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 40% | 928.0152 | 25.6292 | 26.5156 | 29.3388 | 31.3471 | 32.5513 | 33.5154 | 34.2979 | 35.0506 | 35.7022 | 36.0292 | 36.5109 | 37.0621 | 37.6246 | 38.3322 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427
35% | 3006.7842 | 19.9358 | 20.5417 | 23.0052 | 24.7825 | 25.7175 | 26.5549 | 27.0867 | 27.6938 | 28.179 | 28.4951 | 29.2481 | 29.7689 | 30.043 | 30.5512 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 35% | 1530.4309 | 22.4255 | 23.2011 | 25.6714 | 27.4287 | 28.4824 | 29.326 | 30.0107 | 30.6693 | 31.2395 | 31.5255 | 31.9471 | 32.4293 | 32.9215 | 33.5407 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374
30% | 3276.4154 | 17.0878 | 17.6072 | 19.7187 | 21.2422 | 22.0435 | 22.7613 | 23.2172 | 23.7376 | 24.1534 | 24.4244 | 25.0698 | 25.5162 | 25.7511 | 26.1867 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 30% | 2592.3162 | 19.2219 | 19.8867 | 22.0041 | 23.5103 | 24.4135 | 25.1365 | 25.7234 | 26.288 | 26.7767 | 27.0219 | 27.3832 | 27.7966 | 28.2185 | 28.7492 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832
25% | 3466.632 | 14.2399 | 14.6727 | 16.4323 | 17.7018 | 18.3696 | 18.9678 | 19.3477 | 19.7813 | 20.1278 | 20.3537 | 20.8915 | 21.2635 | 21.4593 | 21.8223 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 25% | 3659.4958 | 16.0182 | 16.5722 | 18.3367 | 19.592 | 20.3446 | 20.9471 | 21.4362 | 21.9066 | 22.3139 | 22.5182 | 22.8193 | 23.1638 | 23.5154 | 23.9577 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267
20% | 3713.9514 | 11.3919 | 11.7381 | 13.1458 | 14.1614 | 14.6957 | 15.1742 | 15.4781 | 15.825 | 16.1023 | 16.2829 | 16.7132 | 17.0108 | 17.1674 | 17.4578 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 20% | 4005.5161 | 12.8146 | 13.2578 | 14.6694 | 15.6736 | 16.2757 | 16.7577 | 17.149 | 17.5253 | 17.8511 | 18.0146 | 18.2555 | 18.531 | 18.8123 | 19.1661 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214
15% | 4043.3325 | 8.5439 | 8.8036 | 9.8594 | 10.6211 | 11.0218 | 11.3807 | 11.6086 | 11.8688 | 12.0767 | 12.2122 | 12.5349 | 12.7581 | 12.8756 | 13.0934 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 15% | 4281.1979 | 9.6109 | 9.9433 | 11.002 | 11.7552 | 12.2067 | 12.5683 | 12.8617 | 13.144 | 13.3883 | 13.5109 | 13.6916 | 13.8983 | 14.1092 | 14.3746 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416
10% | 4350.7801 | 5.6959 | 5.8691 | 6.5729 | 7.0807 | 7.3478 | 7.5871 | 7.7391 | 7.9125 | 8.0511 | 8.1415 | 8.3566 | 8.5054 | 8.5837 | 8.7289 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 10% | 4391.6218 | 6.4073 | 6.6289 | 7.3347 | 7.8368 | 8.1378 | 8.3788 | 8.5745 | 8.7627 | 8.9256 | 9.0073 | 9.1277 | 9.2655 | 9.4062 | 9.5831 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107
5% | 4391.6218 | 2.848 | 2.9345 | 3.2865 | 3.5404 | 3.6739 | 3.7936 | 3.8695 | 3.9563 | 4.0256 | 4.0707 | 4.1783 | 4.2527 | 4.2919 | 4.3645 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 5% | 4391.6218 | 3.2036 | 3.3144 | 3.6673 | 3.9184 | 4.0689 | 4.1894 | 4.2872 | 4.3813 | 4.4628 | 4.5036 | 4.5639 | 4.6328 | 4.7031 | 4.7915 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053
9.992e-14% | 4391.6218 | 5.6914e-14 | 5.8644e-14 | 6.5677e-14 | 7.0751e-14 | 7.342e-14 | 7.581e-14 | 7.7329e-14 | 7.9062e-14 | 8.0447e-14 | 8.135e-14 | 8.3499e-14 | 8.4986e-14 | 8.5768e-14 | 8.7219e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 9.992e-14% | 4391.6218 | 6.4022e-14 | 6.6236e-14 | 7.3288e-14 | 7.8305e-14 | 8.1313e-14 | 8.3721e-14 | 8.5676e-14 | 8.7557e-14 | 8.9184e-14 | 9.0001e-14 | 9.1204e-14 | 9.2581e-14 | 9.3986e-14 | 9.5754e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 50.4065 | 52.8183 | 60.0302 | 58.8539 | 47.6305 | 49.9982 | 52.7273 | 54.7694 | 57.0207 | 58.2006 | 59.2226 | 61.7525 | 60.2268 | 64.3524 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 69.7339 | 100% | 0 | 53.6497 | 56.1536 | 63.3095 | 62.3629 | 51.1509 | 53.8173 | 56.3529 | 58.5132 | 60.7634 | 61.7497 | 63.0959 | 65.5915 | 64.7755 | 68.0351 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153 | 69.9153
99% | 0.8916 | 49.9025 | 52.2901 | 59.4299 | 58.2654 | 47.1542 | 49.4982 | 52.2001 | 54.2217 | 56.4504 | 57.6186 | 58.6304 | 61.135 | 59.6245 | 63.7088 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 69.0365 | 99% | 0.8916 | 53.1132 | 55.592 | 62.6764 | 61.7393 | 50.6394 | 53.2791 | 55.7894 | 57.9281 | 60.1558 | 61.1322 | 62.4649 | 64.9356 | 64.1277 | 67.3547 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161 | 69.2161
98% | 3.5664 | 49.3984 | 51.7619 | 58.8296 | 57.6768 | 46.6779 | 48.9982 | 51.6728 | 53.674 | 55.8802 | 57.0366 | 58.0382 | 60.5174 | 59.0222 | 63.0653 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 68.3392 | 98% | 3.5664 | 52.5767 | 55.0305 | 62.0433 | 61.1156 | 50.1279 | 52.7409 | 55.2259 | 57.343 | 59.5482 | 60.5147 | 61.8339 | 64.2796 | 63.48 | 66.6744 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517 | 68.517
97% | 4.7552 | 48.8943 | 51.2337 | 58.2293 | 57.0883 | 46.2016 | 48.4982 | 51.1455 | 53.1263 | 55.31 | 56.4546 | 57.4459 | 59.8999 | 58.4199 | 62.4218 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 67.6419 | 97% | 4.7552 | 52.0402 | 54.469 | 61.4102 | 60.492 | 49.6164 | 52.2028 | 54.6623 | 56.7579 | 58.9405 | 59.8972 | 61.203 | 63.6237 | 62.8322 | 65.994 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178 | 67.8178
95% | 7.7272 | 47.8862 | 50.1774 | 57.0287 | 55.9112 | 45.249 | 47.4983 | 50.091 | 52.0309 | 54.1696 | 55.2906 | 56.2615 | 58.6649 | 57.2154 | 61.1347 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 66.2472 | 95% | 7.7272 | 50.9672 | 53.3459 | 60.144 | 59.2447 | 48.5934 | 51.1264 | 53.5353 | 55.5876 | 57.7253 | 58.6622 | 59.9411 | 62.3119 | 61.5367 | 64.6333 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195 | 66.4195
90% | 39.2302 | 45.3659 | 47.5365 | 54.0272 | 52.9685 | 42.8675 | 44.9984 | 47.4546 | 49.2924 | 51.3186 | 52.3806 | 53.3003 | 55.5772 | 54.2041 | 57.9171 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 62.7605 | 90% | 39.2302 | 48.2848 | 50.5382 | 56.9785 | 56.1266 | 46.0358 | 48.4356 | 50.7176 | 52.6619 | 54.6871 | 55.5747 | 56.7863 | 59.0323 | 58.2979 | 61.2316 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237 | 62.9237
85% | 117.6906 | 42.8456 | 44.8955 | 51.0257 | 50.0258 | 40.486 | 42.4985 | 44.8182 | 46.554 | 48.4676 | 49.4705 | 50.3392 | 52.4896 | 51.1927 | 54.6995 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 59.2738 | 85% | 117.6906 | 45.6023 | 47.7305 | 53.813 | 53.0085 | 43.4783 | 45.7447 | 47.9 | 49.7363 | 51.6489 | 52.4873 | 53.6315 | 55.7528 | 55.0592 | 57.8298 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428 | 59.428
80% | 268.3703 | 40.3252 | 42.2546 | 48.0242 | 47.0831 | 38.1044 | 39.9985 | 42.1819 | 43.8155 | 45.6165 | 46.5605 | 47.3781 | 49.402 | 48.1814 | 51.4819 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 55.7871 | 80% | 268.3703 | 42.9198 | 44.9228 | 50.6476 | 49.8903 | 40.9207 | 43.0538 | 45.0824 | 46.8106 | 48.6108 | 49.3998 | 50.4767 | 52.4732 | 51.8204 | 54.4281 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322 | 55.9322
75% | 455.9026 | 37.8049 | 39.6137 | 45.0227 | 44.1404 | 35.7229 | 37.4986 | 39.5455 | 41.077 | 42.7655 | 43.6505 | 44.417 | 46.3144 | 45.1701 | 48.2643 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 52.3004 | 75% | 455.9026 | 40.2373 | 42.1152 | 47.4821 | 46.7722 | 38.3632 | 40.363 | 42.2647 | 43.8849 | 45.5726 | 46.3123 | 47.3219 | 49.1936 | 48.5816 | 51.0263 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365 | 52.4365
70% | 690.9866 | 35.2846 | 36.9728 | 42.0212 | 41.1977 | 33.3414 | 34.9987 | 36.9091 | 38.3386 | 39.9145 | 40.7404 | 41.4558 | 43.2267 | 42.1587 | 45.0467 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 48.8137 | 70% | 690.9866 | 37.5548 | 39.3075 | 44.3166 | 43.654 | 35.8057 | 37.6721 | 39.4471 | 40.9593 | 42.5344 | 43.2248 | 44.1671 | 45.914 | 45.3428 | 47.6245 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407 | 48.9407
65% | 967.6784 | 32.7642 | 34.3319 | 39.0196 | 38.255 | 30.9598 | 32.4988 | 34.2728 | 35.6001 | 37.0634 | 37.8304 | 38.4947 | 40.1391 | 39.1474 | 41.829 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 45.327 | 65% | 967.6784 | 34.8723 | 36.4998 | 41.1511 | 40.5359 | 33.2481 | 34.9812 | 36.6294 | 38.0336 | 39.4962 | 40.1373 | 41.0123 | 42.6345 | 42.1041 | 44.2228 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449 | 45.4449
60% | 1292.8136 | 30.2439 | 31.691 | 36.0181 | 35.3123 | 28.5783 | 29.9989 | 31.6364 | 32.8616 | 34.2124 | 34.9204 | 35.5336 | 37.0515 | 36.1361 | 38.6114 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 41.8403 | 60% | 1292.8136 | 32.1898 | 33.6921 | 37.9857 | 37.4177 | 30.6906 | 32.2904 | 33.8118 | 35.1079 | 36.4581 | 37.0498 | 37.8575 | 39.3549 | 38.8653 | 40.821 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492 | 41.9492
55% | 1647.0743 | 27.7236 | 29.0501 | 33.0166 | 32.3696 | 26.1968 | 27.499 | 29 | 30.1232 | 31.3614 | 32.0103 | 32.5724 | 33.9639 | 33.1247 | 35.3938 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 38.3536 | 55% | 1647.0743 | 29.5074 | 30.8845 | 34.8202 | 34.2996 | 28.133 | 29.5995 | 30.9941 | 32.1823 | 33.4199 | 33.9623 | 34.7027 | 36.0753 | 35.6265 | 37.4193 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534 | 38.4534
50% | 2104.1657 | 25.2033 | 26.4091 | 30.0151 | 29.4269 | 23.8153 | 24.9991 | 26.3637 | 27.3847 | 28.5103 | 29.1003 | 29.6113 | 30.8762 | 30.1134 | 32.1762 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 34.8669 | 50% | 2104.1657 | 26.8249 | 28.0768 | 31.6547 | 31.1814 | 25.5755 | 26.9086 | 28.1765 | 29.2566 | 30.3817 | 30.8749 | 31.5479 | 32.7957 | 32.3877 | 34.0175 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576 | 34.9576
45% | 2736.0097 | 22.6829 | 23.7682 | 27.0136 | 26.4843 | 21.4337 | 22.4992 | 23.7273 | 24.6462 | 25.6593 | 26.1903 | 26.6502 | 27.7886 | 27.102 | 28.9586 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 31.3802 | 45% | 2736.0097 | 24.1424 | 25.2691 | 28.4893 | 28.0633 | 23.0179 | 24.2178 | 25.3588 | 26.331 | 27.3436 | 27.7874 | 28.3931 | 29.5162 | 29.149 | 30.6158 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619 | 31.4619
40% | 3483.7613 | 20.1626 | 21.1273 | 24.0121 | 23.5416 | 19.0522 | 19.9993 | 21.0909 | 21.9078 | 22.8083 | 23.2802 | 23.689 | 24.701 | 24.0907 | 25.7409 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 27.8936 | 40% | 3483.7613 | 21.4599 | 22.4614 | 25.3238 | 24.9452 | 20.4604 | 21.5269 | 22.5412 | 23.4053 | 24.3054 | 24.6999 | 25.2383 | 26.2366 | 25.9102 | 27.214 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661 | 27.9661
35% | 3830.2948 | 17.6423 | 18.4864 | 21.0106 | 20.5989 | 16.6707 | 17.4994 | 18.4546 | 19.1693 | 19.9572 | 20.3702 | 20.7279 | 21.6134 | 21.0794 | 22.5233 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 24.4069 | 35% | 3830.2948 | 18.7774 | 19.6537 | 22.1583 | 21.827 | 17.9028 | 18.836 | 19.7235 | 20.4796 | 21.2672 | 21.6124 | 22.0835 | 22.957 | 22.6714 | 23.8123 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703 | 24.4703
30% | 3953.6322 | 15.122 | 15.8455 | 18.0091 | 17.6562 | 14.2892 | 14.9995 | 15.8182 | 16.4308 | 17.1062 | 17.4602 | 17.7668 | 18.5257 | 18.068 | 19.3057 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 20.9202 | 30% | 3953.6322 | 16.0949 | 16.8461 | 18.9928 | 18.7089 | 15.3453 | 16.1452 | 16.9059 | 17.554 | 18.229 | 18.5249 | 18.9288 | 19.6774 | 19.4326 | 20.4105 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746 | 20.9746
25% | 4060.9208 | 12.6016 | 13.2046 | 15.0076 | 14.7135 | 11.9076 | 12.4995 | 13.1818 | 13.6923 | 14.2552 | 14.5502 | 14.8057 | 15.4381 | 15.0567 | 16.0881 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 17.4335 | 25% | 4060.9208 | 13.4124 | 14.0384 | 15.8274 | 15.5907 | 12.7877 | 13.4543 | 14.0882 | 14.6283 | 15.1909 | 15.4374 | 15.774 | 16.3979 | 16.1939 | 17.0088 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788 | 17.4788
20% | 4165.2375 | 10.0813 | 10.5637 | 12.006 | 11.7708 | 9.5261 | 9.9996 | 10.5455 | 10.9539 | 11.4041 | 11.6401 | 11.8445 | 12.3505 | 12.0454 | 12.8705 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 13.9468 | 20% | 4165.2375 | 10.7299 | 11.2307 | 12.6619 | 12.4726 | 10.2302 | 10.7635 | 11.2706 | 11.7026 | 12.1527 | 12.3499 | 12.6192 | 13.1183 | 12.9551 | 13.607 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831 | 13.9831
15% | 4270.4458 | 7.561 | 7.9227 | 9.0045 | 8.8281 | 7.1446 | 7.4997 | 7.9091 | 8.2154 | 8.5531 | 8.7301 | 8.8834 | 9.2629 | 9.034 | 9.6529 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 10.4601 | 15% | 4270.4458 | 8.0475 | 8.423 | 9.4964 | 9.3544 | 7.6726 | 8.0726 | 8.4529 | 8.777 | 9.1145 | 9.2625 | 9.4644 | 9.8387 | 9.7163 | 10.2053 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873 | 10.4873
10% | 4373.8709 | 5.0407 | 5.2818 | 6.003 | 5.8854 | 4.7631 | 4.9998 | 5.2727 | 5.4769 | 5.7021 | 5.8201 | 5.9223 | 6.1752 | 6.0227 | 6.4352 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 6.9734 | 10% | 4373.8709 | 5.365 | 5.6154 | 6.3309 | 6.2363 | 5.1151 | 5.3817 | 5.6353 | 5.8513 | 6.0763 | 6.175 | 6.3096 | 6.5591 | 6.4775 | 6.8035 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915 | 6.9915
5% | 4391.7028 | 2.5203 | 2.6409 | 3.0015 | 2.9427 | 2.3815 | 2.4999 | 2.6364 | 2.7385 | 2.851 | 2.91 | 2.9611 | 3.0876 | 3.0113 | 3.2176 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 3.4867 | 5% | 4391.7028 | 2.6825 | 2.8077 | 3.1655 | 3.1181 | 2.5575 | 2.6909 | 2.8176 | 2.9257 | 3.0382 | 3.0875 | 3.1548 | 3.2796 | 3.2388 | 3.4018 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958 | 3.4958
9.992e-14% | 4391.7028 | 5.0366e-14 | 5.2776e-14 | 5.9982e-14 | 5.8807e-14 | 4.7592e-14 | 4.9958e-14 | 5.2685e-14 | 5.4726e-14 | 5.6975e-14 | 5.8154e-14 | 5.9175e-14 | 6.1703e-14 | 6.0179e-14 | 6.4301e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 6.9678e-14 | 9.992e-14% | 4391.7028 | 5.3607e-14 | 5.6109e-14 | 6.3259e-14 | 6.2313e-14 | 5.111e-14 | 5.3774e-14 | 5.6308e-14 | 5.8466e-14 | 6.0715e-14 | 6.17e-14 | 6.3045e-14 | 6.5539e-14 | 6.4724e-14 | 6.7981e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14 | 6.9859e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.9594 | 58.6907 | 65.7291 | 63.5572 | 51.7284 | 54.1211 | 55.6406 | 57.3752 | 58.7613 | 59.6646 | 61.816 | 63.304 | 64.087 | 65.5391 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 65.1165 | 100% | 0 | 64.073 | 66.289 | 73.347 | 71.1178 | 59.6283 | 62.0384 | 63.9948 | 65.8765 | 67.5056 | 68.3229 | 69.5273 | 70.9052 | 72.3116 | 74.0806 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568 | 74.3568
99% | 0 | 56.3898 | 58.1038 | 65.0718 | 62.9217 | 51.2112 | 53.5799 | 55.0842 | 56.8015 | 58.1737 | 59.068 | 61.1979 | 62.671 | 63.4462 | 64.8837 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 64.4653 | 99% | 0.75633 | 63.4323 | 65.6261 | 72.6135 | 70.4066 | 59.032 | 61.4181 | 63.3549 | 65.2178 | 66.8305 | 67.6396 | 68.832 | 70.1961 | 71.5885 | 73.3398 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132 | 73.6132
98% | 0.37816 | 55.8202 | 57.5169 | 64.4145 | 62.2861 | 50.6939 | 53.0387 | 54.5278 | 56.2277 | 57.5861 | 58.4713 | 60.5797 | 62.0379 | 62.8053 | 64.2283 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 63.8142 | 98% | 1.1345 | 62.7915 | 64.9632 | 71.88 | 69.6955 | 58.4357 | 60.7977 | 62.7149 | 64.559 | 66.1555 | 66.9564 | 68.1367 | 69.4871 | 70.8653 | 72.599 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697 | 72.8697
97% | 0.75633 | 55.2506 | 56.93 | 63.7572 | 61.6505 | 50.1766 | 52.4975 | 53.9714 | 55.654 | 56.9985 | 57.8747 | 59.9615 | 61.4049 | 62.1644 | 63.573 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 63.163 | 97% | 1.8908 | 62.1508 | 64.3003 | 71.1466 | 68.9843 | 57.8394 | 60.1773 | 62.075 | 63.9002 | 65.4804 | 66.2732 | 67.4415 | 68.778 | 70.1422 | 71.8582 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261 | 72.1261
95% | 1.8908 | 54.1115 | 55.7561 | 62.4427 | 60.3794 | 49.142 | 51.415 | 52.8586 | 54.5065 | 55.8232 | 56.6814 | 58.7252 | 60.1388 | 60.8827 | 62.2622 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 61.8607 | 95% | 3.4035 | 60.8693 | 62.9745 | 69.6796 | 67.5619 | 56.6469 | 58.9365 | 60.7951 | 62.5827 | 64.1303 | 64.9067 | 66.0509 | 67.3599 | 68.696 | 70.3766 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639 | 70.639
90% | 4.538 | 51.2635 | 52.8216 | 59.1562 | 57.2015 | 46.5556 | 48.709 | 50.0765 | 51.6377 | 52.8852 | 53.6982 | 55.6344 | 56.9736 | 57.6783 | 58.9852 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 58.6049 | 90% | 9.0759 | 57.6657 | 59.6601 | 66.0123 | 64.006 | 53.6655 | 55.8346 | 57.5953 | 59.2889 | 60.755 | 61.4906 | 62.5746 | 63.8147 | 65.0804 | 66.6726 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211 | 66.9211
85% | 9.0759 | 48.4155 | 49.8871 | 55.8697 | 54.0237 | 43.9692 | 46.0029 | 47.2945 | 48.769 | 49.9471 | 50.7149 | 52.5436 | 53.8084 | 54.474 | 55.7083 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 55.349 | 85% | 16.2611 | 54.462 | 56.3456 | 62.3449 | 60.4501 | 50.6841 | 52.7327 | 54.3956 | 55.9951 | 57.3798 | 58.0744 | 59.0982 | 60.2694 | 61.4648 | 62.9685 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033 | 63.2033
80% | 27.606 | 45.5675 | 46.9525 | 52.5833 | 50.8458 | 41.3827 | 43.2969 | 44.5125 | 45.9002 | 47.009 | 47.7317 | 49.4528 | 50.6432 | 51.2696 | 52.4313 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 52.0932 | 80% | 24.9588 | 51.2584 | 53.0312 | 58.6776 | 56.8943 | 47.7026 | 49.6308 | 51.1959 | 52.7012 | 54.0045 | 54.6583 | 55.6218 | 56.7241 | 57.8493 | 59.2645 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854 | 59.4854
75% | 57.481 | 42.7196 | 44.018 | 49.2968 | 47.6679 | 38.7963 | 40.5908 | 41.7305 | 43.0314 | 44.071 | 44.7485 | 46.362 | 47.478 | 48.0653 | 49.1543 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 48.8374 | 75% | 32.9003 | 48.0547 | 49.7167 | 55.0102 | 53.3384 | 44.7212 | 46.5288 | 47.9961 | 49.4074 | 50.6292 | 51.2422 | 52.1455 | 53.1789 | 54.2337 | 55.5605 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676 | 55.7676
70% | 106.2642 | 39.8716 | 41.0835 | 46.0104 | 44.4901 | 36.2099 | 37.8848 | 38.9484 | 40.1627 | 41.1329 | 41.7652 | 43.2712 | 44.3128 | 44.8609 | 45.8774 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 45.5816 | 70% | 41.9762 | 44.8511 | 46.4023 | 51.3429 | 49.7825 | 41.7398 | 43.4269 | 44.7964 | 46.1136 | 47.2539 | 47.826 | 48.6691 | 49.6336 | 50.6181 | 51.8564 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498 | 52.0498
65% | 201.9397 | 37.0236 | 38.1489 | 42.7239 | 41.3122 | 33.6235 | 35.1787 | 36.1664 | 37.2939 | 38.1948 | 38.782 | 40.1804 | 41.1476 | 41.6566 | 42.6004 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 42.3257 | 65% | 67.6914 | 41.6474 | 43.0878 | 47.6755 | 46.2266 | 38.7584 | 40.325 | 41.5966 | 42.8198 | 43.8786 | 44.4099 | 45.1927 | 46.0884 | 47.0025 | 48.1524 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319 | 48.3319
60% | 402.745 | 34.1757 | 35.2144 | 39.4375 | 38.1343 | 31.0371 | 32.4727 | 33.3844 | 34.4251 | 35.2568 | 35.7988 | 37.0896 | 37.9824 | 38.4522 | 39.3235 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 39.0699 | 60% | 98.7009 | 38.4438 | 39.7734 | 44.0082 | 42.6707 | 35.777 | 37.2231 | 38.3969 | 39.5259 | 40.5034 | 40.9937 | 41.7164 | 42.5431 | 43.3869 | 44.4484 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141 | 44.6141
55% | 655.7369 | 31.3277 | 32.2799 | 36.151 | 34.9565 | 28.4506 | 29.7666 | 30.6023 | 31.5564 | 32.3187 | 32.8155 | 33.9988 | 34.8172 | 35.2479 | 36.0465 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 35.8141 | 55% | 153.5347 | 35.2401 | 36.4589 | 40.3408 | 39.1148 | 32.7956 | 34.1211 | 35.1971 | 36.2321 | 37.1281 | 37.5776 | 38.24 | 38.9979 | 39.7714 | 40.7443 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962 | 40.8962
50% | 981.7145 | 28.4797 | 29.3453 | 32.8646 | 31.7786 | 25.8642 | 27.0605 | 27.8203 | 28.6876 | 29.3807 | 29.8323 | 30.908 | 31.652 | 32.0435 | 32.7696 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 32.5583 | 50% | 258.2862 | 32.0365 | 33.1445 | 36.6735 | 35.5589 | 29.8141 | 31.0192 | 31.9974 | 32.9383 | 33.7528 | 34.1614 | 34.7636 | 35.4526 | 36.1558 | 37.0403 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784 | 37.1784
45% | 1622.7029 | 25.6317 | 26.4108 | 29.5781 | 28.6008 | 23.2778 | 24.3545 | 25.0383 | 25.8189 | 26.4426 | 26.8491 | 27.8172 | 28.4868 | 28.8392 | 29.4926 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 29.3024 | 45% | 488.9664 | 28.8328 | 29.83 | 33.0061 | 32.003 | 26.8327 | 27.9173 | 28.7977 | 29.6444 | 30.3775 | 30.7453 | 31.2873 | 31.9073 | 32.5402 | 33.3363 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606 | 33.4606
40% | 2442.9413 | 22.7838 | 23.4763 | 26.2916 | 25.4229 | 20.6914 | 21.6484 | 22.2562 | 22.9501 | 23.5045 | 23.8659 | 24.7264 | 25.3216 | 25.6348 | 26.2157 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 26.0466 | 40% | 928.0152 | 25.6292 | 26.5156 | 29.3388 | 28.4471 | 23.8513 | 24.8154 | 25.5979 | 26.3506 | 27.0022 | 27.3292 | 27.8109 | 28.3621 | 28.9246 | 29.6322 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427 | 29.7427
35% | 3006.7842 | 19.9358 | 20.5417 | 23.0052 | 22.245 | 18.105 | 18.9424 | 19.4742 | 20.0813 | 20.5665 | 20.8826 | 21.6356 | 22.1564 | 22.4305 | 22.9387 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 22.7908 | 35% | 1530.4309 | 22.4255 | 23.2011 | 25.6714 | 24.8912 | 20.8699 | 21.7135 | 22.3982 | 23.0568 | 23.627 | 23.913 | 24.3346 | 24.8168 | 25.309 | 25.9282 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249 | 26.0249
30% | 3276.4154 | 17.0878 | 17.6072 | 19.7187 | 19.0672 | 15.5185 | 16.2363 | 16.6922 | 17.2126 | 17.6284 | 17.8994 | 18.5448 | 18.9912 | 19.2261 | 19.6617 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 19.535 | 30% | 2592.3162 | 19.2219 | 19.8867 | 22.0041 | 21.3353 | 17.8885 | 18.6115 | 19.1984 | 19.763 | 20.2517 | 20.4969 | 20.8582 | 21.2716 | 21.6935 | 22.2242 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307 | 22.307
25% | 3466.632 | 14.2399 | 14.6727 | 16.4323 | 15.8893 | 12.9321 | 13.5303 | 13.9102 | 14.3438 | 14.6903 | 14.9162 | 15.454 | 15.826 | 16.0218 | 16.3848 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 16.2791 | 25% | 3659.4958 | 16.0182 | 16.5722 | 18.3367 | 17.7795 | 14.9071 | 15.5096 | 15.9987 | 16.4691 | 16.8764 | 17.0807 | 17.3818 | 17.7263 | 18.0779 | 18.5202 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892 | 18.5892
20% | 3713.9514 | 11.3919 | 11.7381 | 13.1458 | 12.7114 | 10.3457 | 10.8242 | 11.1281 | 11.475 | 11.7523 | 11.9329 | 12.3632 | 12.6608 | 12.8174 | 13.1078 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 13.0233 | 20% | 4005.5161 | 12.8146 | 13.2578 | 14.6694 | 14.2236 | 11.9257 | 12.4077 | 12.799 | 13.1753 | 13.5011 | 13.6646 | 13.9055 | 14.181 | 14.4623 | 14.8161 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714 | 14.8714
15% | 4043.3325 | 8.5439 | 8.8036 | 9.8594 | 9.5336 | 7.7593 | 8.1182 | 8.3461 | 8.6063 | 8.8142 | 8.9497 | 9.2724 | 9.4956 | 9.6131 | 9.8309 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 9.7675 | 15% | 4281.1979 | 9.6109 | 9.9433 | 11.002 | 10.6677 | 8.9442 | 9.3058 | 9.5992 | 9.8815 | 10.1258 | 10.2484 | 10.4291 | 10.6358 | 10.8467 | 11.1121 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535 | 11.1535
10% | 4350.7801 | 5.6959 | 5.8691 | 6.5729 | 6.3557 | 5.1728 | 5.4121 | 5.5641 | 5.7375 | 5.8761 | 5.9665 | 6.1816 | 6.3304 | 6.4087 | 6.5539 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 6.5117 | 10% | 4391.6218 | 6.4073 | 6.6289 | 7.3347 | 7.1118 | 5.9628 | 6.2038 | 6.3995 | 6.5877 | 6.7506 | 6.8323 | 6.9527 | 7.0905 | 7.2312 | 7.4081 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357 | 7.4357
5% | 4391.6218 | 2.848 | 2.9345 | 3.2865 | 3.1779 | 2.5864 | 2.7061 | 2.782 | 2.8688 | 2.9381 | 2.9832 | 3.0908 | 3.1652 | 3.2044 | 3.277 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 3.2558 | 5% | 4391.6218 | 3.2036 | 3.3144 | 3.6673 | 3.5559 | 2.9814 | 3.1019 | 3.1997 | 3.2938 | 3.3753 | 3.4161 | 3.4764 | 3.5453 | 3.6156 | 3.704 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178 | 3.7178
9.992e-14% | 4391.6218 | 5.6914e-14 | 5.8644e-14 | 6.5677e-14 | 6.3506e-14 | 5.1687e-14 | 5.4078e-14 | 5.5596e-14 | 5.7329e-14 | 5.8714e-14 | 5.9617e-14 | 6.1767e-14 | 6.3253e-14 | 6.4036e-14 | 6.5487e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 6.5064e-14 | 9.992e-14% | 4391.6218 | 6.4022e-14 | 6.6236e-14 | 7.3288e-14 | 7.1061e-14 | 5.9581e-14 | 6.1989e-14 | 6.3944e-14 | 6.5824e-14 | 6.7452e-14 | 6.8268e-14 | 6.9472e-14 | 7.0849e-14 | 7.2254e-14 | 7.4021e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14 | 7.4297e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 100% | 0 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
99% | 0.8916 | 49.9025 | 52.2901 | 59.4299 | 65.4429 | 68.6867 | 71.0307 | 73.7326 | 75.7542 | 77.9829 | 79.1511 | 80.1629 | 82.6675 | 81.157 | 85.2413 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 99% | 0.8916 | 53.1132 | 55.592 | 62.6764 | 68.9168 | 72.1719 | 74.8116 | 77.3219 | 79.4606 | 81.6883 | 82.6647 | 83.9974 | 86.4681 | 85.6602 | 88.8872 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486
98% | 3.5664 | 49.3984 | 51.7619 | 58.8296 | 64.7818 | 67.9929 | 70.3132 | 72.9878 | 74.989 | 77.1952 | 78.3516 | 79.3532 | 81.8324 | 80.3372 | 84.3803 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 98% | 3.5664 | 52.5767 | 55.0305 | 62.0433 | 68.2206 | 71.4429 | 74.0559 | 76.5409 | 78.658 | 80.8632 | 81.8297 | 83.1489 | 85.5946 | 84.795 | 87.9894 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832
97% | 4.7552 | 48.8943 | 51.2337 | 58.2293 | 64.1208 | 67.2991 | 69.5957 | 72.243 | 74.2238 | 76.4075 | 77.5521 | 78.5434 | 80.9974 | 79.5174 | 83.5193 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 97% | 4.7552 | 52.0402 | 54.469 | 61.4102 | 67.5245 | 70.7139 | 73.3003 | 75.7598 | 77.8554 | 80.038 | 80.9947 | 82.3005 | 84.7212 | 83.9297 | 87.0915 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153
95% | 7.7272 | 47.8862 | 50.1774 | 57.0287 | 62.7987 | 65.9115 | 68.1608 | 70.7535 | 72.6934 | 74.8321 | 75.9531 | 76.924 | 79.3274 | 77.8779 | 81.7972 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 95% | 7.7272 | 50.9672 | 53.3459 | 60.144 | 66.1322 | 69.2559 | 71.7889 | 74.1978 | 76.2501 | 78.3878 | 79.3247 | 80.6036 | 82.9744 | 82.1992 | 85.2958 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082
90% | 39.2302 | 45.3659 | 47.5365 | 54.0272 | 59.4935 | 62.4425 | 64.5734 | 67.0296 | 68.8674 | 70.8936 | 71.9556 | 72.8753 | 75.1522 | 73.7791 | 77.4921 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 90% | 39.2302 | 48.2848 | 50.5382 | 56.9785 | 62.6516 | 65.6108 | 68.0106 | 70.2926 | 72.2369 | 74.2621 | 75.1497 | 76.3613 | 78.6073 | 77.8729 | 80.8066 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987
85% | 117.6906 | 42.8456 | 44.8955 | 51.0257 | 56.1883 | 58.9735 | 60.986 | 63.3057 | 65.0415 | 66.9551 | 67.958 | 68.8267 | 70.9771 | 69.6802 | 73.187 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 85% | 117.6906 | 45.6023 | 47.7305 | 53.813 | 59.171 | 61.9658 | 64.2322 | 66.3875 | 68.2238 | 70.1364 | 70.9748 | 72.119 | 74.2403 | 73.5467 | 76.3173 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155
80% | 268.3703 | 40.3252 | 42.2546 | 48.0242 | 52.8831 | 55.5044 | 57.3985 | 59.5819 | 61.2155 | 63.0165 | 63.9605 | 64.7781 | 66.802 | 65.5814 | 68.8819 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 80% | 268.3703 | 42.9198 | 44.9228 | 50.6476 | 55.6903 | 58.3207 | 60.4538 | 62.4824 | 64.2106 | 66.0108 | 66.7998 | 67.8767 | 69.8732 | 69.2204 | 71.8281 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322
75% | 455.9026 | 37.8049 | 39.6137 | 45.0227 | 49.5779 | 52.0354 | 53.8111 | 55.858 | 57.3895 | 59.078 | 59.963 | 60.7295 | 62.6269 | 61.4826 | 64.5768 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 75% | 455.9026 | 40.2373 | 42.1152 | 47.4821 | 52.2097 | 54.6757 | 56.6755 | 58.5772 | 60.1974 | 61.8851 | 62.6248 | 63.6344 | 65.5061 | 64.8941 | 67.3388 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749
70% | 690.9866 | 35.2846 | 36.9728 | 42.0212 | 46.2727 | 48.5664 | 50.2237 | 52.1341 | 53.5636 | 55.1395 | 55.9654 | 56.6808 | 58.4517 | 57.3837 | 60.2717 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 70% | 690.9866 | 37.5548 | 39.3075 | 44.3166 | 48.729 | 51.0307 | 52.8971 | 54.6721 | 56.1843 | 57.7594 | 58.4498 | 59.3921 | 61.139 | 60.5678 | 62.8495 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657
65% | 967.6784 | 32.7642 | 34.3319 | 39.0196 | 42.9675 | 45.0973 | 46.6363 | 48.4103 | 49.7376 | 51.2009 | 51.9679 | 52.6322 | 54.2766 | 53.2849 | 55.9665 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 65% | 967.6784 | 34.8723 | 36.4998 | 41.1511 | 45.2484 | 47.3856 | 49.1187 | 50.7669 | 52.1711 | 53.6337 | 54.2748 | 55.1498 | 56.772 | 56.2416 | 58.3603 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824
60% | 1292.8136 | 30.2439 | 31.691 | 36.0181 | 39.6623 | 41.6283 | 43.0489 | 44.6864 | 45.9116 | 47.2624 | 47.9704 | 48.5836 | 50.1015 | 49.1861 | 51.6614 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 60% | 1292.8136 | 32.1898 | 33.6921 | 37.9857 | 41.7677 | 43.7406 | 45.3404 | 46.8618 | 48.1579 | 49.5081 | 50.0998 | 50.9075 | 52.4049 | 51.9153 | 53.871 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992
55% | 1647.0743 | 27.7236 | 29.0501 | 33.0166 | 36.3571 | 38.1593 | 39.4615 | 40.9625 | 42.0857 | 43.3239 | 43.9728 | 44.5349 | 45.9264 | 45.0872 | 47.3563 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 55% | 1647.0743 | 29.5074 | 30.8845 | 34.8202 | 38.2871 | 40.0955 | 41.562 | 42.9566 | 44.1448 | 45.3824 | 45.9248 | 46.6652 | 48.0378 | 47.589 | 49.3818 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159
50% | 2104.1657 | 25.2033 | 26.4091 | 30.0151 | 33.0519 | 34.6903 | 35.8741 | 37.2387 | 38.2597 | 39.3853 | 39.9753 | 40.4863 | 41.7512 | 40.9884 | 43.0512 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 50% | 2104.1657 | 26.8249 | 28.0768 | 31.6547 | 34.8064 | 36.4505 | 37.7836 | 39.0515 | 40.1316 | 41.2567 | 41.7499 | 42.4229 | 43.6707 | 43.2627 | 44.8925 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326
45% | 2736.0097 | 22.6829 | 23.7682 | 27.0136 | 29.7468 | 31.2212 | 32.2867 | 33.5148 | 34.4337 | 35.4468 | 35.9778 | 36.4377 | 37.5761 | 36.8895 | 38.7461 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 45% | 2736.0097 | 24.1424 | 25.2691 | 28.4893 | 31.3258 | 32.8054 | 34.0053 | 35.1463 | 36.1185 | 37.1311 | 37.5749 | 38.1806 | 39.3037 | 38.9365 | 40.4033 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494
40% | 3483.7613 | 20.1626 | 21.1273 | 24.0121 | 26.4416 | 27.7522 | 28.6993 | 29.7909 | 30.6078 | 31.5083 | 31.9802 | 32.389 | 33.401 | 32.7907 | 34.4409 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 40% | 3483.7613 | 21.4599 | 22.4614 | 25.3238 | 27.8452 | 29.1604 | 30.2269 | 31.2412 | 32.1053 | 33.0054 | 33.3999 | 33.9383 | 34.9366 | 34.6102 | 35.914 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661
35% | 3830.2948 | 17.6423 | 18.4864 | 21.0106 | 23.1364 | 24.2832 | 25.1119 | 26.0671 | 26.7818 | 27.5697 | 27.9827 | 28.3404 | 29.2259 | 28.6919 | 30.1358 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 35% | 3830.2948 | 18.7774 | 19.6537 | 22.1583 | 24.3645 | 25.5153 | 26.4485 | 27.336 | 28.0921 | 28.8797 | 29.2249 | 29.696 | 30.5695 | 30.2839 | 31.4248 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828
30% | 3953.6322 | 15.122 | 15.8455 | 18.0091 | 19.8312 | 20.8142 | 21.5245 | 22.3432 | 22.9558 | 23.6312 | 23.9852 | 24.2918 | 25.0507 | 24.593 | 25.8307 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 30% | 3953.6322 | 16.0949 | 16.8461 | 18.9928 | 20.8839 | 21.8703 | 22.6702 | 23.4309 | 24.079 | 24.754 | 25.0499 | 25.4538 | 26.2024 | 25.9576 | 26.9355 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996
25% | 4060.9208 | 12.6016 | 13.2046 | 15.0076 | 16.526 | 17.3451 | 17.937 | 18.6193 | 19.1298 | 19.6927 | 19.9877 | 20.2432 | 20.8756 | 20.4942 | 21.5256 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 25% | 4060.9208 | 13.4124 | 14.0384 | 15.8274 | 17.4032 | 18.2252 | 18.8918 | 19.5257 | 20.0658 | 20.6284 | 20.8749 | 21.2115 | 21.8354 | 21.6314 | 22.4463 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163
20% | 4165.2375 | 10.0813 | 10.5637 | 12.006 | 13.2208 | 13.8761 | 14.3496 | 14.8955 | 15.3039 | 15.7541 | 15.9901 | 16.1945 | 16.7005 | 16.3954 | 17.2205 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 20% | 4165.2375 | 10.7299 | 11.2307 | 12.6619 | 13.9226 | 14.5802 | 15.1135 | 15.6206 | 16.0526 | 16.5027 | 16.6999 | 16.9692 | 17.4683 | 17.3051 | 17.957 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331
15% | 4270.4458 | 7.561 | 7.9227 | 9.0045 | 9.9156 | 10.4071 | 10.7622 | 11.1716 | 11.4779 | 11.8156 | 11.9926 | 12.1459 | 12.5254 | 12.2965 | 12.9154 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 15% | 4270.4458 | 8.0475 | 8.423 | 9.4964 | 10.4419 | 10.9351 | 11.3351 | 11.7154 | 12.0395 | 12.377 | 12.525 | 12.7269 | 13.1012 | 12.9788 | 13.4678 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498
10% | 4373.8709 | 5.0407 | 5.2818 | 6.003 | 6.6104 | 6.9381 | 7.1748 | 7.4477 | 7.6519 | 7.8771 | 7.9951 | 8.0973 | 8.3502 | 8.1977 | 8.6102 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 10% | 4373.8709 | 5.365 | 5.6154 | 6.3309 | 6.9613 | 7.2901 | 7.5567 | 7.8103 | 8.0263 | 8.2513 | 8.35 | 8.4846 | 8.7341 | 8.6525 | 8.9785 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665
5% | 4391.7028 | 2.5203 | 2.6409 | 3.0015 | 3.3052 | 3.469 | 3.5874 | 3.7239 | 3.826 | 3.9385 | 3.9975 | 4.0486 | 4.1751 | 4.0988 | 4.3051 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 5% | 4391.7028 | 2.6825 | 2.8077 | 3.1655 | 3.4806 | 3.645 | 3.7784 | 3.9051 | 4.0132 | 4.1257 | 4.175 | 4.2423 | 4.3671 | 4.3263 | 4.4893 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833
9.992e-14% | 4391.7028 | 5.0366e-14 | 5.2776e-14 | 5.9982e-14 | 6.6051e-14 | 6.9325e-14 | 7.1691e-14 | 7.4418e-14 | 7.6458e-14 | 7.8708e-14 | 7.9887e-14 | 8.0908e-14 | 8.3436e-14 | 8.1911e-14 | 8.6034e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.992e-14% | 4391.7028 | 5.3607e-14 | 5.6109e-14 | 6.3259e-14 | 6.9557e-14 | 7.2843e-14 | 7.5507e-14 | 7.8041e-14 | 8.0199e-14 | 8.2447e-14 | 8.3433e-14 | 8.4778e-14 | 8.7272e-14 | 8.6456e-14 | 8.9713e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 100% | 0 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068
99% | 0 | 56.3898 | 58.1038 | 65.0718 | 70.0992 | 72.7437 | 75.1124 | 76.6167 | 78.334 | 79.7062 | 80.6005 | 82.7304 | 84.2035 | 84.9787 | 86.4162 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 99% | 0.75633 | 63.4323 | 65.6261 | 72.6135 | 77.5841 | 80.5645 | 82.9506 | 84.8874 | 86.7503 | 88.363 | 89.1721 | 90.3645 | 91.7286 | 93.121 | 94.8723 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457
98% | 0.37816 | 55.8202 | 57.5169 | 64.4145 | 69.3911 | 72.0089 | 74.3537 | 75.8428 | 77.5427 | 78.9011 | 79.7863 | 81.8947 | 83.3529 | 84.1203 | 85.5433 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 98% | 1.1345 | 62.7915 | 64.9632 | 71.88 | 76.8005 | 79.7507 | 82.1127 | 84.0299 | 85.874 | 87.4705 | 88.2714 | 89.4517 | 90.8021 | 92.1803 | 93.914 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847
97% | 0.75633 | 55.2506 | 56.93 | 63.7572 | 68.683 | 71.2741 | 73.595 | 75.0689 | 76.7515 | 78.096 | 78.9722 | 81.059 | 82.5024 | 83.2619 | 84.6705 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 97% | 1.8908 | 62.1508 | 64.3003 | 71.1466 | 76.0168 | 78.9369 | 81.2748 | 83.1725 | 84.9977 | 86.5779 | 87.3707 | 88.539 | 89.8755 | 91.2397 | 92.9557 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236
95% | 1.8908 | 54.1115 | 55.7561 | 62.4427 | 67.2669 | 69.8045 | 72.0775 | 73.5211 | 75.169 | 76.4857 | 77.3439 | 79.3877 | 80.8013 | 81.5452 | 82.9247 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 95% | 3.4035 | 60.8693 | 62.9745 | 69.6796 | 74.4494 | 77.3094 | 79.599 | 81.4576 | 83.2452 | 84.7928 | 85.5692 | 86.7134 | 88.0224 | 89.3585 | 91.0391 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015
90% | 4.538 | 51.2635 | 52.8216 | 59.1562 | 63.7265 | 66.1306 | 68.284 | 69.6515 | 71.2127 | 72.4602 | 73.2732 | 75.2094 | 76.5486 | 77.2533 | 78.5602 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 90% | 9.0759 | 57.6657 | 59.6601 | 66.0123 | 70.531 | 73.2405 | 75.4096 | 77.1703 | 78.8639 | 80.33 | 81.0656 | 82.1496 | 83.3897 | 84.6554 | 86.2476 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961
85% | 9.0759 | 48.4155 | 49.8871 | 55.8697 | 60.1862 | 62.4567 | 64.4904 | 65.782 | 67.2565 | 68.4346 | 69.2024 | 71.0311 | 72.2959 | 72.9615 | 74.1958 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 85% | 16.2611 | 54.462 | 56.3456 | 62.3449 | 66.6126 | 69.1716 | 71.2202 | 72.8831 | 74.4826 | 75.8673 | 76.5619 | 77.5857 | 78.7569 | 79.9523 | 81.456 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908
80% | 27.606 | 45.5675 | 46.9525 | 52.5833 | 56.6458 | 58.7827 | 60.6969 | 61.9125 | 63.3002 | 64.409 | 65.1317 | 66.8528 | 68.0432 | 68.6696 | 69.8313 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 80% | 24.9588 | 51.2584 | 53.0312 | 58.6776 | 62.6943 | 65.1026 | 67.0308 | 68.5959 | 70.1012 | 71.4045 | 72.0583 | 73.0218 | 74.1241 | 75.2493 | 76.6645 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854
75% | 57.481 | 42.7196 | 44.018 | 49.2968 | 53.1054 | 55.1088 | 56.9033 | 58.043 | 59.3439 | 60.3835 | 61.061 | 62.6745 | 63.7905 | 64.3778 | 65.4668 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 75% | 32.9003 | 48.0547 | 49.7167 | 55.0102 | 58.7759 | 61.0337 | 62.8413 | 64.3086 | 65.7199 | 66.9417 | 67.5547 | 68.458 | 69.4914 | 70.5462 | 71.873 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801
70% | 106.2642 | 39.8716 | 41.0835 | 46.0104 | 49.5651 | 51.4349 | 53.1098 | 54.1734 | 55.3877 | 56.3579 | 56.9902 | 58.4962 | 59.5378 | 60.0859 | 61.1024 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 70% | 41.9762 | 44.8511 | 46.4023 | 51.3429 | 54.8575 | 56.9648 | 58.6519 | 60.0214 | 61.3386 | 62.4789 | 63.051 | 63.8941 | 64.8586 | 65.8431 | 67.0814 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748
65% | 201.9397 | 37.0236 | 38.1489 | 42.7239 | 46.0247 | 47.761 | 49.3162 | 50.3039 | 51.4314 | 52.3323 | 52.9195 | 54.3179 | 55.2851 | 55.7941 | 56.7379 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 65% | 67.6914 | 41.6474 | 43.0878 | 47.6755 | 50.9391 | 52.8959 | 54.4625 | 55.7341 | 56.9573 | 58.0161 | 58.5474 | 59.3302 | 60.2259 | 61.14 | 62.2899 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694
60% | 402.745 | 34.1757 | 35.2144 | 39.4375 | 42.4843 | 44.0871 | 45.5227 | 46.4344 | 47.4751 | 48.3068 | 48.8488 | 50.1396 | 51.0324 | 51.5022 | 52.3735 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 60% | 98.7009 | 38.4438 | 39.7734 | 44.0082 | 47.0207 | 48.827 | 50.2731 | 51.4469 | 52.5759 | 53.5534 | 54.0437 | 54.7664 | 55.5931 | 56.4369 | 57.4984 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641
55% | 655.7369 | 31.3277 | 32.2799 | 36.151 | 38.944 | 40.4131 | 41.7291 | 42.5648 | 43.5189 | 44.2812 | 44.778 | 45.9613 | 46.7797 | 47.2104 | 48.009 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 55% | 153.5347 | 35.2401 | 36.4589 | 40.3408 | 43.1023 | 44.7581 | 46.0836 | 47.1596 | 48.1946 | 49.0906 | 49.5401 | 50.2025 | 50.9604 | 51.7339 | 52.7068 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587
50% | 981.7145 | 28.4797 | 29.3453 | 32.8646 | 35.4036 | 36.7392 | 37.9355 | 38.6953 | 39.5626 | 40.2557 | 40.7073 | 41.783 | 42.527 | 42.9185 | 43.6446 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 50% | 258.2862 | 32.0365 | 33.1445 | 36.6735 | 39.1839 | 40.6891 | 41.8942 | 42.8724 | 43.8133 | 44.6278 | 45.0364 | 45.6386 | 46.3276 | 47.0308 | 47.9153 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534
45% | 1622.7029 | 25.6317 | 26.4108 | 29.5781 | 31.8633 | 33.0653 | 34.142 | 34.8258 | 35.6064 | 36.2301 | 36.6366 | 37.6047 | 38.2743 | 38.6267 | 39.2801 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 45% | 488.9664 | 28.8328 | 29.83 | 33.0061 | 35.2655 | 36.6202 | 37.7048 | 38.5852 | 39.4319 | 40.165 | 40.5328 | 41.0748 | 41.6948 | 42.3277 | 43.1238 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481
40% | 2442.9413 | 22.7838 | 23.4763 | 26.2916 | 28.3229 | 29.3914 | 30.3484 | 30.9562 | 31.6501 | 32.2045 | 32.5659 | 33.4264 | 34.0216 | 34.3348 | 34.9157 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 40% | 928.0152 | 25.6292 | 26.5156 | 29.3388 | 31.3471 | 32.5513 | 33.5154 | 34.2979 | 35.0506 | 35.7022 | 36.0292 | 36.5109 | 37.0621 | 37.6246 | 38.3322 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427
35% | 3006.7842 | 19.9358 | 20.5417 | 23.0052 | 24.7825 | 25.7175 | 26.5549 | 27.0867 | 27.6938 | 28.179 | 28.4951 | 29.2481 | 29.7689 | 30.043 | 30.5512 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 35% | 1530.4309 | 22.4255 | 23.2011 | 25.6714 | 27.4287 | 28.4824 | 29.326 | 30.0107 | 30.6693 | 31.2395 | 31.5255 | 31.9471 | 32.4293 | 32.9215 | 33.5407 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374
30% | 3276.4154 | 17.0878 | 17.6072 | 19.7187 | 21.2422 | 22.0435 | 22.7613 | 23.2172 | 23.7376 | 24.1534 | 24.4244 | 25.0698 | 25.5162 | 25.7511 | 26.1867 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 30% | 2592.3162 | 19.2219 | 19.8867 | 22.0041 | 23.5103 | 24.4135 | 25.1365 | 25.7234 | 26.288 | 26.7767 | 27.0219 | 27.3832 | 27.7966 | 28.2185 | 28.7492 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832
25% | 3466.632 | 14.2399 | 14.6727 | 16.4323 | 17.7018 | 18.3696 | 18.9678 | 19.3477 | 19.7813 | 20.1278 | 20.3537 | 20.8915 | 21.2635 | 21.4593 | 21.8223 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 25% | 3659.4958 | 16.0182 | 16.5722 | 18.3367 | 19.592 | 20.3446 | 20.9471 | 21.4362 | 21.9066 | 22.3139 | 22.5182 | 22.8193 | 23.1638 | 23.5154 | 23.9577 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267
20% | 3713.9514 | 11.3919 | 11.7381 | 13.1458 | 14.1614 | 14.6957 | 15.1742 | 15.4781 | 15.825 | 16.1023 | 16.2829 | 16.7132 | 17.0108 | 17.1674 | 17.4578 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 20% | 4005.5161 | 12.8146 | 13.2578 | 14.6694 | 15.6736 | 16.2757 | 16.7577 | 17.149 | 17.5253 | 17.8511 | 18.0146 | 18.2555 | 18.531 | 18.8123 | 19.1661 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214
15% | 4043.3325 | 8.5439 | 8.8036 | 9.8594 | 10.6211 | 11.0218 | 11.3807 | 11.6086 | 11.8688 | 12.0767 | 12.2122 | 12.5349 | 12.7581 | 12.8756 | 13.0934 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 15% | 4281.1979 | 9.6109 | 9.9433 | 11.002 | 11.7552 | 12.2067 | 12.5683 | 12.8617 | 13.144 | 13.3883 | 13.5109 | 13.6916 | 13.8983 | 14.1092 | 14.3746 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416
10% | 4350.7801 | 5.6959 | 5.8691 | 6.5729 | 7.0807 | 7.3478 | 7.5871 | 7.7391 | 7.9125 | 8.0511 | 8.1415 | 8.3566 | 8.5054 | 8.5837 | 8.7289 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 10% | 4391.6218 | 6.4073 | 6.6289 | 7.3347 | 7.8368 | 8.1378 | 8.3788 | 8.5745 | 8.7627 | 8.9256 | 9.0073 | 9.1277 | 9.2655 | 9.4062 | 9.5831 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107
5% | 4391.6218 | 2.848 | 2.9345 | 3.2865 | 3.5404 | 3.6739 | 3.7936 | 3.8695 | 3.9563 | 4.0256 | 4.0707 | 4.1783 | 4.2527 | 4.2919 | 4.3645 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 5% | 4391.6218 | 3.2036 | 3.3144 | 3.6673 | 3.9184 | 4.0689 | 4.1894 | 4.2872 | 4.3813 | 4.4628 | 4.5036 | 4.5639 | 4.6328 | 4.7031 | 4.7915 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053
9.992e-14% | 4391.6218 | 5.6914e-14 | 5.8644e-14 | 6.5677e-14 | 7.0751e-14 | 7.342e-14 | 7.581e-14 | 7.7329e-14 | 7.9062e-14 | 8.0447e-14 | 8.135e-14 | 8.3499e-14 | 8.4986e-14 | 8.5768e-14 | 8.7219e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 9.992e-14% | 4391.6218 | 6.4022e-14 | 6.6236e-14 | 7.3288e-14 | 7.8305e-14 | 8.1313e-14 | 8.3721e-14 | 8.5676e-14 | 8.7557e-14 | 8.9184e-14 | 9.0001e-14 | 9.1204e-14 | 9.2581e-14 | 9.3986e-14 | 9.5754e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 100% | 0 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
99% | 0.8916 | 49.9025 | 52.2901 | 59.4299 | 65.4429 | 68.6867 | 71.0307 | 73.7326 | 75.7542 | 77.9829 | 79.1511 | 80.1629 | 82.6675 | 81.157 | 85.2413 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 99% | 0.8916 | 53.1132 | 55.592 | 62.6764 | 68.9168 | 72.1719 | 74.8116 | 77.3219 | 79.4606 | 81.6883 | 82.6647 | 83.9974 | 86.4681 | 85.6602 | 88.8872 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486
98% | 3.5664 | 49.3984 | 51.7619 | 58.8296 | 64.7818 | 67.9929 | 70.3132 | 72.9878 | 74.989 | 77.1952 | 78.3516 | 79.3532 | 81.8324 | 80.3372 | 84.3803 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 98% | 3.5664 | 52.5767 | 55.0305 | 62.0433 | 68.2206 | 71.4429 | 74.0559 | 76.5409 | 78.658 | 80.8632 | 81.8297 | 83.1489 | 85.5946 | 84.795 | 87.9894 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832
97% | 4.7552 | 48.8943 | 51.2337 | 58.2293 | 64.1208 | 67.2991 | 69.5957 | 72.243 | 74.2238 | 76.4075 | 77.5521 | 78.5434 | 80.9974 | 79.5174 | 83.5193 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 97% | 4.7552 | 52.0402 | 54.469 | 61.4102 | 67.5245 | 70.7139 | 73.3003 | 75.7598 | 77.8554 | 80.038 | 80.9947 | 82.3005 | 84.7212 | 83.9297 | 87.0915 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153
95% | 7.7272 | 47.8862 | 50.1774 | 57.0287 | 62.7987 | 65.9115 | 68.1608 | 70.7535 | 72.6934 | 74.8321 | 75.9531 | 76.924 | 79.3274 | 77.8779 | 81.7972 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 95% | 7.7272 | 50.9672 | 53.3459 | 60.144 | 66.1322 | 69.2559 | 71.7889 | 74.1978 | 76.2501 | 78.3878 | 79.3247 | 80.6036 | 82.9744 | 82.1992 | 85.2958 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082
90% | 39.2302 | 45.3659 | 47.5365 | 54.0272 | 59.4935 | 62.4425 | 64.5734 | 67.0296 | 68.8674 | 70.8936 | 71.9556 | 72.8753 | 75.1522 | 73.7791 | 77.4921 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 90% | 39.2302 | 48.2848 | 50.5382 | 56.9785 | 62.6516 | 65.6108 | 68.0106 | 70.2926 | 72.2369 | 74.2621 | 75.1497 | 76.3613 | 78.6073 | 77.8729 | 80.8066 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987
85% | 117.6906 | 42.8456 | 44.8955 | 51.0257 | 56.1883 | 58.9735 | 60.986 | 63.3057 | 65.0415 | 66.9551 | 67.958 | 68.8267 | 70.9771 | 69.6802 | 73.187 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 85% | 117.6906 | 45.6023 | 47.7305 | 53.813 | 59.171 | 61.9658 | 64.2322 | 66.3875 | 68.2238 | 70.1364 | 70.9748 | 72.119 | 74.2403 | 73.5467 | 76.3173 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155
80% | 268.3703 | 40.3252 | 42.2546 | 48.0242 | 52.8831 | 55.5044 | 57.3985 | 59.5819 | 61.2155 | 63.0165 | 63.9605 | 64.7781 | 66.802 | 65.5814 | 68.8819 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 80% | 268.3703 | 42.9198 | 44.9228 | 50.6476 | 55.6903 | 58.3207 | 60.4538 | 62.4824 | 64.2106 | 66.0108 | 66.7998 | 67.8767 | 69.8732 | 69.2204 | 71.8281 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322
75% | 455.9026 | 37.8049 | 39.6137 | 45.0227 | 49.5779 | 52.0354 | 53.8111 | 55.858 | 57.3895 | 59.078 | 59.963 | 60.7295 | 62.6269 | 61.4826 | 64.5768 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 75% | 455.9026 | 40.2373 | 42.1152 | 47.4821 | 52.2097 | 54.6757 | 56.6755 | 58.5772 | 60.1974 | 61.8851 | 62.6248 | 63.6344 | 65.5061 | 64.8941 | 67.3388 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749
70% | 690.9866 | 35.2846 | 36.9728 | 42.0212 | 46.2727 | 48.5664 | 50.2237 | 52.1341 | 53.5636 | 55.1395 | 55.9654 | 56.6808 | 58.4517 | 57.3837 | 60.2717 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 70% | 690.9866 | 37.5548 | 39.3075 | 44.3166 | 48.729 | 51.0307 | 52.8971 | 54.6721 | 56.1843 | 57.7594 | 58.4498 | 59.3921 | 61.139 | 60.5678 | 62.8495 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657
65% | 967.6784 | 32.7642 | 34.3319 | 39.0196 | 42.9675 | 45.0973 | 46.6363 | 48.4103 | 49.7376 | 51.2009 | 51.9679 | 52.6322 | 54.2766 | 53.2849 | 55.9665 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 65% | 967.6784 | 34.8723 | 36.4998 | 41.1511 | 45.2484 | 47.3856 | 49.1187 | 50.7669 | 52.1711 | 53.6337 | 54.2748 | 55.1498 | 56.772 | 56.2416 | 58.3603 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824
60% | 1292.8136 | 30.2439 | 31.691 | 36.0181 | 39.6623 | 41.6283 | 43.0489 | 44.6864 | 45.9116 | 47.2624 | 47.9704 | 48.5836 | 50.1015 | 49.1861 | 51.6614 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 60% | 1292.8136 | 32.1898 | 33.6921 | 37.9857 | 41.7677 | 43.7406 | 45.3404 | 46.8618 | 48.1579 | 49.5081 | 50.0998 | 50.9075 | 52.4049 | 51.9153 | 53.871 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992
55% | 1647.0743 | 27.7236 | 29.0501 | 33.0166 | 36.3571 | 38.1593 | 39.4615 | 40.9625 | 42.0857 | 43.3239 | 43.9728 | 44.5349 | 45.9264 | 45.0872 | 47.3563 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 55% | 1647.0743 | 29.5074 | 30.8845 | 34.8202 | 38.2871 | 40.0955 | 41.562 | 42.9566 | 44.1448 | 45.3824 | 45.9248 | 46.6652 | 48.0378 | 47.589 | 49.3818 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159
50% | 2104.1657 | 25.2033 | 26.4091 | 30.0151 | 33.0519 | 34.6903 | 35.8741 | 37.2387 | 38.2597 | 39.3853 | 39.9753 | 40.4863 | 41.7512 | 40.9884 | 43.0512 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 50% | 2104.1657 | 26.8249 | 28.0768 | 31.6547 | 34.8064 | 36.4505 | 37.7836 | 39.0515 | 40.1316 | 41.2567 | 41.7499 | 42.4229 | 43.6707 | 43.2627 | 44.8925 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326
45% | 2736.0097 | 22.6829 | 23.7682 | 27.0136 | 29.7468 | 31.2212 | 32.2867 | 33.5148 | 34.4337 | 35.4468 | 35.9778 | 36.4377 | 37.5761 | 36.8895 | 38.7461 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 45% | 2736.0097 | 24.1424 | 25.2691 | 28.4893 | 31.3258 | 32.8054 | 34.0053 | 35.1463 | 36.1185 | 37.1311 | 37.5749 | 38.1806 | 39.3037 | 38.9365 | 40.4033 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494
40% | 3483.7613 | 20.1626 | 21.1273 | 24.0121 | 26.4416 | 27.7522 | 28.6993 | 29.7909 | 30.6078 | 31.5083 | 31.9802 | 32.389 | 33.401 | 32.7907 | 34.4409 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 40% | 3483.7613 | 21.4599 | 22.4614 | 25.3238 | 27.8452 | 29.1604 | 30.2269 | 31.2412 | 32.1053 | 33.0054 | 33.3999 | 33.9383 | 34.9366 | 34.6102 | 35.914 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661
35% | 3830.2948 | 17.6423 | 18.4864 | 21.0106 | 23.1364 | 24.2832 | 25.1119 | 26.0671 | 26.7818 | 27.5697 | 27.9827 | 28.3404 | 29.2259 | 28.6919 | 30.1358 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 35% | 3830.2948 | 18.7774 | 19.6537 | 22.1583 | 24.3645 | 25.5153 | 26.4485 | 27.336 | 28.0921 | 28.8797 | 29.2249 | 29.696 | 30.5695 | 30.2839 | 31.4248 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828
30% | 3953.6322 | 15.122 | 15.8455 | 18.0091 | 19.8312 | 20.8142 | 21.5245 | 22.3432 | 22.9558 | 23.6312 | 23.9852 | 24.2918 | 25.0507 | 24.593 | 25.8307 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 30% | 3953.6322 | 16.0949 | 16.8461 | 18.9928 | 20.8839 | 21.8703 | 22.6702 | 23.4309 | 24.079 | 24.754 | 25.0499 | 25.4538 | 26.2024 | 25.9576 | 26.9355 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996
25% | 4060.9208 | 12.6016 | 13.2046 | 15.0076 | 16.526 | 17.3451 | 17.937 | 18.6193 | 19.1298 | 19.6927 | 19.9877 | 20.2432 | 20.8756 | 20.4942 | 21.5256 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 25% | 4060.9208 | 13.4124 | 14.0384 | 15.8274 | 17.4032 | 18.2252 | 18.8918 | 19.5257 | 20.0658 | 20.6284 | 20.8749 | 21.2115 | 21.8354 | 21.6314 | 22.4463 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163
20% | 4165.2375 | 10.0813 | 10.5637 | 12.006 | 13.2208 | 13.8761 | 14.3496 | 14.8955 | 15.3039 | 15.7541 | 15.9901 | 16.1945 | 16.7005 | 16.3954 | 17.2205 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 20% | 4165.2375 | 10.7299 | 11.2307 | 12.6619 | 13.9226 | 14.5802 | 15.1135 | 15.6206 | 16.0526 | 16.5027 | 16.6999 | 16.9692 | 17.4683 | 17.3051 | 17.957 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331
15% | 4270.4458 | 7.561 | 7.9227 | 9.0045 | 9.9156 | 10.4071 | 10.7622 | 11.1716 | 11.4779 | 11.8156 | 11.9926 | 12.1459 | 12.5254 | 12.2965 | 12.9154 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 15% | 4270.4458 | 8.0475 | 8.423 | 9.4964 | 10.4419 | 10.9351 | 11.3351 | 11.7154 | 12.0395 | 12.377 | 12.525 | 12.7269 | 13.1012 | 12.9788 | 13.4678 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498
10% | 4373.8709 | 5.0407 | 5.2818 | 6.003 | 6.6104 | 6.9381 | 7.1748 | 7.4477 | 7.6519 | 7.8771 | 7.9951 | 8.0973 | 8.3502 | 8.1977 | 8.6102 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 10% | 4373.8709 | 5.365 | 5.6154 | 6.3309 | 6.9613 | 7.2901 | 7.5567 | 7.8103 | 8.0263 | 8.2513 | 8.35 | 8.4846 | 8.7341 | 8.6525 | 8.9785 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665
5% | 4391.7028 | 2.5203 | 2.6409 | 3.0015 | 3.3052 | 3.469 | 3.5874 | 3.7239 | 3.826 | 3.9385 | 3.9975 | 4.0486 | 4.1751 | 4.0988 | 4.3051 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 5% | 4391.7028 | 2.6825 | 2.8077 | 3.1655 | 3.4806 | 3.645 | 3.7784 | 3.9051 | 4.0132 | 4.1257 | 4.175 | 4.2423 | 4.3671 | 4.3263 | 4.4893 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833
9.992e-14% | 4391.7028 | 5.0366e-14 | 5.2776e-14 | 5.9982e-14 | 6.6051e-14 | 6.9325e-14 | 7.1691e-14 | 7.4418e-14 | 7.6458e-14 | 7.8708e-14 | 7.9887e-14 | 8.0908e-14 | 8.3436e-14 | 8.1911e-14 | 8.6034e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.992e-14% | 4391.7028 | 5.3607e-14 | 5.6109e-14 | 6.3259e-14 | 6.9557e-14 | 7.2843e-14 | 7.5507e-14 | 7.8041e-14 | 8.0199e-14 | 8.2447e-14 | 8.3433e-14 | 8.4778e-14 | 8.7272e-14 | 8.6456e-14 | 8.9713e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 100% | 0 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068
99% | 0 | 56.3898 | 58.1038 | 65.0718 | 70.0992 | 72.7437 | 75.1124 | 76.6167 | 78.334 | 79.7062 | 80.6005 | 82.7304 | 84.2035 | 84.9787 | 86.4162 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 99% | 0.75633 | 63.4323 | 65.6261 | 72.6135 | 77.5841 | 80.5645 | 82.9506 | 84.8874 | 86.7503 | 88.363 | 89.1721 | 90.3645 | 91.7286 | 93.121 | 94.8723 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457
98% | 0.37816 | 55.8202 | 57.5169 | 64.4145 | 69.3911 | 72.0089 | 74.3537 | 75.8428 | 77.5427 | 78.9011 | 79.7863 | 81.8947 | 83.3529 | 84.1203 | 85.5433 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 98% | 1.1345 | 62.7915 | 64.9632 | 71.88 | 76.8005 | 79.7507 | 82.1127 | 84.0299 | 85.874 | 87.4705 | 88.2714 | 89.4517 | 90.8021 | 92.1803 | 93.914 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847
97% | 0.75633 | 55.2506 | 56.93 | 63.7572 | 68.683 | 71.2741 | 73.595 | 75.0689 | 76.7515 | 78.096 | 78.9722 | 81.059 | 82.5024 | 83.2619 | 84.6705 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 97% | 1.8908 | 62.1508 | 64.3003 | 71.1466 | 76.0168 | 78.9369 | 81.2748 | 83.1725 | 84.9977 | 86.5779 | 87.3707 | 88.539 | 89.8755 | 91.2397 | 92.9557 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236
95% | 1.8908 | 54.1115 | 55.7561 | 62.4427 | 67.2669 | 69.8045 | 72.0775 | 73.5211 | 75.169 | 76.4857 | 77.3439 | 79.3877 | 80.8013 | 81.5452 | 82.9247 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 95% | 3.4035 | 60.8693 | 62.9745 | 69.6796 | 74.4494 | 77.3094 | 79.599 | 81.4576 | 83.2452 | 84.7928 | 85.5692 | 86.7134 | 88.0224 | 89.3585 | 91.0391 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015
90% | 4.538 | 51.2635 | 52.8216 | 59.1562 | 63.7265 | 66.1306 | 68.284 | 69.6515 | 71.2127 | 72.4602 | 73.2732 | 75.2094 | 76.5486 | 77.2533 | 78.5602 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 90% | 9.0759 | 57.6657 | 59.6601 | 66.0123 | 70.531 | 73.2405 | 75.4096 | 77.1703 | 78.8639 | 80.33 | 81.0656 | 82.1496 | 83.3897 | 84.6554 | 86.2476 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961
85% | 9.0759 | 48.4155 | 49.8871 | 55.8697 | 60.1862 | 62.4567 | 64.4904 | 65.782 | 67.2565 | 68.4346 | 69.2024 | 71.0311 | 72.2959 | 72.9615 | 74.1958 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 85% | 16.2611 | 54.462 | 56.3456 | 62.3449 | 66.6126 | 69.1716 | 71.2202 | 72.8831 | 74.4826 | 75.8673 | 76.5619 | 77.5857 | 78.7569 | 79.9523 | 81.456 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908
80% | 27.606 | 45.5675 | 46.9525 | 52.5833 | 56.6458 | 58.7827 | 60.6969 | 61.9125 | 63.3002 | 64.409 | 65.1317 | 66.8528 | 68.0432 | 68.6696 | 69.8313 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 80% | 24.9588 | 51.2584 | 53.0312 | 58.6776 | 62.6943 | 65.1026 | 67.0308 | 68.5959 | 70.1012 | 71.4045 | 72.0583 | 73.0218 | 74.1241 | 75.2493 | 76.6645 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854
75% | 57.481 | 42.7196 | 44.018 | 49.2968 | 53.1054 | 55.1088 | 56.9033 | 58.043 | 59.3439 | 60.3835 | 61.061 | 62.6745 | 63.7905 | 64.3778 | 65.4668 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 75% | 32.9003 | 48.0547 | 49.7167 | 55.0102 | 58.7759 | 61.0337 | 62.8413 | 64.3086 | 65.7199 | 66.9417 | 67.5547 | 68.458 | 69.4914 | 70.5462 | 71.873 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801
70% | 106.2642 | 39.8716 | 41.0835 | 46.0104 | 49.5651 | 51.4349 | 53.1098 | 54.1734 | 55.3877 | 56.3579 | 56.9902 | 58.4962 | 59.5378 | 60.0859 | 61.1024 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 70% | 41.9762 | 44.8511 | 46.4023 | 51.3429 | 54.8575 | 56.9648 | 58.6519 | 60.0214 | 61.3386 | 62.4789 | 63.051 | 63.8941 | 64.8586 | 65.8431 | 67.0814 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748
65% | 201.9397 | 37.0236 | 38.1489 | 42.7239 | 46.0247 | 47.761 | 49.3162 | 50.3039 | 51.4314 | 52.3323 | 52.9195 | 54.3179 | 55.2851 | 55.7941 | 56.7379 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 65% | 67.6914 | 41.6474 | 43.0878 | 47.6755 | 50.9391 | 52.8959 | 54.4625 | 55.7341 | 56.9573 | 58.0161 | 58.5474 | 59.3302 | 60.2259 | 61.14 | 62.2899 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694
60% | 402.745 | 34.1757 | 35.2144 | 39.4375 | 42.4843 | 44.0871 | 45.5227 | 46.4344 | 47.4751 | 48.3068 | 48.8488 | 50.1396 | 51.0324 | 51.5022 | 52.3735 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 60% | 98.7009 | 38.4438 | 39.7734 | 44.0082 | 47.0207 | 48.827 | 50.2731 | 51.4469 | 52.5759 | 53.5534 | 54.0437 | 54.7664 | 55.5931 | 56.4369 | 57.4984 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641
55% | 655.7369 | 31.3277 | 32.2799 | 36.151 | 38.944 | 40.4131 | 41.7291 | 42.5648 | 43.5189 | 44.2812 | 44.778 | 45.9613 | 46.7797 | 47.2104 | 48.009 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 55% | 153.5347 | 35.2401 | 36.4589 | 40.3408 | 43.1023 | 44.7581 | 46.0836 | 47.1596 | 48.1946 | 49.0906 | 49.5401 | 50.2025 | 50.9604 | 51.7339 | 52.7068 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587
50% | 981.7145 | 28.4797 | 29.3453 | 32.8646 | 35.4036 | 36.7392 | 37.9355 | 38.6953 | 39.5626 | 40.2557 | 40.7073 | 41.783 | 42.527 | 42.9185 | 43.6446 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 50% | 258.2862 | 32.0365 | 33.1445 | 36.6735 | 39.1839 | 40.6891 | 41.8942 | 42.8724 | 43.8133 | 44.6278 | 45.0364 | 45.6386 | 46.3276 | 47.0308 | 47.9153 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534
45% | 1622.7029 | 25.6317 | 26.4108 | 29.5781 | 31.8633 | 33.0653 | 34.142 | 34.8258 | 35.6064 | 36.2301 | 36.6366 | 37.6047 | 38.2743 | 38.6267 | 39.2801 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 45% | 488.9664 | 28.8328 | 29.83 | 33.0061 | 35.2655 | 36.6202 | 37.7048 | 38.5852 | 39.4319 | 40.165 | 40.5328 | 41.0748 | 41.6948 | 42.3277 | 43.1238 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481
40% | 2442.9413 | 22.7838 | 23.4763 | 26.2916 | 28.3229 | 29.3914 | 30.3484 | 30.9562 | 31.6501 | 32.2045 | 32.5659 | 33.4264 | 34.0216 | 34.3348 | 34.9157 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 40% | 928.0152 | 25.6292 | 26.5156 | 29.3388 | 31.3471 | 32.5513 | 33.5154 | 34.2979 | 35.0506 | 35.7022 | 36.0292 | 36.5109 | 37.0621 | 37.6246 | 38.3322 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427
35% | 3006.7842 | 19.9358 | 20.5417 | 23.0052 | 24.7825 | 25.7175 | 26.5549 | 27.0867 | 27.6938 | 28.179 | 28.4951 | 29.2481 | 29.7689 | 30.043 | 30.5512 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 35% | 1530.4309 | 22.4255 | 23.2011 | 25.6714 | 27.4287 | 28.4824 | 29.326 | 30.0107 | 30.6693 | 31.2395 | 31.5255 | 31.9471 | 32.4293 | 32.9215 | 33.5407 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374
30% | 3276.4154 | 17.0878 | 17.6072 | 19.7187 | 21.2422 | 22.0435 | 22.7613 | 23.2172 | 23.7376 | 24.1534 | 24.4244 | 25.0698 | 25.5162 | 25.7511 | 26.1867 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 30% | 2592.3162 | 19.2219 | 19.8867 | 22.0041 | 23.5103 | 24.4135 | 25.1365 | 25.7234 | 26.288 | 26.7767 | 27.0219 | 27.3832 | 27.7966 | 28.2185 | 28.7492 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832
25% | 3466.632 | 14.2399 | 14.6727 | 16.4323 | 17.7018 | 18.3696 | 18.9678 | 19.3477 | 19.7813 | 20.1278 | 20.3537 | 20.8915 | 21.2635 | 21.4593 | 21.8223 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 25% | 3659.4958 | 16.0182 | 16.5722 | 18.3367 | 19.592 | 20.3446 | 20.9471 | 21.4362 | 21.9066 | 22.3139 | 22.5182 | 22.8193 | 23.1638 | 23.5154 | 23.9577 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267
20% | 3713.9514 | 11.3919 | 11.7381 | 13.1458 | 14.1614 | 14.6957 | 15.1742 | 15.4781 | 15.825 | 16.1023 | 16.2829 | 16.7132 | 17.0108 | 17.1674 | 17.4578 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 20% | 4005.5161 | 12.8146 | 13.2578 | 14.6694 | 15.6736 | 16.2757 | 16.7577 | 17.149 | 17.5253 | 17.8511 | 18.0146 | 18.2555 | 18.531 | 18.8123 | 19.1661 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214
15% | 4043.3325 | 8.5439 | 8.8036 | 9.8594 | 10.6211 | 11.0218 | 11.3807 | 11.6086 | 11.8688 | 12.0767 | 12.2122 | 12.5349 | 12.7581 | 12.8756 | 13.0934 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 15% | 4281.1979 | 9.6109 | 9.9433 | 11.002 | 11.7552 | 12.2067 | 12.5683 | 12.8617 | 13.144 | 13.3883 | 13.5109 | 13.6916 | 13.8983 | 14.1092 | 14.3746 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416
10% | 4350.7801 | 5.6959 | 5.8691 | 6.5729 | 7.0807 | 7.3478 | 7.5871 | 7.7391 | 7.9125 | 8.0511 | 8.1415 | 8.3566 | 8.5054 | 8.5837 | 8.7289 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 10% | 4391.6218 | 6.4073 | 6.6289 | 7.3347 | 7.8368 | 8.1378 | 8.3788 | 8.5745 | 8.7627 | 8.9256 | 9.0073 | 9.1277 | 9.2655 | 9.4062 | 9.5831 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107
5% | 4391.6218 | 2.848 | 2.9345 | 3.2865 | 3.5404 | 3.6739 | 3.7936 | 3.8695 | 3.9563 | 4.0256 | 4.0707 | 4.1783 | 4.2527 | 4.2919 | 4.3645 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 5% | 4391.6218 | 3.2036 | 3.3144 | 3.6673 | 3.9184 | 4.0689 | 4.1894 | 4.2872 | 4.3813 | 4.4628 | 4.5036 | 4.5639 | 4.6328 | 4.7031 | 4.7915 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053
9.992e-14% | 4391.6218 | 5.6914e-14 | 5.8644e-14 | 6.5677e-14 | 7.0751e-14 | 7.342e-14 | 7.581e-14 | 7.7329e-14 | 7.9062e-14 | 8.0447e-14 | 8.135e-14 | 8.3499e-14 | 8.4986e-14 | 8.5768e-14 | 8.7219e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 9.992e-14% | 4391.6218 | 6.4022e-14 | 6.6236e-14 | 7.3288e-14 | 7.8305e-14 | 8.1313e-14 | 8.3721e-14 | 8.5676e-14 | 8.7557e-14 | 8.9184e-14 | 9.0001e-14 | 9.1204e-14 | 9.2581e-14 | 9.3986e-14 | 9.5754e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 50.4065 | 52.8183 | 60.0302 | 66.1039 | 69.3805 | 71.7482 | 74.4773 | 76.5194 | 78.7707 | 79.9506 | 80.9726 | 83.5025 | 81.9768 | 86.1024 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 91.4839 | 100% | 0 | 53.6497 | 56.1536 | 63.3095 | 69.6129 | 72.9009 | 75.5673 | 78.1029 | 80.2632 | 82.5134 | 83.4997 | 84.8459 | 87.3415 | 86.5255 | 89.7851 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653 | 91.6653
99% | 0.8916 | 49.9025 | 52.2901 | 59.4299 | 65.4429 | 68.6867 | 71.0307 | 73.7326 | 75.7542 | 77.9829 | 79.1511 | 80.1629 | 82.6675 | 81.157 | 85.2413 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 90.569 | 99% | 0.8916 | 53.1132 | 55.592 | 62.6764 | 68.9168 | 72.1719 | 74.8116 | 77.3219 | 79.4606 | 81.6883 | 82.6647 | 83.9974 | 86.4681 | 85.6602 | 88.8872 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486 | 90.7486
98% | 3.5664 | 49.3984 | 51.7619 | 58.8296 | 64.7818 | 67.9929 | 70.3132 | 72.9878 | 74.989 | 77.1952 | 78.3516 | 79.3532 | 81.8324 | 80.3372 | 84.3803 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 89.6542 | 98% | 3.5664 | 52.5767 | 55.0305 | 62.0433 | 68.2206 | 71.4429 | 74.0559 | 76.5409 | 78.658 | 80.8632 | 81.8297 | 83.1489 | 85.5946 | 84.795 | 87.9894 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832 | 89.832
97% | 4.7552 | 48.8943 | 51.2337 | 58.2293 | 64.1208 | 67.2991 | 69.5957 | 72.243 | 74.2238 | 76.4075 | 77.5521 | 78.5434 | 80.9974 | 79.5174 | 83.5193 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 88.7394 | 97% | 4.7552 | 52.0402 | 54.469 | 61.4102 | 67.5245 | 70.7139 | 73.3003 | 75.7598 | 77.8554 | 80.038 | 80.9947 | 82.3005 | 84.7212 | 83.9297 | 87.0915 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153 | 88.9153
95% | 7.7272 | 47.8862 | 50.1774 | 57.0287 | 62.7987 | 65.9115 | 68.1608 | 70.7535 | 72.6934 | 74.8321 | 75.9531 | 76.924 | 79.3274 | 77.8779 | 81.7972 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 86.9097 | 95% | 7.7272 | 50.9672 | 53.3459 | 60.144 | 66.1322 | 69.2559 | 71.7889 | 74.1978 | 76.2501 | 78.3878 | 79.3247 | 80.6036 | 82.9744 | 82.1992 | 85.2958 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082 | 87.082
90% | 39.2302 | 45.3659 | 47.5365 | 54.0272 | 59.4935 | 62.4425 | 64.5734 | 67.0296 | 68.8674 | 70.8936 | 71.9556 | 72.8753 | 75.1522 | 73.7791 | 77.4921 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 82.3355 | 90% | 39.2302 | 48.2848 | 50.5382 | 56.9785 | 62.6516 | 65.6108 | 68.0106 | 70.2926 | 72.2369 | 74.2621 | 75.1497 | 76.3613 | 78.6073 | 77.8729 | 80.8066 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987 | 82.4987
85% | 117.6906 | 42.8456 | 44.8955 | 51.0257 | 56.1883 | 58.9735 | 60.986 | 63.3057 | 65.0415 | 66.9551 | 67.958 | 68.8267 | 70.9771 | 69.6802 | 73.187 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 77.7613 | 85% | 117.6906 | 45.6023 | 47.7305 | 53.813 | 59.171 | 61.9658 | 64.2322 | 66.3875 | 68.2238 | 70.1364 | 70.9748 | 72.119 | 74.2403 | 73.5467 | 76.3173 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155 | 77.9155
80% | 268.3703 | 40.3252 | 42.2546 | 48.0242 | 52.8831 | 55.5044 | 57.3985 | 59.5819 | 61.2155 | 63.0165 | 63.9605 | 64.7781 | 66.802 | 65.5814 | 68.8819 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 73.1871 | 80% | 268.3703 | 42.9198 | 44.9228 | 50.6476 | 55.6903 | 58.3207 | 60.4538 | 62.4824 | 64.2106 | 66.0108 | 66.7998 | 67.8767 | 69.8732 | 69.2204 | 71.8281 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322 | 73.3322
75% | 455.9026 | 37.8049 | 39.6137 | 45.0227 | 49.5779 | 52.0354 | 53.8111 | 55.858 | 57.3895 | 59.078 | 59.963 | 60.7295 | 62.6269 | 61.4826 | 64.5768 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 68.6129 | 75% | 455.9026 | 40.2373 | 42.1152 | 47.4821 | 52.2097 | 54.6757 | 56.6755 | 58.5772 | 60.1974 | 61.8851 | 62.6248 | 63.6344 | 65.5061 | 64.8941 | 67.3388 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749 | 68.749
70% | 690.9866 | 35.2846 | 36.9728 | 42.0212 | 46.2727 | 48.5664 | 50.2237 | 52.1341 | 53.5636 | 55.1395 | 55.9654 | 56.6808 | 58.4517 | 57.3837 | 60.2717 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 64.0387 | 70% | 690.9866 | 37.5548 | 39.3075 | 44.3166 | 48.729 | 51.0307 | 52.8971 | 54.6721 | 56.1843 | 57.7594 | 58.4498 | 59.3921 | 61.139 | 60.5678 | 62.8495 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657 | 64.1657
65% | 967.6784 | 32.7642 | 34.3319 | 39.0196 | 42.9675 | 45.0973 | 46.6363 | 48.4103 | 49.7376 | 51.2009 | 51.9679 | 52.6322 | 54.2766 | 53.2849 | 55.9665 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 59.4645 | 65% | 967.6784 | 34.8723 | 36.4998 | 41.1511 | 45.2484 | 47.3856 | 49.1187 | 50.7669 | 52.1711 | 53.6337 | 54.2748 | 55.1498 | 56.772 | 56.2416 | 58.3603 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824 | 59.5824
60% | 1292.8136 | 30.2439 | 31.691 | 36.0181 | 39.6623 | 41.6283 | 43.0489 | 44.6864 | 45.9116 | 47.2624 | 47.9704 | 48.5836 | 50.1015 | 49.1861 | 51.6614 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 54.8903 | 60% | 1292.8136 | 32.1898 | 33.6921 | 37.9857 | 41.7677 | 43.7406 | 45.3404 | 46.8618 | 48.1579 | 49.5081 | 50.0998 | 50.9075 | 52.4049 | 51.9153 | 53.871 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992 | 54.9992
55% | 1647.0743 | 27.7236 | 29.0501 | 33.0166 | 36.3571 | 38.1593 | 39.4615 | 40.9625 | 42.0857 | 43.3239 | 43.9728 | 44.5349 | 45.9264 | 45.0872 | 47.3563 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 50.3161 | 55% | 1647.0743 | 29.5074 | 30.8845 | 34.8202 | 38.2871 | 40.0955 | 41.562 | 42.9566 | 44.1448 | 45.3824 | 45.9248 | 46.6652 | 48.0378 | 47.589 | 49.3818 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159 | 50.4159
50% | 2104.1657 | 25.2033 | 26.4091 | 30.0151 | 33.0519 | 34.6903 | 35.8741 | 37.2387 | 38.2597 | 39.3853 | 39.9753 | 40.4863 | 41.7512 | 40.9884 | 43.0512 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 45.7419 | 50% | 2104.1657 | 26.8249 | 28.0768 | 31.6547 | 34.8064 | 36.4505 | 37.7836 | 39.0515 | 40.1316 | 41.2567 | 41.7499 | 42.4229 | 43.6707 | 43.2627 | 44.8925 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326 | 45.8326
45% | 2736.0097 | 22.6829 | 23.7682 | 27.0136 | 29.7468 | 31.2212 | 32.2867 | 33.5148 | 34.4337 | 35.4468 | 35.9778 | 36.4377 | 37.5761 | 36.8895 | 38.7461 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 41.1677 | 45% | 2736.0097 | 24.1424 | 25.2691 | 28.4893 | 31.3258 | 32.8054 | 34.0053 | 35.1463 | 36.1185 | 37.1311 | 37.5749 | 38.1806 | 39.3037 | 38.9365 | 40.4033 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494 | 41.2494
40% | 3483.7613 | 20.1626 | 21.1273 | 24.0121 | 26.4416 | 27.7522 | 28.6993 | 29.7909 | 30.6078 | 31.5083 | 31.9802 | 32.389 | 33.401 | 32.7907 | 34.4409 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 36.5936 | 40% | 3483.7613 | 21.4599 | 22.4614 | 25.3238 | 27.8452 | 29.1604 | 30.2269 | 31.2412 | 32.1053 | 33.0054 | 33.3999 | 33.9383 | 34.9366 | 34.6102 | 35.914 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661 | 36.6661
35% | 3830.2948 | 17.6423 | 18.4864 | 21.0106 | 23.1364 | 24.2832 | 25.1119 | 26.0671 | 26.7818 | 27.5697 | 27.9827 | 28.3404 | 29.2259 | 28.6919 | 30.1358 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 32.0194 | 35% | 3830.2948 | 18.7774 | 19.6537 | 22.1583 | 24.3645 | 25.5153 | 26.4485 | 27.336 | 28.0921 | 28.8797 | 29.2249 | 29.696 | 30.5695 | 30.2839 | 31.4248 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828 | 32.0828
30% | 3953.6322 | 15.122 | 15.8455 | 18.0091 | 19.8312 | 20.8142 | 21.5245 | 22.3432 | 22.9558 | 23.6312 | 23.9852 | 24.2918 | 25.0507 | 24.593 | 25.8307 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 27.4452 | 30% | 3953.6322 | 16.0949 | 16.8461 | 18.9928 | 20.8839 | 21.8703 | 22.6702 | 23.4309 | 24.079 | 24.754 | 25.0499 | 25.4538 | 26.2024 | 25.9576 | 26.9355 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996 | 27.4996
25% | 4060.9208 | 12.6016 | 13.2046 | 15.0076 | 16.526 | 17.3451 | 17.937 | 18.6193 | 19.1298 | 19.6927 | 19.9877 | 20.2432 | 20.8756 | 20.4942 | 21.5256 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 22.871 | 25% | 4060.9208 | 13.4124 | 14.0384 | 15.8274 | 17.4032 | 18.2252 | 18.8918 | 19.5257 | 20.0658 | 20.6284 | 20.8749 | 21.2115 | 21.8354 | 21.6314 | 22.4463 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163 | 22.9163
20% | 4165.2375 | 10.0813 | 10.5637 | 12.006 | 13.2208 | 13.8761 | 14.3496 | 14.8955 | 15.3039 | 15.7541 | 15.9901 | 16.1945 | 16.7005 | 16.3954 | 17.2205 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 18.2968 | 20% | 4165.2375 | 10.7299 | 11.2307 | 12.6619 | 13.9226 | 14.5802 | 15.1135 | 15.6206 | 16.0526 | 16.5027 | 16.6999 | 16.9692 | 17.4683 | 17.3051 | 17.957 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331 | 18.3331
15% | 4270.4458 | 7.561 | 7.9227 | 9.0045 | 9.9156 | 10.4071 | 10.7622 | 11.1716 | 11.4779 | 11.8156 | 11.9926 | 12.1459 | 12.5254 | 12.2965 | 12.9154 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 13.7226 | 15% | 4270.4458 | 8.0475 | 8.423 | 9.4964 | 10.4419 | 10.9351 | 11.3351 | 11.7154 | 12.0395 | 12.377 | 12.525 | 12.7269 | 13.1012 | 12.9788 | 13.4678 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498 | 13.7498
10% | 4373.8709 | 5.0407 | 5.2818 | 6.003 | 6.6104 | 6.9381 | 7.1748 | 7.4477 | 7.6519 | 7.8771 | 7.9951 | 8.0973 | 8.3502 | 8.1977 | 8.6102 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 9.1484 | 10% | 4373.8709 | 5.365 | 5.6154 | 6.3309 | 6.9613 | 7.2901 | 7.5567 | 7.8103 | 8.0263 | 8.2513 | 8.35 | 8.4846 | 8.7341 | 8.6525 | 8.9785 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665 | 9.1665
5% | 4391.7028 | 2.5203 | 2.6409 | 3.0015 | 3.3052 | 3.469 | 3.5874 | 3.7239 | 3.826 | 3.9385 | 3.9975 | 4.0486 | 4.1751 | 4.0988 | 4.3051 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 4.5742 | 5% | 4391.7028 | 2.6825 | 2.8077 | 3.1655 | 3.4806 | 3.645 | 3.7784 | 3.9051 | 4.0132 | 4.1257 | 4.175 | 4.2423 | 4.3671 | 4.3263 | 4.4893 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833 | 4.5833
9.992e-14% | 4391.7028 | 5.0366e-14 | 5.2776e-14 | 5.9982e-14 | 6.6051e-14 | 6.9325e-14 | 7.1691e-14 | 7.4418e-14 | 7.6458e-14 | 7.8708e-14 | 7.9887e-14 | 8.0908e-14 | 8.3436e-14 | 8.1911e-14 | 8.6034e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.1411e-14 | 9.992e-14% | 4391.7028 | 5.3607e-14 | 5.6109e-14 | 6.3259e-14 | 6.9557e-14 | 7.2843e-14 | 7.5507e-14 | 7.8041e-14 | 8.0199e-14 | 8.2447e-14 | 8.3433e-14 | 8.4778e-14 | 8.7272e-14 | 8.6456e-14 | 8.9713e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14 | 9.1592e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.9594 | 58.6907 | 65.7291 | 70.8072 | 73.4784 | 75.8711 | 77.3906 | 79.1252 | 80.5113 | 81.4146 | 83.566 | 85.054 | 85.837 | 87.2891 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 86.8665 | 100% | 0 | 64.073 | 66.289 | 73.347 | 78.3678 | 81.3783 | 83.7884 | 85.7448 | 87.6265 | 89.2556 | 90.0729 | 91.2773 | 92.6552 | 94.0616 | 95.8306 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068 | 96.1068
99% | 0 | 56.3898 | 58.1038 | 65.0718 | 70.0992 | 72.7437 | 75.1124 | 76.6167 | 78.334 | 79.7062 | 80.6005 | 82.7304 | 84.2035 | 84.9787 | 86.4162 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 85.9978 | 99% | 0.75633 | 63.4323 | 65.6261 | 72.6135 | 77.5841 | 80.5645 | 82.9506 | 84.8874 | 86.7503 | 88.363 | 89.1721 | 90.3645 | 91.7286 | 93.121 | 94.8723 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457 | 95.1457
98% | 0.37816 | 55.8202 | 57.5169 | 64.4145 | 69.3911 | 72.0089 | 74.3537 | 75.8428 | 77.5427 | 78.9011 | 79.7863 | 81.8947 | 83.3529 | 84.1203 | 85.5433 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 85.1292 | 98% | 1.1345 | 62.7915 | 64.9632 | 71.88 | 76.8005 | 79.7507 | 82.1127 | 84.0299 | 85.874 | 87.4705 | 88.2714 | 89.4517 | 90.8021 | 92.1803 | 93.914 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847 | 94.1847
97% | 0.75633 | 55.2506 | 56.93 | 63.7572 | 68.683 | 71.2741 | 73.595 | 75.0689 | 76.7515 | 78.096 | 78.9722 | 81.059 | 82.5024 | 83.2619 | 84.6705 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 84.2605 | 97% | 1.8908 | 62.1508 | 64.3003 | 71.1466 | 76.0168 | 78.9369 | 81.2748 | 83.1725 | 84.9977 | 86.5779 | 87.3707 | 88.539 | 89.8755 | 91.2397 | 92.9557 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236 | 93.2236
95% | 1.8908 | 54.1115 | 55.7561 | 62.4427 | 67.2669 | 69.8045 | 72.0775 | 73.5211 | 75.169 | 76.4857 | 77.3439 | 79.3877 | 80.8013 | 81.5452 | 82.9247 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 82.5232 | 95% | 3.4035 | 60.8693 | 62.9745 | 69.6796 | 74.4494 | 77.3094 | 79.599 | 81.4576 | 83.2452 | 84.7928 | 85.5692 | 86.7134 | 88.0224 | 89.3585 | 91.0391 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015 | 91.3015
90% | 4.538 | 51.2635 | 52.8216 | 59.1562 | 63.7265 | 66.1306 | 68.284 | 69.6515 | 71.2127 | 72.4602 | 73.2732 | 75.2094 | 76.5486 | 77.2533 | 78.5602 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 78.1799 | 90% | 9.0759 | 57.6657 | 59.6601 | 66.0123 | 70.531 | 73.2405 | 75.4096 | 77.1703 | 78.8639 | 80.33 | 81.0656 | 82.1496 | 83.3897 | 84.6554 | 86.2476 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961 | 86.4961
85% | 9.0759 | 48.4155 | 49.8871 | 55.8697 | 60.1862 | 62.4567 | 64.4904 | 65.782 | 67.2565 | 68.4346 | 69.2024 | 71.0311 | 72.2959 | 72.9615 | 74.1958 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 73.8365 | 85% | 16.2611 | 54.462 | 56.3456 | 62.3449 | 66.6126 | 69.1716 | 71.2202 | 72.8831 | 74.4826 | 75.8673 | 76.5619 | 77.5857 | 78.7569 | 79.9523 | 81.456 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908 | 81.6908
80% | 27.606 | 45.5675 | 46.9525 | 52.5833 | 56.6458 | 58.7827 | 60.6969 | 61.9125 | 63.3002 | 64.409 | 65.1317 | 66.8528 | 68.0432 | 68.6696 | 69.8313 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 69.4932 | 80% | 24.9588 | 51.2584 | 53.0312 | 58.6776 | 62.6943 | 65.1026 | 67.0308 | 68.5959 | 70.1012 | 71.4045 | 72.0583 | 73.0218 | 74.1241 | 75.2493 | 76.6645 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854 | 76.8854
75% | 57.481 | 42.7196 | 44.018 | 49.2968 | 53.1054 | 55.1088 | 56.9033 | 58.043 | 59.3439 | 60.3835 | 61.061 | 62.6745 | 63.7905 | 64.3778 | 65.4668 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 65.1499 | 75% | 32.9003 | 48.0547 | 49.7167 | 55.0102 | 58.7759 | 61.0337 | 62.8413 | 64.3086 | 65.7199 | 66.9417 | 67.5547 | 68.458 | 69.4914 | 70.5462 | 71.873 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801 | 72.0801
70% | 106.2642 | 39.8716 | 41.0835 | 46.0104 | 49.5651 | 51.4349 | 53.1098 | 54.1734 | 55.3877 | 56.3579 | 56.9902 | 58.4962 | 59.5378 | 60.0859 | 61.1024 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 60.8066 | 70% | 41.9762 | 44.8511 | 46.4023 | 51.3429 | 54.8575 | 56.9648 | 58.6519 | 60.0214 | 61.3386 | 62.4789 | 63.051 | 63.8941 | 64.8586 | 65.8431 | 67.0814 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748 | 67.2748
65% | 201.9397 | 37.0236 | 38.1489 | 42.7239 | 46.0247 | 47.761 | 49.3162 | 50.3039 | 51.4314 | 52.3323 | 52.9195 | 54.3179 | 55.2851 | 55.7941 | 56.7379 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 56.4632 | 65% | 67.6914 | 41.6474 | 43.0878 | 47.6755 | 50.9391 | 52.8959 | 54.4625 | 55.7341 | 56.9573 | 58.0161 | 58.5474 | 59.3302 | 60.2259 | 61.14 | 62.2899 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694 | 62.4694
60% | 402.745 | 34.1757 | 35.2144 | 39.4375 | 42.4843 | 44.0871 | 45.5227 | 46.4344 | 47.4751 | 48.3068 | 48.8488 | 50.1396 | 51.0324 | 51.5022 | 52.3735 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 52.1199 | 60% | 98.7009 | 38.4438 | 39.7734 | 44.0082 | 47.0207 | 48.827 | 50.2731 | 51.4469 | 52.5759 | 53.5534 | 54.0437 | 54.7664 | 55.5931 | 56.4369 | 57.4984 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641 | 57.6641
55% | 655.7369 | 31.3277 | 32.2799 | 36.151 | 38.944 | 40.4131 | 41.7291 | 42.5648 | 43.5189 | 44.2812 | 44.778 | 45.9613 | 46.7797 | 47.2104 | 48.009 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 47.7766 | 55% | 153.5347 | 35.2401 | 36.4589 | 40.3408 | 43.1023 | 44.7581 | 46.0836 | 47.1596 | 48.1946 | 49.0906 | 49.5401 | 50.2025 | 50.9604 | 51.7339 | 52.7068 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587 | 52.8587
50% | 981.7145 | 28.4797 | 29.3453 | 32.8646 | 35.4036 | 36.7392 | 37.9355 | 38.6953 | 39.5626 | 40.2557 | 40.7073 | 41.783 | 42.527 | 42.9185 | 43.6446 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 43.4333 | 50% | 258.2862 | 32.0365 | 33.1445 | 36.6735 | 39.1839 | 40.6891 | 41.8942 | 42.8724 | 43.8133 | 44.6278 | 45.0364 | 45.6386 | 46.3276 | 47.0308 | 47.9153 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534 | 48.0534
45% | 1622.7029 | 25.6317 | 26.4108 | 29.5781 | 31.8633 | 33.0653 | 34.142 | 34.8258 | 35.6064 | 36.2301 | 36.6366 | 37.6047 | 38.2743 | 38.6267 | 39.2801 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 39.0899 | 45% | 488.9664 | 28.8328 | 29.83 | 33.0061 | 35.2655 | 36.6202 | 37.7048 | 38.5852 | 39.4319 | 40.165 | 40.5328 | 41.0748 | 41.6948 | 42.3277 | 43.1238 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481 | 43.2481
40% | 2442.9413 | 22.7838 | 23.4763 | 26.2916 | 28.3229 | 29.3914 | 30.3484 | 30.9562 | 31.6501 | 32.2045 | 32.5659 | 33.4264 | 34.0216 | 34.3348 | 34.9157 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 34.7466 | 40% | 928.0152 | 25.6292 | 26.5156 | 29.3388 | 31.3471 | 32.5513 | 33.5154 | 34.2979 | 35.0506 | 35.7022 | 36.0292 | 36.5109 | 37.0621 | 37.6246 | 38.3322 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427 | 38.4427
35% | 3006.7842 | 19.9358 | 20.5417 | 23.0052 | 24.7825 | 25.7175 | 26.5549 | 27.0867 | 27.6938 | 28.179 | 28.4951 | 29.2481 | 29.7689 | 30.043 | 30.5512 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 30.4033 | 35% | 1530.4309 | 22.4255 | 23.2011 | 25.6714 | 27.4287 | 28.4824 | 29.326 | 30.0107 | 30.6693 | 31.2395 | 31.5255 | 31.9471 | 32.4293 | 32.9215 | 33.5407 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374 | 33.6374
30% | 3276.4154 | 17.0878 | 17.6072 | 19.7187 | 21.2422 | 22.0435 | 22.7613 | 23.2172 | 23.7376 | 24.1534 | 24.4244 | 25.0698 | 25.5162 | 25.7511 | 26.1867 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 26.06 | 30% | 2592.3162 | 19.2219 | 19.8867 | 22.0041 | 23.5103 | 24.4135 | 25.1365 | 25.7234 | 26.288 | 26.7767 | 27.0219 | 27.3832 | 27.7966 | 28.2185 | 28.7492 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832 | 28.832
25% | 3466.632 | 14.2399 | 14.6727 | 16.4323 | 17.7018 | 18.3696 | 18.9678 | 19.3477 | 19.7813 | 20.1278 | 20.3537 | 20.8915 | 21.2635 | 21.4593 | 21.8223 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 21.7166 | 25% | 3659.4958 | 16.0182 | 16.5722 | 18.3367 | 19.592 | 20.3446 | 20.9471 | 21.4362 | 21.9066 | 22.3139 | 22.5182 | 22.8193 | 23.1638 | 23.5154 | 23.9577 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267 | 24.0267
20% | 3713.9514 | 11.3919 | 11.7381 | 13.1458 | 14.1614 | 14.6957 | 15.1742 | 15.4781 | 15.825 | 16.1023 | 16.2829 | 16.7132 | 17.0108 | 17.1674 | 17.4578 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 17.3733 | 20% | 4005.5161 | 12.8146 | 13.2578 | 14.6694 | 15.6736 | 16.2757 | 16.7577 | 17.149 | 17.5253 | 17.8511 | 18.0146 | 18.2555 | 18.531 | 18.8123 | 19.1661 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214 | 19.2214
15% | 4043.3325 | 8.5439 | 8.8036 | 9.8594 | 10.6211 | 11.0218 | 11.3807 | 11.6086 | 11.8688 | 12.0767 | 12.2122 | 12.5349 | 12.7581 | 12.8756 | 13.0934 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 13.03 | 15% | 4281.1979 | 9.6109 | 9.9433 | 11.002 | 11.7552 | 12.2067 | 12.5683 | 12.8617 | 13.144 | 13.3883 | 13.5109 | 13.6916 | 13.8983 | 14.1092 | 14.3746 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416 | 14.416
10% | 4350.7801 | 5.6959 | 5.8691 | 6.5729 | 7.0807 | 7.3478 | 7.5871 | 7.7391 | 7.9125 | 8.0511 | 8.1415 | 8.3566 | 8.5054 | 8.5837 | 8.7289 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 8.6867 | 10% | 4391.6218 | 6.4073 | 6.6289 | 7.3347 | 7.8368 | 8.1378 | 8.3788 | 8.5745 | 8.7627 | 8.9256 | 9.0073 | 9.1277 | 9.2655 | 9.4062 | 9.5831 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107 | 9.6107
5% | 4391.6218 | 2.848 | 2.9345 | 3.2865 | 3.5404 | 3.6739 | 3.7936 | 3.8695 | 3.9563 | 4.0256 | 4.0707 | 4.1783 | 4.2527 | 4.2919 | 4.3645 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 4.3433 | 5% | 4391.6218 | 3.2036 | 3.3144 | 3.6673 | 3.9184 | 4.0689 | 4.1894 | 4.2872 | 4.3813 | 4.4628 | 4.5036 | 4.5639 | 4.6328 | 4.7031 | 4.7915 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053 | 4.8053
9.992e-14% | 4391.6218 | 5.6914e-14 | 5.8644e-14 | 6.5677e-14 | 7.0751e-14 | 7.342e-14 | 7.581e-14 | 7.7329e-14 | 7.9062e-14 | 8.0447e-14 | 8.135e-14 | 8.3499e-14 | 8.4986e-14 | 8.5768e-14 | 8.7219e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 8.6797e-14 | 9.992e-14% | 4391.6218 | 6.4022e-14 | 6.6236e-14 | 7.3288e-14 | 7.8305e-14 | 8.1313e-14 | 8.3721e-14 | 8.5676e-14 | 8.7557e-14 | 8.9184e-14 | 9.0001e-14 | 9.1204e-14 | 9.2581e-14 | 9.3986e-14 | 9.5754e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14 | 9.603e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 105212961.6203 | 61.5% | 30.2784
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 59818974.1027 | 34.97% | 12.0256
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 2268426.58 | 1.326% | 0.44409
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 3766583.5488 | 2.202% | 0.4899
|  | 171066945.8518 |  | 43.238 | KW/h
|  |  |  | 43237.9539 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [43 empty] | 0.29844 | 1.6272 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835
98% | [44 empty] | 0.45121 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
97% | [44 empty] | 0.20117 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128
95% | [45 empty] | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29844 | 2.2796 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089531 | 0.68388 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [43 empty] | 0.29844 | 1.6272 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835
98% | [44 empty] | 0.45121 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
97% | [44 empty] | 0.20117 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128
95% | [45 empty] | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29844 | 2.2796 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089531 | 0.68388 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [43 empty] | 0.29844 | 1.6272 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835
98% | [44 empty] | 0.45121 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
97% | [44 empty] | 0.20117 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128
95% | [45 empty] | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29844 | 2.2796 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089531 | 0.68388 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [43 empty] | 0.29844 | 1.6272 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835 | 1.835
98% | [44 empty] | 0.45121 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408 | 0.55408
97% | [44 empty] | 0.20117 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128 | 0.38128
95% | [45 empty] | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889 | 0.00021889
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29844 | 2.2796 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706 | 2.7706
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089531 | 0.68388 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119 | 0.83119

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 1.9209 | 4.0605 | 10.4585 | 15.8467 | 18.7535 | 20.8539 | 23.2751 | 25.0866 | 27.0838 | 28.1306 | 29.0373 | 31.2816 | 29.9281 | 33.5881 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 |  | 4.7981 | 7.0193 | 13.3676 | 18.9596 | 21.8766 | 24.242 | 26.4915 | 28.408 | 30.4042 | 31.2792 | 32.4734 | 34.6873 | 33.9634 | 36.8551 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231
98% | 4.4146 | 10.7687 | 29.7698 | 45.7719 | 54.4047 | 60.6427 | 67.8331 | 73.2132 | 79.1445 | 82.2533 | 84.9459 | 91.6113 | 87.5915 | 98.4611 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 |  | 12.9593 | 19.5561 | 38.4094 | 55.0169 | 63.6798 | 70.7047 | 77.3853 | 83.077 | 89.0055 | 91.604 | 95.1506 | 101.7258 | 99.5759 | 108.1638 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175
97% | 1.3628 | 4.1582 | 12.5174 | 19.5572 | 23.3551 | 26.0994 | 29.2627 | 31.6295 | 34.2389 | 35.6066 | 36.7911 | 39.7235 | 37.955 | 42.7369 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 |  | 5.1219 | 8.024 | 16.3182 | 23.6244 | 27.4355 | 30.526 | 33.465 | 35.969 | 38.5771 | 39.7203 | 41.2805 | 44.1731 | 43.2273 | 47.0054 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847
95% | 1.179 | 8.0409 | 28.6173 | 45.9461 | 55.2947 | 62.0499 | 69.8365 | 75.6626 | 82.0857 | 85.4523 | 88.3681 | 95.5861 | 91.2331 | 103.0039 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 |  | 10.4131 | 17.5568 | 37.9733 | 55.9576 | 65.3388 | 72.9462 | 80.1807 | 86.3443 | 92.7643 | 95.5783 | 99.4189 | 106.5392 | 104.2111 | 113.511 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754
90% |  | 28.2772 | 237.1537 | 414.1424 | 509.6246 | 578.6186 | 658.1473 | 717.653 | 783.2556 | 817.64 | 847.4212 | 921.1424 | 876.6824 | 996.9039 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 |  | 51.224 | 124.1864 | 332.7113 | 516.3954 | 612.2101 | 689.9084 | 763.7982 | 826.7504 | 892.3218 | 921.0622 | 960.2889 | 1033.0121 | 1009.2336 | 1104.2192 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089
85% |  |  | 355.147 | 772.122 | 997.0725 | 1159.6182 | 1346.9832 | 1487.1752 | 1641.731 | 1722.7386 | 1792.9013 | 1966.5841 | 1861.8388 | 2145.0736 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 |  | 1.1859 | 90.0175 | 580.2752 | 1013.0241 | 1238.7577 | 1421.8105 | 1595.8904 | 1744.202 | 1898.6845 | 1966.395 | 2058.8109 | 2230.1425 | 2174.1218 | 2397.9022 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834
80% |  |  | 229.7771 | 984.7996 | 1392.1206 | 1686.4445 | 2025.7089 | 2279.5565 | 2559.4129 | 2706.0946 | 2833.1392 | 3147.6291 | 2957.9653 | 3470.8227 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 |  |  |  | 637.4198 | 1421.0045 | 1829.7435 | 2161.1999 | 2476.4087 | 2744.9586 | 3024.6824 | 3147.2868 | 3314.6255 | 3624.8581 | 3523.4206 | 3928.6229 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522
75% |  |  | 0.018268 | 605.8271 | 1082.0453 | 1426.1532 | 1822.8033 | 2119.5884 | 2446.7817 | 2618.2742 | 2766.808 | 3134.493 | 2912.7481 | 3512.3538 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 |  |  |  | 207.6345 | 1115.8148 | 1593.6908 | 1981.2121 | 2349.7376 | 2663.7119 | 2990.7502 | 3134.0927 | 3329.7364 | 3692.4439 | 3573.8485 | 4047.5896 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536
70% |  |  |  | 88.5459 | 540.9022 | 944.4342 | 1409.582 | 1757.6192 | 2141.3156 | 2342.4232 | 2516.6074 | 2947.7881 | 2687.75 | 3390.9019 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 |  |  |  |  | 580.5033 | 1140.904 | 1595.3465 | 2027.5129 | 2395.7076 | 2779.2223 | 2947.3187 | 3176.7482 | 3602.0919 | 3463.0162 | 4018.5679 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022
65% |  |  |  |  | 12.7928 | 190.6991 | 628.7018 | 1010.0877 | 1430.5497 | 1650.9273 | 1841.8016 | 2314.2979 | 2029.3431 | 2799.8706 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 |  |  |  |  | 21.1245 | 348.6064 | 832.2662 | 1305.8425 | 1709.3174 | 2129.5801 | 2313.7835 | 2565.1967 | 3031.2966 | 2878.8947 | 3487.6791 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388
60% | [6 empty] | 7.3484 | 128.2902 | 422.9124 | 640.2703 | 847.9131 | 1362.0067 | 1051.9652 | 1890.328 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | [6 empty] | 53.8499 | 318.7033 | 703.7652 | 1161.0269 | 1361.4471 | 1634.9941 | 2142.1283 | 1976.3093 | 2638.6896 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645
55% | [10 empty] | 14.8991 | 187.3598 | 60.791 | 551.5769 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | [8 empty] | 1.1011 | 97.6428 | 187.0714 | 352.9682 | 786.9367 | 627.6332 | 1284.6962 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932
50% | FY39: 268.0325; FY40: 268.0325; FY41: 268.0325; FY42: 268.0325; FY43: 268.0325; FY44: 268.0325; FY45: 268.0325; FY46: 268.0325; FY47: 268.0325; FY48: 268.0325; FY49: 268.0325; FY50: 268.0325; FY51: 268.0325; FY52: 268.0325; FY53: 268.0325; FY54: 268.0325 | [12 empty] | 0.074826 |  | 97.2035 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 8.8773 | 55.3055 | 903.459 | 2992.5588 | 4686.3661 | 6155.6135 | 8089.4822 | 9705.5622 | 11648.5119 | 12729.8111 | 13700.6333 | 16239.5036 | 14685.7915 | 19035.6214 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | E @ R (MWh) | 85.7023 | 266.36 | 1864.1094 | 4821.4253 | 6942.2431 | 8934.0123 | 11055.4161 | 13023.3125 | 15224.6621 | 16236.6391 | 17661.6923 | 20430.1104 | 19507.4556 | 23310.7057 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597
Option 1 Winter POE50 W E @ R (MWh) N 1 | 6.2141 | 38.7139 | 632.4213 | 2094.7912 | 3280.4563 | 4308.9295 | 5662.6375 | 6793.8935 | 8153.9583 | 8910.8678 | 9590.4433 | 11367.6525 | 10280.054 | 13324.935 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 25.7107 | 79.908 | 559.2328 | 1446.4276 | 2082.6729 | 2680.2037 | 3316.6248 | 3906.9937 | 4567.3986 | 4870.9917 | 5298.5077 | 6129.0331 | 5852.2367 | 6993.2117 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14.0319 | 15.6995 | 21.011 | 24.7894 | 27.0549 | 28.8687 | 30.3409 | 31.757 | 32.983 | 33.598 | 34.5044 | 35.5413 | 36.5997 | 37.931 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388
98% | 4.1239 | 4.7688 | 7.3905 | 9.2821 | 10.2771 | 11.1683 | 11.7343 | 12.3805 | 12.8968 | 13.2333 | 14.0346 | 14.5889 | 14.8806 | 15.4215 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 |  | 6.7736 | 7.5991 | 10.2281 | 12.0983 | 13.2197 | 14.1175 | 14.8462 | 15.5471 | 16.154 | 16.4584 | 16.907 | 17.4203 | 17.9441 | 18.6031 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706
97% | 3.9085 | 4.5468 | 7.142 | 9.0143 | 9.9992 | 10.8814 | 11.4417 | 12.0813 | 12.5923 | 12.9254 | 13.7186 | 14.2673 | 14.556 | 15.0914 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 |  | 13.0627 | 14.6968 | 19.9015 | 23.604 | 25.824 | 27.6013 | 29.0439 | 30.4315 | 31.6328 | 32.2355 | 33.1237 | 34.1398 | 35.1769 | 36.4814 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851
95% | 10.7562 | 12.6417 | 20.3074 | 25.838 | 28.7473 | 31.3531 | 33.008 | 34.8973 | 36.4068 | 37.3907 | 39.7338 | 41.3544 | 42.2072 | 43.7887 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 |  | 24.6715 | 27.8895 | 38.1388 | 45.4298 | 49.8015 | 53.3014 | 56.1423 | 58.8749 | 61.2405 | 62.4273 | 64.1763 | 66.1772 | 68.2195 | 70.7884 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895
90% | 19.8204 | 24.0596 | 41.294 | 53.7284 | 60.2691 | 66.1278 | 69.8485 | 74.096 | 77.4899 | 79.7018 | 84.9697 | 88.6132 | 90.5306 | 94.0862 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 |  | 79.7975 | 91.4248 | 128.4583 | 154.8028 | 170.5989 | 183.2451 | 193.5102 | 203.3837 | 211.9314 | 216.2197 | 222.5393 | 229.7691 | 237.1484 | 246.4307 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798
85% | 21.0539 | 27.9282 | 55.8759 | 76.0398 | 86.6464 | 96.1469 | 102.1805 | 109.0683 | 114.5719 | 118.1588 | 126.7014 | 132.6098 | 135.719 | 141.4848 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 |  | 78.0582 | 91.99 | 136.3635 | 167.9295 | 186.8563 | 202.0089 | 214.3085 | 226.139 | 236.3808 | 241.519 | 249.0911 | 257.7539 | 266.5958 | 277.7178 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541
80% | 33.197 | 59.6631 | 167.2618 | 244.8926 | 285.728 | 322.3052 | 345.5345 | 372.0524 | 393.2415 | 407.0509 | 439.9399 | 462.6871 | 474.6575 | 496.8561 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 |  | 66.6268 | 82.528 | 133.1738 | 169.2018 | 190.804 | 208.0984 | 222.1367 | 235.6393 | 247.3289 | 253.1934 | 261.8359 | 271.7232 | 281.8149 | 294.509 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908
75% | 0.70851 | 15.6341 | 171.4842 | 289.0586 | 350.9052 | 406.3026 | 441.4841 | 481.6463 | 513.738 | 534.6527 | 584.4641 | 618.9156 | 637.0452 | 670.6657 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 |  | 35.3916 | 49.0301 | 92.4694 | 123.3709 | 141.8993 | 156.7328 | 168.7735 | 180.3549 | 190.3811 | 195.4111 | 202.8239 | 211.3043 | 219.96 | 230.8478 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476
70% |  |  | 119.6948 | 299.2969 | 393.7715 | 478.3945 | 532.1363 | 593.4867 | 642.5087 | 674.4572 | 750.5473 | 803.174 | 830.8681 | 882.2255 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 |  | 11.5438 | 25.9526 | 72.3947 | 105.4322 | 125.2414 | 141.1003 | 153.9733 | 166.3552 | 177.0745 | 182.4522 | 190.3773 | 199.4439 | 208.698 | 220.3384 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557
65% |  |  | 9.5592 | 248.267 | 420.7759 | 575.296 | 673.4277 | 785.4524 | 874.9657 | 933.3031 | 1072.2422 | 1168.3378 | 1218.9066 | 1312.6844 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 |  |  | 5.6073 | 110.8118 | 197.9624 | 250.2177 | 292.0523 | 326.0105 | 358.6731 | 386.9498 | 401.1359 | 422.0418 | 445.9589 | 470.3706 | 501.0772 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871
60% |  |  |  | 19.2882 | 179.2375 | 445.6738 | 636.3776 | 854.0805 | 1028.0358 | 1141.4057 | 1411.4125 | 1598.1595 | 1696.4322 | 1878.6749 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 |  |  |  | 25.9088 | 117.2122 | 175.5582 | 222.269 | 260.1852 | 296.6549 | 328.2275 | 344.0671 | 367.4098 | 394.1146 | 421.3716 | 455.6573 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099
55% | [5 empty] | 3.4714 | 49.8086 | 165.5048 | 303.2996 | 413.7128 | 721.1439 | 937.6016 | 1051.5091 | 1262.7459 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 |  |  |  |  | 23.1943 | 88.6401 | 163.3146 | 224.9978 | 284.3278 | 335.6911 | 361.4593 | 399.4339 | 442.878 | 487.2206 | 542.9975 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052
50% | [10 empty] | 22.6091 | 95.641 | 153.4846 | 294.6713 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | [6 empty] | 9.7618 | 46.9146 | 107.2018 | 177.6453 | 219.0596 | 284.9847 | 360.7613 | 438.1048 | 535.3924 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807
45% | [41 empty] | 4.8627 | 31.6552 | 82.2002 | 177.4776 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 93.5685 | 149.2423 | 600.0098 | 1274.7059 | 1826.3571 | 2447.1212 | 2906.9819 | 3494.7464 | 4009.7471 | 4365.9923 | 5281.5172 | 5975.9501 | 6360.7964 | 7108.3964 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | E @ R (MWh) | 329.9576 | 412.4176 | 788.8598 | 1165.0275 | 1445.7159 | 1702.472 | 1941.1838 | 2195.3401 | 2433.6207 | 2559.2366 | 2754.1117 | 2998.641 | 3271.4254 | 3646.2496 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389
Option 1 Summer POE50 W E @ R (MWh) N 1 | 65.4979 | 104.4696 | 420.0069 | 892.2941 | 1278.45 | 1712.9848 | 2034.8873 | 2446.3225 | 2806.823 | 3056.1946 | 3697.062 | 4183.1651 | 4452.5575 | 4975.8775 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 98.9873 | 123.7253 | 236.6579 | 349.5083 | 433.7148 | 510.7416 | 582.3551 | 658.602 | 730.0862 | 767.771 | 826.2335 | 899.5923 | 981.4276 | 1093.8749 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 1.9209 | 4.0605 | 10.4585 | 15.8467 | 5.89 | 7.9904 | 10.4116 | 12.2231 | 14.2203 | 15.2671 | 16.1738 | 18.4181 | 17.0646 | 20.7246 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 | 25.4987 |  | 4.7981 | 7.0193 | 13.3676 | 18.9596 | 9.0131 | 11.3785 | 13.628 | 15.5445 | 17.5407 | 18.4157 | 19.6099 | 21.8238 | 21.0999 | 23.9916 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596 | 25.6596
98% | 4.4146 | 10.7687 | 29.7698 | 45.7719 | 16.2021 | 22.44 | 29.6305 | 35.0105 | 40.9419 | 44.0507 | 46.7433 | 53.4086 | 49.3889 | 60.2585 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 | 74.437 |  | 12.9593 | 19.5561 | 38.4094 | 55.0169 | 25.4771 | 32.5021 | 39.1827 | 44.8744 | 50.8029 | 53.4014 | 56.948 | 63.5231 | 61.3732 | 69.9612 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149 | 74.9149
97% | 1.3628 | 4.1582 | 12.5174 | 19.5572 | 6.5485 | 9.2928 | 12.4561 | 14.823 | 17.4323 | 18.8 | 19.9846 | 22.9169 | 21.1484 | 25.9303 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 | 32.1679 |  | 5.1219 | 8.024 | 16.3182 | 23.6244 | 10.6289 | 13.7194 | 16.6584 | 19.1624 | 21.7705 | 22.9137 | 24.474 | 27.3666 | 26.4208 | 30.1989 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782 | 32.3782
95% | 1.179 | 8.0409 | 28.6173 | 45.9461 | 13.9247 | 20.6798 | 28.4664 | 34.2926 | 40.7157 | 44.0822 | 46.9981 | 54.2161 | 49.863 | 61.6338 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 | 76.9879 |  | 10.4131 | 17.5568 | 37.9733 | 55.9576 | 23.9687 | 31.5761 | 38.8106 | 44.9742 | 51.3943 | 54.2082 | 58.0489 | 65.1692 | 62.841 | 72.141 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054 | 77.5054
90% |  | 28.2772 | 237.1537 | 414.1424 | 87.09 | 156.084 | 235.6127 | 295.1185 | 360.721 | 395.1054 | 424.8866 | 498.6078 | 454.1478 | 574.3693 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 | 731.1887 |  | 51.224 | 124.1864 | 332.7113 | 516.3954 | 189.6755 | 267.3739 | 341.2636 | 404.2158 | 469.7872 | 498.5276 | 537.7543 | 610.4775 | 586.699 | 681.6846 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743 | 736.4743
85% |  |  | 355.147 | 772.122 | 27.7212 | 164.1517 | 351.5167 | 491.7087 | 646.2644 | 727.2721 | 797.4348 | 971.1176 | 866.3723 | 1149.6071 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 | 1519.0644 |  | 1.1859 | 90.0175 | 580.2752 | 1013.0241 | 243.2912 | 426.344 | 600.4239 | 748.7355 | 903.218 | 970.9285 | 1063.3444 | 1234.676 | 1178.6553 | 1402.4357 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169 | 1531.5169
80% |  |  | 229.7771 | 984.7996 |  | 11.4984 | 223.2118 | 477.0511 | 756.9075 | 903.5892 | 1030.6337 | 1345.1237 | 1155.4599 | 1668.3173 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 | 2337.2988 |  |  |  | 637.4198 | 1421.0045 | 69.4611 | 358.6944 | 673.9033 | 942.4532 | 1222.1769 | 1344.7813 | 1512.1201 | 1822.3527 | 1720.9152 | 2126.1175 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468 | 2359.8468
75% |  |  | 0.018268 | 605.8271 |  |  |  | 78.9166 | 339.3877 | 510.8802 | 659.414 | 1027.099 | 805.3541 | 1404.9598 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 | 2187.0977 |  |  |  | 207.6345 | 1115.8148 |  | 22.3876 | 244.9584 | 556.318 | 883.3562 | 1026.6987 | 1222.3424 | 1585.0499 | 1466.4545 | 1940.1957 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596 | 2213.4596
70% |  |  |  | 88.5459 |  |  |  |  | 1.5072 | 42.5143 | 121.6221 | 476.4671 | 236.8857 | 919.5809 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 | 1836.7866 |  |  |  |  | 580.5033 |  |  |  | 62.5158 | 313.1743 | 475.9977 | 705.4272 | 1130.7709 | 991.6952 | 1547.2469 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701 | 1867.701
65% | [11 empty] | 3.6507 |  | 173.9472 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 | 1096.8409 |  |  |  |  | 21.1245 | [5 empty] | 3.6044 | 60.6834 | 339.3746 | 224.5759 | 779.5577 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174 | 1130.7174
60% | FY39: 175.6803; FY40: 175.6803; FY41: 175.6803; FY42: 175.6803; FY43: 175.6803; FY44: 175.6803; FY45: 175.6803; FY46: 175.6803; FY47: 175.6803; FY48: 175.6803; FY49: 175.6803; FY50: 175.6803; FY51: 175.6803; FY52: 175.6803; FY53: 175.6803; FY54: 175.6803 | [14 empty] | 37.7792 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166 | 196.1166
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 8.8773 | 55.3055 | 903.459 | 2992.5588 | 157.3764 | 392.1371 | 891.3057 | 1439.144 | 2218.0981 | 2701.5613 | 3163.8909 | 4471.0257 | 3655.6848 | 6059.3289 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | 10093.0489 | E @ R (MWh) | 85.7023 | 266.36 | 1864.1094 | 4821.4253 | 571.5156 | 1163.9761 | 1968.8289 | 2838.7936 | 3933.2211 | 4469.4772 | 5260.7524 | 6900.5844 | 6340.73 | 8711.31 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907 | 10246.2907
Option 2 Winter POE50 W E @ R (MWh) N 1 | 6.2141 | 38.7139 | 632.4213 | 2094.7912 | 110.1635 | 274.496 | 623.914 | 1007.4008 | 1552.6687 | 1891.0929 | 2214.7237 | 3129.718 | 2558.9793 | 4241.5302 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | 7065.1342 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 25.7107 | 79.908 | 559.2328 | 1446.4276 | 171.4547 | 349.1928 | 590.6487 | 851.6381 | 1179.9663 | 1340.8432 | 1578.2257 | 2070.1753 | 1902.219 | 2613.393 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872 | 3073.8872
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14.0319 | 15.6995 | 21.011 | 24.7894 | 16.143 | 17.9568 | 19.429 | 20.8451 | 22.071 | 22.6861 | 23.5925 | 24.6294 | 25.6878 | 27.0191 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269 | 27.2269
98% | 4.1239 | 4.7688 | 7.3905 | 9.2821 | 4.876 | 5.7672 | 6.3332 | 6.9793 | 7.4956 | 7.8321 | 8.6335 | 9.1878 | 9.4794 | 10.0203 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 | 9.8629 |  | 6.7736 | 7.5991 | 10.2281 | 12.0983 | 7.8186 | 8.7164 | 9.4451 | 10.146 | 10.7528 | 11.0573 | 11.5059 | 12.0191 | 12.543 | 13.202 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048 | 13.3048
97% | 3.9085 | 4.5468 | 7.142 | 9.0143 | 4.6529 | 5.5351 | 6.0954 | 6.735 | 7.246 | 7.5791 | 8.3723 | 8.921 | 9.2097 | 9.7451 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 | 9.5892 |  | 13.0627 | 14.6968 | 19.9015 | 23.604 | 15.1314 | 16.9087 | 18.3513 | 19.739 | 20.9403 | 21.5429 | 22.4311 | 23.4472 | 24.4843 | 25.7888 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925 | 25.9925
95% | 10.7562 | 12.6417 | 20.3074 | 25.838 | 12.9551 | 15.561 | 17.2159 | 19.1051 | 20.6147 | 21.5985 | 23.9416 | 25.5622 | 26.415 | 27.9965 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 | 27.5362 |  | 24.6715 | 27.8895 | 38.1388 | 45.4298 | 28.7453 | 32.2452 | 35.0861 | 37.8187 | 40.1843 | 41.3711 | 43.1201 | 45.121 | 47.1633 | 49.7322 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333 | 50.1333
90% | 19.8204 | 24.0596 | 41.294 | 53.7284 | 24.7642 | 30.6229 | 34.3436 | 38.5911 | 41.985 | 44.1969 | 49.4648 | 53.1083 | 55.0257 | 58.5813 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 | 57.5464 |  | 79.7975 | 91.4248 | 128.4583 | 154.8028 | 94.517 | 107.1631 | 117.4282 | 127.3017 | 135.8495 | 140.1377 | 146.4573 | 153.6872 | 161.0665 | 170.3487 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978 | 171.7978
85% | 21.0539 | 27.9282 | 55.8759 | 76.0398 | 29.0708 | 38.5714 | 44.605 | 51.4928 | 56.9964 | 60.5833 | 69.1259 | 75.0342 | 78.1434 | 83.9093 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 | 82.2312 |  | 78.0582 | 91.99 | 136.3635 | 167.9295 | 95.6951 | 110.8477 | 123.1473 | 134.9777 | 145.2196 | 150.3578 | 157.9299 | 166.5927 | 175.4346 | 186.5565 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929 | 188.2929
80% | 33.197 | 59.6631 | 167.2618 | 244.8926 | 64.0623 | 100.6395 | 123.8688 | 150.3867 | 171.5758 | 185.3852 | 218.2741 | 241.0214 | 252.9918 | 275.1904 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 | 268.7296 |  | 66.6268 | 82.528 | 133.1738 | 169.2018 | 86.7568 | 104.0512 | 118.0895 | 131.5922 | 143.2817 | 149.1462 | 157.7887 | 167.676 | 177.7678 | 190.4618 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436 | 192.4436
75% | 0.70851 | 15.6341 | 171.4842 | 289.0586 | 19.9136 | 70.5825 | 105.764 | 145.9263 | 178.0179 | 198.9326 | 248.7441 | 283.1955 | 301.3251 | 334.9456 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 | 325.1606 |  | 35.3916 | 49.0301 | 92.4694 | 123.3709 | 52.6572 | 67.4908 | 79.5315 | 91.1128 | 101.1391 | 106.1691 | 113.5818 | 122.0622 | 130.718 | 141.6058 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055 | 143.3055
70% |  |  | 119.6948 | 299.2969 |  | 5.4538 | 30.041 | 80.6534 | 129.6754 | 161.6239 | 237.714 | 290.3407 | 318.0347 | 369.3922 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 | 354.445 |  | 11.5438 | 25.9526 | 72.3947 | 105.4322 | 29.8305 | 45.6894 | 58.5624 | 70.9443 | 81.6636 | 87.0413 | 94.9665 | 104.0331 | 113.2872 | 124.9276 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448 | 126.7448
65% |  |  | 9.5592 | 248.267 |  |  |  | 0.02101 | 14.7242 | 38.4676 | 137.124 | 231.9132 | 282.482 | 376.2598 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 | 348.9664 |  |  | 5.6073 | 110.8118 | 197.9624 | 10.0264 | 40.4631 | 74.3232 | 106.9858 | 135.2626 | 149.4487 | 170.3546 | 194.2717 | 218.6834 | 249.3899 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837 | 254.1837
60% |  |  |  | 19.2882 | [7 empty] | 12.4016 | 38.4719 | 123.1632 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 | 93.7643 |  |  |  | 25.9088 | 117.2122 |  |  | 5.3543 | 23.0659 | 47.7026 | 63.0438 | 86.3864 | 113.0913 | 140.3483 | 174.6339 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865 | 179.9865
55% | [34 empty] | 23.1943 | [5 empty] | 0.14988 | 5.3608 | 20.1123 | 44.3574 | 87.2982 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003 | 95.2003
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 93.5685 | 149.2423 | 600.0098 | 1274.7059 | 160.295 | 272.7336 | 368.2669 | 499.8906 | 628.3311 | 726.1992 | 1001.3943 | 1230.686 | 1371.5787 | 1669.2037 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | 1577.832 | E @ R (MWh) | 329.9576 | 412.4176 | 788.8598 | 1165.0275 | 437.3214 | 551.5323 | 658.7481 | 774.5293 | 884.0671 | 942.1519 | 1033.4756 | 1146.7431 | 1271.5415 | 1440.9646 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127 | 1468.6127
Option 2 Summer POE50 W E @ R (MWh) N 1 | 65.4979 | 104.4696 | 420.0069 | 892.2941 | 112.2065 | 190.9135 | 257.7868 | 349.9234 | 439.8317 | 508.3394 | 700.976 | 861.4802 | 960.1051 | 1168.4426 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | 1104.4824 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 98.9873 | 123.7253 | 236.6579 | 349.5083 | 131.1964 | 165.4597 | 197.6244 | 232.3588 | 265.2201 | 282.6456 | 310.0427 | 344.0229 | 381.4625 | 432.2894 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838 | 440.5838
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 1.9209 | 4.0605 | 10.4585 | 9.4149 |  | 1.5587 | 3.9798 | 5.7914 | 7.7886 | 8.8354 | 9.742 | 11.9864 | 10.6328 | 14.2928 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 |  | 4.7981 | 7.0193 | 13.3676 | 12.5279 | 2.5813 | 4.9467 | 7.1962 | 9.1127 | 11.109 | 11.9839 | 13.1781 | 15.3921 | 14.6682 | 17.5599 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279
98% | 4.4146 | 10.7687 | 29.7698 | 26.6705 |  | 3.3387 | 10.5291 | 15.9092 | 21.8406 | 24.9494 | 27.642 | 34.3073 | 30.2875 | 41.1571 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 |  | 12.9593 | 19.5561 | 38.4094 | 35.9156 | 6.3758 | 13.4008 | 20.0813 | 25.773 | 31.7016 | 34.3001 | 37.8467 | 44.4218 | 42.2719 | 50.8599 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136
97% | 1.3628 | 4.1582 | 12.5174 | 11.1539 |  | 0.88949 | 4.0528 | 6.4197 | 9.0291 | 10.3967 | 11.5813 | 14.5136 | 12.7452 | 17.527 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 |  | 5.1219 | 8.024 | 16.3182 | 15.2211 | 2.2256 | 5.3161 | 8.2551 | 10.7591 | 13.3672 | 14.5104 | 16.0707 | 18.9633 | 18.0175 | 21.7956 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749
95% | 1.179 | 8.0409 | 28.6173 | 25.2611 |  | 0.3689 | 7.7814 | 13.6076 | 20.0307 | 23.3972 | 26.3131 | 33.5311 | 29.178 | 40.9488 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 |  | 10.4131 | 17.5568 | 37.9733 | 35.2726 | 3.2837 | 10.8911 | 18.1256 | 24.2892 | 30.7093 | 33.5232 | 37.3639 | 44.4841 | 42.156 | 51.456 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204
90% |  | 28.2772 | 237.1537 | 202.8751 |  |  | 26.1226 | 83.8512 | 149.4537 | 183.8382 | 213.6193 | 287.3405 | 242.8805 | 363.102 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 |  | 51.224 | 124.1864 | 332.7113 | 305.1281 | 2.1686 | 56.1066 | 129.9963 | 192.9485 | 258.52 | 287.2603 | 326.487 | 399.2102 | 375.4317 | 470.4173 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207
85% |  |  | 355.147 | 274.3888 |  |  |  | 23.9298 | 148.5312 | 229.5388 | 299.7015 | 473.3843 | 368.639 | 651.8739 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 |  | 1.1859 | 90.0175 | 580.2752 | 515.2909 |  | 2.7658 | 102.8299 | 251.0022 | 405.4847 | 473.1953 | 565.6111 | 736.9428 | 680.922 | 904.7024 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837
80% |  |  | 229.7771 | 105.07 |  |  |  |  | 5.7768 | 55.9848 | 139.2218 | 443.871 | 254.2072 | 767.0646 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 |  |  |  | 637.4198 | 519.7518 |  |  |  | 77.6303 | 320.9242 | 443.5286 | 610.8674 | 921.1 | 819.6625 | 1224.8648 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941
75% |  |  | 0.018268 | [8 empty] | 59.6906 | 1.0246 | 351.2628 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 |  |  |  | 207.6345 | 107.4524 |  |  |  |  | 11.5126 | 59.5057 | 182.3124 | 531.353 | 412.7575 | 886.4987 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626
70% | FY38: 2.5513; FY39: 601.1261; FY40: 601.1261; FY41: 601.1261; FY42: 601.1261; FY43: 601.1261; FY44: 601.1261; FY45: 601.1261; FY46: 601.1261; FY47: 601.1261; FY48: 601.1261; FY49: 601.1261; FY50: 601.1261; FY51: 601.1261; FY52: 601.1261; FY53: 601.1261; FY54: 601.1261 | [12 empty] | 51.0621 | 12.2764 | 316.4572 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405
65% | FY39: 26.2727; FY40: 26.2727; FY41: 26.2727; FY42: 26.2727; FY43: 26.2727; FY44: 26.2727; FY45: 26.2727; FY46: 26.2727; FY47: 26.2727; FY48: 26.2727; FY49: 26.2727; FY50: 26.2727; FY51: 26.2727; FY52: 26.2727; FY53: 26.2727; FY54: 26.2727 | [15 empty] | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 8.8773 | 55.3055 | 903.459 | 654.8343 | 0 | 6.1558 | 52.4658 | 149.5089 | 362.4506 | 536.9404 | 727.821 | 1358.6248 | 949.5949 | 2249.7804 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | E @ R (MWh) | 85.7023 | 266.36 | 1864.1094 | 1546.5604 | 16.635 | 93.4271 | 286.4845 | 591.515 | 1083.3285 | 1357.8075 | 1789.7373 | 2762.9294 | 2418.1638 | 3944.6117 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447
Option 3 Winter POE50 W E @ R (MWh) N 1 | 6.2141 | 38.7139 | 632.4213 | 458.384 | 0 | 4.309 | 36.726 | 104.6562 | 253.7154 | 375.8583 | 509.4747 | 951.0373 | 664.7164 | 1574.8462 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 25.7107 | 79.908 | 559.2328 | 463.9681 | 4.9905 | 28.0281 | 85.9453 | 177.4545 | 324.9986 | 407.3422 | 536.9212 | 828.8788 | 725.4491 | 1183.3835 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14.0319 | 15.6995 | 21.011 | 19.3334 | 10.687 | 12.5008 | 13.973 | 15.3891 | 16.6151 | 17.2301 | 18.1365 | 19.1734 | 20.2318 | 21.5631 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709
98% | 4.1239 | 4.7688 | 7.3905 | 6.5815 | 2.1754 | 3.0666 | 3.6326 | 4.2788 | 4.7951 | 5.1316 | 5.9329 | 6.4872 | 6.7789 | 7.3198 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 |  | 6.7736 | 7.5991 | 10.2281 | 9.3978 | 5.118 | 6.0158 | 6.7445 | 7.4454 | 8.0523 | 8.3567 | 8.8053 | 9.3186 | 9.8424 | 10.5014 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043
97% | 3.9085 | 4.5468 | 7.142 | 6.3412 | 1.9798 | 2.862 | 3.4222 | 4.0618 | 4.5729 | 4.9059 | 5.6992 | 6.2478 | 6.5365 | 7.0719 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 |  | 13.0627 | 14.6968 | 19.9015 | 18.2577 | 9.7851 | 11.5624 | 13.005 | 14.3927 | 15.594 | 16.1966 | 17.0848 | 18.1009 | 19.138 | 20.4425 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462
95% | 10.7562 | 12.6417 | 20.3074 | 17.9419 | 5.059 | 7.6649 | 9.3198 | 11.2091 | 12.7186 | 13.7025 | 16.0456 | 17.6661 | 18.519 | 20.1005 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 |  | 24.6715 | 27.8895 | 38.1388 | 34.9017 | 18.2172 | 21.7171 | 24.558 | 27.2906 | 29.6562 | 30.843 | 32.592 | 34.5929 | 36.6352 | 39.2041 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052
90% | 19.8204 | 24.0596 | 41.294 | 35.9759 | 7.0118 | 12.8705 | 16.5912 | 20.8386 | 24.2326 | 26.4445 | 31.7124 | 35.3559 | 37.2732 | 40.8288 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 |  | 79.7975 | 91.4248 | 128.4583 | 116.7619 | 56.4761 | 69.1222 | 79.3873 | 89.2608 | 97.8085 | 102.0968 | 108.4164 | 115.6462 | 123.0256 | 132.3078 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569
85% | 21.0539 | 27.9282 | 55.8759 | 47.252 | 1.6121 | 9.7837 | 15.8172 | 22.705 | 28.2087 | 31.7955 | 40.3381 | 46.2465 | 49.3557 | 55.1216 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 |  | 78.0582 | 91.99 | 136.3635 | 122.3489 | 50.1145 | 65.2671 | 77.5667 | 89.3971 | 99.639 | 104.7772 | 112.3493 | 121.0121 | 129.854 | 140.9759 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123
80% | 33.197 | 59.6631 | 167.2618 | 134.0597 |  | 2.2073 | 14.6101 | 39.5538 | 60.743 | 74.5523 | 107.4413 | 130.1885 | 142.1589 | 164.3575 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 |  | 66.6268 | 82.528 | 133.1738 | 117.1782 | 34.7332 | 52.0276 | 66.0659 | 79.5686 | 91.2581 | 97.1227 | 105.7651 | 115.6524 | 125.7442 | 138.4382 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42
75% | 0.70851 | 15.6341 | 171.4842 | 121.1985 |  |  |  | 2.5528 | 16.6385 | 32.0934 | 80.884 | 115.3355 | 133.465 | 167.0856 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 |  | 35.3916 | 49.0301 | 92.4694 | 78.7498 | 8.3415 | 22.8697 | 34.9105 | 46.4918 | 56.518 | 61.5481 | 68.9608 | 77.4412 | 86.097 | 96.9848 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845
70% |  |  | 119.6948 | 46.7487 | [6 empty] | 10.656 | 39.9897 | 62.4933 | 112.9755 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 |  | 11.5438 | 25.9526 | 72.3947 | 57.7268 |  | 2.5833 | 11.0881 | 23.2389 | 33.9582 | 39.3359 | 47.261 | 56.3277 | 65.5818 | 77.2221 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394
65% |  |  | 9.5592 | [10 empty] | 6.6985 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 |  |  | 5.6073 | 110.8118 | 72.1188 |  |  |  | 3.258 | 16.07 | 25.9548 | 44.5112 | 68.4281 | 92.8397 | 123.5463 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401
60% | [33 empty] | 25.9088 | 4.5952 | [7 empty] | 3.4515 | 13.9331 | 36.4871 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 93.5685 | 149.2423 | 600.0098 | 416.0996 | 17.8381 | 38.455 | 63.3932 | 105.1999 | 151.9093 | 188.6257 | 298.7094 | 397.5173 | 456.5805 | 581.5597 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | E @ R (MWh) | 329.9576 | 412.4176 | 788.8598 | 651.37 | 193.4726 | 263.6659 | 327.299 | 395.733 | 465.1694 | 503.4618 | 563.8824 | 639.1449 | 722.9227 | 837.6734 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863
Option 3 Summer POE50 W E @ R (MWh) N 1 | 65.4979 | 104.4696 | 420.0069 | 291.2697 | 12.4867 | 26.9185 | 44.3752 | 73.64 | 106.3365 | 132.038 | 209.0966 | 278.2621 | 319.6063 | 407.0918 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 98.9873 | 123.7253 | 236.6579 | 195.411 | 58.0418 | 79.0998 | 98.1897 | 118.7199 | 139.5508 | 151.0385 | 169.1647 | 191.7435 | 216.8768 | 251.302 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 1.9209; FY26: 4.0605; FY27: 10.4585 |  | 4.7981 | 7.0193 | 13.3676
98% | FY25: 4.4146; FY26: 10.7687; FY27: 29.7698 |  | 12.9593 | 19.5561 | 38.4094
97% | FY25: 1.3628; FY26: 4.1582; FY27: 12.5174 |  | 5.1219 | 8.024 | 16.3182
95% | FY25: 1.179; FY26: 8.0409; FY27: 28.6173 |  | 10.4131 | 17.5568 | 37.9733
90% | FY26: 28.2772; FY27: 237.1537 |  | 51.224 | 124.1864 | 332.7113
85% | FY27: 355.147 |  | 1.1859 | 90.0175 | 580.2752
80% | FY27: 229.7771 |  |  |  | 637.4198
75% | FY27: 0.018268 |  |  |  | 207.6345
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 8.8773 | 55.3055 | 903.459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 85.7023 | 266.36 | 1864.1094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) N 1 | 6.2141 | 38.7139 | 632.4213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 25.7107 | 79.908 | 559.2328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 14.0319 | 15.6995 | 21.011 | [7 empty] | 0.31886 | 1.3553 | 2.4136 | 3.7449 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528 | 3.9528
98% | FY25: 4.1239; FY26: 4.7688; FY27: 7.3905 |  | 6.7736 | 7.5991 | 10.2281 | [8 empty] | 0.32725 | 0.85111 | 1.5101 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129 | 1.6129
97% | FY25: 3.9085; FY26: 4.5468; FY27: 7.142 |  | 13.0627 | 14.6968 | 19.9015 | [8 empty] | 0.065984 | 0.99081 | 2.2953 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499 | 2.499
95% | FY25: 10.7562; FY26: 12.6417; FY27: 20.3074 |  | 24.6715 | 27.8895 | 38.1388 | [9 empty] | 0.28349 | 2.4163 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174 | 2.8174
90% | FY25: 19.8204; FY26: 24.0596; FY27: 41.294 |  | 79.7975 | 91.4248 | 128.4583 | [10 empty] | 0.24176 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962 | 0.47962
85% | FY25: 21.0539; FY26: 27.9282; FY27: 55.8759 |  | 78.0582 | 91.99 | 136.3635
80% | FY25: 33.197; FY26: 59.6631; FY27: 167.2618 |  | 66.6268 | 82.528 | 133.1738
75% | FY25: 0.70851; FY26: 15.6341; FY27: 171.4842 |  | 35.3916 | 49.0301 | 92.4694
70% | FY27: 119.6948 |  | 11.5438 | 25.9526 | 72.3947
65% | FY27: 9.5592 |  |  | 5.6073 | 110.8118
60% | [33 empty] | 25.9088
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 93.5685 | 149.2423 | 600.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 329.9576 | 412.4176 | 788.8598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31886 | 1.7485 | 4.5391 | 10.2084 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617 | 11.3617
Option 4 Summer POE50 W E @ R (MWh) N 1 | 65.4979 | 104.4696 | 420.0069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 98.9873 | 123.7253 | 236.6579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.095659 | 0.52455 | 1.3617 | 3.0625 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085 | 3.4085
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 1.9209 | 4.0605 | 10.4585 | 9.4149 |  | 1.5587 | 3.9798 | 5.7914 | 7.7886 | 8.8354 | 9.742 | 11.9864 | 10.6328 | 14.2928 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 | 19.067 |  | 4.7981 | 7.0193 | 13.3676 | 12.5279 | 2.5813 | 4.9467 | 7.1962 | 9.1127 | 11.109 | 11.9839 | 13.1781 | 15.3921 | 14.6682 | 17.5599 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279 | 19.2279
98% | 4.4146 | 10.7687 | 29.7698 | 26.6705 |  | 3.3387 | 10.5291 | 15.9092 | 21.8406 | 24.9494 | 27.642 | 34.3073 | 30.2875 | 41.1571 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 | 55.3357 |  | 12.9593 | 19.5561 | 38.4094 | 35.9156 | 6.3758 | 13.4008 | 20.0813 | 25.773 | 31.7016 | 34.3001 | 37.8467 | 44.4218 | 42.2719 | 50.8599 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136 | 55.8136
97% | 1.3628 | 4.1582 | 12.5174 | 11.1539 |  | 0.88949 | 4.0528 | 6.4197 | 9.0291 | 10.3967 | 11.5813 | 14.5136 | 12.7452 | 17.527 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 | 23.7646 |  | 5.1219 | 8.024 | 16.3182 | 15.2211 | 2.2256 | 5.3161 | 8.2551 | 10.7591 | 13.3672 | 14.5104 | 16.0707 | 18.9633 | 18.0175 | 21.7956 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749 | 23.9749
95% | 1.179 | 8.0409 | 28.6173 | 25.2611 |  | 0.3689 | 7.7814 | 13.6076 | 20.0307 | 23.3972 | 26.3131 | 33.5311 | 29.178 | 40.9488 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 | 56.3029 |  | 10.4131 | 17.5568 | 37.9733 | 35.2726 | 3.2837 | 10.8911 | 18.1256 | 24.2892 | 30.7093 | 33.5232 | 37.3639 | 44.4841 | 42.156 | 51.456 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204 | 56.8204
90% |  | 28.2772 | 237.1537 | 202.8751 |  |  | 26.1226 | 83.8512 | 149.4537 | 183.8382 | 213.6193 | 287.3405 | 242.8805 | 363.102 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 | 519.9214 |  | 51.224 | 124.1864 | 332.7113 | 305.1281 | 2.1686 | 56.1066 | 129.9963 | 192.9485 | 258.52 | 287.2603 | 326.487 | 399.2102 | 375.4317 | 470.4173 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207 | 525.207
85% |  |  | 355.147 | 274.3888 |  |  |  | 23.9298 | 148.5312 | 229.5388 | 299.7015 | 473.3843 | 368.639 | 651.8739 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 | 1021.3311 |  | 1.1859 | 90.0175 | 580.2752 | 515.2909 |  | 2.7658 | 102.8299 | 251.0022 | 405.4847 | 473.1953 | 565.6111 | 736.9428 | 680.922 | 904.7024 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837 | 1033.7837
80% |  |  | 229.7771 | 105.07 |  |  |  |  | 5.7768 | 55.9848 | 139.2218 | 443.871 | 254.2072 | 767.0646 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 | 1436.0461 |  |  |  | 637.4198 | 519.7518 |  |  |  | 77.6303 | 320.9242 | 443.5286 | 610.8674 | 921.1 | 819.6625 | 1224.8648 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941 | 1458.5941
75% |  |  | 0.018268 | [8 empty] | 59.6906 | 1.0246 | 351.2628 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 | 1133.4007 |  |  |  | 207.6345 | 107.4524 |  |  |  |  | 11.5126 | 59.5057 | 182.3124 | 531.353 | 412.7575 | 886.4987 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626 | 1159.7626
70% | FY38: 2.5513; FY39: 601.1261; FY40: 601.1261; FY41: 601.1261; FY42: 601.1261; FY43: 601.1261; FY44: 601.1261; FY45: 601.1261; FY46: 601.1261; FY47: 601.1261; FY48: 601.1261; FY49: 601.1261; FY50: 601.1261; FY51: 601.1261; FY52: 601.1261; FY53: 601.1261; FY54: 601.1261 | [12 empty] | 51.0621 | 12.2764 | 316.4572 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405 | 632.0405
65% | FY39: 26.2727; FY40: 26.2727; FY41: 26.2727; FY42: 26.2727; FY43: 26.2727; FY44: 26.2727; FY45: 26.2727; FY46: 26.2727; FY47: 26.2727; FY48: 26.2727; FY49: 26.2727; FY50: 26.2727; FY51: 26.2727; FY52: 26.2727; FY53: 26.2727; FY54: 26.2727 | [15 empty] | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201 | 35.0201
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 8.8773 | 55.3055 | 903.459 | 654.8343 | 0 | 6.1558 | 52.4658 | 149.5089 | 362.4506 | 536.9404 | 727.821 | 1358.6248 | 949.5949 | 2249.7804 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | 4892.5682 | E @ R (MWh) | 85.7023 | 266.36 | 1864.1094 | 1546.5604 | 16.635 | 93.4271 | 286.4845 | 591.515 | 1083.3285 | 1357.8075 | 1789.7373 | 2762.9294 | 2418.1638 | 3944.6117 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447 | 5000.2447
Option 5 Winter POE50 W E @ R (MWh) N 1 | 6.2141 | 38.7139 | 632.4213 | 458.384 | 0 | 4.309 | 36.726 | 104.6562 | 253.7154 | 375.8583 | 509.4747 | 951.0373 | 664.7164 | 1574.8462 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | 3424.7977 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 25.7107 | 79.908 | 559.2328 | 463.9681 | 4.9905 | 28.0281 | 85.9453 | 177.4545 | 324.9986 | 407.3422 | 536.9212 | 828.8788 | 725.4491 | 1183.3835 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734 | 1500.0734
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14.0319 | 15.6995 | 21.011 | 19.3334 | 10.687 | 12.5008 | 13.973 | 15.3891 | 16.6151 | 17.2301 | 18.1365 | 19.1734 | 20.2318 | 21.5631 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709 | 21.7709
98% | 4.1239 | 4.7688 | 7.3905 | 6.5815 | 2.1754 | 3.0666 | 3.6326 | 4.2788 | 4.7951 | 5.1316 | 5.9329 | 6.4872 | 6.7789 | 7.3198 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 | 7.1623 |  | 6.7736 | 7.5991 | 10.2281 | 9.3978 | 5.118 | 6.0158 | 6.7445 | 7.4454 | 8.0523 | 8.3567 | 8.8053 | 9.3186 | 9.8424 | 10.5014 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043 | 10.6043
97% | 3.9085 | 4.5468 | 7.142 | 6.3412 | 1.9798 | 2.862 | 3.4222 | 4.0618 | 4.5729 | 4.9059 | 5.6992 | 6.2478 | 6.5365 | 7.0719 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 | 6.9161 |  | 13.0627 | 14.6968 | 19.9015 | 18.2577 | 9.7851 | 11.5624 | 13.005 | 14.3927 | 15.594 | 16.1966 | 17.0848 | 18.1009 | 19.138 | 20.4425 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462 | 20.6462
95% | 10.7562 | 12.6417 | 20.3074 | 17.9419 | 5.059 | 7.6649 | 9.3198 | 11.2091 | 12.7186 | 13.7025 | 16.0456 | 17.6661 | 18.519 | 20.1005 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 | 19.6402 |  | 24.6715 | 27.8895 | 38.1388 | 34.9017 | 18.2172 | 21.7171 | 24.558 | 27.2906 | 29.6562 | 30.843 | 32.592 | 34.5929 | 36.6352 | 39.2041 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052 | 39.6052
90% | 19.8204 | 24.0596 | 41.294 | 35.9759 | 7.0118 | 12.8705 | 16.5912 | 20.8386 | 24.2326 | 26.4445 | 31.7124 | 35.3559 | 37.2732 | 40.8288 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 | 39.794 |  | 79.7975 | 91.4248 | 128.4583 | 116.7619 | 56.4761 | 69.1222 | 79.3873 | 89.2608 | 97.8085 | 102.0968 | 108.4164 | 115.6462 | 123.0256 | 132.3078 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569 | 133.7569
85% | 21.0539 | 27.9282 | 55.8759 | 47.252 | 1.6121 | 9.7837 | 15.8172 | 22.705 | 28.2087 | 31.7955 | 40.3381 | 46.2465 | 49.3557 | 55.1216 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 | 53.4434 |  | 78.0582 | 91.99 | 136.3635 | 122.3489 | 50.1145 | 65.2671 | 77.5667 | 89.3971 | 99.639 | 104.7772 | 112.3493 | 121.0121 | 129.854 | 140.9759 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123 | 142.7123
80% | 33.197 | 59.6631 | 167.2618 | 134.0597 |  | 2.2073 | 14.6101 | 39.5538 | 60.743 | 74.5523 | 107.4413 | 130.1885 | 142.1589 | 164.3575 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 | 157.8968 |  | 66.6268 | 82.528 | 133.1738 | 117.1782 | 34.7332 | 52.0276 | 66.0659 | 79.5686 | 91.2581 | 97.1227 | 105.7651 | 115.6524 | 125.7442 | 138.4382 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42 | 140.42
75% | 0.70851 | 15.6341 | 171.4842 | 121.1985 |  |  |  | 2.5528 | 16.6385 | 32.0934 | 80.884 | 115.3355 | 133.465 | 167.0856 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 | 157.3006 |  | 35.3916 | 49.0301 | 92.4694 | 78.7498 | 8.3415 | 22.8697 | 34.9105 | 46.4918 | 56.518 | 61.5481 | 68.9608 | 77.4412 | 86.097 | 96.9848 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845 | 98.6845
70% |  |  | 119.6948 | 46.7487 | [6 empty] | 10.656 | 39.9897 | 62.4933 | 112.9755 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 | 98.0283 |  | 11.5438 | 25.9526 | 72.3947 | 57.7268 |  | 2.5833 | 11.0881 | 23.2389 | 33.9582 | 39.3359 | 47.261 | 56.3277 | 65.5818 | 77.2221 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394 | 79.0394
65% |  |  | 9.5592 | [10 empty] | 6.6985 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 | 2.1391 |  |  | 5.6073 | 110.8118 | 72.1188 |  |  |  | 3.258 | 16.07 | 25.9548 | 44.5112 | 68.4281 | 92.8397 | 123.5463 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401 | 128.3401
60% | [33 empty] | 25.9088 | 4.5952 | [7 empty] | 3.4515 | 13.9331 | 36.4871 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066 | 40.9066
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 93.5685 | 149.2423 | 600.0098 | 416.0996 | 17.8381 | 38.455 | 63.3932 | 105.1999 | 151.9093 | 188.6257 | 298.7094 | 397.5173 | 456.5805 | 581.5597 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | 542.3208 | E @ R (MWh) | 329.9576 | 412.4176 | 788.8598 | 651.37 | 193.4726 | 263.6659 | 327.299 | 395.733 | 465.1694 | 503.4618 | 563.8824 | 639.1449 | 722.9227 | 837.6734 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863 | 856.4863
Option 5 Summer POE50 W E @ R (MWh) N 1 | 65.4979 | 104.4696 | 420.0069 | 291.2697 | 12.4867 | 26.9185 | 44.3752 | 73.64 | 106.3365 | 132.038 | 209.0966 | 278.2621 | 319.6063 | 407.0918 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | 379.6245 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 98.9873 | 123.7253 | 236.6579 | 195.411 | 58.0418 | 79.0998 | 98.1897 | 118.7199 | 139.5508 | 151.0385 | 169.1647 | 191.7435 | 216.8768 | 251.302 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459 | 256.9459
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 1.9209 | 4.0605 | 10.4585 | 15.8467 | 18.7535 | 20.8539 | 23.2751 | 25.0866 | 27.0838 | 28.1306 | 29.0373 | 31.2816 | 29.9281 | 33.5881 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 |  | 4.7981 | 7.0193 | 13.3676 | 18.9596 | 21.8766 | 24.242 | 26.4915 | 28.408 | 30.4042 | 31.2792 | 32.4734 | 34.6873 | 33.9634 | 36.8551 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231
98% | 4.4146 | 10.7687 | 29.7698 | 45.7719 | 54.4047 | 60.6427 | 67.8331 | 73.2132 | 79.1445 | 82.2533 | 84.9459 | 91.6113 | 87.5915 | 98.4611 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 |  | 12.9593 | 19.5561 | 38.4094 | 55.0169 | 63.6798 | 70.7047 | 77.3853 | 83.077 | 89.0055 | 91.604 | 95.1506 | 101.7258 | 99.5759 | 108.1638 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175
97% | 1.3628 | 4.1582 | 12.5174 | 19.5572 | 23.3551 | 26.0994 | 29.2627 | 31.6295 | 34.2389 | 35.6066 | 36.7911 | 39.7235 | 37.955 | 42.7369 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 |  | 5.1219 | 8.024 | 16.3182 | 23.6244 | 27.4355 | 30.526 | 33.465 | 35.969 | 38.5771 | 39.7203 | 41.2805 | 44.1731 | 43.2273 | 47.0054 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847
95% | 1.179 | 8.0409 | 28.6173 | 45.9461 | 55.2947 | 62.0499 | 69.8365 | 75.6626 | 82.0857 | 85.4523 | 88.3681 | 95.5861 | 91.2331 | 103.0039 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 |  | 10.4131 | 17.5568 | 37.9733 | 55.9576 | 65.3388 | 72.9462 | 80.1807 | 86.3443 | 92.7643 | 95.5783 | 99.4189 | 106.5392 | 104.2111 | 113.511 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754
90% |  | 28.2772 | 237.1537 | 414.1424 | 509.6246 | 578.6186 | 658.1473 | 717.653 | 783.2556 | 817.64 | 847.4212 | 921.1424 | 876.6824 | 996.9039 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 |  | 51.224 | 124.1864 | 332.7113 | 516.3954 | 612.2101 | 689.9084 | 763.7982 | 826.7504 | 892.3218 | 921.0622 | 960.2889 | 1033.0121 | 1009.2336 | 1104.2192 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089
85% |  |  | 355.147 | 772.122 | 997.0725 | 1159.6182 | 1346.9832 | 1487.1752 | 1641.731 | 1722.7386 | 1792.9013 | 1966.5841 | 1861.8388 | 2145.0736 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 |  | 1.1859 | 90.0175 | 580.2752 | 1013.0241 | 1238.7577 | 1421.8105 | 1595.8904 | 1744.202 | 1898.6845 | 1966.395 | 2058.8109 | 2230.1425 | 2174.1218 | 2397.9022 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834
80% |  |  | 229.7771 | 984.7996 | 1392.1206 | 1686.4445 | 2025.7089 | 2279.5565 | 2559.4129 | 2706.0946 | 2833.1392 | 3147.6291 | 2957.9653 | 3470.8227 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 |  |  |  | 637.4198 | 1421.0045 | 1829.7435 | 2161.1999 | 2476.4087 | 2744.9586 | 3024.6824 | 3147.2868 | 3314.6255 | 3624.8581 | 3523.4206 | 3928.6229 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522
75% |  |  | 0.018268 | 605.8271 | 1082.0453 | 1426.1532 | 1822.8033 | 2119.5884 | 2446.7817 | 2618.2742 | 2766.808 | 3134.493 | 2912.7481 | 3512.3538 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 |  |  |  | 207.6345 | 1115.8148 | 1593.6908 | 1981.2121 | 2349.7376 | 2663.7119 | 2990.7502 | 3134.0927 | 3329.7364 | 3692.4439 | 3573.8485 | 4047.5896 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536
70% |  |  |  | 88.5459 | 540.9022 | 944.4342 | 1409.582 | 1757.6192 | 2141.3156 | 2342.4232 | 2516.6074 | 2947.7881 | 2687.75 | 3390.9019 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 |  |  |  |  | 580.5033 | 1140.904 | 1595.3465 | 2027.5129 | 2395.7076 | 2779.2223 | 2947.3187 | 3176.7482 | 3602.0919 | 3463.0162 | 4018.5679 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022
65% |  |  |  |  | 12.7928 | 190.6991 | 628.7018 | 1010.0877 | 1430.5497 | 1650.9273 | 1841.8016 | 2314.2979 | 2029.3431 | 2799.8706 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 |  |  |  |  | 21.1245 | 348.6064 | 832.2662 | 1305.8425 | 1709.3174 | 2129.5801 | 2313.7835 | 2565.1967 | 3031.2966 | 2878.8947 | 3487.6791 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388
60% | [6 empty] | 7.3484 | 128.2902 | 422.9124 | 640.2703 | 847.9131 | 1362.0067 | 1051.9652 | 1890.328 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | [6 empty] | 53.8499 | 318.7033 | 703.7652 | 1161.0269 | 1361.4471 | 1634.9941 | 2142.1283 | 1976.3093 | 2638.6896 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645
55% | [10 empty] | 14.8991 | 187.3598 | 60.791 | 551.5769 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | [8 empty] | 1.1011 | 97.6428 | 187.0714 | 352.9682 | 786.9367 | 627.6332 | 1284.6962 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932
50% | FY39: 268.0325; FY40: 268.0325; FY41: 268.0325; FY42: 268.0325; FY43: 268.0325; FY44: 268.0325; FY45: 268.0325; FY46: 268.0325; FY47: 268.0325; FY48: 268.0325; FY49: 268.0325; FY50: 268.0325; FY51: 268.0325; FY52: 268.0325; FY53: 268.0325; FY54: 268.0325 | [12 empty] | 0.074826 |  | 97.2035 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 8.8773 | 55.3055 | 903.459 | 2992.5588 | 4686.3661 | 6155.6135 | 8089.4822 | 9705.5622 | 11648.5119 | 12729.8111 | 13700.6333 | 16239.5036 | 14685.7915 | 19035.6214 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | E @ R (MWh) | 85.7023 | 266.36 | 1864.1094 | 4821.4253 | 6942.2431 | 8934.0123 | 11055.4161 | 13023.3125 | 15224.6621 | 16236.6391 | 17661.6923 | 20430.1104 | 19507.4556 | 23310.7057 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597
Option 6 Winter POE50 W E @ R (MWh) N 1 | 6.2141 | 38.7139 | 632.4213 | 2094.7912 | 3280.4563 | 4308.9295 | 5662.6375 | 6793.8935 | 8153.9583 | 8910.8678 | 9590.4433 | 11367.6525 | 10280.054 | 13324.935 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 25.7107 | 79.908 | 559.2328 | 1446.4276 | 2082.6729 | 2680.2037 | 3316.6248 | 3906.9937 | 4567.3986 | 4870.9917 | 5298.5077 | 6129.0331 | 5852.2367 | 6993.2117 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14.0319 | 15.6995 | 21.011 | 24.7894 | 27.0549 | 28.8687 | 30.3409 | 31.757 | 32.983 | 33.598 | 34.5044 | 35.5413 | 36.5997 | 37.931 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388
98% | 4.1239 | 4.7688 | 7.3905 | 9.2821 | 10.2771 | 11.1683 | 11.7343 | 12.3805 | 12.8968 | 13.2333 | 14.0346 | 14.5889 | 14.8806 | 15.4215 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 |  | 6.7736 | 7.5991 | 10.2281 | 12.0983 | 13.2197 | 14.1175 | 14.8462 | 15.5471 | 16.154 | 16.4584 | 16.907 | 17.4203 | 17.9441 | 18.6031 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706
97% | 3.9085 | 4.5468 | 7.142 | 9.0143 | 9.9992 | 10.8814 | 11.4417 | 12.0813 | 12.5923 | 12.9254 | 13.7186 | 14.2673 | 14.556 | 15.0914 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 |  | 13.0627 | 14.6968 | 19.9015 | 23.604 | 25.824 | 27.6013 | 29.0439 | 30.4315 | 31.6328 | 32.2355 | 33.1237 | 34.1398 | 35.1769 | 36.4814 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851
95% | 10.7562 | 12.6417 | 20.3074 | 25.838 | 28.7473 | 31.3531 | 33.008 | 34.8973 | 36.4068 | 37.3907 | 39.7338 | 41.3544 | 42.2072 | 43.7887 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 |  | 24.6715 | 27.8895 | 38.1388 | 45.4298 | 49.8015 | 53.3014 | 56.1423 | 58.8749 | 61.2405 | 62.4273 | 64.1763 | 66.1772 | 68.2195 | 70.7884 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895
90% | 19.8204 | 24.0596 | 41.294 | 53.7284 | 60.2691 | 66.1278 | 69.8485 | 74.096 | 77.4899 | 79.7018 | 84.9697 | 88.6132 | 90.5306 | 94.0862 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 |  | 79.7975 | 91.4248 | 128.4583 | 154.8028 | 170.5989 | 183.2451 | 193.5102 | 203.3837 | 211.9314 | 216.2197 | 222.5393 | 229.7691 | 237.1484 | 246.4307 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798
85% | 21.0539 | 27.9282 | 55.8759 | 76.0398 | 86.6464 | 96.1469 | 102.1805 | 109.0683 | 114.5719 | 118.1588 | 126.7014 | 132.6098 | 135.719 | 141.4848 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 |  | 78.0582 | 91.99 | 136.3635 | 167.9295 | 186.8563 | 202.0089 | 214.3085 | 226.139 | 236.3808 | 241.519 | 249.0911 | 257.7539 | 266.5958 | 277.7178 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541
80% | 33.197 | 59.6631 | 167.2618 | 244.8926 | 285.728 | 322.3052 | 345.5345 | 372.0524 | 393.2415 | 407.0509 | 439.9399 | 462.6871 | 474.6575 | 496.8561 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 |  | 66.6268 | 82.528 | 133.1738 | 169.2018 | 190.804 | 208.0984 | 222.1367 | 235.6393 | 247.3289 | 253.1934 | 261.8359 | 271.7232 | 281.8149 | 294.509 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908
75% | 0.70851 | 15.6341 | 171.4842 | 289.0586 | 350.9052 | 406.3026 | 441.4841 | 481.6463 | 513.738 | 534.6527 | 584.4641 | 618.9156 | 637.0452 | 670.6657 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 |  | 35.3916 | 49.0301 | 92.4694 | 123.3709 | 141.8993 | 156.7328 | 168.7735 | 180.3549 | 190.3811 | 195.4111 | 202.8239 | 211.3043 | 219.96 | 230.8478 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476
70% |  |  | 119.6948 | 299.2969 | 393.7715 | 478.3945 | 532.1363 | 593.4867 | 642.5087 | 674.4572 | 750.5473 | 803.174 | 830.8681 | 882.2255 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 |  | 11.5438 | 25.9526 | 72.3947 | 105.4322 | 125.2414 | 141.1003 | 153.9733 | 166.3552 | 177.0745 | 182.4522 | 190.3773 | 199.4439 | 208.698 | 220.3384 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557
65% |  |  | 9.5592 | 248.267 | 420.7759 | 575.296 | 673.4277 | 785.4524 | 874.9657 | 933.3031 | 1072.2422 | 1168.3378 | 1218.9066 | 1312.6844 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 |  |  | 5.6073 | 110.8118 | 197.9624 | 250.2177 | 292.0523 | 326.0105 | 358.6731 | 386.9498 | 401.1359 | 422.0418 | 445.9589 | 470.3706 | 501.0772 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871
60% |  |  |  | 19.2882 | 179.2375 | 445.6738 | 636.3776 | 854.0805 | 1028.0358 | 1141.4057 | 1411.4125 | 1598.1595 | 1696.4322 | 1878.6749 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 |  |  |  | 25.9088 | 117.2122 | 175.5582 | 222.269 | 260.1852 | 296.6549 | 328.2275 | 344.0671 | 367.4098 | 394.1146 | 421.3716 | 455.6573 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099
55% | [5 empty] | 3.4714 | 49.8086 | 165.5048 | 303.2996 | 413.7128 | 721.1439 | 937.6016 | 1051.5091 | 1262.7459 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 |  |  |  |  | 23.1943 | 88.6401 | 163.3146 | 224.9978 | 284.3278 | 335.6911 | 361.4593 | 399.4339 | 442.878 | 487.2206 | 542.9975 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052
50% | [10 empty] | 22.6091 | 95.641 | 153.4846 | 294.6713 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | [6 empty] | 9.7618 | 46.9146 | 107.2018 | 177.6453 | 219.0596 | 284.9847 | 360.7613 | 438.1048 | 535.3924 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807
45% | [41 empty] | 4.8627 | 31.6552 | 82.2002 | 177.4776 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 93.5685 | 149.2423 | 600.0098 | 1274.7059 | 1826.3571 | 2447.1212 | 2906.9819 | 3494.7464 | 4009.7471 | 4365.9923 | 5281.5172 | 5975.9501 | 6360.7964 | 7108.3964 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | E @ R (MWh) | 329.9576 | 412.4176 | 788.8598 | 1165.0275 | 1445.7159 | 1702.472 | 1941.1838 | 2195.3401 | 2433.6207 | 2559.2366 | 2754.1117 | 2998.641 | 3271.4254 | 3646.2496 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389
Option 6 Summer POE50 W E @ R (MWh) N 1 | 65.4979 | 104.4696 | 420.0069 | 892.2941 | 1278.45 | 1712.9848 | 2034.8873 | 2446.3225 | 2806.823 | 3056.1946 | 3697.062 | 4183.1651 | 4452.5575 | 4975.8775 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 98.9873 | 123.7253 | 236.6579 | 349.5083 | 433.7148 | 510.7416 | 582.3551 | 658.602 | 730.0862 | 767.771 | 826.2335 | 899.5923 | 981.4276 | 1093.8749 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 1.9209 | 4.0605 | 10.4585 | 15.8467 | 18.7535 | 20.8539 | 23.2751 | 25.0866 | 27.0838 | 28.1306 | 29.0373 | 31.2816 | 29.9281 | 33.5881 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 |  | 4.7981 | 7.0193 | 13.3676 | 18.9596 | 21.8766 | 24.242 | 26.4915 | 28.408 | 30.4042 | 31.2792 | 32.4734 | 34.6873 | 33.9634 | 36.8551 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231
98% | 4.4146 | 10.7687 | 29.7698 | 45.7719 | 54.4047 | 60.6427 | 67.8331 | 73.2132 | 79.1445 | 82.2533 | 84.9459 | 91.6113 | 87.5915 | 98.4611 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 |  | 12.9593 | 19.5561 | 38.4094 | 55.0169 | 63.6798 | 70.7047 | 77.3853 | 83.077 | 89.0055 | 91.604 | 95.1506 | 101.7258 | 99.5759 | 108.1638 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175
97% | 1.3628 | 4.1582 | 12.5174 | 19.5572 | 23.3551 | 26.0994 | 29.2627 | 31.6295 | 34.2389 | 35.6066 | 36.7911 | 39.7235 | 37.955 | 42.7369 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 |  | 5.1219 | 8.024 | 16.3182 | 23.6244 | 27.4355 | 30.526 | 33.465 | 35.969 | 38.5771 | 39.7203 | 41.2805 | 44.1731 | 43.2273 | 47.0054 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847
95% | 1.179 | 8.0409 | 28.6173 | 45.9461 | 55.2947 | 62.0499 | 69.8365 | 75.6626 | 82.0857 | 85.4523 | 88.3681 | 95.5861 | 91.2331 | 103.0039 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 |  | 10.4131 | 17.5568 | 37.9733 | 55.9576 | 65.3388 | 72.9462 | 80.1807 | 86.3443 | 92.7643 | 95.5783 | 99.4189 | 106.5392 | 104.2111 | 113.511 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754
90% |  | 28.2772 | 237.1537 | 414.1424 | 509.6246 | 578.6186 | 658.1473 | 717.653 | 783.2556 | 817.64 | 847.4212 | 921.1424 | 876.6824 | 996.9039 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 |  | 51.224 | 124.1864 | 332.7113 | 516.3954 | 612.2101 | 689.9084 | 763.7982 | 826.7504 | 892.3218 | 921.0622 | 960.2889 | 1033.0121 | 1009.2336 | 1104.2192 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089
85% |  |  | 355.147 | 772.122 | 997.0725 | 1159.6182 | 1346.9832 | 1487.1752 | 1641.731 | 1722.7386 | 1792.9013 | 1966.5841 | 1861.8388 | 2145.0736 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 |  | 1.1859 | 90.0175 | 580.2752 | 1013.0241 | 1238.7577 | 1421.8105 | 1595.8904 | 1744.202 | 1898.6845 | 1966.395 | 2058.8109 | 2230.1425 | 2174.1218 | 2397.9022 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834
80% |  |  | 229.7771 | 984.7996 | 1392.1206 | 1686.4445 | 2025.7089 | 2279.5565 | 2559.4129 | 2706.0946 | 2833.1392 | 3147.6291 | 2957.9653 | 3470.8227 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 |  |  |  | 637.4198 | 1421.0045 | 1829.7435 | 2161.1999 | 2476.4087 | 2744.9586 | 3024.6824 | 3147.2868 | 3314.6255 | 3624.8581 | 3523.4206 | 3928.6229 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522
75% |  |  | 0.018268 | 605.8271 | 1082.0453 | 1426.1532 | 1822.8033 | 2119.5884 | 2446.7817 | 2618.2742 | 2766.808 | 3134.493 | 2912.7481 | 3512.3538 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 |  |  |  | 207.6345 | 1115.8148 | 1593.6908 | 1981.2121 | 2349.7376 | 2663.7119 | 2990.7502 | 3134.0927 | 3329.7364 | 3692.4439 | 3573.8485 | 4047.5896 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536
70% |  |  |  | 88.5459 | 540.9022 | 944.4342 | 1409.582 | 1757.6192 | 2141.3156 | 2342.4232 | 2516.6074 | 2947.7881 | 2687.75 | 3390.9019 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 |  |  |  |  | 580.5033 | 1140.904 | 1595.3465 | 2027.5129 | 2395.7076 | 2779.2223 | 2947.3187 | 3176.7482 | 3602.0919 | 3463.0162 | 4018.5679 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022
65% |  |  |  |  | 12.7928 | 190.6991 | 628.7018 | 1010.0877 | 1430.5497 | 1650.9273 | 1841.8016 | 2314.2979 | 2029.3431 | 2799.8706 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 |  |  |  |  | 21.1245 | 348.6064 | 832.2662 | 1305.8425 | 1709.3174 | 2129.5801 | 2313.7835 | 2565.1967 | 3031.2966 | 2878.8947 | 3487.6791 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388
60% | [6 empty] | 7.3484 | 128.2902 | 422.9124 | 640.2703 | 847.9131 | 1362.0067 | 1051.9652 | 1890.328 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | [6 empty] | 53.8499 | 318.7033 | 703.7652 | 1161.0269 | 1361.4471 | 1634.9941 | 2142.1283 | 1976.3093 | 2638.6896 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645
55% | [10 empty] | 14.8991 | 187.3598 | 60.791 | 551.5769 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | [8 empty] | 1.1011 | 97.6428 | 187.0714 | 352.9682 | 786.9367 | 627.6332 | 1284.6962 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932
50% | FY39: 268.0325; FY40: 268.0325; FY41: 268.0325; FY42: 268.0325; FY43: 268.0325; FY44: 268.0325; FY45: 268.0325; FY46: 268.0325; FY47: 268.0325; FY48: 268.0325; FY49: 268.0325; FY50: 268.0325; FY51: 268.0325; FY52: 268.0325; FY53: 268.0325; FY54: 268.0325 | [12 empty] | 0.074826 |  | 97.2035 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 8.8773 | 55.3055 | 903.459 | 2992.5588 | 4686.3661 | 6155.6135 | 8089.4822 | 9705.5622 | 11648.5119 | 12729.8111 | 13700.6333 | 16239.5036 | 14685.7915 | 19035.6214 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | E @ R (MWh) | 85.7023 | 266.36 | 1864.1094 | 4821.4253 | 6942.2431 | 8934.0123 | 11055.4161 | 13023.3125 | 15224.6621 | 16236.6391 | 17661.6923 | 20430.1104 | 19507.4556 | 23310.7057 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597
Option 7 Winter POE50 W E @ R (MWh) N 1 | 6.2141 | 38.7139 | 632.4213 | 2094.7912 | 3280.4563 | 4308.9295 | 5662.6375 | 6793.8935 | 8153.9583 | 8910.8678 | 9590.4433 | 11367.6525 | 10280.054 | 13324.935 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 25.7107 | 79.908 | 559.2328 | 1446.4276 | 2082.6729 | 2680.2037 | 3316.6248 | 3906.9937 | 4567.3986 | 4870.9917 | 5298.5077 | 6129.0331 | 5852.2367 | 6993.2117 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14.0319 | 15.6995 | 21.011 | 24.7894 | 27.0549 | 28.8687 | 30.3409 | 31.757 | 32.983 | 33.598 | 34.5044 | 35.5413 | 36.5997 | 37.931 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388
98% | 4.1239 | 4.7688 | 7.3905 | 9.2821 | 10.2771 | 11.1683 | 11.7343 | 12.3805 | 12.8968 | 13.2333 | 14.0346 | 14.5889 | 14.8806 | 15.4215 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 |  | 6.7736 | 7.5991 | 10.2281 | 12.0983 | 13.2197 | 14.1175 | 14.8462 | 15.5471 | 16.154 | 16.4584 | 16.907 | 17.4203 | 17.9441 | 18.6031 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706
97% | 3.9085 | 4.5468 | 7.142 | 9.0143 | 9.9992 | 10.8814 | 11.4417 | 12.0813 | 12.5923 | 12.9254 | 13.7186 | 14.2673 | 14.556 | 15.0914 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 |  | 13.0627 | 14.6968 | 19.9015 | 23.604 | 25.824 | 27.6013 | 29.0439 | 30.4315 | 31.6328 | 32.2355 | 33.1237 | 34.1398 | 35.1769 | 36.4814 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851
95% | 10.7562 | 12.6417 | 20.3074 | 25.838 | 28.7473 | 31.3531 | 33.008 | 34.8973 | 36.4068 | 37.3907 | 39.7338 | 41.3544 | 42.2072 | 43.7887 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 |  | 24.6715 | 27.8895 | 38.1388 | 45.4298 | 49.8015 | 53.3014 | 56.1423 | 58.8749 | 61.2405 | 62.4273 | 64.1763 | 66.1772 | 68.2195 | 70.7884 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895
90% | 19.8204 | 24.0596 | 41.294 | 53.7284 | 60.2691 | 66.1278 | 69.8485 | 74.096 | 77.4899 | 79.7018 | 84.9697 | 88.6132 | 90.5306 | 94.0862 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 |  | 79.7975 | 91.4248 | 128.4583 | 154.8028 | 170.5989 | 183.2451 | 193.5102 | 203.3837 | 211.9314 | 216.2197 | 222.5393 | 229.7691 | 237.1484 | 246.4307 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798
85% | 21.0539 | 27.9282 | 55.8759 | 76.0398 | 86.6464 | 96.1469 | 102.1805 | 109.0683 | 114.5719 | 118.1588 | 126.7014 | 132.6098 | 135.719 | 141.4848 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 |  | 78.0582 | 91.99 | 136.3635 | 167.9295 | 186.8563 | 202.0089 | 214.3085 | 226.139 | 236.3808 | 241.519 | 249.0911 | 257.7539 | 266.5958 | 277.7178 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541
80% | 33.197 | 59.6631 | 167.2618 | 244.8926 | 285.728 | 322.3052 | 345.5345 | 372.0524 | 393.2415 | 407.0509 | 439.9399 | 462.6871 | 474.6575 | 496.8561 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 |  | 66.6268 | 82.528 | 133.1738 | 169.2018 | 190.804 | 208.0984 | 222.1367 | 235.6393 | 247.3289 | 253.1934 | 261.8359 | 271.7232 | 281.8149 | 294.509 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908
75% | 0.70851 | 15.6341 | 171.4842 | 289.0586 | 350.9052 | 406.3026 | 441.4841 | 481.6463 | 513.738 | 534.6527 | 584.4641 | 618.9156 | 637.0452 | 670.6657 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 |  | 35.3916 | 49.0301 | 92.4694 | 123.3709 | 141.8993 | 156.7328 | 168.7735 | 180.3549 | 190.3811 | 195.4111 | 202.8239 | 211.3043 | 219.96 | 230.8478 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476
70% |  |  | 119.6948 | 299.2969 | 393.7715 | 478.3945 | 532.1363 | 593.4867 | 642.5087 | 674.4572 | 750.5473 | 803.174 | 830.8681 | 882.2255 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 |  | 11.5438 | 25.9526 | 72.3947 | 105.4322 | 125.2414 | 141.1003 | 153.9733 | 166.3552 | 177.0745 | 182.4522 | 190.3773 | 199.4439 | 208.698 | 220.3384 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557
65% |  |  | 9.5592 | 248.267 | 420.7759 | 575.296 | 673.4277 | 785.4524 | 874.9657 | 933.3031 | 1072.2422 | 1168.3378 | 1218.9066 | 1312.6844 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 |  |  | 5.6073 | 110.8118 | 197.9624 | 250.2177 | 292.0523 | 326.0105 | 358.6731 | 386.9498 | 401.1359 | 422.0418 | 445.9589 | 470.3706 | 501.0772 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871
60% |  |  |  | 19.2882 | 179.2375 | 445.6738 | 636.3776 | 854.0805 | 1028.0358 | 1141.4057 | 1411.4125 | 1598.1595 | 1696.4322 | 1878.6749 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 |  |  |  | 25.9088 | 117.2122 | 175.5582 | 222.269 | 260.1852 | 296.6549 | 328.2275 | 344.0671 | 367.4098 | 394.1146 | 421.3716 | 455.6573 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099
55% | [5 empty] | 3.4714 | 49.8086 | 165.5048 | 303.2996 | 413.7128 | 721.1439 | 937.6016 | 1051.5091 | 1262.7459 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 |  |  |  |  | 23.1943 | 88.6401 | 163.3146 | 224.9978 | 284.3278 | 335.6911 | 361.4593 | 399.4339 | 442.878 | 487.2206 | 542.9975 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052
50% | [10 empty] | 22.6091 | 95.641 | 153.4846 | 294.6713 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | [6 empty] | 9.7618 | 46.9146 | 107.2018 | 177.6453 | 219.0596 | 284.9847 | 360.7613 | 438.1048 | 535.3924 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807
45% | [41 empty] | 4.8627 | 31.6552 | 82.2002 | 177.4776 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 93.5685 | 149.2423 | 600.0098 | 1274.7059 | 1826.3571 | 2447.1212 | 2906.9819 | 3494.7464 | 4009.7471 | 4365.9923 | 5281.5172 | 5975.9501 | 6360.7964 | 7108.3964 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | E @ R (MWh) | 329.9576 | 412.4176 | 788.8598 | 1165.0275 | 1445.7159 | 1702.472 | 1941.1838 | 2195.3401 | 2433.6207 | 2559.2366 | 2754.1117 | 2998.641 | 3271.4254 | 3646.2496 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389
Option 7 Summer POE50 W E @ R (MWh) N 1 | 65.4979 | 104.4696 | 420.0069 | 892.2941 | 1278.45 | 1712.9848 | 2034.8873 | 2446.3225 | 2806.823 | 3056.1946 | 3697.062 | 4183.1651 | 4452.5575 | 4975.8775 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 98.9873 | 123.7253 | 236.6579 | 349.5083 | 433.7148 | 510.7416 | 582.3551 | 658.602 | 730.0862 | 767.771 | 826.2335 | 899.5923 | 981.4276 | 1093.8749 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 1.9209 | 4.0605 | 10.4585 | 15.8467 | 18.7535 | 20.8539 | 23.2751 | 25.0866 | 27.0838 | 28.1306 | 29.0373 | 31.2816 | 29.9281 | 33.5881 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 | 38.3622 |  | 4.7981 | 7.0193 | 13.3676 | 18.9596 | 21.8766 | 24.242 | 26.4915 | 28.408 | 30.4042 | 31.2792 | 32.4734 | 34.6873 | 33.9634 | 36.8551 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231 | 38.5231
98% | 4.4146 | 10.7687 | 29.7698 | 45.7719 | 54.4047 | 60.6427 | 67.8331 | 73.2132 | 79.1445 | 82.2533 | 84.9459 | 91.6113 | 87.5915 | 98.4611 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 | 112.6396 |  | 12.9593 | 19.5561 | 38.4094 | 55.0169 | 63.6798 | 70.7047 | 77.3853 | 83.077 | 89.0055 | 91.604 | 95.1506 | 101.7258 | 99.5759 | 108.1638 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175 | 113.1175
97% | 1.3628 | 4.1582 | 12.5174 | 19.5572 | 23.3551 | 26.0994 | 29.2627 | 31.6295 | 34.2389 | 35.6066 | 36.7911 | 39.7235 | 37.955 | 42.7369 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 | 48.9745 |  | 5.1219 | 8.024 | 16.3182 | 23.6244 | 27.4355 | 30.526 | 33.465 | 35.969 | 38.5771 | 39.7203 | 41.2805 | 44.1731 | 43.2273 | 47.0054 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847 | 49.1847
95% | 1.179 | 8.0409 | 28.6173 | 45.9461 | 55.2947 | 62.0499 | 69.8365 | 75.6626 | 82.0857 | 85.4523 | 88.3681 | 95.5861 | 91.2331 | 103.0039 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 | 118.3579 |  | 10.4131 | 17.5568 | 37.9733 | 55.9576 | 65.3388 | 72.9462 | 80.1807 | 86.3443 | 92.7643 | 95.5783 | 99.4189 | 106.5392 | 104.2111 | 113.511 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754 | 118.8754
90% |  | 28.2772 | 237.1537 | 414.1424 | 509.6246 | 578.6186 | 658.1473 | 717.653 | 783.2556 | 817.64 | 847.4212 | 921.1424 | 876.6824 | 996.9039 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 | 1153.7233 |  | 51.224 | 124.1864 | 332.7113 | 516.3954 | 612.2101 | 689.9084 | 763.7982 | 826.7504 | 892.3218 | 921.0622 | 960.2889 | 1033.0121 | 1009.2336 | 1104.2192 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089 | 1159.0089
85% |  |  | 355.147 | 772.122 | 997.0725 | 1159.6182 | 1346.9832 | 1487.1752 | 1641.731 | 1722.7386 | 1792.9013 | 1966.5841 | 1861.8388 | 2145.0736 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 | 2514.5309 |  | 1.1859 | 90.0175 | 580.2752 | 1013.0241 | 1238.7577 | 1421.8105 | 1595.8904 | 1744.202 | 1898.6845 | 1966.395 | 2058.8109 | 2230.1425 | 2174.1218 | 2397.9022 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834 | 2526.9834
80% |  |  | 229.7771 | 984.7996 | 1392.1206 | 1686.4445 | 2025.7089 | 2279.5565 | 2559.4129 | 2706.0946 | 2833.1392 | 3147.6291 | 2957.9653 | 3470.8227 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 | 4139.8042 |  |  |  | 637.4198 | 1421.0045 | 1829.7435 | 2161.1999 | 2476.4087 | 2744.9586 | 3024.6824 | 3147.2868 | 3314.6255 | 3624.8581 | 3523.4206 | 3928.6229 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522 | 4162.3522
75% |  |  | 0.018268 | 605.8271 | 1082.0453 | 1426.1532 | 1822.8033 | 2119.5884 | 2446.7817 | 2618.2742 | 2766.808 | 3134.493 | 2912.7481 | 3512.3538 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 | 4294.4916 |  |  |  | 207.6345 | 1115.8148 | 1593.6908 | 1981.2121 | 2349.7376 | 2663.7119 | 2990.7502 | 3134.0927 | 3329.7364 | 3692.4439 | 3573.8485 | 4047.5896 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536 | 4320.8536
70% |  |  |  | 88.5459 | 540.9022 | 944.4342 | 1409.582 | 1757.6192 | 2141.3156 | 2342.4232 | 2516.6074 | 2947.7881 | 2687.75 | 3390.9019 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 | 4308.1076 |  |  |  |  | 580.5033 | 1140.904 | 1595.3465 | 2027.5129 | 2395.7076 | 2779.2223 | 2947.3187 | 3176.7482 | 3602.0919 | 3463.0162 | 4018.5679 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022 | 4339.022
65% |  |  |  |  | 12.7928 | 190.6991 | 628.7018 | 1010.0877 | 1430.5497 | 1650.9273 | 1841.8016 | 2314.2979 | 2029.3431 | 2799.8706 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 | 3804.9622 |  |  |  |  | 21.1245 | 348.6064 | 832.2662 | 1305.8425 | 1709.3174 | 2129.5801 | 2313.7835 | 2565.1967 | 3031.2966 | 2878.8947 | 3487.6791 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388 | 3838.8388
60% | [6 empty] | 7.3484 | 128.2902 | 422.9124 | 640.2703 | 847.9131 | 1362.0067 | 1051.9652 | 1890.328 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | 2983.9055 | [6 empty] | 53.8499 | 318.7033 | 703.7652 | 1161.0269 | 1361.4471 | 1634.9941 | 2142.1283 | 1976.3093 | 2638.6896 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645 | 3020.7645
55% | [10 empty] | 14.8991 | 187.3598 | 60.791 | 551.5769 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | 1630.7453 | [8 empty] | 1.1011 | 97.6428 | 187.0714 | 352.9682 | 786.9367 | 627.6332 | 1284.6962 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932 | 1667.6932
50% | FY39: 268.0325; FY40: 268.0325; FY41: 268.0325; FY42: 268.0325; FY43: 268.0325; FY44: 268.0325; FY45: 268.0325; FY46: 268.0325; FY47: 268.0325; FY48: 268.0325; FY49: 268.0325; FY50: 268.0325; FY51: 268.0325; FY52: 268.0325; FY53: 268.0325; FY54: 268.0325 | [12 empty] | 0.074826 |  | 97.2035 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422 | 291.0422
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 8.8773 | 55.3055 | 903.459 | 2992.5588 | 4686.3661 | 6155.6135 | 8089.4822 | 9705.5622 | 11648.5119 | 12729.8111 | 13700.6333 | 16239.5036 | 14685.7915 | 19035.6214 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | 25416.6374 | E @ R (MWh) | 85.7023 | 266.36 | 1864.1094 | 4821.4253 | 6942.2431 | 8934.0123 | 11055.4161 | 13023.3125 | 15224.6621 | 16236.6391 | 17661.6923 | 20430.1104 | 19507.4556 | 23310.7057 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597 | 25646.2597
Option 8 Winter POE50 W E @ R (MWh) N 1 | 6.2141 | 38.7139 | 632.4213 | 2094.7912 | 3280.4563 | 4308.9295 | 5662.6375 | 6793.8935 | 8153.9583 | 8910.8678 | 9590.4433 | 11367.6525 | 10280.054 | 13324.935 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | 17791.6462 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 25.7107 | 79.908 | 559.2328 | 1446.4276 | 2082.6729 | 2680.2037 | 3316.6248 | 3906.9937 | 4567.3986 | 4870.9917 | 5298.5077 | 6129.0331 | 5852.2367 | 6993.2117 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779 | 7693.8779
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14.0319 | 15.6995 | 21.011 | 24.7894 | 27.0549 | 28.8687 | 30.3409 | 31.757 | 32.983 | 33.598 | 34.5044 | 35.5413 | 36.5997 | 37.931 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388
98% | 4.1239 | 4.7688 | 7.3905 | 9.2821 | 10.2771 | 11.1683 | 11.7343 | 12.3805 | 12.8968 | 13.2333 | 14.0346 | 14.5889 | 14.8806 | 15.4215 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 |  | 6.7736 | 7.5991 | 10.2281 | 12.0983 | 13.2197 | 14.1175 | 14.8462 | 15.5471 | 16.154 | 16.4584 | 16.907 | 17.4203 | 17.9441 | 18.6031 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706
97% | 3.9085 | 4.5468 | 7.142 | 9.0143 | 9.9992 | 10.8814 | 11.4417 | 12.0813 | 12.5923 | 12.9254 | 13.7186 | 14.2673 | 14.556 | 15.0914 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 |  | 13.0627 | 14.6968 | 19.9015 | 23.604 | 25.824 | 27.6013 | 29.0439 | 30.4315 | 31.6328 | 32.2355 | 33.1237 | 34.1398 | 35.1769 | 36.4814 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851
95% | 10.7562 | 12.6417 | 20.3074 | 25.838 | 28.7473 | 31.3531 | 33.008 | 34.8973 | 36.4068 | 37.3907 | 39.7338 | 41.3544 | 42.2072 | 43.7887 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 |  | 24.6715 | 27.8895 | 38.1388 | 45.4298 | 49.8015 | 53.3014 | 56.1423 | 58.8749 | 61.2405 | 62.4273 | 64.1763 | 66.1772 | 68.2195 | 70.7884 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895
90% | 19.8204 | 24.0596 | 41.294 | 53.7284 | 60.2691 | 66.1278 | 69.8485 | 74.096 | 77.4899 | 79.7018 | 84.9697 | 88.6132 | 90.5306 | 94.0862 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 |  | 79.7975 | 91.4248 | 128.4583 | 154.8028 | 170.5989 | 183.2451 | 193.5102 | 203.3837 | 211.9314 | 216.2197 | 222.5393 | 229.7691 | 237.1484 | 246.4307 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798
85% | 21.0539 | 27.9282 | 55.8759 | 76.0398 | 86.6464 | 96.1469 | 102.1805 | 109.0683 | 114.5719 | 118.1588 | 126.7014 | 132.6098 | 135.719 | 141.4848 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 |  | 78.0582 | 91.99 | 136.3635 | 167.9295 | 186.8563 | 202.0089 | 214.3085 | 226.139 | 236.3808 | 241.519 | 249.0911 | 257.7539 | 266.5958 | 277.7178 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541
80% | 33.197 | 59.6631 | 167.2618 | 244.8926 | 285.728 | 322.3052 | 345.5345 | 372.0524 | 393.2415 | 407.0509 | 439.9399 | 462.6871 | 474.6575 | 496.8561 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 |  | 66.6268 | 82.528 | 133.1738 | 169.2018 | 190.804 | 208.0984 | 222.1367 | 235.6393 | 247.3289 | 253.1934 | 261.8359 | 271.7232 | 281.8149 | 294.509 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908
75% | 0.70851 | 15.6341 | 171.4842 | 289.0586 | 350.9052 | 406.3026 | 441.4841 | 481.6463 | 513.738 | 534.6527 | 584.4641 | 618.9156 | 637.0452 | 670.6657 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 |  | 35.3916 | 49.0301 | 92.4694 | 123.3709 | 141.8993 | 156.7328 | 168.7735 | 180.3549 | 190.3811 | 195.4111 | 202.8239 | 211.3043 | 219.96 | 230.8478 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476
70% |  |  | 119.6948 | 299.2969 | 393.7715 | 478.3945 | 532.1363 | 593.4867 | 642.5087 | 674.4572 | 750.5473 | 803.174 | 830.8681 | 882.2255 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 |  | 11.5438 | 25.9526 | 72.3947 | 105.4322 | 125.2414 | 141.1003 | 153.9733 | 166.3552 | 177.0745 | 182.4522 | 190.3773 | 199.4439 | 208.698 | 220.3384 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557
65% |  |  | 9.5592 | 248.267 | 420.7759 | 575.296 | 673.4277 | 785.4524 | 874.9657 | 933.3031 | 1072.2422 | 1168.3378 | 1218.9066 | 1312.6844 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 |  |  | 5.6073 | 110.8118 | 197.9624 | 250.2177 | 292.0523 | 326.0105 | 358.6731 | 386.9498 | 401.1359 | 422.0418 | 445.9589 | 470.3706 | 501.0772 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871
60% |  |  |  | 19.2882 | 179.2375 | 445.6738 | 636.3776 | 854.0805 | 1028.0358 | 1141.4057 | 1411.4125 | 1598.1595 | 1696.4322 | 1878.6749 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 |  |  |  | 25.9088 | 117.2122 | 175.5582 | 222.269 | 260.1852 | 296.6549 | 328.2275 | 344.0671 | 367.4098 | 394.1146 | 421.3716 | 455.6573 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099
55% | [5 empty] | 3.4714 | 49.8086 | 165.5048 | 303.2996 | 413.7128 | 721.1439 | 937.6016 | 1051.5091 | 1262.7459 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 |  |  |  |  | 23.1943 | 88.6401 | 163.3146 | 224.9978 | 284.3278 | 335.6911 | 361.4593 | 399.4339 | 442.878 | 487.2206 | 542.9975 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052
50% | [10 empty] | 22.6091 | 95.641 | 153.4846 | 294.6713 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | [6 empty] | 9.7618 | 46.9146 | 107.2018 | 177.6453 | 219.0596 | 284.9847 | 360.7613 | 438.1048 | 535.3924 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807
45% | [41 empty] | 4.8627 | 31.6552 | 82.2002 | 177.4776 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 93.5685 | 149.2423 | 600.0098 | 1274.7059 | 1826.3571 | 2447.1212 | 2906.9819 | 3494.7464 | 4009.7471 | 4365.9923 | 5281.5172 | 5975.9501 | 6360.7964 | 7108.3964 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | E @ R (MWh) | 329.9576 | 412.4176 | 788.8598 | 1165.0275 | 1445.7159 | 1702.472 | 1941.1838 | 2195.3401 | 2433.6207 | 2559.2366 | 2754.1117 | 2998.641 | 3271.4254 | 3646.2496 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389
Option 8 Summer POE50 W E @ R (MWh) N 1 | 65.4979 | 104.4696 | 420.0069 | 892.2941 | 1278.45 | 1712.9848 | 2034.8873 | 2446.3225 | 2806.823 | 3056.1946 | 3697.062 | 4183.1651 | 4452.5575 | 4975.8775 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 98.9873 | 123.7253 | 236.6579 | 349.5083 | 433.7148 | 510.7416 | 582.3551 | 658.602 | 730.0862 | 767.771 | 826.2335 | 899.5923 | 981.4276 | 1093.8749 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 44.7175 | 46.8571 | 53.2551 | 58.6433 | 61.5501 | 63.6505 | 66.0717 | 67.8832 | 69.8804 | 70.9272 | 71.8338 | 74.0782 | 72.7247 | 76.3846 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 |  | 47.5947 | 49.8159 | 56.1642 | 61.7562 | 64.6732 | 67.0386 | 69.2881 | 71.2045 | 73.2008 | 74.0757 | 75.27 | 77.4839 | 76.76 | 79.6517 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197
98% | 132.8043 | 139.1585 | 158.1595 | 174.1616 | 182.7945 | 189.0324 | 196.2229 | 201.603 | 207.5343 | 210.6431 | 213.3357 | 220.0011 | 215.9813 | 226.8509 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 |  | 141.3491 | 147.9458 | 166.7992 | 183.4066 | 192.0695 | 199.0945 | 205.7751 | 211.4668 | 217.3953 | 219.9938 | 223.5404 | 230.1155 | 227.9656 | 236.5536 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073
97% | 58.4249 | 61.2203 | 69.5795 | 76.6193 | 80.4172 | 83.1615 | 86.3248 | 88.6917 | 91.301 | 92.6687 | 93.8533 | 96.7856 | 95.0171 | 99.799 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 |  | 62.184 | 65.0861 | 73.3804 | 80.6865 | 84.4976 | 87.5881 | 90.5271 | 93.0311 | 95.6392 | 96.7824 | 98.3426 | 101.2353 | 100.2895 | 104.0676 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469
95% | 143.8152 | 150.6962 | 171.2726 | 188.6014 | 197.95 | 204.7052 | 212.4918 | 218.3179 | 224.741 | 228.1076 | 231.0234 | 238.2414 | 233.8884 | 245.6592 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 |  | 153.0684 | 160.2121 | 180.6286 | 198.6129 | 207.9941 | 215.6015 | 222.836 | 228.9996 | 235.4196 | 238.2336 | 242.0742 | 249.1945 | 246.8664 | 256.1663 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307
90% | 1468.8623 | 1539.1418 | 1749.2998 | 1926.2886 | 2021.7708 | 2090.7648 | 2170.2935 | 2229.7992 | 2295.4018 | 2329.7862 | 2359.5674 | 2433.2886 | 2388.8285 | 2509.0501 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 |  | 1563.3702 | 1636.3326 | 1844.8575 | 2028.5416 | 2124.3562 | 2202.0546 | 2275.9443 | 2338.8965 | 2404.468 | 2433.2083 | 2472.4351 | 2545.1583 | 2521.3798 | 2616.3654 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551
85% | 3460.5527 | 3626.127 | 4121.2469 | 4538.2219 | 4763.1724 | 4925.7181 | 5113.0831 | 5253.275 | 5407.8308 | 5488.8385 | 5559.0011 | 5732.684 | 5627.9387 | 5911.1735 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 |  | 3683.2076 | 3855.1027 | 4346.3751 | 4779.124 | 5004.8576 | 5187.9104 | 5361.9903 | 5510.3018 | 5664.7844 | 5732.4949 | 5824.9108 | 5996.2424 | 5940.2217 | 6164.002 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833
80% | 6266.0722 | 6565.8799 | 7462.4007 | 8217.4232 | 8624.7443 | 8919.0681 | 9258.3326 | 9512.1802 | 9792.0365 | 9938.7182 | 10065.7628 | 10380.2528 | 10190.5889 | 10703.4463 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 |  | 6669.2367 | 6980.4895 | 7870.0435 | 8653.6281 | 9062.3671 | 9393.8235 | 9709.0324 | 9977.5822 | 10257.306 | 10379.9104 | 10547.2492 | 10857.4818 | 10756.0442 | 11161.2466 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759
75% | 7325.96 | 7676.4794 | 8724.6441 | 9607.3764 | 10083.5947 | 10427.7025 | 10824.3526 | 11121.1378 | 11448.331 | 11619.8235 | 11768.3573 | 12136.0423 | 11914.2974 | 12513.9031 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 |  | 7797.3187 | 8161.2191 | 9201.2384 | 10117.3642 | 10595.2402 | 10982.7614 | 11351.2869 | 11665.2613 | 11992.2995 | 12135.6421 | 12331.2857 | 12693.9932 | 12575.3978 | 13049.139 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029
70% | 8591.0842 | 9002.1349 | 10231.3077 | 11266.4796 | 11824.9363 | 12228.4683 | 12693.6161 | 13041.6533 | 13425.3497 | 13626.4573 | 13800.6415 | 14231.8223 | 13971.7841 | 14674.936 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 |  | 9143.842 | 9570.5845 | 10790.2054 | 11864.5374 | 12424.9381 | 12879.3806 | 13311.547 | 13679.7417 | 14063.2564 | 14231.3528 | 14460.7823 | 14886.126 | 14747.0503 | 15302.602 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561
65% | 9414.2762 | 9864.7136 | 11211.6649 | 12346.0264 | 12957.9939 | 13400.1921 | 13909.9101 | 14291.296 | 14711.758 | 14932.1356 | 15123.0099 | 15595.5062 | 15310.5513 | 16081.0788 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 |  | 10019.999 | 10487.6317 | 11824.1158 | 13001.3897 | 13615.4876 | 14113.4744 | 14587.0508 | 14990.5257 | 15410.7884 | 15594.9918 | 15846.405 | 16312.5049 | 16160.103 | 16768.8874 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471
60% | 10243.0861 | 10733.1789 | 12198.7125 | 13432.9403 | 14098.784 | 14579.9123 | 15134.5046 | 15549.4667 | 16006.9451 | 16246.7243 | 16454.4027 | 16968.4964 | 16658.4548 | 17496.8177 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 |  | 10902.1352 | 11410.9371 | 12865.0821 | 14146.0002 | 14814.1618 | 15355.9902 | 15871.259 | 16310.2549 | 16767.5165 | 16967.9367 | 17241.4837 | 17748.6179 | 17582.7989 | 18245.1792 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542
55% | 10267.8043 | 10759.0798 | 12228.15 | 13465.3562 | 14132.8067 | 14615.096 | 15171.0266 | 15586.9901 | 16045.5725 | 16285.9303 | 16494.1099 | 17009.4441 | 16698.6544 | 17539.0404 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 |  | 10928.4438 | 11438.4736 | 12896.1276 | 14180.1368 | 14849.9108 | 15393.0467 | 15909.559 | 16349.6142 | 16807.9793 | 17008.8831 | 17283.0902 | 17791.4482 | 17625.2291 | 18289.2078 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048
50% | 12096.2046 | 12674.962 | 14405.6313 | 15863.1483 | 16649.4525 | 17217.6237 | 17872.5495 | 18362.5841 | 18902.8268 | 19185.9854 | 19431.2358 | 20038.3362 | 19672.2038 | 20662.2383 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 |  | 12874.4849 | 13475.3363 | 15192.5565 | 16705.2108 | 17494.2522 | 18134.105 | 18742.5932 | 19261.0096 | 19800.9963 | 20037.6753 | 20360.7109 | 20959.5927 | 20763.7748 | 21545.989 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867
45% | 15128.3079 | 15852.1399 | 18016.6286 | 19839.4951 | 20822.8988 | 21533.4909 | 22352.5842 | 22965.4537 | 23641.1167 | 23995.2534 | 24301.9797 | 25061.2593 | 24603.3501 | 25841.5522 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 |  | 16101.6763 | 16853.1406 | 19000.809 | 20892.6337 | 21879.4607 | 22679.7027 | 23440.718 | 24089.0836 | 24764.4264 | 25060.4327 | 25464.4422 | 26213.4432 | 25968.5404 | 26946.8289 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263
40% | 16018.9133 | 16785.3574 | 19077.2699 | 21007.4488 | 22048.7455 | 22801.1703 | 23668.4837 | 24317.4329 | 25032.8723 | 25407.8571 | 25732.6404 | 26536.6189 | 26051.7525 | 27362.8478 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 |  | 17049.5841 | 17845.2871 | 20119.3891 | 22122.5858 | 23167.5074 | 24014.8597 | 24820.6761 | 25507.211 | 26222.3114 | 26535.7437 | 26963.5372 | 27756.632 | 27497.3118 | 28533.1922 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099
35% | 6550.3318 | 6863.7403 | 7800.9317 | 8590.2057 | 9016.0048 | 9323.6807 | 9678.3358 | 9943.6992 | 10236.2512 | 10389.5871 | 10522.395 | 10851.1518 | 10652.8839 | 11189.007 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 |  | 6971.7859 | 7297.1587 | 8227.0671 | 9046.199 | 9473.4804 | 9819.9733 | 10149.4816 | 10430.2142 | 10722.6276 | 10850.7939 | 11025.724 | 11350.0303 | 11243.991 | 11667.5753 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077
30% | 2020.5283 | 2117.2029 | 2406.2908 | 2649.7518 | 2781.0947 | 2876.001 | 2985.3986 | 3067.2531 | 3157.4943 | 3204.7926 | 3245.7588 | 3347.1678 | 3286.0096 | 3451.3832 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 |  | 2150.5309 | 2250.896 | 2537.7374 | 2790.4084 | 2922.2085 | 3029.0884 | 3130.7292 | 3217.3245 | 3307.5229 | 3347.0574 | 3401.0166 | 3501.0528 | 3468.3437 | 3599.0034 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706
25% | 1487.2137 | 1558.3712 | 1771.1549 | 1950.3549 | 2047.03 | 2116.886 | 2197.4083 | 2257.6575 | 2324.0797 | 2358.8937 | 2389.0469 | 2463.6892 | 2418.6736 | 2540.3972 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 |  | 1582.9023 | 1656.7763 | 1867.9064 | 2053.8854 | 2150.8971 | 2229.5663 | 2304.3791 | 2368.1178 | 2434.5085 | 2463.6079 | 2503.3248 | 2576.9566 | 2552.881 | 2649.0533 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275
20% | 1183.1045 | 1239.7116 | 1408.9847 | 1551.5414 | 1628.4482 | 1684.0199 | 1748.0768 | 1796.006 | 1848.8461 | 1876.5412 | 1900.5286 | 1959.9079 | 1924.0972 | 2020.9304 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 |  | 1259.2265 | 1317.9945 | 1485.9523 | 1633.9018 | 1711.0763 | 1773.659 | 1833.1739 | 1883.8792 | 1936.6941 | 1959.8432 | 1991.4387 | 2050.014 | 2030.8615 | 2107.3682 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989
15% | 928.0573 | 972.4613 | 1105.2435 | 1217.0686 | 1277.3962 | 1320.988 | 1371.2359 | 1408.8329 | 1450.2819 | 1472.0067 | 1490.823 | 1537.4016 | 1509.3108 | 1585.2693 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 |  | 987.7693 | 1033.8685 | 1165.6188 | 1281.6742 | 1342.2118 | 1391.3032 | 1437.9883 | 1477.7628 | 1519.1922 | 1537.3509 | 1562.1352 | 1608.0832 | 1593.0594 | 1653.0733 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905
10% | 651.6625 | 682.8421 | 776.079 | 854.6002 | 896.961 | 927.5703 | 962.8533 | 989.2531 | 1018.3578 | 1033.6124 | 1046.8249 | 1079.5314 | 1059.8066 | 1113.1431 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 |  | 693.591 | 725.9609 | 818.4732 | 899.9649 | 942.4732 | 976.9442 | 1009.7254 | 1037.6542 | 1066.7451 | 1079.4958 | 1096.8988 | 1129.1625 | 1118.6132 | 1160.7536 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611
5% | 67.4134 | 70.6388 | 80.284 | 88.4069 | 92.7891 | 95.9555 | 99.6055 | 102.3365 | 105.3474 | 106.9254 | 108.2922 | 111.6757 | 109.6352 | 115.1527 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 |  | 71.7508 | 75.0994 | 84.6696 | 93.0998 | 97.4972 | 101.0632 | 104.4544 | 107.3435 | 110.3529 | 111.672 | 113.4723 | 116.8099 | 115.7186 | 120.078 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 113549.1973 | 118982.0949 | 135228.1917 | 148910.1601 | 156291.3357 | 161624.858 | 167772.7617 | 172372.8029 | 177444.1564 | 180102.2155 | 182404.4242 | 188103.3826 | 184666.4331 | 193960.0608 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | E @ R (MWh) | 120855.0513 | 126495.349 | 142615.1972 | 156814.7481 | 164221.6187 | 170228.0295 | 175940.0151 | 180806.4807 | 185875.4309 | 188097.1784 | 191129.5697 | 196751.3792 | 194913.2016 | 202255.9836 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557
Option 1 Winter POE50 W E @ R (MWh) N 2 | 79484.4381 | 83287.4664 | 94659.7342 | 104237.112 | 109403.935 | 113137.4006 | 117440.9332 | 120660.962 | 124210.9095 | 126071.5508 | 127683.0969 | 131672.3678 | 129266.5031 | 135772.0426 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 36256.5154 | 37948.6047 | 42784.5592 | 47044.4244 | 49266.4856 | 51068.4088 | 52782.0045 | 54241.9442 | 55762.6293 | 56429.1535 | 57338.8709 | 59025.4138 | 58473.9605 | 60676.7951 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 48.2179 | 49.8856 | 55.197 | 58.9755 | 61.241 | 63.0547 | 64.527 | 65.9431 | 67.169 | 67.7841 | 68.6904 | 69.7274 | 70.7857 | 72.117 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249
98% | 21.2169 | 21.8618 | 24.4836 | 26.3751 | 27.3701 | 28.2614 | 28.8274 | 29.4735 | 29.9898 | 30.3263 | 31.1277 | 31.6819 | 31.9736 | 32.5145 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 |  | 23.8667 | 24.6921 | 27.3211 | 29.1914 | 30.3128 | 31.2105 | 31.9392 | 32.6402 | 33.247 | 33.5514 | 34 | 34.5133 | 35.0372 | 35.6961 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799
97% | 21.0015 | 21.6398 | 24.235 | 26.1073 | 27.0922 | 27.9744 | 28.5347 | 29.1743 | 29.6853 | 30.0184 | 30.8116 | 31.3603 | 31.649 | 32.1844 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 |  | 47.2487 | 48.8828 | 54.0875 | 57.79 | 60.01 | 61.7873 | 63.23 | 64.6176 | 65.8189 | 66.4216 | 67.3097 | 68.3258 | 69.3629 | 70.6674 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711
95% | 62.0353 | 63.9208 | 71.5864 | 77.1171 | 80.0263 | 82.6322 | 84.2871 | 86.1763 | 87.6859 | 88.6697 | 91.0129 | 92.6334 | 93.4862 | 95.0677 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 |  | 93.0436 | 96.2616 | 106.5109 | 113.8019 | 118.1736 | 121.6735 | 124.5144 | 127.247 | 129.6126 | 130.7994 | 132.5484 | 134.5493 | 136.5916 | 139.1605 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616
90% | 139.4716 | 143.7108 | 160.9452 | 173.3796 | 179.9203 | 185.779 | 189.4997 | 193.7472 | 197.1411 | 199.353 | 204.6209 | 208.2644 | 210.1817 | 213.7374 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 |  | 336.1928 | 347.8201 | 384.8537 | 411.1982 | 426.9943 | 439.6404 | 449.9056 | 459.7791 | 468.3268 | 472.615 | 478.9346 | 486.1645 | 493.5438 | 502.826 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752
85% | 226.1702 | 233.0445 | 260.9922 | 281.1561 | 291.7627 | 301.2632 | 307.2968 | 314.1846 | 319.6883 | 323.2751 | 331.8177 | 337.7261 | 340.8353 | 346.6011 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 |  | 402.8257 | 416.7575 | 461.131 | 492.697 | 511.6238 | 526.7764 | 539.076 | 550.9064 | 561.1483 | 566.2865 | 573.8586 | 582.5214 | 591.3633 | 602.4853 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216
80% | 870.7553 | 897.2214 | 1004.8201 | 1082.4508 | 1123.2863 | 1159.8635 | 1183.0927 | 1209.6107 | 1230.7998 | 1244.6091 | 1277.4981 | 1300.2454 | 1312.2158 | 1334.4144 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 |  | 459.7664 | 475.6675 | 526.3134 | 562.3413 | 583.9436 | 601.238 | 615.2763 | 628.7789 | 640.4685 | 646.333 | 654.9755 | 664.8628 | 674.9545 | 687.6486 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303
75% | 1318.7877 | 1358.8714 | 1521.8333 | 1639.4076 | 1701.2542 | 1756.6516 | 1791.8331 | 1831.9954 | 1864.087 | 1885.0017 | 1934.8132 | 1969.2646 | 1987.3942 | 2021.0147 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 |  | 394.3451 | 407.9836 | 451.423 | 482.3244 | 500.8528 | 515.6864 | 527.7271 | 539.3084 | 549.3346 | 554.3647 | 561.7774 | 570.2578 | 578.9136 | 589.8014 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011
70% | 2014.5303 | 2075.7608 | 2324.6951 | 2504.2972 | 2598.7718 | 2683.3948 | 2737.1366 | 2798.487 | 2847.509 | 2879.4575 | 2955.5476 | 3008.1743 | 3035.8684 | 3087.2258 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 |  | 421.604 | 436.1853 | 482.6273 | 515.6648 | 535.474 | 551.3329 | 564.2059 | 576.5878 | 587.3071 | 592.6848 | 600.6099 | 609.6765 | 618.9306 | 630.571 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883
65% | 3678.4968 | 3790.3025 | 4244.8522 | 4572.8025 | 4745.3114 | 4899.8315 | 4997.9632 | 5109.9879 | 5199.5012 | 5257.8386 | 5396.7777 | 5492.8733 | 5543.4421 | 5637.2199 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 |  | 1112.1622 | 1150.6266 | 1273.1376 | 1360.2882 | 1412.5434 | 1454.3781 | 1488.3362 | 1520.9988 | 1549.2756 | 1563.4617 | 1584.3676 | 1608.2847 | 1632.6964 | 1663.4029 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967
60% | 7148.594 | 7365.8712 | 8249.2187 | 8886.5398 | 9221.7843 | 9522.0704 | 9712.7743 | 9930.4771 | 10104.4324 | 10217.8023 | 10487.8092 | 10674.5561 | 10772.8288 | 10955.0715 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 |  | 1241.7934 | 1284.7411 | 1421.5316 | 1518.8403 | 1577.1863 | 1623.8971 | 1661.8133 | 1698.283 | 1729.8556 | 1745.6952 | 1769.0379 | 1795.7427 | 1822.9997 | 1857.2854 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638
55% | 8285.907 | 8537.7521 | 9561.6368 | 10300.3531 | 10688.9337 | 11036.9942 | 11258.0382 | 11510.3768 | 11712.0077 | 11843.4143 | 12156.3781 | 12372.8358 | 12486.7433 | 12697.9801 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 |  | 2020.1858 | 2090.0544 | 2312.5892 | 2470.8938 | 2565.8128 | 2641.8033 | 2703.4866 | 2762.8165 | 2814.1798 | 2839.948 | 2877.9226 | 2921.3668 | 2965.7093 | 3021.4862 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194
50% | 9747.9358 | 10044.2184 | 11248.7651 | 12117.8262 | 12574.971 | 12984.4459 | 13244.4926 | 13541.3557 | 13778.5639 | 13933.1569 | 14301.3425 | 14555.9936 | 14689.9998 | 14938.5089 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 |  | 3523.6644 | 3645.5311 | 4033.6826 | 4309.8019 | 4475.3622 | 4607.9071 | 4715.4967 | 4818.9816 | 4908.5708 | 4953.5166 | 5019.7528 | 5095.5294 | 5172.8729 | 5270.1605 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488
45% | 17342.4082 | 17869.5202 | 20012.5113 | 21558.6451 | 22371.9445 | 23100.4353 | 23563.0806 | 24091.2253 | 24513.2389 | 24788.273 | 25443.3065 | 25896.3525 | 26134.7609 | 26576.8798 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 |  | 7020.6756 | 7263.4873 | 8036.8544 | 8587.0043 | 8916.8725 | 9180.9598 | 9395.3251 | 9601.5122 | 9780.0131 | 9869.5646 | 10001.536 | 10152.516 | 10306.618 | 10500.4574 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719
40% | 19856.1284 | 20459.6435 | 22913.2535 | 24683.4938 | 25614.6782 | 26448.7611 | 26978.4652 | 27583.1626 | 28066.3455 | 28381.2448 | 29131.2231 | 29649.9365 | 29922.9014 | 30429.1038 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 |  | 11955.7442 | 12369.2363 | 13686.2291 | 14623.0978 | 15184.8415 | 15634.5645 | 15999.6145 | 16350.7374 | 16654.7125 | 16807.2128 | 17031.9514 | 17289.0602 | 17551.4858 | 17881.5813 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149
35% | 12043.5634 | 12409.6202 | 13897.8362 | 14971.5602 | 15536.362 | 16042.2678 | 16363.5553 | 16730.3293 | 17023.3997 | 17214.3992 | 17669.292 | 17983.9131 | 18149.4777 | 18456.5104 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 |  | 14474.4645 | 14975.0672 | 16569.5112 | 17703.7504 | 18383.8369 | 18928.3031 | 19370.2583 | 19795.3524 | 20163.3661 | 20347.9936 | 20620.078 | 20931.352 | 21249.0628 | 21648.6997 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898
30% | 4991.361 | 5143.0704 | 5759.8499 | 6204.8465 | 6438.9242 | 6648.5929 | 6781.748 | 6933.7546 | 7055.2154 | 7134.3736 | 7322.9004 | 7453.2927 | 7521.9096 | 7649.1569 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 |  | 22112.4023 | 22877.1648 | 25312.9708 | 27045.7294 | 28084.6864 | 28916.4586 | 29591.6263 | 30241.0355 | 30803.244 | 31085.2964 | 31500.9553 | 31976.4835 | 32461.8451 | 33072.3638 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762
25% | 2979.5232 | 3070.084 | 3438.2619 | 3703.8964 | 3843.6258 | 3968.7846 | 4048.2697 | 4139.0079 | 4211.5122 | 4258.7646 | 4371.3031 | 4449.1389 | 4490.0988 | 4566.0573 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 |  | 18803.7802 | 19454.1133 | 21525.4559 | 22998.9462 | 23882.4467 | 24589.763 | 25163.9071 | 25716.1468 | 26194.2335 | 26434.0832 | 26787.548 | 27191.9242 | 27604.6624 | 28123.8307 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818
20% | 3169.6139 | 3265.9524 | 3657.6197 | 3940.2014 | 4088.8454 | 4221.9892 | 4306.5453 | 4403.0726 | 4480.2026 | 4530.4696 | 4650.1879 | 4732.9896 | 4776.5627 | 4857.3673 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 |  | 4988.3748 | 5160.8989 | 5710.3965 | 6101.2925 | 6335.6726 | 6523.3135 | 6675.6258 | 6822.1271 | 6948.9567 | 7012.5854 | 7106.3546 | 7213.6298 | 7323.1233 | 7460.8513 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353
15% | 3283.2375 | 3383.0295 | 3788.7372 | 4081.4488 | 4235.4214 | 4373.3381 | 4460.9254 | 4560.9129 | 4640.8079 | 4692.8769 | 4816.8868 | 4902.6568 | 4947.7919 | 5031.4931 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 |  | 3091.1568 | 3198.0652 | 3538.5736 | 3780.8009 | 3926.0397 | 4042.3156 | 4136.6992 | 4227.482 | 4306.0748 | 4345.5037 | 4403.6099 | 4470.0853 | 4537.9355 | 4623.2816 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056
10% | 2189.0045 | 2255.5379 | 2526.0319 | 2721.189 | 2823.8458 | 2915.7978 | 2974.1942 | 3040.858 | 3094.1256 | 3128.8412 | 3211.5212 | 3268.7059 | 3298.7984 | 3354.6038 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 |  | 884.3992 | 914.9863 | 1012.4079 | 1081.7106 | 1123.2644 | 1156.5316 | 1183.5353 | 1209.5089 | 1231.9947 | 1243.2756 | 1259.9001 | 1278.9192 | 1298.3315 | 1322.7496 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617
5% | 174.4742 | 179.7772 | 201.3369 | 216.8918 | 225.0741 | 232.4031 | 237.0575 | 242.371 | 246.6167 | 249.3836 | 255.9736 | 260.5315 | 262.9301 | 267.378 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 99564.2165 | 102590.4109 | 114893.5021 | 123769.9854 | 128439.2058 | 132621.532 | 135277.6178 | 138309.7405 | 140732.5559 | 142311.5495 | 146072.1518 | 148673.1266 | 150041.8495 | 152580.0908 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | E @ R (MWh) | 93455.9144 | 96688.1086 | 106982.8055 | 114306.1407 | 118697.1912 | 122212.5953 | 125066.1259 | 127810.7907 | 130186.91 | 131378.9772 | 133135.7188 | 135145.4924 | 137196.8262 | 139777.1238 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523
Option 1 Summer POE50 W E @ R (MWh) N 2 | 69694.9516 | 71813.2876 | 80425.4515 | 86638.9898 | 89907.444 | 92835.0724 | 94694.3324 | 96816.8184 | 98512.7891 | 99618.0846 | 102250.5063 | 104071.1886 | 105029.2947 | 106806.0636 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 28036.7743 | 29006.4326 | 32094.8416 | 34291.8422 | 35609.1573 | 36663.7786 | 37519.8378 | 38343.2372 | 39056.073 | 39413.6932 | 39940.7156 | 40543.6477 | 41159.0479 | 41933.1371 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 44.7175 | 46.8571 | 53.2551 | 58.6433 | 48.6866 | 50.787 | 53.2082 | 55.0197 | 57.0169 | 58.0637 | 58.9704 | 61.2147 | 59.8612 | 63.5211 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 | 68.2953 |  | 47.5947 | 49.8159 | 56.1642 | 61.7562 | 51.8097 | 54.1751 | 56.4246 | 58.3411 | 60.3373 | 61.2122 | 62.4065 | 64.6204 | 63.8965 | 66.7882 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562 | 68.4562
98% | 132.8043 | 139.1585 | 158.1595 | 174.1616 | 144.5918 | 150.8298 | 158.0202 | 163.4003 | 169.3316 | 172.4404 | 175.1331 | 181.7984 | 177.7786 | 188.6482 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 | 202.8268 |  | 141.3491 | 147.9458 | 166.7992 | 183.4066 | 153.8669 | 160.8918 | 167.5724 | 173.2641 | 179.1927 | 181.7912 | 185.3378 | 191.9129 | 189.763 | 198.3509 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046 | 203.3046
97% | 58.4249 | 61.2203 | 69.5795 | 76.6193 | 63.6106 | 66.3549 | 69.5182 | 71.8851 | 74.4945 | 75.8621 | 77.0467 | 79.979 | 78.2106 | 82.9925 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 | 89.23 |  | 62.184 | 65.0861 | 73.3804 | 80.6865 | 67.691 | 70.7815 | 73.7205 | 76.2245 | 78.8326 | 79.9758 | 81.5361 | 84.4287 | 83.4829 | 87.261 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403 | 89.4403
95% | 143.8152 | 150.6962 | 171.2726 | 188.6014 | 156.58 | 163.3351 | 171.1217 | 176.9479 | 183.371 | 186.7375 | 189.6534 | 196.8714 | 192.5183 | 204.2891 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 | 219.6432 |  | 153.0684 | 160.2121 | 180.6286 | 198.6129 | 166.624 | 174.2314 | 181.4659 | 187.6295 | 194.0496 | 196.8635 | 200.7042 | 207.8245 | 205.4963 | 214.7963 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607 | 220.1607
90% | 1468.8623 | 1539.1418 | 1749.2998 | 1926.2886 | 1599.2362 | 1668.2302 | 1747.7589 | 1807.2646 | 1872.8672 | 1907.2516 | 1937.0328 | 2010.754 | 1966.2939 | 2086.5155 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 | 2243.3349 |  | 1563.3702 | 1636.3326 | 1844.8575 | 2028.5416 | 1701.8216 | 1779.52 | 1853.4098 | 1916.3619 | 1981.9334 | 2010.6737 | 2049.9005 | 2122.6237 | 2098.8452 | 2193.8308 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205 | 2248.6205
85% | 3460.5527 | 3626.127 | 4121.2469 | 4538.2219 | 3767.7059 | 3930.2516 | 4117.6166 | 4257.8085 | 4412.3643 | 4493.372 | 4563.5346 | 4737.2175 | 4632.4722 | 4915.707 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 | 5285.1643 |  | 3683.2076 | 3855.1027 | 4346.3751 | 4779.124 | 4009.3911 | 4192.4439 | 4366.5238 | 4514.8353 | 4669.3179 | 4737.0284 | 4829.4443 | 5000.7759 | 4944.7552 | 5168.5355 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168 | 5297.6168
80% | 6266.0722 | 6565.8799 | 7462.4007 | 8217.4232 | 6822.2388 | 7116.5627 | 7455.8271 | 7709.6747 | 7989.5311 | 8136.2128 | 8263.2574 | 8577.7473 | 8388.0835 | 8900.9409 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 | 9569.9224 |  | 6669.2367 | 6980.4895 | 7870.0435 | 8653.6281 | 7259.8617 | 7591.3181 | 7906.5269 | 8175.0768 | 8454.8006 | 8577.405 | 8744.7437 | 9054.9764 | 8953.5388 | 9358.7411 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704 | 9592.4704
75% | 7325.96 | 7676.4794 | 8724.6441 | 9607.3764 | 7976.2007 | 8320.3086 | 8716.9586 | 9013.7438 | 9340.9371 | 9512.4296 | 9660.9633 | 10028.6484 | 9806.9035 | 10406.5092 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 | 11188.647 |  | 7797.3187 | 8161.2191 | 9201.2384 | 10117.3642 | 8487.8462 | 8875.3674 | 9243.893 | 9557.8673 | 9884.9055 | 10028.2481 | 10223.8917 | 10586.5993 | 10468.0038 | 10941.745 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089 | 11215.0089
70% | 8591.0842 | 9002.1349 | 10231.3077 | 11266.4796 | 9353.6152 | 9757.1473 | 10222.2951 | 10570.3322 | 10954.0287 | 11155.1363 | 11329.3205 | 11760.5012 | 11500.4631 | 12203.615 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 | 13120.8207 |  | 9143.842 | 9570.5845 | 10790.2054 | 11864.5374 | 9953.6171 | 10408.0596 | 10840.226 | 11208.4207 | 11591.9354 | 11760.0318 | 11989.4613 | 12414.805 | 12275.7293 | 12831.281 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351 | 13151.7351
65% | 9414.2762 | 9864.7136 | 11211.6649 | 12346.0264 | 10249.8726 | 10692.0708 | 11201.7887 | 11583.1746 | 12003.6366 | 12224.0142 | 12414.8886 | 12887.3848 | 12602.43 | 13372.9575 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 | 14378.0492 |  | 10019.999 | 10487.6317 | 11824.1158 | 13001.3897 | 10907.3662 | 11405.3531 | 11878.9294 | 12282.4043 | 12702.667 | 12886.8704 | 13138.2836 | 13604.3835 | 13451.9816 | 14060.766 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257 | 14411.9257
60% | 10243.0861 | 10733.1789 | 12198.7125 | 13432.9403 | 11152.2463 | 11633.3745 | 12187.9668 | 12602.9289 | 13060.4074 | 13300.1865 | 13507.865 | 14021.9586 | 13711.9171 | 14550.2799 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 | 15643.8574 |  | 10902.1352 | 11410.9371 | 12865.0821 | 14146.0002 | 11867.624 | 12409.4525 | 12924.7213 | 13363.7171 | 13820.9788 | 14021.399 | 14294.946 | 14802.0802 | 14636.2612 | 15298.6415 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164 | 15680.7164
55% | 10267.8043 | 10759.0798 | 12228.15 | 13465.3562 | 11179.1584 | 11661.4478 | 12217.3783 | 12633.3419 | 13091.9243 | 13332.282 | 13540.4617 | 14055.7959 | 13745.0062 | 14585.3921 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 | 15681.6086 |  | 10928.4438 | 11438.4736 | 12896.1276 | 14180.1368 | 11896.2625 | 12439.3985 | 12955.9107 | 13395.966 | 13854.331 | 14055.2349 | 14329.442 | 14837.8 | 14671.5809 | 15335.5596 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565 | 15718.5565
50% | 12096.2046 | 12674.962 | 14405.6313 | 15863.1483 | 13169.8446 | 13738.0157 | 14392.9416 | 14882.9762 | 15423.2189 | 15706.3775 | 15951.6279 | 16558.7283 | 16192.5959 | 17182.6304 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 | 18474.0515 |  | 12874.4849 | 13475.3363 | 15192.5565 | 16705.2108 | 14014.6443 | 14654.4971 | 15262.9853 | 15781.4017 | 16321.3884 | 16558.0674 | 16881.1029 | 17479.9848 | 17284.1669 | 18066.381 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788 | 18517.5788
45% | 15128.3079 | 15852.1399 | 18016.6286 | 19839.4951 | 16471.0726 | 17181.6647 | 18000.758 | 18613.6275 | 19289.2905 | 19643.4272 | 19950.1535 | 20709.4332 | 20251.5239 | 21489.726 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 | 23104.8621 |  | 16101.6763 | 16853.1406 | 19000.809 | 20892.6337 | 17527.6346 | 18327.8765 | 19088.8918 | 19737.2574 | 20412.6002 | 20708.6066 | 21112.616 | 21861.617 | 21616.7142 | 22595.0027 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001 | 23159.3001
40% | 16018.9133 | 16785.3574 | 19077.2699 | 21007.4488 | 17440.7268 | 18193.1516 | 19060.4649 | 19709.4141 | 20424.8536 | 20799.8383 | 21124.6216 | 21928.6002 | 21443.7337 | 22754.829 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 | 24465.0483 |  | 17049.5841 | 17845.2871 | 20119.3891 | 22122.5858 | 18559.4887 | 19406.841 | 20212.6573 | 20899.1923 | 21614.2927 | 21927.7249 | 22355.5184 | 23148.6133 | 22889.293 | 23925.1734 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911 | 24522.6911
35% | 6550.3318 | 6863.7403 | 7800.9317 | 8590.2057 | 7131.729 | 7439.4048 | 7794.0599 | 8059.4233 | 8351.9753 | 8505.3112 | 8638.1191 | 8966.8759 | 8768.608 | 9304.7311 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 | 10004.0609 |  | 6971.7859 | 7297.1587 | 8227.0671 | 9046.199 | 7589.2045 | 7935.6974 | 8265.2057 | 8545.9383 | 8838.3517 | 8966.518 | 9141.4481 | 9465.7544 | 9359.7151 | 9783.2994 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318 | 10027.6318
30% | 2020.5283 | 2117.2029 | 2406.2908 | 2649.7518 | 2199.8672 | 2294.7735 | 2404.1711 | 2486.0257 | 2576.2668 | 2623.5651 | 2664.5313 | 2765.9403 | 2704.7822 | 2870.1558 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 | 3085.8724 |  | 2150.5309 | 2250.896 | 2537.7374 | 2790.4084 | 2340.981 | 2447.8609 | 2549.5017 | 2636.097 | 2726.2954 | 2765.8299 | 2819.7892 | 2919.8253 | 2887.1162 | 3017.7759 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431 | 3093.1431
25% | 1487.2137 | 1558.3712 | 1771.1549 | 1950.3549 | 1619.2165 | 1689.0724 | 1769.5947 | 1829.8439 | 1896.2661 | 1931.0801 | 1961.2333 | 2035.8756 | 1990.8601 | 2112.5836 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 | 2271.3623 |  | 1582.9023 | 1656.7763 | 1867.9064 | 2053.8854 | 1723.0835 | 1801.7527 | 1876.5656 | 1940.3042 | 2006.6949 | 2035.7943 | 2075.5112 | 2149.143 | 2125.0674 | 2221.2397 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139 | 2276.7139
20% | 1183.1045 | 1239.7116 | 1408.9847 | 1551.5414 | 1288.115 | 1343.6867 | 1407.7436 | 1455.6729 | 1508.5129 | 1536.208 | 1560.1954 | 1619.5747 | 1583.764 | 1680.5972 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 | 1806.9084 |  | 1259.2265 | 1317.9945 | 1485.9523 | 1633.9018 | 1370.7431 | 1433.3258 | 1492.8408 | 1543.546 | 1596.3609 | 1619.51 | 1651.1055 | 1709.6808 | 1690.5283 | 1767.035 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657 | 1811.1657
15% | 928.0573 | 972.4613 | 1105.2435 | 1217.0686 | 1010.4302 | 1054.022 | 1104.2699 | 1141.8668 | 1183.3159 | 1205.0407 | 1223.857 | 1270.4356 | 1242.3448 | 1318.3032 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 | 1417.385 |  | 987.7693 | 1033.8685 | 1165.6188 | 1281.6742 | 1075.2458 | 1124.3372 | 1171.0223 | 1210.7967 | 1252.2262 | 1270.3849 | 1295.1691 | 1341.1172 | 1326.0934 | 1386.1073 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245 | 1420.7245
10% | 651.6625 | 682.8421 | 776.079 | 854.6002 | 709.5031 | 740.1123 | 775.3953 | 801.7951 | 830.8998 | 846.1545 | 859.3669 | 892.0734 | 872.3487 | 925.6851 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 | 995.2582 |  | 693.591 | 725.9609 | 818.4732 | 899.9649 | 755.0152 | 789.4862 | 822.2675 | 850.1963 | 879.2871 | 892.0378 | 909.4408 | 941.7046 | 931.1552 | 973.2957 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032 | 997.6032
5% | 67.4134 | 70.6388 | 80.284 | 88.4069 | 73.3969 | 76.5633 | 80.2133 | 82.9443 | 85.9551 | 87.5332 | 88.9 | 92.2835 | 90.243 | 95.7605 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 | 102.9577 |  | 71.7508 | 75.0994 | 84.6696 | 93.0998 | 78.105 | 81.671 | 85.0622 | 87.9513 | 90.9607 | 92.2798 | 94.0801 | 97.4177 | 96.3264 | 100.6858 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003 | 103.2003
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 113549.1973 | 118982.0949 | 135228.1917 | 148910.1601 | 123627.6449 | 128961.1672 | 135109.0709 | 139709.1121 | 144780.4656 | 147438.5247 | 149740.7334 | 155439.6918 | 152002.7423 | 161296.37 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | 173419.1665 | E @ R (MWh) | 120855.0513 | 126495.349 | 142615.1972 | 156814.7481 | 131557.9279 | 137564.3387 | 143276.3243 | 148142.7899 | 153211.7401 | 155433.4876 | 158465.8789 | 164087.6884 | 162249.5108 | 169592.2927 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649 | 173827.7649
Option 2 Winter POE50 W E @ R (MWh) N 2 | 79484.4381 | 83287.4664 | 94659.7342 | 104237.112 | 86539.3514 | 90272.817 | 94576.3496 | 97796.3785 | 101346.3259 | 103206.9673 | 104818.5134 | 108807.7842 | 106401.9196 | 112907.459 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | 121393.4165 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 36256.5154 | 37948.6047 | 42784.5592 | 47044.4244 | 39467.3784 | 41269.3016 | 42982.8973 | 44442.837 | 45963.522 | 46630.0463 | 47539.7637 | 49226.3065 | 48674.8532 | 50877.6878 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295 | 52148.3295
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 48.2179 | 49.8856 | 55.197 | 58.9755 | 50.3291 | 52.1428 | 53.6151 | 55.0312 | 56.2571 | 56.8721 | 57.7785 | 58.8154 | 59.8738 | 61.2051 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129 | 61.4129
98% | 21.2169 | 21.8618 | 24.4836 | 26.3751 | 21.969 | 22.8602 | 23.4262 | 24.0724 | 24.5887 | 24.9252 | 25.7265 | 26.2808 | 26.5725 | 27.1134 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 | 26.9559 |  | 23.8667 | 24.6921 | 27.3211 | 29.1914 | 24.9116 | 25.8094 | 26.5381 | 27.239 | 27.8459 | 28.1503 | 28.5989 | 29.1122 | 29.636 | 30.295 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979 | 30.3979
97% | 21.0015 | 21.6398 | 24.235 | 26.1073 | 21.746 | 22.6281 | 23.1884 | 23.828 | 24.339 | 24.6721 | 25.4653 | 26.014 | 26.3027 | 26.8381 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 | 26.6823 |  | 47.2487 | 48.8828 | 54.0875 | 57.79 | 49.3174 | 51.0947 | 52.5374 | 53.925 | 55.1263 | 55.729 | 56.6171 | 57.6332 | 58.6703 | 59.9748 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785 | 60.1785
95% | 62.0353 | 63.9208 | 71.5864 | 77.1171 | 64.2342 | 66.8401 | 68.495 | 70.3842 | 71.8938 | 72.8776 | 75.2207 | 76.8413 | 77.6941 | 79.2756 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 | 78.8153 |  | 93.0436 | 96.2616 | 106.5109 | 113.8019 | 97.1174 | 100.6173 | 103.4582 | 106.1908 | 108.5564 | 109.7432 | 111.4922 | 113.4931 | 115.5354 | 118.1043 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054 | 118.5054
90% | 139.4716 | 143.7108 | 160.9452 | 173.3796 | 144.4154 | 150.2741 | 153.9948 | 158.2423 | 161.6362 | 163.8481 | 169.116 | 172.7595 | 174.6768 | 178.2325 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 | 177.1976 |  | 336.1928 | 347.8201 | 384.8537 | 411.1982 | 350.9124 | 363.5585 | 373.8236 | 383.6971 | 392.2448 | 396.5331 | 402.8527 | 410.0826 | 417.4619 | 426.7441 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932 | 428.1932
85% | 226.1702 | 233.0445 | 260.9922 | 281.1561 | 234.1872 | 243.6877 | 249.7213 | 256.6091 | 262.1127 | 265.6996 | 274.2422 | 280.1506 | 283.2597 | 289.0256 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 | 287.3475 |  | 402.8257 | 416.7575 | 461.131 | 492.697 | 420.4626 | 435.6152 | 447.9148 | 459.7452 | 469.9871 | 475.1253 | 482.6974 | 491.3602 | 500.2021 | 511.324 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604 | 513.0604
80% | 870.7553 | 897.2214 | 1004.8201 | 1082.4508 | 901.6205 | 938.1978 | 961.427 | 987.9449 | 1009.1341 | 1022.9434 | 1055.8324 | 1078.5796 | 1090.55 | 1112.7486 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 | 1106.2879 |  | 459.7664 | 475.6675 | 526.3134 | 562.3413 | 479.8964 | 497.1908 | 511.2291 | 524.7318 | 536.4213 | 542.2858 | 550.9283 | 560.8156 | 570.9074 | 583.6014 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832 | 585.5832
75% | 1318.7877 | 1358.8714 | 1521.8333 | 1639.4076 | 1365.5342 | 1420.9316 | 1456.113 | 1496.2753 | 1528.3669 | 1549.2817 | 1599.0931 | 1633.5446 | 1651.6741 | 1685.2946 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 | 1675.5096 |  | 394.3451 | 407.9836 | 451.423 | 482.3244 | 411.6108 | 426.4443 | 438.485 | 450.0664 | 460.0926 | 465.1226 | 472.5353 | 481.0158 | 489.6715 | 500.5593 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591 | 502.2591
70% | 2014.5303 | 2075.7608 | 2324.6951 | 2504.2972 | 2085.9384 | 2170.5615 | 2224.3033 | 2285.6537 | 2334.6757 | 2366.6242 | 2442.7143 | 2495.341 | 2523.0351 | 2574.3925 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 | 2559.4453 |  | 421.604 | 436.1853 | 482.6273 | 515.6648 | 440.0631 | 455.922 | 468.795 | 481.1769 | 491.8962 | 497.274 | 505.1991 | 514.2657 | 523.5198 | 535.1602 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775 | 536.9775
65% | 3678.4968 | 3790.3025 | 4244.8522 | 4572.8025 | 3808.8868 | 3963.4069 | 4061.5386 | 4173.5633 | 4263.0766 | 4321.414 | 4460.3531 | 4556.4487 | 4607.0175 | 4700.7953 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 | 4673.5019 |  | 1112.1622 | 1150.6266 | 1273.1376 | 1360.2882 | 1160.8562 | 1202.6909 | 1236.649 | 1269.3116 | 1297.5883 | 1311.7744 | 1332.6803 | 1356.5974 | 1381.0091 | 1411.7157 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095 | 1416.5095
60% | 7148.594 | 7365.8712 | 8249.2187 | 8886.5398 | 7401.9869 | 7702.273 | 7892.9768 | 8110.6797 | 8284.635 | 8398.0049 | 8668.0117 | 8854.7587 | 8953.0314 | 9135.2741 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 | 9082.2337 |  | 1241.7934 | 1284.7411 | 1421.5316 | 1518.8403 | 1296.1629 | 1342.8738 | 1380.79 | 1417.2597 | 1448.8323 | 1464.6719 | 1488.0145 | 1514.7194 | 1541.9764 | 1576.2621 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146 | 1581.6146
55% | 8285.907 | 8537.7521 | 9561.6368 | 10300.3531 | 8579.6137 | 8927.6742 | 9148.7182 | 9401.0568 | 9602.6877 | 9734.0942 | 10047.0581 | 10263.5157 | 10377.4232 | 10588.6601 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 | 10527.1811 |  | 2020.1858 | 2090.0544 | 2312.5892 | 2470.8938 | 2108.6358 | 2184.6264 | 2246.3096 | 2305.6395 | 2357.0028 | 2382.7711 | 2420.7456 | 2464.1898 | 2508.5323 | 2564.3092 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017 | 2573.017
50% | 9747.9358 | 10044.2184 | 11248.7651 | 12117.8262 | 10093.4664 | 10502.9413 | 10762.9881 | 11059.8511 | 11297.0593 | 11451.6523 | 11819.8379 | 12074.489 | 12208.4952 | 12457.0043 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 | 12384.6775 |  | 3523.6644 | 3645.5311 | 4033.6826 | 4309.8019 | 3677.9413 | 3810.4862 | 3918.0758 | 4021.5607 | 4111.15 | 4156.0957 | 4222.332 | 4298.1085 | 4375.4521 | 4472.7397 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279 | 4487.9279
45% | 17342.4082 | 17869.5202 | 20012.5113 | 21558.6451 | 17957.1365 | 18685.6272 | 19148.2726 | 19676.4173 | 20098.4309 | 20373.4649 | 21028.4985 | 21481.5444 | 21719.9529 | 22162.0717 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 | 22033.3962 |  | 7020.6756 | 7263.4873 | 8036.8544 | 8587.0043 | 7328.0626 | 7592.1498 | 7806.5152 | 8012.7022 | 8191.2031 | 8280.7546 | 8412.7261 | 8563.706 | 8717.8081 | 8911.6474 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909 | 8941.909
40% | 19856.1284 | 20459.6435 | 22913.2535 | 24683.4938 | 20559.9595 | 21394.0423 | 21923.7465 | 22528.4439 | 23011.6268 | 23326.5261 | 24076.5044 | 24595.2178 | 24868.1827 | 25374.3851 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 | 25227.0585 |  | 11955.7442 | 12369.2363 | 13686.2291 | 14623.0978 | 12479.2037 | 12928.9267 | 13293.9767 | 13645.0996 | 13949.0747 | 14101.575 | 14326.3136 | 14583.4224 | 14845.848 | 15175.9435 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477 | 15227.477
35% | 12043.5634 | 12409.6202 | 13897.8362 | 14971.5602 | 12470.466 | 12976.3718 | 13297.6593 | 13664.4332 | 13957.5037 | 14148.5031 | 14603.396 | 14918.0171 | 15083.5816 | 15390.6143 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 | 15301.2547 |  | 14474.4645 | 14975.0672 | 16569.5112 | 17703.7504 | 15108.2015 | 15652.6677 | 16094.6229 | 16519.717 | 16887.7307 | 17072.3582 | 17344.4426 | 17655.7166 | 17973.4274 | 18373.0643 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544 | 18435.4544
30% | 4991.361 | 5143.0704 | 5759.8499 | 6204.8465 | 5168.2875 | 5377.9562 | 5511.1113 | 5663.1179 | 5784.5787 | 5863.7369 | 6052.2637 | 6182.656 | 6251.2729 | 6378.5202 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 | 6341.4858 |  | 22112.4023 | 22877.1648 | 25312.9708 | 27045.7294 | 23080.5519 | 23912.3241 | 24587.4918 | 25236.901 | 25799.1095 | 26081.1619 | 26496.8207 | 26972.3489 | 27457.7106 | 28068.2293 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416 | 28163.5416
25% | 2979.5232 | 3070.084 | 3438.2619 | 3703.8964 | 3085.137 | 3210.2958 | 3289.7809 | 3380.5191 | 3453.0234 | 3500.2758 | 3612.8142 | 3690.6501 | 3731.61 | 3807.5685 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 | 3785.4613 |  | 18803.7802 | 19454.1133 | 21525.4559 | 22998.9462 | 19627.068 | 20334.3843 | 20908.5284 | 21460.7681 | 21938.8548 | 22178.7045 | 22532.1693 | 22936.5455 | 23349.2837 | 23868.452 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031 | 23949.5031
20% | 3169.6139 | 3265.9524 | 3657.6197 | 3940.2014 | 3281.9657 | 3415.1095 | 3499.6657 | 3596.1929 | 3673.3229 | 3723.59 | 3843.3082 | 3926.1099 | 3969.6831 | 4050.4876 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 | 4026.97 |  | 4988.3748 | 5160.8989 | 5710.3965 | 6101.2925 | 5206.7813 | 5394.4222 | 5546.7345 | 5693.2358 | 5820.0654 | 5883.6941 | 5977.4633 | 6084.7385 | 6194.2321 | 6331.96 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617 | 6353.4617
15% | 3283.2375 | 3383.0295 | 3788.7372 | 4081.4488 | 3399.6169 | 3537.5336 | 3625.1209 | 3725.1084 | 3805.0034 | 3857.0724 | 3981.0823 | 4066.8522 | 4111.9874 | 4195.6886 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 | 4171.328 |  | 3091.1568 | 3198.0652 | 3538.5736 | 3780.8009 | 3226.4973 | 3342.7731 | 3437.1568 | 3527.9396 | 3606.5323 | 3645.9612 | 3704.0674 | 3770.5429 | 3838.393 | 3923.7391 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631 | 3937.0631
10% | 2189.0045 | 2255.5379 | 2526.0319 | 2721.189 | 2266.5971 | 2358.5491 | 2416.9454 | 2483.6093 | 2536.8769 | 2571.5925 | 2654.2725 | 2711.4572 | 2741.5497 | 2797.3551 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 | 2781.1134 |  | 884.3992 | 914.9863 | 1012.4079 | 1081.7106 | 923.1209 | 956.3882 | 983.3919 | 1009.3654 | 1031.8513 | 1043.1322 | 1059.7567 | 1078.7757 | 1098.1881 | 1122.6061 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182 | 1126.4182
5% | 174.4742 | 179.7772 | 201.3369 | 216.8918 | 180.6587 | 187.9877 | 192.6421 | 197.9556 | 202.2013 | 204.9683 | 211.5583 | 216.1161 | 218.5147 | 222.9626 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 | 221.6681 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 99564.2165 | 102590.4109 | 114893.5021 | 123769.9854 | 103093.4234 | 107275.7497 | 109931.8354 | 112963.9582 | 115386.7735 | 116965.7671 | 120726.3694 | 123327.3442 | 124696.0672 | 127234.3085 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | 126495.5717 | E @ R (MWh) | 93455.9144 | 96688.1086 | 106982.8055 | 114306.1407 | 97547.7041 | 101063.1082 | 103916.6388 | 106661.3036 | 109037.4229 | 110229.4901 | 111986.2317 | 113996.0053 | 116047.3391 | 118627.6367 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652 | 119030.4652
Option 2 Summer POE50 W E @ R (MWh) N 2 | 69694.9516 | 71813.2876 | 80425.4515 | 86638.9898 | 72165.3964 | 75093.0248 | 76952.2848 | 79074.7707 | 80770.7415 | 81876.037 | 84508.4586 | 86329.141 | 87287.247 | 89064.0159 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | 88546.9002 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 28036.7743 | 29006.4326 | 32094.8416 | 34291.8422 | 29264.3112 | 30318.9325 | 31174.9916 | 31998.3911 | 32711.2269 | 33068.847 | 33595.8695 | 34198.8016 | 34814.2017 | 35588.291 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396 | 35709.1396
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 44.7175 | 46.8571 | 53.2551 | 52.2115 | 42.2548 | 44.3553 | 46.7764 | 48.588 | 50.5852 | 51.632 | 52.5386 | 54.7829 | 53.4294 | 57.0894 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 |  | 47.5947 | 49.8159 | 56.1642 | 55.3245 | 45.3779 | 47.7433 | 49.9928 | 51.9093 | 53.9055 | 54.7805 | 55.9747 | 58.1887 | 57.4648 | 60.3565 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245
98% | 132.8043 | 139.1585 | 158.1595 | 155.0603 | 125.4905 | 131.7285 | 138.9189 | 144.299 | 150.2303 | 153.3391 | 156.0317 | 162.6971 | 158.6773 | 169.5469 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 |  | 141.3491 | 147.9458 | 166.7992 | 164.3053 | 134.7656 | 141.7905 | 148.4711 | 154.1628 | 160.0913 | 162.6898 | 166.2364 | 172.8116 | 170.6617 | 179.2496 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033
97% | 58.4249 | 61.2203 | 69.5795 | 68.216 | 55.2073 | 57.9516 | 61.1149 | 63.4818 | 66.0912 | 67.4588 | 68.6434 | 71.5757 | 69.8073 | 74.5892 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 |  | 62.184 | 65.0861 | 73.3804 | 72.2832 | 59.2877 | 62.3782 | 65.3172 | 67.8212 | 70.4294 | 71.5725 | 73.1328 | 76.0254 | 75.0796 | 78.8577 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037
95% | 143.8152 | 150.6962 | 171.2726 | 167.9164 | 135.895 | 142.6501 | 150.4367 | 156.2629 | 162.686 | 166.0525 | 168.9684 | 176.1864 | 171.8333 | 183.6041 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 |  | 153.0684 | 160.2121 | 180.6286 | 177.9279 | 145.939 | 153.5464 | 160.7809 | 166.9445 | 173.3646 | 176.1785 | 180.0192 | 187.1394 | 184.8113 | 194.1113 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757
90% | 1468.8623 | 1539.1418 | 1749.2998 | 1715.0213 | 1387.9689 | 1456.9629 | 1536.4916 | 1595.9973 | 1661.5999 | 1695.9843 | 1725.7655 | 1799.4867 | 1755.0266 | 1875.2482 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 |  | 1563.3702 | 1636.3326 | 1844.8575 | 1817.2743 | 1490.5543 | 1568.2527 | 1642.1425 | 1705.0946 | 1770.6661 | 1799.4064 | 1838.6332 | 1911.3564 | 1887.5779 | 1982.5635 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532
85% | 3460.5527 | 3626.127 | 4121.2469 | 4040.4886 | 3269.9726 | 3432.5183 | 3619.8833 | 3760.0753 | 3914.6311 | 3995.6387 | 4065.8014 | 4239.4842 | 4134.7389 | 4417.9738 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 |  | 3683.2076 | 3855.1027 | 4346.3751 | 4281.3908 | 3511.6578 | 3694.7107 | 3868.7905 | 4017.1021 | 4171.5846 | 4239.2951 | 4331.711 | 4503.0426 | 4447.0219 | 4670.8023 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836
80% | 6266.0722 | 6565.8799 | 7462.4007 | 7316.1705 | 5920.9861 | 6215.31 | 6554.5744 | 6808.422 | 7088.2784 | 7234.9601 | 7362.0047 | 7676.4946 | 7486.8308 | 7999.6882 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 |  | 6669.2367 | 6980.4895 | 7870.0435 | 7752.3754 | 6358.609 | 6690.0654 | 7005.2742 | 7273.8241 | 7553.5479 | 7676.1523 | 7843.491 | 8153.7236 | 8052.2861 | 8457.4884 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177
75% | 7325.96 | 7676.4794 | 8724.6441 | 8553.6795 | 6922.5037 | 7266.6116 | 7663.2616 | 7960.0468 | 8287.2401 | 8458.7326 | 8607.2663 | 8974.9514 | 8753.2065 | 9352.8122 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 |  | 7797.3187 | 8161.2191 | 9201.2384 | 9063.6672 | 7434.1492 | 7821.6705 | 8190.196 | 8504.1703 | 8831.2085 | 8974.5511 | 9170.1947 | 9532.9023 | 9414.3069 | 9888.048 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119
70% | 8591.0842 | 9002.1349 | 10231.3077 | 10030.8191 | 8117.9547 | 8521.4868 | 8986.6346 | 9334.6717 | 9718.3682 | 9919.4758 | 10093.66 | 10524.8407 | 10264.8026 | 10967.9545 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 |  | 9143.842 | 9570.5845 | 10790.2054 | 10628.8769 | 8717.9566 | 9172.3991 | 9604.5655 | 9972.7602 | 10356.2749 | 10524.3713 | 10753.8008 | 11179.1445 | 11040.0688 | 11595.6205 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746
65% | 9414.2762 | 9864.7136 | 11211.6649 | 10991.9657 | 8895.8119 | 9338.0101 | 9847.728 | 10229.1139 | 10649.5759 | 10869.9535 | 11060.8279 | 11533.3241 | 11248.3693 | 12018.8968 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 |  | 10019.999 | 10487.6317 | 11824.1158 | 11647.329 | 9553.3055 | 10051.2924 | 10524.8687 | 10928.3436 | 11348.6063 | 11532.8097 | 11784.2229 | 12250.3228 | 12097.9209 | 12706.7053 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865
60% | 10243.0861 | 10733.1789 | 12198.7125 | 11959.6714 | 9678.9774 | 10160.1056 | 10714.6979 | 11129.6601 | 11587.1385 | 11826.9176 | 12034.5961 | 12548.6897 | 12238.6482 | 13077.011 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 |  | 10902.1352 | 11410.9371 | 12865.0821 | 12672.7313 | 10394.3552 | 10936.1836 | 11451.4524 | 11890.4482 | 12347.7099 | 12548.1301 | 12821.6771 | 13328.8113 | 13162.9923 | 13825.3726 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475
55% | 10267.8043 | 10759.0798 | 12228.15 | 11988.5321 | 9702.3343 | 10184.6236 | 10740.5542 | 11156.5177 | 11615.1002 | 11855.4579 | 12063.6375 | 12578.9718 | 12268.182 | 13108.568 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 |  | 10928.4438 | 11438.4736 | 12896.1276 | 12703.3127 | 10419.4384 | 10962.5744 | 11479.0866 | 11919.1418 | 12377.5069 | 12578.4108 | 12852.6179 | 13360.9759 | 13194.7567 | 13858.7354 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324
50% | 12096.2046 | 12674.962 | 14405.6313 | 14123.3444 | 11430.0406 | 11998.2118 | 12653.1376 | 13143.1722 | 13683.415 | 13966.5735 | 14211.8239 | 14818.9244 | 14452.7919 | 15442.8264 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 |  | 12874.4849 | 13475.3363 | 15192.5565 | 14965.4068 | 12274.8403 | 12914.6931 | 13523.1813 | 14041.5977 | 14581.5844 | 14818.2634 | 15141.299 | 15740.1809 | 15544.3629 | 16326.5771 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748
45% | 15128.3079 | 15852.1399 | 18016.6286 | 17663.582 | 14295.1595 | 15005.7516 | 15824.8449 | 16437.7144 | 17113.3774 | 17467.5141 | 17774.2404 | 18533.5201 | 18075.6108 | 19313.813 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 |  | 16101.6763 | 16853.1406 | 19000.809 | 18716.7206 | 15351.7215 | 16151.9634 | 16912.9787 | 17561.3443 | 18236.6871 | 18532.6935 | 18936.7029 | 19685.7039 | 19440.8011 | 20419.0896 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871
40% | 16018.9133 | 16785.3574 | 19077.2699 | 18703.4394 | 15136.7174 | 15889.1422 | 16756.4555 | 17405.4048 | 18120.8442 | 18495.8289 | 18820.6122 | 19624.5908 | 19139.7243 | 20450.8196 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 |  | 17049.5841 | 17845.2871 | 20119.3891 | 19818.5764 | 16255.4793 | 17102.8316 | 17908.648 | 18595.1829 | 19310.2833 | 19623.7155 | 20051.5091 | 20844.6039 | 20585.2836 | 21621.164 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818
35% | 6550.3318 | 6863.7403 | 7800.9317 | 7648.0678 | 6189.591 | 6497.2668 | 6851.922 | 7117.2854 | 7409.8374 | 7563.1733 | 7695.9812 | 8024.738 | 7826.4701 | 8362.5932 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 |  | 6971.7859 | 7297.1587 | 8227.0671 | 8104.0611 | 6647.0666 | 6993.5594 | 7323.0677 | 7603.8004 | 7896.2137 | 8024.3801 | 8199.3101 | 8523.6164 | 8417.5772 | 8841.1615 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939
30% | 2020.5283 | 2117.2029 | 2406.2908 | 2359.1381 | 1909.2535 | 2004.1598 | 2113.5574 | 2195.4119 | 2285.6531 | 2332.9514 | 2373.9176 | 2475.3266 | 2414.1684 | 2579.542 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 |  | 2150.5309 | 2250.896 | 2537.7374 | 2499.7947 | 2050.3673 | 2157.2472 | 2258.888 | 2345.4833 | 2435.6817 | 2475.2162 | 2529.1754 | 2629.2116 | 2596.5025 | 2727.1622 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294
25% | 1487.2137 | 1558.3712 | 1771.1549 | 1736.4481 | 1405.3097 | 1475.1656 | 1555.6879 | 1615.9371 | 1682.3593 | 1717.1733 | 1747.3265 | 1821.9688 | 1776.9533 | 1898.6768 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 |  | 1582.9023 | 1656.7763 | 1867.9064 | 1839.9786 | 1509.1768 | 1587.8459 | 1662.6588 | 1726.3974 | 1792.7882 | 1821.8876 | 1861.6044 | 1935.2362 | 1911.1606 | 2007.3329 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071
20% | 1183.1045 | 1239.7116 | 1408.9847 | 1381.3748 | 1117.9484 | 1173.5201 | 1237.577 | 1285.5063 | 1338.3463 | 1366.0414 | 1390.0289 | 1449.4081 | 1413.5974 | 1510.4306 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 |  | 1259.2265 | 1317.9945 | 1485.9523 | 1463.7352 | 1200.5765 | 1263.1592 | 1322.6742 | 1373.3794 | 1426.1944 | 1449.3434 | 1480.9389 | 1539.5143 | 1520.3617 | 1596.8684 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992
15% | 928.0573 | 972.4613 | 1105.2435 | 1083.5856 | 876.9472 | 920.539 | 970.7869 | 1008.3838 | 1049.8329 | 1071.5577 | 1090.374 | 1136.9526 | 1108.8618 | 1184.8202 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 |  | 987.7693 | 1033.8685 | 1165.6188 | 1148.1912 | 941.7628 | 990.8542 | 1037.5393 | 1077.3137 | 1118.7431 | 1136.9019 | 1161.6861 | 1207.6342 | 1192.6104 | 1252.6243 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415
10% | 651.6625 | 682.8421 | 776.079 | 760.8712 | 615.7741 | 646.3833 | 681.6663 | 708.0661 | 737.1708 | 752.4255 | 765.6379 | 798.3444 | 778.6197 | 831.9561 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 |  | 693.591 | 725.9609 | 818.4732 | 806.2359 | 661.2862 | 695.7572 | 728.5385 | 756.4673 | 785.5581 | 798.3088 | 815.7118 | 847.9756 | 837.4262 | 879.5667 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742
5% | 67.4134 | 70.6388 | 80.284 | 78.7108 | 63.7008 | 66.8672 | 70.5172 | 73.2482 | 76.259 | 77.8371 | 79.2039 | 82.5874 | 80.5469 | 86.0644 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 |  | 71.7508 | 75.0994 | 84.6696 | 83.4037 | 68.4089 | 71.9749 | 75.366 | 78.2552 | 81.2646 | 82.5837 | 84.384 | 87.7216 | 86.6303 | 90.9897 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 113549.1973 | 118982.0949 | 135228.1917 | 132578.3147 | 107295.7995 | 112629.3218 | 118777.2255 | 123377.2667 | 128448.6202 | 131106.6792 | 133408.888 | 139107.8464 | 135670.8969 | 144964.5246 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | E @ R (MWh) | 120855.0513 | 126495.349 | 142615.1972 | 140482.9027 | 115226.0825 | 121232.4933 | 126944.4789 | 131810.9445 | 136879.8947 | 139101.6422 | 142134.0335 | 147755.843 | 145917.6654 | 153260.4473 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195
Option 3 Winter POE50 W E @ R (MWh) N 2 | 79484.4381 | 83287.4664 | 94659.7342 | 92804.8203 | 75107.0597 | 78840.5252 | 83144.0578 | 86364.0867 | 89914.0342 | 91774.6755 | 93386.2216 | 97375.4925 | 94969.6278 | 101475.1672 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 36256.5154 | 37948.6047 | 42784.5592 | 42144.8708 | 34567.8247 | 36369.748 | 38083.3437 | 39543.2834 | 41063.9684 | 41730.4927 | 42640.21 | 44326.7529 | 43775.2996 | 45978.1342 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 48.2179 | 49.8856 | 55.197 | 53.5195 | 44.8731 | 46.6868 | 48.1591 | 49.5752 | 50.8011 | 51.4162 | 52.3226 | 53.3595 | 54.4179 | 55.7491 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957
98% | 21.2169 | 21.8618 | 24.4836 | 23.6746 | 19.2684 | 20.1597 | 20.7257 | 21.3718 | 21.8881 | 22.2246 | 23.026 | 23.5802 | 23.8719 | 24.4128 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 |  | 23.8667 | 24.6921 | 27.3211 | 26.4908 | 22.2111 | 23.1088 | 23.8375 | 24.5385 | 25.1453 | 25.4497 | 25.8983 | 26.4116 | 26.9355 | 27.5944 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973
97% | 21.0015 | 21.6398 | 24.235 | 23.4342 | 19.0728 | 19.955 | 20.5153 | 21.1548 | 21.6659 | 21.999 | 22.7922 | 23.3408 | 23.6295 | 24.1649 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 |  | 47.2487 | 48.8828 | 54.0875 | 52.4437 | 43.9711 | 45.7484 | 47.1911 | 48.5787 | 49.78 | 50.3827 | 51.2708 | 52.2869 | 53.324 | 54.6286 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322
95% | 62.0353 | 63.9208 | 71.5864 | 69.221 | 56.3381 | 58.944 | 60.5989 | 62.4881 | 63.9977 | 64.9815 | 67.3246 | 68.9452 | 69.798 | 71.3795 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 |  | 93.0436 | 96.2616 | 106.5109 | 103.2738 | 86.5893 | 90.0892 | 92.9301 | 95.6627 | 98.0283 | 99.2151 | 100.9641 | 102.965 | 105.0073 | 107.5762 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773
90% | 139.4716 | 143.7108 | 160.9452 | 155.6271 | 126.663 | 132.5217 | 136.2424 | 140.4898 | 143.8837 | 146.0956 | 151.3636 | 155.0071 | 156.9244 | 160.48 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 |  | 336.1928 | 347.8201 | 384.8537 | 373.1573 | 312.8714 | 325.5175 | 335.7827 | 345.6562 | 354.2039 | 358.4922 | 364.8118 | 372.0416 | 379.4209 | 388.7032 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523
85% | 226.1702 | 233.0445 | 260.9922 | 252.3683 | 205.3994 | 214.9 | 220.9335 | 227.8213 | 233.325 | 236.9118 | 245.4544 | 251.3628 | 254.472 | 260.2379 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 |  | 402.8257 | 416.7575 | 461.131 | 447.1164 | 374.882 | 390.0345 | 402.3342 | 414.1646 | 424.4065 | 429.5447 | 437.1168 | 445.7796 | 454.6215 | 465.7434 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797
80% | 870.7553 | 897.2214 | 1004.8201 | 971.618 | 790.7877 | 827.3649 | 850.5941 | 877.1121 | 898.3012 | 912.1106 | 944.9995 | 967.7468 | 979.7172 | 1001.9158 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 |  | 459.7664 | 475.6675 | 526.3134 | 510.3178 | 427.8728 | 445.1672 | 459.2055 | 472.7082 | 484.3977 | 490.2622 | 498.9047 | 508.792 | 518.8838 | 531.5778 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596
75% | 1318.7877 | 1358.8714 | 1521.8333 | 1471.5476 | 1197.6741 | 1253.0715 | 1288.253 | 1328.4153 | 1360.5069 | 1381.4216 | 1431.233 | 1465.6845 | 1483.8141 | 1517.4346 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 |  | 394.3451 | 407.9836 | 451.423 | 437.7034 | 366.9897 | 381.8233 | 393.864 | 405.4453 | 415.4716 | 420.5016 | 427.9143 | 436.3947 | 445.0505 | 455.9383 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381
70% | 2014.5303 | 2075.7608 | 2324.6951 | 2247.8805 | 1829.5218 | 1914.1448 | 1967.8866 | 2029.237 | 2078.259 | 2110.2075 | 2186.2976 | 2238.9244 | 2266.6184 | 2317.9758 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 |  | 421.604 | 436.1853 | 482.6273 | 467.9594 | 392.3577 | 408.2166 | 421.0896 | 433.4715 | 444.1908 | 449.5685 | 457.4937 | 466.5603 | 475.8144 | 487.4548 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272
65% | 3678.4968 | 3790.3025 | 4244.8522 | 4104.5902 | 3340.6745 | 3495.1946 | 3593.3263 | 3705.351 | 3794.8643 | 3853.2017 | 3992.1409 | 4088.2364 | 4138.8052 | 4232.583 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 |  | 1112.1622 | 1150.6266 | 1273.1376 | 1234.4445 | 1035.0125 | 1076.8472 | 1110.8054 | 1143.468 | 1171.7447 | 1185.9308 | 1206.8367 | 1230.7538 | 1255.1655 | 1285.8721 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659
60% | 7148.594 | 7365.8712 | 8249.2187 | 7976.641 | 6492.0881 | 6792.3743 | 6983.0781 | 7200.781 | 7374.7363 | 7488.1062 | 7758.113 | 7944.8599 | 8043.1326 | 8225.3754 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 |  | 1241.7934 | 1284.7411 | 1421.5316 | 1378.3286 | 1155.6513 | 1202.3621 | 1240.2783 | 1276.748 | 1308.3206 | 1324.1602 | 1347.5029 | 1374.2077 | 1401.4647 | 1435.7504 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103
55% | 8285.907 | 8537.7521 | 9561.6368 | 9245.6931 | 7524.9537 | 7873.0142 | 8094.0582 | 8346.3967 | 8548.0276 | 8679.4342 | 8992.3981 | 9208.8557 | 9322.7632 | 9534.0001 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 |  | 2020.1858 | 2090.0544 | 2312.5892 | 2242.3053 | 1880.0473 | 1956.0379 | 2017.7211 | 2077.051 | 2128.4143 | 2154.1826 | 2192.1571 | 2235.6013 | 2279.9439 | 2335.7207 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285
50% | 9747.9358 | 10044.2184 | 11248.7651 | 10877.0739 | 8852.7141 | 9262.189 | 9522.2358 | 9819.0988 | 10056.307 | 10210.9 | 10579.0856 | 10833.7367 | 10967.7429 | 11216.252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 |  | 3523.6644 | 3645.5311 | 4033.6826 | 3911.0915 | 3279.2309 | 3411.7758 | 3519.3654 | 3622.8503 | 3712.4396 | 3757.3853 | 3823.6215 | 3899.3981 | 3976.7417 | 4074.0293 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175
45% | 17342.4082 | 17869.5202 | 20012.5113 | 19351.241 | 15749.7325 | 16478.2232 | 16940.8686 | 17469.0133 | 17891.0269 | 18166.0609 | 18821.0945 | 19274.1404 | 19512.5489 | 19954.6677 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 |  | 7020.6756 | 7263.4873 | 8036.8544 | 7792.5993 | 6533.6576 | 6797.7448 | 7012.1102 | 7218.2973 | 7396.7981 | 7486.3496 | 7618.3211 | 7769.301 | 7923.4031 | 8117.2424 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041
40% | 19856.1284 | 20459.6435 | 22913.2535 | 22156.1345 | 18032.6001 | 18866.683 | 19396.3871 | 20001.0845 | 20484.2675 | 20799.1667 | 21549.145 | 22067.8584 | 22340.8233 | 22847.0257 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 |  | 11955.7442 | 12369.2363 | 13686.2291 | 13270.2789 | 11126.3848 | 11576.1078 | 11941.1578 | 12292.2807 | 12596.2558 | 12748.7561 | 12973.4947 | 13230.6035 | 13493.0291 | 13823.1246 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581
35% | 12043.5634 | 12409.6202 | 13897.8362 | 13438.6122 | 10937.518 | 11443.4238 | 11764.7113 | 12131.4852 | 12424.5557 | 12615.5551 | 13070.448 | 13385.0691 | 13550.6336 | 13857.6663 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 |  | 14474.4645 | 14975.0672 | 16569.5112 | 16065.9327 | 13470.3838 | 14014.85 | 14456.8052 | 14881.8993 | 15249.913 | 15434.5405 | 15706.6249 | 16017.8989 | 16335.6097 | 16735.2466 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367
30% | 4991.361 | 5143.0704 | 5759.8499 | 5569.5281 | 4532.9691 | 4742.6378 | 4875.7929 | 5027.7995 | 5149.2603 | 5228.4185 | 5416.9453 | 5547.3376 | 5615.9545 | 5743.2018 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 |  | 22112.4023 | 22877.1648 | 25312.9708 | 24543.6621 | 20578.4846 | 21410.2568 | 22085.4245 | 22734.8337 | 23297.0422 | 23579.0946 | 23994.7535 | 24470.2817 | 24955.6433 | 25566.162 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744
25% | 2979.5232 | 3070.084 | 3438.2619 | 3324.652 | 2705.8926 | 2831.0514 | 2910.5364 | 3001.2747 | 3073.779 | 3121.0314 | 3233.5698 | 3311.4056 | 3352.3656 | 3428.3241 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 |  | 18803.7802 | 19454.1133 | 21525.4559 | 20871.2569 | 17499.3787 | 18206.6949 | 18780.839 | 19333.0788 | 19811.1654 | 20051.0151 | 20404.48 | 20808.8561 | 21221.5944 | 21740.7627 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137
20% | 3169.6139 | 3265.9524 | 3657.6197 | 3536.7615 | 2878.5259 | 3011.6697 | 3096.2258 | 3192.7531 | 3269.8831 | 3320.1501 | 3439.8684 | 3522.6701 | 3566.2432 | 3647.0478 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 |  | 4988.3748 | 5160.8989 | 5710.3965 | 5536.8469 | 4642.3357 | 4829.9766 | 4982.2888 | 5128.7902 | 5255.6197 | 5319.2484 | 5413.0176 | 5520.2928 | 5629.7864 | 5767.5144 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016
15% | 3283.2375 | 3383.0295 | 3788.7372 | 3663.5465 | 2981.7146 | 3119.6313 | 3207.2186 | 3307.2061 | 3387.1011 | 3439.1701 | 3563.18 | 3648.95 | 3694.0851 | 3777.7863 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 |  | 3091.1568 | 3198.0652 | 3538.5736 | 3431.0297 | 2876.726 | 2993.0019 | 3087.3855 | 3178.1683 | 3256.7611 | 3296.19 | 3354.2962 | 3420.7716 | 3488.6217 | 3573.9679 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919
10% | 2189.0045 | 2255.5379 | 2526.0319 | 2442.5647 | 1987.9728 | 2079.9248 | 2138.3211 | 2204.9849 | 2258.2526 | 2292.9681 | 2375.6482 | 2432.8328 | 2462.9254 | 2518.7308 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 |  | 884.3992 | 914.9863 | 1012.4079 | 981.6389 | 823.0492 | 856.3164 | 883.3202 | 909.2937 | 931.7796 | 943.0604 | 959.685 | 978.704 | 998.1164 | 1022.5344 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465
5% | 174.4742 | 179.7772 | 201.3369 | 194.6841 | 158.451 | 165.78 | 170.4344 | 175.7479 | 179.9936 | 182.7606 | 189.3506 | 193.9084 | 196.307 | 200.7549 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 99564.2165 | 102590.4109 | 114893.5021 | 111097.0942 | 90420.5322 | 94602.8585 | 97258.9442 | 100291.067 | 102713.8824 | 104292.876 | 108053.4783 | 110654.4531 | 112023.176 | 114561.4173 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | E @ R (MWh) | 93455.9144 | 96688.1086 | 106982.8055 | 103731.3972 | 86972.9605 | 90488.3647 | 93341.8953 | 96086.56 | 98462.6793 | 99654.7466 | 101411.4881 | 103421.2618 | 105472.5956 | 108052.8932 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217
Option 3 Summer POE50 W E @ R (MWh) N 2 | 69694.9516 | 71813.2876 | 80425.4515 | 77767.9659 | 63294.3726 | 66222.001 | 68081.261 | 70203.7469 | 71899.7177 | 73005.0132 | 75637.4348 | 77458.1171 | 78416.2232 | 80192.9921 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 28036.7743 | 29006.4326 | 32094.8416 | 31119.4191 | 26091.8881 | 27146.5094 | 28002.5686 | 28825.968 | 29538.8038 | 29896.424 | 30423.4464 | 31026.3785 | 31641.7787 | 32415.8679 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 44.7175 | 46.8571 | 53.2551 | 18.3431 | 21.25 | 23.3504 | 25.7715 | 27.5831 | 29.5803 | 30.6271 | 31.5337 | 33.7781 | 32.4245 | 36.0845 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 | 40.8587 |  | 47.5947 | 49.8159 | 56.1642 | 21.4561 | 24.373 | 26.7385 | 28.9879 | 30.9044 | 32.9007 | 33.7756 | 34.9698 | 37.1838 | 36.4599 | 39.3516 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196 | 41.0196
98% | 132.8043 | 139.1585 | 158.1595 | 53.2613 | 61.8941 | 68.1321 | 75.3225 | 80.7026 | 86.6339 | 89.7427 | 92.4353 | 99.1007 | 95.0809 | 105.9505 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 | 120.129 |  | 141.3491 | 147.9458 | 166.7992 | 62.5063 | 71.1692 | 78.1941 | 84.8747 | 90.5664 | 96.4949 | 99.0934 | 102.64 | 109.2152 | 107.0653 | 115.6532 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069 | 120.6069
97% | 58.4249 | 61.2203 | 69.5795 | 22.8858 | 26.6837 | 29.428 | 32.5913 | 34.9582 | 37.5675 | 38.9352 | 40.1198 | 43.0521 | 41.2837 | 46.0655 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 | 52.3031 |  | 62.184 | 65.0861 | 73.3804 | 26.953 | 30.7641 | 33.8546 | 36.7936 | 39.2976 | 41.9057 | 43.0489 | 44.6092 | 47.5018 | 46.556 | 50.3341 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134 | 52.5134
95% | 143.8152 | 150.6962 | 171.2726 | 54.2677 | 63.6163 | 70.3714 | 78.158 | 83.9842 | 90.4073 | 93.7738 | 96.6897 | 103.9077 | 99.5546 | 111.3254 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 | 126.6795 |  | 153.0684 | 160.2121 | 180.6286 | 64.2792 | 73.6603 | 81.2677 | 88.5022 | 94.6658 | 101.0859 | 103.8998 | 107.7405 | 114.8607 | 112.5326 | 121.8326 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197 | 127.197
90% | 1468.8623 | 1539.1418 | 1749.2998 | 502.3509 | 597.8331 | 666.8271 | 746.3558 | 805.8616 | 871.4641 | 905.8486 | 935.6297 | 1009.3509 | 964.8909 | 1085.1124 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 | 1241.9318 |  | 1563.3702 | 1636.3326 | 1844.8575 | 604.604 | 700.4186 | 778.117 | 852.0067 | 914.9589 | 980.5304 | 1009.2707 | 1048.4974 | 1121.2207 | 1097.4422 | 1192.4277 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174 | 1247.2174
85% | 3460.5527 | 3626.127 | 4121.2469 | 991.8112 | 1216.7617 | 1379.3074 | 1566.6724 | 1706.8643 | 1861.4201 | 1942.4278 | 2012.5904 | 2186.2733 | 2081.528 | 2364.7628 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 | 2734.2201 |  | 3683.2076 | 3855.1027 | 4346.3751 | 1232.7133 | 1458.4469 | 1641.4997 | 1815.5795 | 1963.8911 | 2118.3737 | 2186.0842 | 2278.5001 | 2449.8317 | 2393.8109 | 2617.5913 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726 | 2746.6726
80% | 6266.0722 | 6565.8799 | 7462.4007 | 1406.7026 | 1814.0237 | 2108.3475 | 2447.612 | 2701.4596 | 2981.316 | 3127.9977 | 3255.0422 | 3569.5322 | 3379.8684 | 3892.7257 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 | 4561.7073 |  | 6669.2367 | 6980.4895 | 7870.0435 | 1842.9075 | 2251.6465 | 2583.1029 | 2898.3118 | 3166.8617 | 3446.5854 | 3569.1898 | 3736.5286 | 4046.7612 | 3945.3236 | 4350.526 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553 | 4584.2553
75% | 7325.96 | 7676.4794 | 8724.6441 | 1130.9175 | 1607.1357 | 1951.2436 | 2347.8936 | 2644.6788 | 2971.8721 | 3143.3646 | 3291.8983 | 3659.5834 | 3437.8385 | 4037.4442 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 | 4819.582 |  | 7797.3187 | 8161.2191 | 9201.2384 | 1640.9052 | 2118.7812 | 2506.3025 | 2874.828 | 3188.8023 | 3515.8405 | 3659.1831 | 3854.8267 | 4217.5343 | 4098.9389 | 4572.68 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439 | 4845.9439
70% | 8591.0842 | 9002.1349 | 10231.3077 | 640.6809 | 1199.1375 | 1602.6695 | 2067.8173 | 2415.8545 | 2799.5509 | 3000.6586 | 3174.8427 | 3606.0235 | 3345.9853 | 4049.1373 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 | 4966.3429 |  | 9143.842 | 9570.5845 | 10790.2054 | 1238.7386 | 1799.1393 | 2253.5818 | 2685.7482 | 3053.943 | 3437.4576 | 3605.5541 | 3834.9835 | 4260.3272 | 4121.2515 | 4676.8033 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573 | 4997.2573
65% | 9414.2762 | 9864.7136 | 11211.6649 | 48.167 | 451.943 | 893.721 | 1403.439 | 1784.8248 | 2205.2868 | 2425.6644 | 2616.5388 | 3089.035 | 2804.0802 | 3574.6077 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 | 4579.6994 |  | 10019.999 | 10487.6317 | 11824.1158 | 494.9185 | 1109.0164 | 1607.0033 | 2080.5796 | 2484.0545 | 2904.3173 | 3088.5206 | 3339.9339 | 3806.0338 | 3653.6319 | 4262.4162 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576 | 4613.576
60% | 10243.0861 | 10733.1789 | 12198.7125 |  |  | 93.4877 | 449.9088 | 853.3556 | 1310.8341 | 1550.6132 | 1758.2917 | 2272.3853 | 1962.3437 | 2800.7066 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 | 3894.2841 |  | 10902.1352 | 11410.9371 | 12865.0821 | 0.10931 | 213.0465 | 659.8791 | 1175.148 | 1614.1438 | 2071.4054 | 2271.8256 | 2545.3727 | 3052.5068 | 2886.6879 | 3549.0681 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431 | 3931.1431
55% | 10267.8043 | 10759.0798 | 12228.15 |  |  |  |  | 23.4457 | 191.2938 | 340.0761 | 500.8797 | 996.8624 | 686.6224 | 1526.4586 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 | 2622.6751 |  | 10928.4438 | 11438.4736 | 12896.1276 |  |  | 0.92373 | 125.2546 | 386.1782 | 795.3975 | 996.3014 | 1270.5085 | 1778.8665 | 1612.6474 | 2276.6261 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623 | 2659.623
50% | 12096.2046 | 12674.962 | 14405.6313 | [8 empty] | 28.8808 |  | 246.8344 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 | 1293.1303 |  | 12874.4849 | 13475.3363 | 15192.5565 | [5 empty] | 1.8429 | 28.7614 | 115.6586 | 421.4537 | 301.5059 | 890.2726 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576 | 1336.6576
45% | 15128.3079 | 15852.1399 | 18016.6286 | [11 empty] | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 | 20.285 |  | 16101.6763 | 16853.1406 | 19000.809 | [11 empty] | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875 | 27.5875
40% | FY25: 16018.9133; FY26: 16785.3574; FY27: 19077.2699 |  | 17049.5841 | 17845.2871 | 20119.3891
35% | FY25: 6550.3318; FY26: 6863.7403; FY27: 7800.9317 |  | 6971.7859 | 7297.1587 | 8227.0671
30% | FY25: 2020.5283; FY26: 2117.2029; FY27: 2406.2908 |  | 2150.5309 | 2250.896 | 2537.7374
25% | FY25: 1487.2137; FY26: 1558.3712; FY27: 1771.1549 |  | 1582.9023 | 1656.7763 | 1867.9064
20% | FY25: 1183.1045; FY26: 1239.7116; FY27: 1408.9847 |  | 1259.2265 | 1317.9945 | 1485.9523
15% | FY25: 928.0573; FY26: 972.4613; FY27: 1105.2435 |  | 987.7693 | 1033.8685 | 1165.6188
10% | FY25: 651.6625; FY26: 682.8421; FY27: 776.079 |  | 693.591 | 725.9609 | 818.4732
5% | FY25: 67.4134; FY26: 70.6388; FY27: 80.284 |  | 71.7508 | 75.0994 | 84.6696
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 113549.1973 | 118982.0949 | 135228.1917 | 4869.388 | 7060.2788 | 8886.8857 | 11241.5422 | 13163.573 | 15437.227 | 16689.7297 | 17806.492 | 20697.7653 | 18931.5011 | 23877.2157 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | 31073.8282 | E @ R (MWh) | 120855.0513 | 126495.349 | 142615.1972 | 7230.0911 | 9850.4621 | 12250.4649 | 14746.6149 | 17028.2678 | 19544.1379 | 20694.5087 | 22314.7695 | 25463.2973 | 24413.8538 | 28715.5828 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706 | 31331.2706
Option 4 Winter POE50 W E @ R (MWh) N 2 | 79484.4381 | 83287.4664 | 94659.7342 | 3408.5716 | 4942.1951 | 6220.82 | 7869.0795 | 9214.5011 | 10806.0589 | 11682.8108 | 12464.5444 | 14488.4357 | 13252.0507 | 16714.051 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | 21751.6798 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 36256.5154 | 37948.6047 | 42784.5592 | 2169.0273 | 2955.1386 | 3675.1395 | 4423.9845 | 5108.4803 | 5863.2414 | 6208.3526 | 6694.4308 | 7638.9892 | 7324.1561 | 8614.6748 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812 | 9399.3812
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 48.2179 | 49.8856 | 55.197 | 24.7894 | 27.0549 | 28.8687 | 30.3409 | 31.757 | 32.983 | 33.598 | 34.5044 | 35.5413 | 36.5997 | 37.931 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388 | 38.1388
98% | 21.2169 | 21.8618 | 24.4836 | 9.2821 | 10.2771 | 11.1683 | 11.7343 | 12.3805 | 12.8968 | 13.2333 | 14.0346 | 14.5889 | 14.8806 | 15.4215 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 | 15.264 |  | 23.8667 | 24.6921 | 27.3211 | 12.0983 | 13.2197 | 14.1175 | 14.8462 | 15.5471 | 16.154 | 16.4584 | 16.907 | 17.4203 | 17.9441 | 18.6031 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706 | 18.706
97% | 21.0015 | 21.6398 | 24.235 | 9.0143 | 9.9992 | 10.8814 | 11.4417 | 12.0813 | 12.5923 | 12.9254 | 13.7186 | 14.2673 | 14.556 | 15.0914 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 | 14.9355 |  | 47.2487 | 48.8828 | 54.0875 | 23.604 | 25.824 | 27.6013 | 29.0439 | 30.4315 | 31.6328 | 32.2355 | 33.1237 | 34.1398 | 35.1769 | 36.4814 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851 | 36.6851
95% | 62.0353 | 63.9208 | 71.5864 | 25.838 | 28.7473 | 31.3531 | 33.008 | 34.8973 | 36.4068 | 37.3907 | 39.7338 | 41.3544 | 42.2072 | 43.7887 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 | 43.3284 |  | 93.0436 | 96.2616 | 106.5109 | 45.4298 | 49.8015 | 53.3014 | 56.1423 | 58.8749 | 61.2405 | 62.4273 | 64.1763 | 66.1772 | 68.2195 | 70.7884 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895 | 71.1895
90% | 139.4716 | 143.7108 | 160.9452 | 53.7284 | 60.2691 | 66.1278 | 69.8485 | 74.096 | 77.4899 | 79.7018 | 84.9697 | 88.6132 | 90.5306 | 94.0862 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 | 93.0513 |  | 336.1928 | 347.8201 | 384.8537 | 154.8028 | 170.5989 | 183.2451 | 193.5102 | 203.3837 | 211.9314 | 216.2197 | 222.5393 | 229.7691 | 237.1484 | 246.4307 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798 | 247.8798
85% | 226.1702 | 233.0445 | 260.9922 | 76.0398 | 86.6464 | 96.1469 | 102.1805 | 109.0683 | 114.5719 | 118.1588 | 126.7014 | 132.6098 | 135.719 | 141.4848 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 | 139.8067 |  | 402.8257 | 416.7575 | 461.131 | 167.9295 | 186.8563 | 202.0089 | 214.3085 | 226.139 | 236.3808 | 241.519 | 249.0911 | 257.7539 | 266.5958 | 277.7178 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541 | 279.4541
80% | 870.7553 | 897.2214 | 1004.8201 | 244.8926 | 285.728 | 322.3052 | 345.5345 | 372.0524 | 393.2415 | 407.0509 | 439.9399 | 462.6871 | 474.6575 | 496.8561 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 | 490.3954 |  | 459.7664 | 475.6675 | 526.3134 | 169.2018 | 190.804 | 208.0984 | 222.1367 | 235.6393 | 247.3289 | 253.1934 | 261.8359 | 271.7232 | 281.8149 | 294.509 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908 | 296.4908
75% | 1318.7877 | 1358.8714 | 1521.8333 | 289.0586 | 350.9052 | 406.3026 | 441.4841 | 481.6463 | 513.738 | 534.6527 | 584.4641 | 618.9156 | 637.0452 | 670.6657 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 | 660.8807 |  | 394.3451 | 407.9836 | 451.423 | 123.3709 | 141.8993 | 156.7328 | 168.7735 | 180.3549 | 190.3811 | 195.4111 | 202.8239 | 211.3043 | 219.96 | 230.8478 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476 | 232.5476
70% | 2014.5303 | 2075.7608 | 2324.6951 | 299.2969 | 393.7715 | 478.3945 | 532.1363 | 593.4867 | 642.5087 | 674.4572 | 750.5473 | 803.174 | 830.8681 | 882.2255 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 | 867.2783 |  | 421.604 | 436.1853 | 482.6273 | 105.4322 | 125.2414 | 141.1003 | 153.9733 | 166.3552 | 177.0745 | 182.4522 | 190.3773 | 199.4439 | 208.698 | 220.3384 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557 | 222.1557
65% | 3678.4968 | 3790.3025 | 4244.8522 | 248.267 | 420.7759 | 575.296 | 673.4277 | 785.4524 | 874.9657 | 933.3031 | 1072.2422 | 1168.3378 | 1218.9066 | 1312.6844 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 | 1285.391 |  | 1112.1622 | 1150.6266 | 1273.1376 | 197.9624 | 250.2177 | 292.0523 | 326.0105 | 358.6731 | 386.9498 | 401.1359 | 422.0418 | 445.9589 | 470.3706 | 501.0772 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871 | 505.871
60% | 7148.594 | 7365.8712 | 8249.2187 | 19.2882 | 179.2375 | 445.6738 | 636.3776 | 854.0805 | 1028.0358 | 1141.4057 | 1411.4125 | 1598.1595 | 1696.4322 | 1878.6749 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 | 1825.6345 |  | 1241.7934 | 1284.7411 | 1421.5316 | 117.2122 | 175.5582 | 222.269 | 260.1852 | 296.6549 | 328.2275 | 344.0671 | 367.4098 | 394.1146 | 421.3716 | 455.6573 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099 | 461.0099
55% | 8285.907 | 8537.7521 | 9561.6368 |  |  | 3.4714 | 49.8086 | 165.5048 | 303.2996 | 413.7128 | 721.1439 | 937.6016 | 1051.5091 | 1262.7459 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 | 1201.267 |  | 2020.1858 | 2090.0544 | 2312.5892 | 23.1943 | 88.6401 | 163.3146 | 224.9978 | 284.3278 | 335.6911 | 361.4593 | 399.4339 | 442.878 | 487.2206 | 542.9975 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052 | 551.7052
50% | 9747.9358 | 10044.2184 | 11248.7651 | [7 empty] | 22.6091 | 95.641 | 153.4846 | 294.6713 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 | 249.1281 |  | 3523.6644 | 3645.5311 | 4033.6826 |  |  | 9.7618 | 46.9146 | 107.2018 | 177.6453 | 219.0596 | 284.9847 | 360.7613 | 438.1048 | 535.3924 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807 | 550.5807
45% | FY25: 17342.4082; FY26: 17869.5202; FY27: 20012.5113 |  | 7020.6756 | 7263.4873 | 8036.8544 | [7 empty] | 4.8627 | 31.6552 | 82.2002 | 177.4776 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425 | 195.425
40% | FY25: 19856.1284; FY26: 20459.6435; FY27: 22913.2535 |  | 11955.7442 | 12369.2363 | 13686.2291
35% | FY25: 12043.5634; FY26: 12409.6202; FY27: 13897.8362 |  | 14474.4645 | 14975.0672 | 16569.5112
30% | FY25: 4991.361; FY26: 5143.0704; FY27: 5759.8499 |  | 22112.4023 | 22877.1648 | 25312.9708
25% | FY25: 2979.5232; FY26: 3070.084; FY27: 3438.2619 |  | 18803.7802 | 19454.1133 | 21525.4559
20% | FY25: 3169.6139; FY26: 3265.9524; FY27: 3657.6197 |  | 4988.3748 | 5160.8989 | 5710.3965
15% | FY25: 3283.2375; FY26: 3383.0295; FY27: 3788.7372 |  | 3091.1568 | 3198.0652 | 3538.5736
10% | FY25: 2189.0045; FY26: 2255.5379; FY27: 2526.0319 |  | 884.3992 | 914.9863 | 1012.4079
5% | FY25: 174.4742; FY26: 179.7772; FY27: 201.3369 |  | 0 | 0 | 0
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 99564.2165 | 102590.4109 | 114893.5021 | 1274.7059 | 1826.3571 | 2447.1212 | 2906.9819 | 3494.7464 | 4009.7471 | 4365.9923 | 5281.5172 | 5975.9501 | 6360.7964 | 7108.3964 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | 6886.3609 | E @ R (MWh) | 93455.9144 | 96688.1086 | 106982.8055 | 1165.0275 | 1445.7159 | 1702.472 | 1941.1838 | 2195.3401 | 2433.6207 | 2559.2366 | 2754.1117 | 2998.641 | 3271.4254 | 3646.2496 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389 | 3707.8389
Option 4 Summer POE50 W E @ R (MWh) N 2 | 69694.9516 | 71813.2876 | 80425.4515 | 892.2941 | 1278.45 | 1712.9848 | 2034.8873 | 2446.3225 | 2806.823 | 3056.1946 | 3697.062 | 4183.1651 | 4452.5575 | 4975.8775 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | 4820.4526 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 28036.7743 | 29006.4326 | 32094.8416 | 349.5083 | 433.7148 | 510.7416 | 582.3551 | 658.602 | 730.0862 | 767.771 | 826.2335 | 899.5923 | 981.4276 | 1093.8749 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517 | 1112.3517
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 44.7175 | 46.8571 | 53.2551 | 52.2115 | 42.2548 | 44.3553 | 46.7764 | 48.588 | 50.5852 | 51.632 | 52.5386 | 54.7829 | 53.4294 | 57.0894 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 | 61.8636 |  | 47.5947 | 49.8159 | 56.1642 | 55.3245 | 45.3779 | 47.7433 | 49.9928 | 51.9093 | 53.9055 | 54.7805 | 55.9747 | 58.1887 | 57.4648 | 60.3565 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245 | 62.0245
98% | 132.8043 | 139.1585 | 158.1595 | 155.0603 | 125.4905 | 131.7285 | 138.9189 | 144.299 | 150.2303 | 153.3391 | 156.0317 | 162.6971 | 158.6773 | 169.5469 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 | 183.7254 |  | 141.3491 | 147.9458 | 166.7992 | 164.3053 | 134.7656 | 141.7905 | 148.4711 | 154.1628 | 160.0913 | 162.6898 | 166.2364 | 172.8116 | 170.6617 | 179.2496 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033 | 184.2033
97% | 58.4249 | 61.2203 | 69.5795 | 68.216 | 55.2073 | 57.9516 | 61.1149 | 63.4818 | 66.0912 | 67.4588 | 68.6434 | 71.5757 | 69.8073 | 74.5892 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 | 80.8268 |  | 62.184 | 65.0861 | 73.3804 | 72.2832 | 59.2877 | 62.3782 | 65.3172 | 67.8212 | 70.4294 | 71.5725 | 73.1328 | 76.0254 | 75.0796 | 78.8577 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037 | 81.037
95% | 143.8152 | 150.6962 | 171.2726 | 167.9164 | 135.895 | 142.6501 | 150.4367 | 156.2629 | 162.686 | 166.0525 | 168.9684 | 176.1864 | 171.8333 | 183.6041 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 | 198.9582 |  | 153.0684 | 160.2121 | 180.6286 | 177.9279 | 145.939 | 153.5464 | 160.7809 | 166.9445 | 173.3646 | 176.1785 | 180.0192 | 187.1394 | 184.8113 | 194.1113 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757 | 199.4757
90% | 1468.8623 | 1539.1418 | 1749.2998 | 1715.0213 | 1387.9689 | 1456.9629 | 1536.4916 | 1595.9973 | 1661.5999 | 1695.9843 | 1725.7655 | 1799.4867 | 1755.0266 | 1875.2482 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 | 2032.0676 |  | 1563.3702 | 1636.3326 | 1844.8575 | 1817.2743 | 1490.5543 | 1568.2527 | 1642.1425 | 1705.0946 | 1770.6661 | 1799.4064 | 1838.6332 | 1911.3564 | 1887.5779 | 1982.5635 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532 | 2037.3532
85% | 3460.5527 | 3626.127 | 4121.2469 | 4040.4886 | 3269.9726 | 3432.5183 | 3619.8833 | 3760.0753 | 3914.6311 | 3995.6387 | 4065.8014 | 4239.4842 | 4134.7389 | 4417.9738 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 | 4787.431 |  | 3683.2076 | 3855.1027 | 4346.3751 | 4281.3908 | 3511.6578 | 3694.7107 | 3868.7905 | 4017.1021 | 4171.5846 | 4239.2951 | 4331.711 | 4503.0426 | 4447.0219 | 4670.8023 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836 | 4799.8836
80% | 6266.0722 | 6565.8799 | 7462.4007 | 7316.1705 | 5920.9861 | 6215.31 | 6554.5744 | 6808.422 | 7088.2784 | 7234.9601 | 7362.0047 | 7676.4946 | 7486.8308 | 7999.6882 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 | 8668.6697 |  | 6669.2367 | 6980.4895 | 7870.0435 | 7752.3754 | 6358.609 | 6690.0654 | 7005.2742 | 7273.8241 | 7553.5479 | 7676.1523 | 7843.491 | 8153.7236 | 8052.2861 | 8457.4884 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177 | 8691.2177
75% | 7325.96 | 7676.4794 | 8724.6441 | 8553.6795 | 6922.5037 | 7266.6116 | 7663.2616 | 7960.0468 | 8287.2401 | 8458.7326 | 8607.2663 | 8974.9514 | 8753.2065 | 9352.8122 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 | 10134.95 |  | 7797.3187 | 8161.2191 | 9201.2384 | 9063.6672 | 7434.1492 | 7821.6705 | 8190.196 | 8504.1703 | 8831.2085 | 8974.5511 | 9170.1947 | 9532.9023 | 9414.3069 | 9888.048 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119 | 10161.3119
70% | 8591.0842 | 9002.1349 | 10231.3077 | 10030.8191 | 8117.9547 | 8521.4868 | 8986.6346 | 9334.6717 | 9718.3682 | 9919.4758 | 10093.66 | 10524.8407 | 10264.8026 | 10967.9545 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 | 11885.1602 |  | 9143.842 | 9570.5845 | 10790.2054 | 10628.8769 | 8717.9566 | 9172.3991 | 9604.5655 | 9972.7602 | 10356.2749 | 10524.3713 | 10753.8008 | 11179.1445 | 11040.0688 | 11595.6205 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746 | 11916.0746
65% | 9414.2762 | 9864.7136 | 11211.6649 | 10991.9657 | 8895.8119 | 9338.0101 | 9847.728 | 10229.1139 | 10649.5759 | 10869.9535 | 11060.8279 | 11533.3241 | 11248.3693 | 12018.8968 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 | 13023.9885 |  | 10019.999 | 10487.6317 | 11824.1158 | 11647.329 | 9553.3055 | 10051.2924 | 10524.8687 | 10928.3436 | 11348.6063 | 11532.8097 | 11784.2229 | 12250.3228 | 12097.9209 | 12706.7053 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865 | 13057.865
60% | 10243.0861 | 10733.1789 | 12198.7125 | 11959.6714 | 9678.9774 | 10160.1056 | 10714.6979 | 11129.6601 | 11587.1385 | 11826.9176 | 12034.5961 | 12548.6897 | 12238.6482 | 13077.011 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 | 14170.5886 |  | 10902.1352 | 11410.9371 | 12865.0821 | 12672.7313 | 10394.3552 | 10936.1836 | 11451.4524 | 11890.4482 | 12347.7099 | 12548.1301 | 12821.6771 | 13328.8113 | 13162.9923 | 13825.3726 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475 | 14207.4475
55% | 10267.8043 | 10759.0798 | 12228.15 | 11988.5321 | 9702.3343 | 10184.6236 | 10740.5542 | 11156.5177 | 11615.1002 | 11855.4579 | 12063.6375 | 12578.9718 | 12268.182 | 13108.568 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 | 14204.7845 |  | 10928.4438 | 11438.4736 | 12896.1276 | 12703.3127 | 10419.4384 | 10962.5744 | 11479.0866 | 11919.1418 | 12377.5069 | 12578.4108 | 12852.6179 | 13360.9759 | 13194.7567 | 13858.7354 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324 | 14241.7324
50% | 12096.2046 | 12674.962 | 14405.6313 | 14123.3444 | 11430.0406 | 11998.2118 | 12653.1376 | 13143.1722 | 13683.415 | 13966.5735 | 14211.8239 | 14818.9244 | 14452.7919 | 15442.8264 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 | 16734.2475 |  | 12874.4849 | 13475.3363 | 15192.5565 | 14965.4068 | 12274.8403 | 12914.6931 | 13523.1813 | 14041.5977 | 14581.5844 | 14818.2634 | 15141.299 | 15740.1809 | 15544.3629 | 16326.5771 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748 | 16777.7748
45% | 15128.3079 | 15852.1399 | 18016.6286 | 17663.582 | 14295.1595 | 15005.7516 | 15824.8449 | 16437.7144 | 17113.3774 | 17467.5141 | 17774.2404 | 18533.5201 | 18075.6108 | 19313.813 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 | 20928.949 |  | 16101.6763 | 16853.1406 | 19000.809 | 18716.7206 | 15351.7215 | 16151.9634 | 16912.9787 | 17561.3443 | 18236.6871 | 18532.6935 | 18936.7029 | 19685.7039 | 19440.8011 | 20419.0896 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871 | 20983.3871
40% | 16018.9133 | 16785.3574 | 19077.2699 | 18703.4394 | 15136.7174 | 15889.1422 | 16756.4555 | 17405.4048 | 18120.8442 | 18495.8289 | 18820.6122 | 19624.5908 | 19139.7243 | 20450.8196 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 | 22161.0389 |  | 17049.5841 | 17845.2871 | 20119.3891 | 19818.5764 | 16255.4793 | 17102.8316 | 17908.648 | 18595.1829 | 19310.2833 | 19623.7155 | 20051.5091 | 20844.6039 | 20585.2836 | 21621.164 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818 | 22218.6818
35% | 6550.3318 | 6863.7403 | 7800.9317 | 7648.0678 | 6189.591 | 6497.2668 | 6851.922 | 7117.2854 | 7409.8374 | 7563.1733 | 7695.9812 | 8024.738 | 7826.4701 | 8362.5932 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 | 9061.923 |  | 6971.7859 | 7297.1587 | 8227.0671 | 8104.0611 | 6647.0666 | 6993.5594 | 7323.0677 | 7603.8004 | 7896.2137 | 8024.3801 | 8199.3101 | 8523.6164 | 8417.5772 | 8841.1615 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939 | 9085.4939
30% | 2020.5283 | 2117.2029 | 2406.2908 | 2359.1381 | 1909.2535 | 2004.1598 | 2113.5574 | 2195.4119 | 2285.6531 | 2332.9514 | 2373.9176 | 2475.3266 | 2414.1684 | 2579.542 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 | 2795.2587 |  | 2150.5309 | 2250.896 | 2537.7374 | 2499.7947 | 2050.3673 | 2157.2472 | 2258.888 | 2345.4833 | 2435.6817 | 2475.2162 | 2529.1754 | 2629.2116 | 2596.5025 | 2727.1622 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294 | 2802.5294
25% | 1487.2137 | 1558.3712 | 1771.1549 | 1736.4481 | 1405.3097 | 1475.1656 | 1555.6879 | 1615.9371 | 1682.3593 | 1717.1733 | 1747.3265 | 1821.9688 | 1776.9533 | 1898.6768 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 | 2057.4555 |  | 1582.9023 | 1656.7763 | 1867.9064 | 1839.9786 | 1509.1768 | 1587.8459 | 1662.6588 | 1726.3974 | 1792.7882 | 1821.8876 | 1861.6044 | 1935.2362 | 1911.1606 | 2007.3329 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071 | 2062.8071
20% | 1183.1045 | 1239.7116 | 1408.9847 | 1381.3748 | 1117.9484 | 1173.5201 | 1237.577 | 1285.5063 | 1338.3463 | 1366.0414 | 1390.0289 | 1449.4081 | 1413.5974 | 1510.4306 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 | 1636.7418 |  | 1259.2265 | 1317.9945 | 1485.9523 | 1463.7352 | 1200.5765 | 1263.1592 | 1322.6742 | 1373.3794 | 1426.1944 | 1449.3434 | 1480.9389 | 1539.5143 | 1520.3617 | 1596.8684 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992 | 1640.9992
15% | 928.0573 | 972.4613 | 1105.2435 | 1083.5856 | 876.9472 | 920.539 | 970.7869 | 1008.3838 | 1049.8329 | 1071.5577 | 1090.374 | 1136.9526 | 1108.8618 | 1184.8202 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 | 1283.902 |  | 987.7693 | 1033.8685 | 1165.6188 | 1148.1912 | 941.7628 | 990.8542 | 1037.5393 | 1077.3137 | 1118.7431 | 1136.9019 | 1161.6861 | 1207.6342 | 1192.6104 | 1252.6243 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415 | 1287.2415
10% | 651.6625 | 682.8421 | 776.079 | 760.8712 | 615.7741 | 646.3833 | 681.6663 | 708.0661 | 737.1708 | 752.4255 | 765.6379 | 798.3444 | 778.6197 | 831.9561 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 | 901.5292 |  | 693.591 | 725.9609 | 818.4732 | 806.2359 | 661.2862 | 695.7572 | 728.5385 | 756.4673 | 785.5581 | 798.3088 | 815.7118 | 847.9756 | 837.4262 | 879.5667 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742 | 903.8742
5% | 67.4134 | 70.6388 | 80.284 | 78.7108 | 63.7008 | 66.8672 | 70.5172 | 73.2482 | 76.259 | 77.8371 | 79.2039 | 82.5874 | 80.5469 | 86.0644 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 | 93.2616 |  | 71.7508 | 75.0994 | 84.6696 | 83.4037 | 68.4089 | 71.9749 | 75.366 | 78.2552 | 81.2646 | 82.5837 | 84.384 | 87.7216 | 86.6303 | 90.9897 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042 | 93.5042
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 113549.1973 | 118982.0949 | 135228.1917 | 132578.3147 | 107295.7995 | 112629.3218 | 118777.2255 | 123377.2667 | 128448.6202 | 131106.6792 | 133408.888 | 139107.8464 | 135670.8969 | 144964.5246 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | 157087.3211 | E @ R (MWh) | 120855.0513 | 126495.349 | 142615.1972 | 140482.9027 | 115226.0825 | 121232.4933 | 126944.4789 | 131810.9445 | 136879.8947 | 139101.6422 | 142134.0335 | 147755.843 | 145917.6654 | 153260.4473 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195 | 157495.9195
Option 5 Winter POE50 W E @ R (MWh) N 2 | 79484.4381 | 83287.4664 | 94659.7342 | 92804.8203 | 75107.0597 | 78840.5252 | 83144.0578 | 86364.0867 | 89914.0342 | 91774.6755 | 93386.2216 | 97375.4925 | 94969.6278 | 101475.1672 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | 109961.1248 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 36256.5154 | 37948.6047 | 42784.5592 | 42144.8708 | 34567.8247 | 36369.748 | 38083.3437 | 39543.2834 | 41063.9684 | 41730.4927 | 42640.21 | 44326.7529 | 43775.2996 | 45978.1342 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758 | 47248.7758
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 48.2179 | 49.8856 | 55.197 | 53.5195 | 44.8731 | 46.6868 | 48.1591 | 49.5752 | 50.8011 | 51.4162 | 52.3226 | 53.3595 | 54.4179 | 55.7491 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957 | 55.957
98% | 21.2169 | 21.8618 | 24.4836 | 23.6746 | 19.2684 | 20.1597 | 20.7257 | 21.3718 | 21.8881 | 22.2246 | 23.026 | 23.5802 | 23.8719 | 24.4128 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 | 24.2554 |  | 23.8667 | 24.6921 | 27.3211 | 26.4908 | 22.2111 | 23.1088 | 23.8375 | 24.5385 | 25.1453 | 25.4497 | 25.8983 | 26.4116 | 26.9355 | 27.5944 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973 | 27.6973
97% | 21.0015 | 21.6398 | 24.235 | 23.4342 | 19.0728 | 19.955 | 20.5153 | 21.1548 | 21.6659 | 21.999 | 22.7922 | 23.3408 | 23.6295 | 24.1649 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 | 24.0091 |  | 47.2487 | 48.8828 | 54.0875 | 52.4437 | 43.9711 | 45.7484 | 47.1911 | 48.5787 | 49.78 | 50.3827 | 51.2708 | 52.2869 | 53.324 | 54.6286 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322 | 54.8322
95% | 62.0353 | 63.9208 | 71.5864 | 69.221 | 56.3381 | 58.944 | 60.5989 | 62.4881 | 63.9977 | 64.9815 | 67.3246 | 68.9452 | 69.798 | 71.3795 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 | 70.9192 |  | 93.0436 | 96.2616 | 106.5109 | 103.2738 | 86.5893 | 90.0892 | 92.9301 | 95.6627 | 98.0283 | 99.2151 | 100.9641 | 102.965 | 105.0073 | 107.5762 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773 | 107.9773
90% | 139.4716 | 143.7108 | 160.9452 | 155.6271 | 126.663 | 132.5217 | 136.2424 | 140.4898 | 143.8837 | 146.0956 | 151.3636 | 155.0071 | 156.9244 | 160.48 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 | 159.4452 |  | 336.1928 | 347.8201 | 384.8537 | 373.1573 | 312.8714 | 325.5175 | 335.7827 | 345.6562 | 354.2039 | 358.4922 | 364.8118 | 372.0416 | 379.4209 | 388.7032 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523 | 390.1523
85% | 226.1702 | 233.0445 | 260.9922 | 252.3683 | 205.3994 | 214.9 | 220.9335 | 227.8213 | 233.325 | 236.9118 | 245.4544 | 251.3628 | 254.472 | 260.2379 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 | 258.5597 |  | 402.8257 | 416.7575 | 461.131 | 447.1164 | 374.882 | 390.0345 | 402.3342 | 414.1646 | 424.4065 | 429.5447 | 437.1168 | 445.7796 | 454.6215 | 465.7434 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797 | 467.4797
80% | 870.7553 | 897.2214 | 1004.8201 | 971.618 | 790.7877 | 827.3649 | 850.5941 | 877.1121 | 898.3012 | 912.1106 | 944.9995 | 967.7468 | 979.7172 | 1001.9158 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 | 995.455 |  | 459.7664 | 475.6675 | 526.3134 | 510.3178 | 427.8728 | 445.1672 | 459.2055 | 472.7082 | 484.3977 | 490.2622 | 498.9047 | 508.792 | 518.8838 | 531.5778 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596 | 533.5596
75% | 1318.7877 | 1358.8714 | 1521.8333 | 1471.5476 | 1197.6741 | 1253.0715 | 1288.253 | 1328.4153 | 1360.5069 | 1381.4216 | 1431.233 | 1465.6845 | 1483.8141 | 1517.4346 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 | 1507.6496 |  | 394.3451 | 407.9836 | 451.423 | 437.7034 | 366.9897 | 381.8233 | 393.864 | 405.4453 | 415.4716 | 420.5016 | 427.9143 | 436.3947 | 445.0505 | 455.9383 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381 | 457.6381
70% | 2014.5303 | 2075.7608 | 2324.6951 | 2247.8805 | 1829.5218 | 1914.1448 | 1967.8866 | 2029.237 | 2078.259 | 2110.2075 | 2186.2976 | 2238.9244 | 2266.6184 | 2317.9758 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 | 2303.0286 |  | 421.604 | 436.1853 | 482.6273 | 467.9594 | 392.3577 | 408.2166 | 421.0896 | 433.4715 | 444.1908 | 449.5685 | 457.4937 | 466.5603 | 475.8144 | 487.4548 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272 | 489.272
65% | 3678.4968 | 3790.3025 | 4244.8522 | 4104.5902 | 3340.6745 | 3495.1946 | 3593.3263 | 3705.351 | 3794.8643 | 3853.2017 | 3992.1409 | 4088.2364 | 4138.8052 | 4232.583 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 | 4205.2896 |  | 1112.1622 | 1150.6266 | 1273.1376 | 1234.4445 | 1035.0125 | 1076.8472 | 1110.8054 | 1143.468 | 1171.7447 | 1185.9308 | 1206.8367 | 1230.7538 | 1255.1655 | 1285.8721 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659 | 1290.6659
60% | 7148.594 | 7365.8712 | 8249.2187 | 7976.641 | 6492.0881 | 6792.3743 | 6983.0781 | 7200.781 | 7374.7363 | 7488.1062 | 7758.113 | 7944.8599 | 8043.1326 | 8225.3754 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 | 8172.3349 |  | 1241.7934 | 1284.7411 | 1421.5316 | 1378.3286 | 1155.6513 | 1202.3621 | 1240.2783 | 1276.748 | 1308.3206 | 1324.1602 | 1347.5029 | 1374.2077 | 1401.4647 | 1435.7504 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103 | 1441.103
55% | 8285.907 | 8537.7521 | 9561.6368 | 9245.6931 | 7524.9537 | 7873.0142 | 8094.0582 | 8346.3967 | 8548.0276 | 8679.4342 | 8992.3981 | 9208.8557 | 9322.7632 | 9534.0001 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 | 9472.5211 |  | 2020.1858 | 2090.0544 | 2312.5892 | 2242.3053 | 1880.0473 | 1956.0379 | 2017.7211 | 2077.051 | 2128.4143 | 2154.1826 | 2192.1571 | 2235.6013 | 2279.9439 | 2335.7207 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285 | 2344.4285
50% | 9747.9358 | 10044.2184 | 11248.7651 | 10877.0739 | 8852.7141 | 9262.189 | 9522.2358 | 9819.0988 | 10056.307 | 10210.9 | 10579.0856 | 10833.7367 | 10967.7429 | 11216.252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 | 11143.9252 |  | 3523.6644 | 3645.5311 | 4033.6826 | 3911.0915 | 3279.2309 | 3411.7758 | 3519.3654 | 3622.8503 | 3712.4396 | 3757.3853 | 3823.6215 | 3899.3981 | 3976.7417 | 4074.0293 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175 | 4089.2175
45% | 17342.4082 | 17869.5202 | 20012.5113 | 19351.241 | 15749.7325 | 16478.2232 | 16940.8686 | 17469.0133 | 17891.0269 | 18166.0609 | 18821.0945 | 19274.1404 | 19512.5489 | 19954.6677 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 | 19825.9922 |  | 7020.6756 | 7263.4873 | 8036.8544 | 7792.5993 | 6533.6576 | 6797.7448 | 7012.1102 | 7218.2973 | 7396.7981 | 7486.3496 | 7618.3211 | 7769.301 | 7923.4031 | 8117.2424 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041 | 8147.5041
40% | 19856.1284 | 20459.6435 | 22913.2535 | 22156.1345 | 18032.6001 | 18866.683 | 19396.3871 | 20001.0845 | 20484.2675 | 20799.1667 | 21549.145 | 22067.8584 | 22340.8233 | 22847.0257 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 | 22699.6992 |  | 11955.7442 | 12369.2363 | 13686.2291 | 13270.2789 | 11126.3848 | 11576.1078 | 11941.1578 | 12292.2807 | 12596.2558 | 12748.7561 | 12973.4947 | 13230.6035 | 13493.0291 | 13823.1246 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581 | 13874.6581
35% | 12043.5634 | 12409.6202 | 13897.8362 | 13438.6122 | 10937.518 | 11443.4238 | 11764.7113 | 12131.4852 | 12424.5557 | 12615.5551 | 13070.448 | 13385.0691 | 13550.6336 | 13857.6663 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 | 13768.3067 |  | 14474.4645 | 14975.0672 | 16569.5112 | 16065.9327 | 13470.3838 | 14014.85 | 14456.8052 | 14881.8993 | 15249.913 | 15434.5405 | 15706.6249 | 16017.8989 | 16335.6097 | 16735.2466 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367 | 16797.6367
30% | 4991.361 | 5143.0704 | 5759.8499 | 5569.5281 | 4532.9691 | 4742.6378 | 4875.7929 | 5027.7995 | 5149.2603 | 5228.4185 | 5416.9453 | 5547.3376 | 5615.9545 | 5743.2018 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 | 5706.1674 |  | 22112.4023 | 22877.1648 | 25312.9708 | 24543.6621 | 20578.4846 | 21410.2568 | 22085.4245 | 22734.8337 | 23297.0422 | 23579.0946 | 23994.7535 | 24470.2817 | 24955.6433 | 25566.162 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744 | 25661.4744
25% | 2979.5232 | 3070.084 | 3438.2619 | 3324.652 | 2705.8926 | 2831.0514 | 2910.5364 | 3001.2747 | 3073.779 | 3121.0314 | 3233.5698 | 3311.4056 | 3352.3656 | 3428.3241 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 | 3406.2169 |  | 18803.7802 | 19454.1133 | 21525.4559 | 20871.2569 | 17499.3787 | 18206.6949 | 18780.839 | 19333.0788 | 19811.1654 | 20051.0151 | 20404.48 | 20808.8561 | 21221.5944 | 21740.7627 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137 | 21821.8137
20% | 3169.6139 | 3265.9524 | 3657.6197 | 3536.7615 | 2878.5259 | 3011.6697 | 3096.2258 | 3192.7531 | 3269.8831 | 3320.1501 | 3439.8684 | 3522.6701 | 3566.2432 | 3647.0478 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 | 3623.5302 |  | 4988.3748 | 5160.8989 | 5710.3965 | 5536.8469 | 4642.3357 | 4829.9766 | 4982.2888 | 5128.7902 | 5255.6197 | 5319.2484 | 5413.0176 | 5520.2928 | 5629.7864 | 5767.5144 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016 | 5789.016
15% | 3283.2375 | 3383.0295 | 3788.7372 | 3663.5465 | 2981.7146 | 3119.6313 | 3207.2186 | 3307.2061 | 3387.1011 | 3439.1701 | 3563.18 | 3648.95 | 3694.0851 | 3777.7863 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 | 3753.4257 |  | 3091.1568 | 3198.0652 | 3538.5736 | 3431.0297 | 2876.726 | 2993.0019 | 3087.3855 | 3178.1683 | 3256.7611 | 3296.19 | 3354.2962 | 3420.7716 | 3488.6217 | 3573.9679 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919 | 3587.2919
10% | 2189.0045 | 2255.5379 | 2526.0319 | 2442.5647 | 1987.9728 | 2079.9248 | 2138.3211 | 2204.9849 | 2258.2526 | 2292.9681 | 2375.6482 | 2432.8328 | 2462.9254 | 2518.7308 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 | 2502.489 |  | 884.3992 | 914.9863 | 1012.4079 | 981.6389 | 823.0492 | 856.3164 | 883.3202 | 909.2937 | 931.7796 | 943.0604 | 959.685 | 978.704 | 998.1164 | 1022.5344 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465 | 1026.3465
5% | 174.4742 | 179.7772 | 201.3369 | 194.6841 | 158.451 | 165.78 | 170.4344 | 175.7479 | 179.9936 | 182.7606 | 189.3506 | 193.9084 | 196.307 | 200.7549 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 | 199.4604 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 99564.2165 | 102590.4109 | 114893.5021 | 111097.0942 | 90420.5322 | 94602.8585 | 97258.9442 | 100291.067 | 102713.8824 | 104292.876 | 108053.4783 | 110654.4531 | 112023.176 | 114561.4173 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | 113822.6805 | E @ R (MWh) | 93455.9144 | 96688.1086 | 106982.8055 | 103731.3972 | 86972.9605 | 90488.3647 | 93341.8953 | 96086.56 | 98462.6793 | 99654.7466 | 101411.4881 | 103421.2618 | 105472.5956 | 108052.8932 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217 | 108455.7217
Option 5 Summer POE50 W E @ R (MWh) N 2 | 69694.9516 | 71813.2876 | 80425.4515 | 77767.9659 | 63294.3726 | 66222.001 | 68081.261 | 70203.7469 | 71899.7177 | 73005.0132 | 75637.4348 | 77458.1171 | 78416.2232 | 80192.9921 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | 79675.8763 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 28036.7743 | 29006.4326 | 32094.8416 | 31119.4191 | 26091.8881 | 27146.5094 | 28002.5686 | 28825.968 | 29538.8038 | 29896.424 | 30423.4464 | 31026.3785 | 31641.7787 | 32415.8679 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165 | 32536.7165
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 44.7175 | 46.8571 | 53.2551 | 58.6433 | 61.5501 | 63.6505 | 66.0717 | 67.8832 | 69.8804 | 70.9272 | 71.8338 | 74.0782 | 72.7247 | 76.3846 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 |  | 47.5947 | 49.8159 | 56.1642 | 61.7562 | 64.6732 | 67.0386 | 69.2881 | 71.2045 | 73.2008 | 74.0757 | 75.27 | 77.4839 | 76.76 | 79.6517 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197
98% | 132.8043 | 139.1585 | 158.1595 | 174.1616 | 182.7945 | 189.0324 | 196.2229 | 201.603 | 207.5343 | 210.6431 | 213.3357 | 220.0011 | 215.9813 | 226.8509 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 |  | 141.3491 | 147.9458 | 166.7992 | 183.4066 | 192.0695 | 199.0945 | 205.7751 | 211.4668 | 217.3953 | 219.9938 | 223.5404 | 230.1155 | 227.9656 | 236.5536 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073
97% | 58.4249 | 61.2203 | 69.5795 | 76.6193 | 80.4172 | 83.1615 | 86.3248 | 88.6917 | 91.301 | 92.6687 | 93.8533 | 96.7856 | 95.0171 | 99.799 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 |  | 62.184 | 65.0861 | 73.3804 | 80.6865 | 84.4976 | 87.5881 | 90.5271 | 93.0311 | 95.6392 | 96.7824 | 98.3426 | 101.2353 | 100.2895 | 104.0676 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469
95% | 143.8152 | 150.6962 | 171.2726 | 188.6014 | 197.95 | 204.7052 | 212.4918 | 218.3179 | 224.741 | 228.1076 | 231.0234 | 238.2414 | 233.8884 | 245.6592 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 |  | 153.0684 | 160.2121 | 180.6286 | 198.6129 | 207.9941 | 215.6015 | 222.836 | 228.9996 | 235.4196 | 238.2336 | 242.0742 | 249.1945 | 246.8664 | 256.1663 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307
90% | 1468.8623 | 1539.1418 | 1749.2998 | 1926.2886 | 2021.7708 | 2090.7648 | 2170.2935 | 2229.7992 | 2295.4018 | 2329.7862 | 2359.5674 | 2433.2886 | 2388.8285 | 2509.0501 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 |  | 1563.3702 | 1636.3326 | 1844.8575 | 2028.5416 | 2124.3562 | 2202.0546 | 2275.9443 | 2338.8965 | 2404.468 | 2433.2083 | 2472.4351 | 2545.1583 | 2521.3798 | 2616.3654 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551
85% | 3460.5527 | 3626.127 | 4121.2469 | 4538.2219 | 4763.1724 | 4925.7181 | 5113.0831 | 5253.275 | 5407.8308 | 5488.8385 | 5559.0011 | 5732.684 | 5627.9387 | 5911.1735 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 |  | 3683.2076 | 3855.1027 | 4346.3751 | 4779.124 | 5004.8576 | 5187.9104 | 5361.9903 | 5510.3018 | 5664.7844 | 5732.4949 | 5824.9108 | 5996.2424 | 5940.2217 | 6164.002 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833
80% | 6266.0722 | 6565.8799 | 7462.4007 | 8217.4232 | 8624.7443 | 8919.0681 | 9258.3326 | 9512.1802 | 9792.0365 | 9938.7182 | 10065.7628 | 10380.2528 | 10190.5889 | 10703.4463 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 |  | 6669.2367 | 6980.4895 | 7870.0435 | 8653.6281 | 9062.3671 | 9393.8235 | 9709.0324 | 9977.5822 | 10257.306 | 10379.9104 | 10547.2492 | 10857.4818 | 10756.0442 | 11161.2466 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759
75% | 7325.96 | 7676.4794 | 8724.6441 | 9607.3764 | 10083.5947 | 10427.7025 | 10824.3526 | 11121.1378 | 11448.331 | 11619.8235 | 11768.3573 | 12136.0423 | 11914.2974 | 12513.9031 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 |  | 7797.3187 | 8161.2191 | 9201.2384 | 10117.3642 | 10595.2402 | 10982.7614 | 11351.2869 | 11665.2613 | 11992.2995 | 12135.6421 | 12331.2857 | 12693.9932 | 12575.3978 | 13049.139 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029
70% | 8591.0842 | 9002.1349 | 10231.3077 | 11266.4796 | 11824.9363 | 12228.4683 | 12693.6161 | 13041.6533 | 13425.3497 | 13626.4573 | 13800.6415 | 14231.8223 | 13971.7841 | 14674.936 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 |  | 9143.842 | 9570.5845 | 10790.2054 | 11864.5374 | 12424.9381 | 12879.3806 | 13311.547 | 13679.7417 | 14063.2564 | 14231.3528 | 14460.7823 | 14886.126 | 14747.0503 | 15302.602 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561
65% | 9414.2762 | 9864.7136 | 11211.6649 | 12346.0264 | 12957.9939 | 13400.1921 | 13909.9101 | 14291.296 | 14711.758 | 14932.1356 | 15123.0099 | 15595.5062 | 15310.5513 | 16081.0788 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 |  | 10019.999 | 10487.6317 | 11824.1158 | 13001.3897 | 13615.4876 | 14113.4744 | 14587.0508 | 14990.5257 | 15410.7884 | 15594.9918 | 15846.405 | 16312.5049 | 16160.103 | 16768.8874 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471
60% | 10243.0861 | 10733.1789 | 12198.7125 | 13432.9403 | 14098.784 | 14579.9123 | 15134.5046 | 15549.4667 | 16006.9451 | 16246.7243 | 16454.4027 | 16968.4964 | 16658.4548 | 17496.8177 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 |  | 10902.1352 | 11410.9371 | 12865.0821 | 14146.0002 | 14814.1618 | 15355.9902 | 15871.259 | 16310.2549 | 16767.5165 | 16967.9367 | 17241.4837 | 17748.6179 | 17582.7989 | 18245.1792 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542
55% | 10267.8043 | 10759.0798 | 12228.15 | 13465.3562 | 14132.8067 | 14615.096 | 15171.0266 | 15586.9901 | 16045.5725 | 16285.9303 | 16494.1099 | 17009.4441 | 16698.6544 | 17539.0404 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 |  | 10928.4438 | 11438.4736 | 12896.1276 | 14180.1368 | 14849.9108 | 15393.0467 | 15909.559 | 16349.6142 | 16807.9793 | 17008.8831 | 17283.0902 | 17791.4482 | 17625.2291 | 18289.2078 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048
50% | 12096.2046 | 12674.962 | 14405.6313 | 15863.1483 | 16649.4525 | 17217.6237 | 17872.5495 | 18362.5841 | 18902.8268 | 19185.9854 | 19431.2358 | 20038.3362 | 19672.2038 | 20662.2383 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 |  | 12874.4849 | 13475.3363 | 15192.5565 | 16705.2108 | 17494.2522 | 18134.105 | 18742.5932 | 19261.0096 | 19800.9963 | 20037.6753 | 20360.7109 | 20959.5927 | 20763.7748 | 21545.989 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867
45% | 15128.3079 | 15852.1399 | 18016.6286 | 19839.4951 | 20822.8988 | 21533.4909 | 22352.5842 | 22965.4537 | 23641.1167 | 23995.2534 | 24301.9797 | 25061.2593 | 24603.3501 | 25841.5522 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 |  | 16101.6763 | 16853.1406 | 19000.809 | 20892.6337 | 21879.4607 | 22679.7027 | 23440.718 | 24089.0836 | 24764.4264 | 25060.4327 | 25464.4422 | 26213.4432 | 25968.5404 | 26946.8289 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263
40% | 16018.9133 | 16785.3574 | 19077.2699 | 21007.4488 | 22048.7455 | 22801.1703 | 23668.4837 | 24317.4329 | 25032.8723 | 25407.8571 | 25732.6404 | 26536.6189 | 26051.7525 | 27362.8478 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 |  | 17049.5841 | 17845.2871 | 20119.3891 | 22122.5858 | 23167.5074 | 24014.8597 | 24820.6761 | 25507.211 | 26222.3114 | 26535.7437 | 26963.5372 | 27756.632 | 27497.3118 | 28533.1922 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099
35% | 6550.3318 | 6863.7403 | 7800.9317 | 8590.2057 | 9016.0048 | 9323.6807 | 9678.3358 | 9943.6992 | 10236.2512 | 10389.5871 | 10522.395 | 10851.1518 | 10652.8839 | 11189.007 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 |  | 6971.7859 | 7297.1587 | 8227.0671 | 9046.199 | 9473.4804 | 9819.9733 | 10149.4816 | 10430.2142 | 10722.6276 | 10850.7939 | 11025.724 | 11350.0303 | 11243.991 | 11667.5753 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077
30% | 2020.5283 | 2117.2029 | 2406.2908 | 2649.7518 | 2781.0947 | 2876.001 | 2985.3986 | 3067.2531 | 3157.4943 | 3204.7926 | 3245.7588 | 3347.1678 | 3286.0096 | 3451.3832 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 |  | 2150.5309 | 2250.896 | 2537.7374 | 2790.4084 | 2922.2085 | 3029.0884 | 3130.7292 | 3217.3245 | 3307.5229 | 3347.0574 | 3401.0166 | 3501.0528 | 3468.3437 | 3599.0034 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706
25% | 1487.2137 | 1558.3712 | 1771.1549 | 1950.3549 | 2047.03 | 2116.886 | 2197.4083 | 2257.6575 | 2324.0797 | 2358.8937 | 2389.0469 | 2463.6892 | 2418.6736 | 2540.3972 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 |  | 1582.9023 | 1656.7763 | 1867.9064 | 2053.8854 | 2150.8971 | 2229.5663 | 2304.3791 | 2368.1178 | 2434.5085 | 2463.6079 | 2503.3248 | 2576.9566 | 2552.881 | 2649.0533 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275
20% | 1183.1045 | 1239.7116 | 1408.9847 | 1551.5414 | 1628.4482 | 1684.0199 | 1748.0768 | 1796.006 | 1848.8461 | 1876.5412 | 1900.5286 | 1959.9079 | 1924.0972 | 2020.9304 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 |  | 1259.2265 | 1317.9945 | 1485.9523 | 1633.9018 | 1711.0763 | 1773.659 | 1833.1739 | 1883.8792 | 1936.6941 | 1959.8432 | 1991.4387 | 2050.014 | 2030.8615 | 2107.3682 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989
15% | 928.0573 | 972.4613 | 1105.2435 | 1217.0686 | 1277.3962 | 1320.988 | 1371.2359 | 1408.8329 | 1450.2819 | 1472.0067 | 1490.823 | 1537.4016 | 1509.3108 | 1585.2693 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 |  | 987.7693 | 1033.8685 | 1165.6188 | 1281.6742 | 1342.2118 | 1391.3032 | 1437.9883 | 1477.7628 | 1519.1922 | 1537.3509 | 1562.1352 | 1608.0832 | 1593.0594 | 1653.0733 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905
10% | 651.6625 | 682.8421 | 776.079 | 854.6002 | 896.961 | 927.5703 | 962.8533 | 989.2531 | 1018.3578 | 1033.6124 | 1046.8249 | 1079.5314 | 1059.8066 | 1113.1431 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 |  | 693.591 | 725.9609 | 818.4732 | 899.9649 | 942.4732 | 976.9442 | 1009.7254 | 1037.6542 | 1066.7451 | 1079.4958 | 1096.8988 | 1129.1625 | 1118.6132 | 1160.7536 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611
5% | 67.4134 | 70.6388 | 80.284 | 88.4069 | 92.7891 | 95.9555 | 99.6055 | 102.3365 | 105.3474 | 106.9254 | 108.2922 | 111.6757 | 109.6352 | 115.1527 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 |  | 71.7508 | 75.0994 | 84.6696 | 93.0998 | 97.4972 | 101.0632 | 104.4544 | 107.3435 | 110.3529 | 111.672 | 113.4723 | 116.8099 | 115.7186 | 120.078 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 113549.1973 | 118982.0949 | 135228.1917 | 148910.1601 | 156291.3357 | 161624.858 | 167772.7617 | 172372.8029 | 177444.1564 | 180102.2155 | 182404.4242 | 188103.3826 | 184666.4331 | 193960.0608 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | E @ R (MWh) | 120855.0513 | 126495.349 | 142615.1972 | 156814.7481 | 164221.6187 | 170228.0295 | 175940.0151 | 180806.4807 | 185875.4309 | 188097.1784 | 191129.5697 | 196751.3792 | 194913.2016 | 202255.9836 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557
Option 6 Winter POE50 W E @ R (MWh) N 2 | 79484.4381 | 83287.4664 | 94659.7342 | 104237.112 | 109403.935 | 113137.4006 | 117440.9332 | 120660.962 | 124210.9095 | 126071.5508 | 127683.0969 | 131672.3678 | 129266.5031 | 135772.0426 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 36256.5154 | 37948.6047 | 42784.5592 | 47044.4244 | 49266.4856 | 51068.4088 | 52782.0045 | 54241.9442 | 55762.6293 | 56429.1535 | 57338.8709 | 59025.4138 | 58473.9605 | 60676.7951 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 48.2179 | 49.8856 | 55.197 | 58.9755 | 61.241 | 63.0547 | 64.527 | 65.9431 | 67.169 | 67.7841 | 68.6904 | 69.7274 | 70.7857 | 72.117 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249
98% | 21.2169 | 21.8618 | 24.4836 | 26.3751 | 27.3701 | 28.2614 | 28.8274 | 29.4735 | 29.9898 | 30.3263 | 31.1277 | 31.6819 | 31.9736 | 32.5145 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 |  | 23.8667 | 24.6921 | 27.3211 | 29.1914 | 30.3128 | 31.2105 | 31.9392 | 32.6402 | 33.247 | 33.5514 | 34 | 34.5133 | 35.0372 | 35.6961 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799
97% | 21.0015 | 21.6398 | 24.235 | 26.1073 | 27.0922 | 27.9744 | 28.5347 | 29.1743 | 29.6853 | 30.0184 | 30.8116 | 31.3603 | 31.649 | 32.1844 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 |  | 47.2487 | 48.8828 | 54.0875 | 57.79 | 60.01 | 61.7873 | 63.23 | 64.6176 | 65.8189 | 66.4216 | 67.3097 | 68.3258 | 69.3629 | 70.6674 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711
95% | 62.0353 | 63.9208 | 71.5864 | 77.1171 | 80.0263 | 82.6322 | 84.2871 | 86.1763 | 87.6859 | 88.6697 | 91.0129 | 92.6334 | 93.4862 | 95.0677 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 |  | 93.0436 | 96.2616 | 106.5109 | 113.8019 | 118.1736 | 121.6735 | 124.5144 | 127.247 | 129.6126 | 130.7994 | 132.5484 | 134.5493 | 136.5916 | 139.1605 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616
90% | 139.4716 | 143.7108 | 160.9452 | 173.3796 | 179.9203 | 185.779 | 189.4997 | 193.7472 | 197.1411 | 199.353 | 204.6209 | 208.2644 | 210.1817 | 213.7374 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 |  | 336.1928 | 347.8201 | 384.8537 | 411.1982 | 426.9943 | 439.6404 | 449.9056 | 459.7791 | 468.3268 | 472.615 | 478.9346 | 486.1645 | 493.5438 | 502.826 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752
85% | 226.1702 | 233.0445 | 260.9922 | 281.1561 | 291.7627 | 301.2632 | 307.2968 | 314.1846 | 319.6883 | 323.2751 | 331.8177 | 337.7261 | 340.8353 | 346.6011 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 |  | 402.8257 | 416.7575 | 461.131 | 492.697 | 511.6238 | 526.7764 | 539.076 | 550.9064 | 561.1483 | 566.2865 | 573.8586 | 582.5214 | 591.3633 | 602.4853 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216
80% | 870.7553 | 897.2214 | 1004.8201 | 1082.4508 | 1123.2863 | 1159.8635 | 1183.0927 | 1209.6107 | 1230.7998 | 1244.6091 | 1277.4981 | 1300.2454 | 1312.2158 | 1334.4144 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 |  | 459.7664 | 475.6675 | 526.3134 | 562.3413 | 583.9436 | 601.238 | 615.2763 | 628.7789 | 640.4685 | 646.333 | 654.9755 | 664.8628 | 674.9545 | 687.6486 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303
75% | 1318.7877 | 1358.8714 | 1521.8333 | 1639.4076 | 1701.2542 | 1756.6516 | 1791.8331 | 1831.9954 | 1864.087 | 1885.0017 | 1934.8132 | 1969.2646 | 1987.3942 | 2021.0147 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 |  | 394.3451 | 407.9836 | 451.423 | 482.3244 | 500.8528 | 515.6864 | 527.7271 | 539.3084 | 549.3346 | 554.3647 | 561.7774 | 570.2578 | 578.9136 | 589.8014 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011
70% | 2014.5303 | 2075.7608 | 2324.6951 | 2504.2972 | 2598.7718 | 2683.3948 | 2737.1366 | 2798.487 | 2847.509 | 2879.4575 | 2955.5476 | 3008.1743 | 3035.8684 | 3087.2258 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 |  | 421.604 | 436.1853 | 482.6273 | 515.6648 | 535.474 | 551.3329 | 564.2059 | 576.5878 | 587.3071 | 592.6848 | 600.6099 | 609.6765 | 618.9306 | 630.571 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883
65% | 3678.4968 | 3790.3025 | 4244.8522 | 4572.8025 | 4745.3114 | 4899.8315 | 4997.9632 | 5109.9879 | 5199.5012 | 5257.8386 | 5396.7777 | 5492.8733 | 5543.4421 | 5637.2199 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 |  | 1112.1622 | 1150.6266 | 1273.1376 | 1360.2882 | 1412.5434 | 1454.3781 | 1488.3362 | 1520.9988 | 1549.2756 | 1563.4617 | 1584.3676 | 1608.2847 | 1632.6964 | 1663.4029 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967
60% | 7148.594 | 7365.8712 | 8249.2187 | 8886.5398 | 9221.7843 | 9522.0704 | 9712.7743 | 9930.4771 | 10104.4324 | 10217.8023 | 10487.8092 | 10674.5561 | 10772.8288 | 10955.0715 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 |  | 1241.7934 | 1284.7411 | 1421.5316 | 1518.8403 | 1577.1863 | 1623.8971 | 1661.8133 | 1698.283 | 1729.8556 | 1745.6952 | 1769.0379 | 1795.7427 | 1822.9997 | 1857.2854 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638
55% | 8285.907 | 8537.7521 | 9561.6368 | 10300.3531 | 10688.9337 | 11036.9942 | 11258.0382 | 11510.3768 | 11712.0077 | 11843.4143 | 12156.3781 | 12372.8358 | 12486.7433 | 12697.9801 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 |  | 2020.1858 | 2090.0544 | 2312.5892 | 2470.8938 | 2565.8128 | 2641.8033 | 2703.4866 | 2762.8165 | 2814.1798 | 2839.948 | 2877.9226 | 2921.3668 | 2965.7093 | 3021.4862 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194
50% | 9747.9358 | 10044.2184 | 11248.7651 | 12117.8262 | 12574.971 | 12984.4459 | 13244.4926 | 13541.3557 | 13778.5639 | 13933.1569 | 14301.3425 | 14555.9936 | 14689.9998 | 14938.5089 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 |  | 3523.6644 | 3645.5311 | 4033.6826 | 4309.8019 | 4475.3622 | 4607.9071 | 4715.4967 | 4818.9816 | 4908.5708 | 4953.5166 | 5019.7528 | 5095.5294 | 5172.8729 | 5270.1605 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488
45% | 17342.4082 | 17869.5202 | 20012.5113 | 21558.6451 | 22371.9445 | 23100.4353 | 23563.0806 | 24091.2253 | 24513.2389 | 24788.273 | 25443.3065 | 25896.3525 | 26134.7609 | 26576.8798 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 |  | 7020.6756 | 7263.4873 | 8036.8544 | 8587.0043 | 8916.8725 | 9180.9598 | 9395.3251 | 9601.5122 | 9780.0131 | 9869.5646 | 10001.536 | 10152.516 | 10306.618 | 10500.4574 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719
40% | 19856.1284 | 20459.6435 | 22913.2535 | 24683.4938 | 25614.6782 | 26448.7611 | 26978.4652 | 27583.1626 | 28066.3455 | 28381.2448 | 29131.2231 | 29649.9365 | 29922.9014 | 30429.1038 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 |  | 11955.7442 | 12369.2363 | 13686.2291 | 14623.0978 | 15184.8415 | 15634.5645 | 15999.6145 | 16350.7374 | 16654.7125 | 16807.2128 | 17031.9514 | 17289.0602 | 17551.4858 | 17881.5813 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149
35% | 12043.5634 | 12409.6202 | 13897.8362 | 14971.5602 | 15536.362 | 16042.2678 | 16363.5553 | 16730.3293 | 17023.3997 | 17214.3992 | 17669.292 | 17983.9131 | 18149.4777 | 18456.5104 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 |  | 14474.4645 | 14975.0672 | 16569.5112 | 17703.7504 | 18383.8369 | 18928.3031 | 19370.2583 | 19795.3524 | 20163.3661 | 20347.9936 | 20620.078 | 20931.352 | 21249.0628 | 21648.6997 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898
30% | 4991.361 | 5143.0704 | 5759.8499 | 6204.8465 | 6438.9242 | 6648.5929 | 6781.748 | 6933.7546 | 7055.2154 | 7134.3736 | 7322.9004 | 7453.2927 | 7521.9096 | 7649.1569 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 |  | 22112.4023 | 22877.1648 | 25312.9708 | 27045.7294 | 28084.6864 | 28916.4586 | 29591.6263 | 30241.0355 | 30803.244 | 31085.2964 | 31500.9553 | 31976.4835 | 32461.8451 | 33072.3638 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762
25% | 2979.5232 | 3070.084 | 3438.2619 | 3703.8964 | 3843.6258 | 3968.7846 | 4048.2697 | 4139.0079 | 4211.5122 | 4258.7646 | 4371.3031 | 4449.1389 | 4490.0988 | 4566.0573 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 |  | 18803.7802 | 19454.1133 | 21525.4559 | 22998.9462 | 23882.4467 | 24589.763 | 25163.9071 | 25716.1468 | 26194.2335 | 26434.0832 | 26787.548 | 27191.9242 | 27604.6624 | 28123.8307 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818
20% | 3169.6139 | 3265.9524 | 3657.6197 | 3940.2014 | 4088.8454 | 4221.9892 | 4306.5453 | 4403.0726 | 4480.2026 | 4530.4696 | 4650.1879 | 4732.9896 | 4776.5627 | 4857.3673 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 |  | 4988.3748 | 5160.8989 | 5710.3965 | 6101.2925 | 6335.6726 | 6523.3135 | 6675.6258 | 6822.1271 | 6948.9567 | 7012.5854 | 7106.3546 | 7213.6298 | 7323.1233 | 7460.8513 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353
15% | 3283.2375 | 3383.0295 | 3788.7372 | 4081.4488 | 4235.4214 | 4373.3381 | 4460.9254 | 4560.9129 | 4640.8079 | 4692.8769 | 4816.8868 | 4902.6568 | 4947.7919 | 5031.4931 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 |  | 3091.1568 | 3198.0652 | 3538.5736 | 3780.8009 | 3926.0397 | 4042.3156 | 4136.6992 | 4227.482 | 4306.0748 | 4345.5037 | 4403.6099 | 4470.0853 | 4537.9355 | 4623.2816 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056
10% | 2189.0045 | 2255.5379 | 2526.0319 | 2721.189 | 2823.8458 | 2915.7978 | 2974.1942 | 3040.858 | 3094.1256 | 3128.8412 | 3211.5212 | 3268.7059 | 3298.7984 | 3354.6038 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 |  | 884.3992 | 914.9863 | 1012.4079 | 1081.7106 | 1123.2644 | 1156.5316 | 1183.5353 | 1209.5089 | 1231.9947 | 1243.2756 | 1259.9001 | 1278.9192 | 1298.3315 | 1322.7496 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617
5% | 174.4742 | 179.7772 | 201.3369 | 216.8918 | 225.0741 | 232.4031 | 237.0575 | 242.371 | 246.6167 | 249.3836 | 255.9736 | 260.5315 | 262.9301 | 267.378 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 99564.2165 | 102590.4109 | 114893.5021 | 123769.9854 | 128439.2058 | 132621.532 | 135277.6178 | 138309.7405 | 140732.5559 | 142311.5495 | 146072.1518 | 148673.1266 | 150041.8495 | 152580.0908 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | E @ R (MWh) | 93455.9144 | 96688.1086 | 106982.8055 | 114306.1407 | 118697.1912 | 122212.5953 | 125066.1259 | 127810.7907 | 130186.91 | 131378.9772 | 133135.7188 | 135145.4924 | 137196.8262 | 139777.1238 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523
Option 6 Summer POE50 W E @ R (MWh) N 2 | 69694.9516 | 71813.2876 | 80425.4515 | 86638.9898 | 89907.444 | 92835.0724 | 94694.3324 | 96816.8184 | 98512.7891 | 99618.0846 | 102250.5063 | 104071.1886 | 105029.2947 | 106806.0636 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 28036.7743 | 29006.4326 | 32094.8416 | 34291.8422 | 35609.1573 | 36663.7786 | 37519.8378 | 38343.2372 | 39056.073 | 39413.6932 | 39940.7156 | 40543.6477 | 41159.0479 | 41933.1371 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 44.7175 | 46.8571 | 53.2551 | 58.6433 | 61.5501 | 63.6505 | 66.0717 | 67.8832 | 69.8804 | 70.9272 | 71.8338 | 74.0782 | 72.7247 | 76.3846 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 |  | 47.5947 | 49.8159 | 56.1642 | 61.7562 | 64.6732 | 67.0386 | 69.2881 | 71.2045 | 73.2008 | 74.0757 | 75.27 | 77.4839 | 76.76 | 79.6517 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197
98% | 132.8043 | 139.1585 | 158.1595 | 174.1616 | 182.7945 | 189.0324 | 196.2229 | 201.603 | 207.5343 | 210.6431 | 213.3357 | 220.0011 | 215.9813 | 226.8509 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 |  | 141.3491 | 147.9458 | 166.7992 | 183.4066 | 192.0695 | 199.0945 | 205.7751 | 211.4668 | 217.3953 | 219.9938 | 223.5404 | 230.1155 | 227.9656 | 236.5536 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073
97% | 58.4249 | 61.2203 | 69.5795 | 76.6193 | 80.4172 | 83.1615 | 86.3248 | 88.6917 | 91.301 | 92.6687 | 93.8533 | 96.7856 | 95.0171 | 99.799 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 |  | 62.184 | 65.0861 | 73.3804 | 80.6865 | 84.4976 | 87.5881 | 90.5271 | 93.0311 | 95.6392 | 96.7824 | 98.3426 | 101.2353 | 100.2895 | 104.0676 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469
95% | 143.8152 | 150.6962 | 171.2726 | 188.6014 | 197.95 | 204.7052 | 212.4918 | 218.3179 | 224.741 | 228.1076 | 231.0234 | 238.2414 | 233.8884 | 245.6592 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 |  | 153.0684 | 160.2121 | 180.6286 | 198.6129 | 207.9941 | 215.6015 | 222.836 | 228.9996 | 235.4196 | 238.2336 | 242.0742 | 249.1945 | 246.8664 | 256.1663 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307
90% | 1468.8623 | 1539.1418 | 1749.2998 | 1926.2886 | 2021.7708 | 2090.7648 | 2170.2935 | 2229.7992 | 2295.4018 | 2329.7862 | 2359.5674 | 2433.2886 | 2388.8285 | 2509.0501 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 |  | 1563.3702 | 1636.3326 | 1844.8575 | 2028.5416 | 2124.3562 | 2202.0546 | 2275.9443 | 2338.8965 | 2404.468 | 2433.2083 | 2472.4351 | 2545.1583 | 2521.3798 | 2616.3654 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551
85% | 3460.5527 | 3626.127 | 4121.2469 | 4538.2219 | 4763.1724 | 4925.7181 | 5113.0831 | 5253.275 | 5407.8308 | 5488.8385 | 5559.0011 | 5732.684 | 5627.9387 | 5911.1735 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 |  | 3683.2076 | 3855.1027 | 4346.3751 | 4779.124 | 5004.8576 | 5187.9104 | 5361.9903 | 5510.3018 | 5664.7844 | 5732.4949 | 5824.9108 | 5996.2424 | 5940.2217 | 6164.002 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833
80% | 6266.0722 | 6565.8799 | 7462.4007 | 8217.4232 | 8624.7443 | 8919.0681 | 9258.3326 | 9512.1802 | 9792.0365 | 9938.7182 | 10065.7628 | 10380.2528 | 10190.5889 | 10703.4463 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 |  | 6669.2367 | 6980.4895 | 7870.0435 | 8653.6281 | 9062.3671 | 9393.8235 | 9709.0324 | 9977.5822 | 10257.306 | 10379.9104 | 10547.2492 | 10857.4818 | 10756.0442 | 11161.2466 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759
75% | 7325.96 | 7676.4794 | 8724.6441 | 9607.3764 | 10083.5947 | 10427.7025 | 10824.3526 | 11121.1378 | 11448.331 | 11619.8235 | 11768.3573 | 12136.0423 | 11914.2974 | 12513.9031 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 |  | 7797.3187 | 8161.2191 | 9201.2384 | 10117.3642 | 10595.2402 | 10982.7614 | 11351.2869 | 11665.2613 | 11992.2995 | 12135.6421 | 12331.2857 | 12693.9932 | 12575.3978 | 13049.139 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029
70% | 8591.0842 | 9002.1349 | 10231.3077 | 11266.4796 | 11824.9363 | 12228.4683 | 12693.6161 | 13041.6533 | 13425.3497 | 13626.4573 | 13800.6415 | 14231.8223 | 13971.7841 | 14674.936 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 |  | 9143.842 | 9570.5845 | 10790.2054 | 11864.5374 | 12424.9381 | 12879.3806 | 13311.547 | 13679.7417 | 14063.2564 | 14231.3528 | 14460.7823 | 14886.126 | 14747.0503 | 15302.602 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561
65% | 9414.2762 | 9864.7136 | 11211.6649 | 12346.0264 | 12957.9939 | 13400.1921 | 13909.9101 | 14291.296 | 14711.758 | 14932.1356 | 15123.0099 | 15595.5062 | 15310.5513 | 16081.0788 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 |  | 10019.999 | 10487.6317 | 11824.1158 | 13001.3897 | 13615.4876 | 14113.4744 | 14587.0508 | 14990.5257 | 15410.7884 | 15594.9918 | 15846.405 | 16312.5049 | 16160.103 | 16768.8874 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471
60% | 10243.0861 | 10733.1789 | 12198.7125 | 13432.9403 | 14098.784 | 14579.9123 | 15134.5046 | 15549.4667 | 16006.9451 | 16246.7243 | 16454.4027 | 16968.4964 | 16658.4548 | 17496.8177 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 |  | 10902.1352 | 11410.9371 | 12865.0821 | 14146.0002 | 14814.1618 | 15355.9902 | 15871.259 | 16310.2549 | 16767.5165 | 16967.9367 | 17241.4837 | 17748.6179 | 17582.7989 | 18245.1792 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542
55% | 10267.8043 | 10759.0798 | 12228.15 | 13465.3562 | 14132.8067 | 14615.096 | 15171.0266 | 15586.9901 | 16045.5725 | 16285.9303 | 16494.1099 | 17009.4441 | 16698.6544 | 17539.0404 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 |  | 10928.4438 | 11438.4736 | 12896.1276 | 14180.1368 | 14849.9108 | 15393.0467 | 15909.559 | 16349.6142 | 16807.9793 | 17008.8831 | 17283.0902 | 17791.4482 | 17625.2291 | 18289.2078 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048
50% | 12096.2046 | 12674.962 | 14405.6313 | 15863.1483 | 16649.4525 | 17217.6237 | 17872.5495 | 18362.5841 | 18902.8268 | 19185.9854 | 19431.2358 | 20038.3362 | 19672.2038 | 20662.2383 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 |  | 12874.4849 | 13475.3363 | 15192.5565 | 16705.2108 | 17494.2522 | 18134.105 | 18742.5932 | 19261.0096 | 19800.9963 | 20037.6753 | 20360.7109 | 20959.5927 | 20763.7748 | 21545.989 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867
45% | 15128.3079 | 15852.1399 | 18016.6286 | 19839.4951 | 20822.8988 | 21533.4909 | 22352.5842 | 22965.4537 | 23641.1167 | 23995.2534 | 24301.9797 | 25061.2593 | 24603.3501 | 25841.5522 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 |  | 16101.6763 | 16853.1406 | 19000.809 | 20892.6337 | 21879.4607 | 22679.7027 | 23440.718 | 24089.0836 | 24764.4264 | 25060.4327 | 25464.4422 | 26213.4432 | 25968.5404 | 26946.8289 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263
40% | 16018.9133 | 16785.3574 | 19077.2699 | 21007.4488 | 22048.7455 | 22801.1703 | 23668.4837 | 24317.4329 | 25032.8723 | 25407.8571 | 25732.6404 | 26536.6189 | 26051.7525 | 27362.8478 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 |  | 17049.5841 | 17845.2871 | 20119.3891 | 22122.5858 | 23167.5074 | 24014.8597 | 24820.6761 | 25507.211 | 26222.3114 | 26535.7437 | 26963.5372 | 27756.632 | 27497.3118 | 28533.1922 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099
35% | 6550.3318 | 6863.7403 | 7800.9317 | 8590.2057 | 9016.0048 | 9323.6807 | 9678.3358 | 9943.6992 | 10236.2512 | 10389.5871 | 10522.395 | 10851.1518 | 10652.8839 | 11189.007 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 |  | 6971.7859 | 7297.1587 | 8227.0671 | 9046.199 | 9473.4804 | 9819.9733 | 10149.4816 | 10430.2142 | 10722.6276 | 10850.7939 | 11025.724 | 11350.0303 | 11243.991 | 11667.5753 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077
30% | 2020.5283 | 2117.2029 | 2406.2908 | 2649.7518 | 2781.0947 | 2876.001 | 2985.3986 | 3067.2531 | 3157.4943 | 3204.7926 | 3245.7588 | 3347.1678 | 3286.0096 | 3451.3832 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 |  | 2150.5309 | 2250.896 | 2537.7374 | 2790.4084 | 2922.2085 | 3029.0884 | 3130.7292 | 3217.3245 | 3307.5229 | 3347.0574 | 3401.0166 | 3501.0528 | 3468.3437 | 3599.0034 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706
25% | 1487.2137 | 1558.3712 | 1771.1549 | 1950.3549 | 2047.03 | 2116.886 | 2197.4083 | 2257.6575 | 2324.0797 | 2358.8937 | 2389.0469 | 2463.6892 | 2418.6736 | 2540.3972 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 |  | 1582.9023 | 1656.7763 | 1867.9064 | 2053.8854 | 2150.8971 | 2229.5663 | 2304.3791 | 2368.1178 | 2434.5085 | 2463.6079 | 2503.3248 | 2576.9566 | 2552.881 | 2649.0533 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275
20% | 1183.1045 | 1239.7116 | 1408.9847 | 1551.5414 | 1628.4482 | 1684.0199 | 1748.0768 | 1796.006 | 1848.8461 | 1876.5412 | 1900.5286 | 1959.9079 | 1924.0972 | 2020.9304 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 |  | 1259.2265 | 1317.9945 | 1485.9523 | 1633.9018 | 1711.0763 | 1773.659 | 1833.1739 | 1883.8792 | 1936.6941 | 1959.8432 | 1991.4387 | 2050.014 | 2030.8615 | 2107.3682 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989
15% | 928.0573 | 972.4613 | 1105.2435 | 1217.0686 | 1277.3962 | 1320.988 | 1371.2359 | 1408.8329 | 1450.2819 | 1472.0067 | 1490.823 | 1537.4016 | 1509.3108 | 1585.2693 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 |  | 987.7693 | 1033.8685 | 1165.6188 | 1281.6742 | 1342.2118 | 1391.3032 | 1437.9883 | 1477.7628 | 1519.1922 | 1537.3509 | 1562.1352 | 1608.0832 | 1593.0594 | 1653.0733 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905
10% | 651.6625 | 682.8421 | 776.079 | 854.6002 | 896.961 | 927.5703 | 962.8533 | 989.2531 | 1018.3578 | 1033.6124 | 1046.8249 | 1079.5314 | 1059.8066 | 1113.1431 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 |  | 693.591 | 725.9609 | 818.4732 | 899.9649 | 942.4732 | 976.9442 | 1009.7254 | 1037.6542 | 1066.7451 | 1079.4958 | 1096.8988 | 1129.1625 | 1118.6132 | 1160.7536 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611
5% | 67.4134 | 70.6388 | 80.284 | 88.4069 | 92.7891 | 95.9555 | 99.6055 | 102.3365 | 105.3474 | 106.9254 | 108.2922 | 111.6757 | 109.6352 | 115.1527 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 |  | 71.7508 | 75.0994 | 84.6696 | 93.0998 | 97.4972 | 101.0632 | 104.4544 | 107.3435 | 110.3529 | 111.672 | 113.4723 | 116.8099 | 115.7186 | 120.078 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 113549.1973 | 118982.0949 | 135228.1917 | 148910.1601 | 156291.3357 | 161624.858 | 167772.7617 | 172372.8029 | 177444.1564 | 180102.2155 | 182404.4242 | 188103.3826 | 184666.4331 | 193960.0608 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | E @ R (MWh) | 120855.0513 | 126495.349 | 142615.1972 | 156814.7481 | 164221.6187 | 170228.0295 | 175940.0151 | 180806.4807 | 185875.4309 | 188097.1784 | 191129.5697 | 196751.3792 | 194913.2016 | 202255.9836 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557
Option 7 Winter POE50 W E @ R (MWh) N 2 | 79484.4381 | 83287.4664 | 94659.7342 | 104237.112 | 109403.935 | 113137.4006 | 117440.9332 | 120660.962 | 124210.9095 | 126071.5508 | 127683.0969 | 131672.3678 | 129266.5031 | 135772.0426 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 36256.5154 | 37948.6047 | 42784.5592 | 47044.4244 | 49266.4856 | 51068.4088 | 52782.0045 | 54241.9442 | 55762.6293 | 56429.1535 | 57338.8709 | 59025.4138 | 58473.9605 | 60676.7951 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 48.2179 | 49.8856 | 55.197 | 58.9755 | 61.241 | 63.0547 | 64.527 | 65.9431 | 67.169 | 67.7841 | 68.6904 | 69.7274 | 70.7857 | 72.117 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249
98% | 21.2169 | 21.8618 | 24.4836 | 26.3751 | 27.3701 | 28.2614 | 28.8274 | 29.4735 | 29.9898 | 30.3263 | 31.1277 | 31.6819 | 31.9736 | 32.5145 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 |  | 23.8667 | 24.6921 | 27.3211 | 29.1914 | 30.3128 | 31.2105 | 31.9392 | 32.6402 | 33.247 | 33.5514 | 34 | 34.5133 | 35.0372 | 35.6961 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799
97% | 21.0015 | 21.6398 | 24.235 | 26.1073 | 27.0922 | 27.9744 | 28.5347 | 29.1743 | 29.6853 | 30.0184 | 30.8116 | 31.3603 | 31.649 | 32.1844 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 |  | 47.2487 | 48.8828 | 54.0875 | 57.79 | 60.01 | 61.7873 | 63.23 | 64.6176 | 65.8189 | 66.4216 | 67.3097 | 68.3258 | 69.3629 | 70.6674 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711
95% | 62.0353 | 63.9208 | 71.5864 | 77.1171 | 80.0263 | 82.6322 | 84.2871 | 86.1763 | 87.6859 | 88.6697 | 91.0129 | 92.6334 | 93.4862 | 95.0677 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 |  | 93.0436 | 96.2616 | 106.5109 | 113.8019 | 118.1736 | 121.6735 | 124.5144 | 127.247 | 129.6126 | 130.7994 | 132.5484 | 134.5493 | 136.5916 | 139.1605 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616
90% | 139.4716 | 143.7108 | 160.9452 | 173.3796 | 179.9203 | 185.779 | 189.4997 | 193.7472 | 197.1411 | 199.353 | 204.6209 | 208.2644 | 210.1817 | 213.7374 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 |  | 336.1928 | 347.8201 | 384.8537 | 411.1982 | 426.9943 | 439.6404 | 449.9056 | 459.7791 | 468.3268 | 472.615 | 478.9346 | 486.1645 | 493.5438 | 502.826 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752
85% | 226.1702 | 233.0445 | 260.9922 | 281.1561 | 291.7627 | 301.2632 | 307.2968 | 314.1846 | 319.6883 | 323.2751 | 331.8177 | 337.7261 | 340.8353 | 346.6011 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 |  | 402.8257 | 416.7575 | 461.131 | 492.697 | 511.6238 | 526.7764 | 539.076 | 550.9064 | 561.1483 | 566.2865 | 573.8586 | 582.5214 | 591.3633 | 602.4853 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216
80% | 870.7553 | 897.2214 | 1004.8201 | 1082.4508 | 1123.2863 | 1159.8635 | 1183.0927 | 1209.6107 | 1230.7998 | 1244.6091 | 1277.4981 | 1300.2454 | 1312.2158 | 1334.4144 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 |  | 459.7664 | 475.6675 | 526.3134 | 562.3413 | 583.9436 | 601.238 | 615.2763 | 628.7789 | 640.4685 | 646.333 | 654.9755 | 664.8628 | 674.9545 | 687.6486 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303
75% | 1318.7877 | 1358.8714 | 1521.8333 | 1639.4076 | 1701.2542 | 1756.6516 | 1791.8331 | 1831.9954 | 1864.087 | 1885.0017 | 1934.8132 | 1969.2646 | 1987.3942 | 2021.0147 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 |  | 394.3451 | 407.9836 | 451.423 | 482.3244 | 500.8528 | 515.6864 | 527.7271 | 539.3084 | 549.3346 | 554.3647 | 561.7774 | 570.2578 | 578.9136 | 589.8014 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011
70% | 2014.5303 | 2075.7608 | 2324.6951 | 2504.2972 | 2598.7718 | 2683.3948 | 2737.1366 | 2798.487 | 2847.509 | 2879.4575 | 2955.5476 | 3008.1743 | 3035.8684 | 3087.2258 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 |  | 421.604 | 436.1853 | 482.6273 | 515.6648 | 535.474 | 551.3329 | 564.2059 | 576.5878 | 587.3071 | 592.6848 | 600.6099 | 609.6765 | 618.9306 | 630.571 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883
65% | 3678.4968 | 3790.3025 | 4244.8522 | 4572.8025 | 4745.3114 | 4899.8315 | 4997.9632 | 5109.9879 | 5199.5012 | 5257.8386 | 5396.7777 | 5492.8733 | 5543.4421 | 5637.2199 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 |  | 1112.1622 | 1150.6266 | 1273.1376 | 1360.2882 | 1412.5434 | 1454.3781 | 1488.3362 | 1520.9988 | 1549.2756 | 1563.4617 | 1584.3676 | 1608.2847 | 1632.6964 | 1663.4029 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967
60% | 7148.594 | 7365.8712 | 8249.2187 | 8886.5398 | 9221.7843 | 9522.0704 | 9712.7743 | 9930.4771 | 10104.4324 | 10217.8023 | 10487.8092 | 10674.5561 | 10772.8288 | 10955.0715 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 |  | 1241.7934 | 1284.7411 | 1421.5316 | 1518.8403 | 1577.1863 | 1623.8971 | 1661.8133 | 1698.283 | 1729.8556 | 1745.6952 | 1769.0379 | 1795.7427 | 1822.9997 | 1857.2854 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638
55% | 8285.907 | 8537.7521 | 9561.6368 | 10300.3531 | 10688.9337 | 11036.9942 | 11258.0382 | 11510.3768 | 11712.0077 | 11843.4143 | 12156.3781 | 12372.8358 | 12486.7433 | 12697.9801 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 |  | 2020.1858 | 2090.0544 | 2312.5892 | 2470.8938 | 2565.8128 | 2641.8033 | 2703.4866 | 2762.8165 | 2814.1798 | 2839.948 | 2877.9226 | 2921.3668 | 2965.7093 | 3021.4862 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194
50% | 9747.9358 | 10044.2184 | 11248.7651 | 12117.8262 | 12574.971 | 12984.4459 | 13244.4926 | 13541.3557 | 13778.5639 | 13933.1569 | 14301.3425 | 14555.9936 | 14689.9998 | 14938.5089 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 |  | 3523.6644 | 3645.5311 | 4033.6826 | 4309.8019 | 4475.3622 | 4607.9071 | 4715.4967 | 4818.9816 | 4908.5708 | 4953.5166 | 5019.7528 | 5095.5294 | 5172.8729 | 5270.1605 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488
45% | 17342.4082 | 17869.5202 | 20012.5113 | 21558.6451 | 22371.9445 | 23100.4353 | 23563.0806 | 24091.2253 | 24513.2389 | 24788.273 | 25443.3065 | 25896.3525 | 26134.7609 | 26576.8798 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 |  | 7020.6756 | 7263.4873 | 8036.8544 | 8587.0043 | 8916.8725 | 9180.9598 | 9395.3251 | 9601.5122 | 9780.0131 | 9869.5646 | 10001.536 | 10152.516 | 10306.618 | 10500.4574 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719
40% | 19856.1284 | 20459.6435 | 22913.2535 | 24683.4938 | 25614.6782 | 26448.7611 | 26978.4652 | 27583.1626 | 28066.3455 | 28381.2448 | 29131.2231 | 29649.9365 | 29922.9014 | 30429.1038 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 |  | 11955.7442 | 12369.2363 | 13686.2291 | 14623.0978 | 15184.8415 | 15634.5645 | 15999.6145 | 16350.7374 | 16654.7125 | 16807.2128 | 17031.9514 | 17289.0602 | 17551.4858 | 17881.5813 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149
35% | 12043.5634 | 12409.6202 | 13897.8362 | 14971.5602 | 15536.362 | 16042.2678 | 16363.5553 | 16730.3293 | 17023.3997 | 17214.3992 | 17669.292 | 17983.9131 | 18149.4777 | 18456.5104 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 |  | 14474.4645 | 14975.0672 | 16569.5112 | 17703.7504 | 18383.8369 | 18928.3031 | 19370.2583 | 19795.3524 | 20163.3661 | 20347.9936 | 20620.078 | 20931.352 | 21249.0628 | 21648.6997 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898
30% | 4991.361 | 5143.0704 | 5759.8499 | 6204.8465 | 6438.9242 | 6648.5929 | 6781.748 | 6933.7546 | 7055.2154 | 7134.3736 | 7322.9004 | 7453.2927 | 7521.9096 | 7649.1569 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 |  | 22112.4023 | 22877.1648 | 25312.9708 | 27045.7294 | 28084.6864 | 28916.4586 | 29591.6263 | 30241.0355 | 30803.244 | 31085.2964 | 31500.9553 | 31976.4835 | 32461.8451 | 33072.3638 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762
25% | 2979.5232 | 3070.084 | 3438.2619 | 3703.8964 | 3843.6258 | 3968.7846 | 4048.2697 | 4139.0079 | 4211.5122 | 4258.7646 | 4371.3031 | 4449.1389 | 4490.0988 | 4566.0573 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 |  | 18803.7802 | 19454.1133 | 21525.4559 | 22998.9462 | 23882.4467 | 24589.763 | 25163.9071 | 25716.1468 | 26194.2335 | 26434.0832 | 26787.548 | 27191.9242 | 27604.6624 | 28123.8307 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818
20% | 3169.6139 | 3265.9524 | 3657.6197 | 3940.2014 | 4088.8454 | 4221.9892 | 4306.5453 | 4403.0726 | 4480.2026 | 4530.4696 | 4650.1879 | 4732.9896 | 4776.5627 | 4857.3673 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 |  | 4988.3748 | 5160.8989 | 5710.3965 | 6101.2925 | 6335.6726 | 6523.3135 | 6675.6258 | 6822.1271 | 6948.9567 | 7012.5854 | 7106.3546 | 7213.6298 | 7323.1233 | 7460.8513 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353
15% | 3283.2375 | 3383.0295 | 3788.7372 | 4081.4488 | 4235.4214 | 4373.3381 | 4460.9254 | 4560.9129 | 4640.8079 | 4692.8769 | 4816.8868 | 4902.6568 | 4947.7919 | 5031.4931 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 |  | 3091.1568 | 3198.0652 | 3538.5736 | 3780.8009 | 3926.0397 | 4042.3156 | 4136.6992 | 4227.482 | 4306.0748 | 4345.5037 | 4403.6099 | 4470.0853 | 4537.9355 | 4623.2816 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056
10% | 2189.0045 | 2255.5379 | 2526.0319 | 2721.189 | 2823.8458 | 2915.7978 | 2974.1942 | 3040.858 | 3094.1256 | 3128.8412 | 3211.5212 | 3268.7059 | 3298.7984 | 3354.6038 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 |  | 884.3992 | 914.9863 | 1012.4079 | 1081.7106 | 1123.2644 | 1156.5316 | 1183.5353 | 1209.5089 | 1231.9947 | 1243.2756 | 1259.9001 | 1278.9192 | 1298.3315 | 1322.7496 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617
5% | 174.4742 | 179.7772 | 201.3369 | 216.8918 | 225.0741 | 232.4031 | 237.0575 | 242.371 | 246.6167 | 249.3836 | 255.9736 | 260.5315 | 262.9301 | 267.378 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 99564.2165 | 102590.4109 | 114893.5021 | 123769.9854 | 128439.2058 | 132621.532 | 135277.6178 | 138309.7405 | 140732.5559 | 142311.5495 | 146072.1518 | 148673.1266 | 150041.8495 | 152580.0908 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | E @ R (MWh) | 93455.9144 | 96688.1086 | 106982.8055 | 114306.1407 | 118697.1912 | 122212.5953 | 125066.1259 | 127810.7907 | 130186.91 | 131378.9772 | 133135.7188 | 135145.4924 | 137196.8262 | 139777.1238 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523
Option 7 Summer POE50 W E @ R (MWh) N 2 | 69694.9516 | 71813.2876 | 80425.4515 | 86638.9898 | 89907.444 | 92835.0724 | 94694.3324 | 96816.8184 | 98512.7891 | 99618.0846 | 102250.5063 | 104071.1886 | 105029.2947 | 106806.0636 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 28036.7743 | 29006.4326 | 32094.8416 | 34291.8422 | 35609.1573 | 36663.7786 | 37519.8378 | 38343.2372 | 39056.073 | 39413.6932 | 39940.7156 | 40543.6477 | 41159.0479 | 41933.1371 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 44.7175 | 46.8571 | 53.2551 | 58.6433 | 61.5501 | 63.6505 | 66.0717 | 67.8832 | 69.8804 | 70.9272 | 71.8338 | 74.0782 | 72.7247 | 76.3846 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 | 81.1588 |  | 47.5947 | 49.8159 | 56.1642 | 61.7562 | 64.6732 | 67.0386 | 69.2881 | 71.2045 | 73.2008 | 74.0757 | 75.27 | 77.4839 | 76.76 | 79.6517 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197 | 81.3197
98% | 132.8043 | 139.1585 | 158.1595 | 174.1616 | 182.7945 | 189.0324 | 196.2229 | 201.603 | 207.5343 | 210.6431 | 213.3357 | 220.0011 | 215.9813 | 226.8509 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 | 241.0294 |  | 141.3491 | 147.9458 | 166.7992 | 183.4066 | 192.0695 | 199.0945 | 205.7751 | 211.4668 | 217.3953 | 219.9938 | 223.5404 | 230.1155 | 227.9656 | 236.5536 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073 | 241.5073
97% | 58.4249 | 61.2203 | 69.5795 | 76.6193 | 80.4172 | 83.1615 | 86.3248 | 88.6917 | 91.301 | 92.6687 | 93.8533 | 96.7856 | 95.0171 | 99.799 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 | 106.0366 |  | 62.184 | 65.0861 | 73.3804 | 80.6865 | 84.4976 | 87.5881 | 90.5271 | 93.0311 | 95.6392 | 96.7824 | 98.3426 | 101.2353 | 100.2895 | 104.0676 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469 | 106.2469
95% | 143.8152 | 150.6962 | 171.2726 | 188.6014 | 197.95 | 204.7052 | 212.4918 | 218.3179 | 224.741 | 228.1076 | 231.0234 | 238.2414 | 233.8884 | 245.6592 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 | 261.0132 |  | 153.0684 | 160.2121 | 180.6286 | 198.6129 | 207.9941 | 215.6015 | 222.836 | 228.9996 | 235.4196 | 238.2336 | 242.0742 | 249.1945 | 246.8664 | 256.1663 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307 | 261.5307
90% | 1468.8623 | 1539.1418 | 1749.2998 | 1926.2886 | 2021.7708 | 2090.7648 | 2170.2935 | 2229.7992 | 2295.4018 | 2329.7862 | 2359.5674 | 2433.2886 | 2388.8285 | 2509.0501 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 | 2665.8695 |  | 1563.3702 | 1636.3326 | 1844.8575 | 2028.5416 | 2124.3562 | 2202.0546 | 2275.9443 | 2338.8965 | 2404.468 | 2433.2083 | 2472.4351 | 2545.1583 | 2521.3798 | 2616.3654 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551 | 2671.1551
85% | 3460.5527 | 3626.127 | 4121.2469 | 4538.2219 | 4763.1724 | 4925.7181 | 5113.0831 | 5253.275 | 5407.8308 | 5488.8385 | 5559.0011 | 5732.684 | 5627.9387 | 5911.1735 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 | 6280.6308 |  | 3683.2076 | 3855.1027 | 4346.3751 | 4779.124 | 5004.8576 | 5187.9104 | 5361.9903 | 5510.3018 | 5664.7844 | 5732.4949 | 5824.9108 | 5996.2424 | 5940.2217 | 6164.002 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833 | 6293.0833
80% | 6266.0722 | 6565.8799 | 7462.4007 | 8217.4232 | 8624.7443 | 8919.0681 | 9258.3326 | 9512.1802 | 9792.0365 | 9938.7182 | 10065.7628 | 10380.2528 | 10190.5889 | 10703.4463 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 | 11372.4279 |  | 6669.2367 | 6980.4895 | 7870.0435 | 8653.6281 | 9062.3671 | 9393.8235 | 9709.0324 | 9977.5822 | 10257.306 | 10379.9104 | 10547.2492 | 10857.4818 | 10756.0442 | 11161.2466 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759 | 11394.9759
75% | 7325.96 | 7676.4794 | 8724.6441 | 9607.3764 | 10083.5947 | 10427.7025 | 10824.3526 | 11121.1378 | 11448.331 | 11619.8235 | 11768.3573 | 12136.0423 | 11914.2974 | 12513.9031 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 | 13296.041 |  | 7797.3187 | 8161.2191 | 9201.2384 | 10117.3642 | 10595.2402 | 10982.7614 | 11351.2869 | 11665.2613 | 11992.2995 | 12135.6421 | 12331.2857 | 12693.9932 | 12575.3978 | 13049.139 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029 | 13322.4029
70% | 8591.0842 | 9002.1349 | 10231.3077 | 11266.4796 | 11824.9363 | 12228.4683 | 12693.6161 | 13041.6533 | 13425.3497 | 13626.4573 | 13800.6415 | 14231.8223 | 13971.7841 | 14674.936 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 | 15592.1417 |  | 9143.842 | 9570.5845 | 10790.2054 | 11864.5374 | 12424.9381 | 12879.3806 | 13311.547 | 13679.7417 | 14063.2564 | 14231.3528 | 14460.7823 | 14886.126 | 14747.0503 | 15302.602 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561 | 15623.0561
65% | 9414.2762 | 9864.7136 | 11211.6649 | 12346.0264 | 12957.9939 | 13400.1921 | 13909.9101 | 14291.296 | 14711.758 | 14932.1356 | 15123.0099 | 15595.5062 | 15310.5513 | 16081.0788 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 | 17086.1705 |  | 10019.999 | 10487.6317 | 11824.1158 | 13001.3897 | 13615.4876 | 14113.4744 | 14587.0508 | 14990.5257 | 15410.7884 | 15594.9918 | 15846.405 | 16312.5049 | 16160.103 | 16768.8874 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471 | 17120.0471
60% | 10243.0861 | 10733.1789 | 12198.7125 | 13432.9403 | 14098.784 | 14579.9123 | 15134.5046 | 15549.4667 | 16006.9451 | 16246.7243 | 16454.4027 | 16968.4964 | 16658.4548 | 17496.8177 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 | 18590.3952 |  | 10902.1352 | 11410.9371 | 12865.0821 | 14146.0002 | 14814.1618 | 15355.9902 | 15871.259 | 16310.2549 | 16767.5165 | 16967.9367 | 17241.4837 | 17748.6179 | 17582.7989 | 18245.1792 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542 | 18627.2542
55% | 10267.8043 | 10759.0798 | 12228.15 | 13465.3562 | 14132.8067 | 14615.096 | 15171.0266 | 15586.9901 | 16045.5725 | 16285.9303 | 16494.1099 | 17009.4441 | 16698.6544 | 17539.0404 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 | 18635.2568 |  | 10928.4438 | 11438.4736 | 12896.1276 | 14180.1368 | 14849.9108 | 15393.0467 | 15909.559 | 16349.6142 | 16807.9793 | 17008.8831 | 17283.0902 | 17791.4482 | 17625.2291 | 18289.2078 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048 | 18672.2048
50% | 12096.2046 | 12674.962 | 14405.6313 | 15863.1483 | 16649.4525 | 17217.6237 | 17872.5495 | 18362.5841 | 18902.8268 | 19185.9854 | 19431.2358 | 20038.3362 | 19672.2038 | 20662.2383 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 | 21953.6594 |  | 12874.4849 | 13475.3363 | 15192.5565 | 16705.2108 | 17494.2522 | 18134.105 | 18742.5932 | 19261.0096 | 19800.9963 | 20037.6753 | 20360.7109 | 20959.5927 | 20763.7748 | 21545.989 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867 | 21997.1867
45% | 15128.3079 | 15852.1399 | 18016.6286 | 19839.4951 | 20822.8988 | 21533.4909 | 22352.5842 | 22965.4537 | 23641.1167 | 23995.2534 | 24301.9797 | 25061.2593 | 24603.3501 | 25841.5522 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 | 27456.6882 |  | 16101.6763 | 16853.1406 | 19000.809 | 20892.6337 | 21879.4607 | 22679.7027 | 23440.718 | 24089.0836 | 24764.4264 | 25060.4327 | 25464.4422 | 26213.4432 | 25968.5404 | 26946.8289 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263 | 27511.1263
40% | 16018.9133 | 16785.3574 | 19077.2699 | 21007.4488 | 22048.7455 | 22801.1703 | 23668.4837 | 24317.4329 | 25032.8723 | 25407.8571 | 25732.6404 | 26536.6189 | 26051.7525 | 27362.8478 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 | 29073.067 |  | 17049.5841 | 17845.2871 | 20119.3891 | 22122.5858 | 23167.5074 | 24014.8597 | 24820.6761 | 25507.211 | 26222.3114 | 26535.7437 | 26963.5372 | 27756.632 | 27497.3118 | 28533.1922 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099 | 29130.7099
35% | 6550.3318 | 6863.7403 | 7800.9317 | 8590.2057 | 9016.0048 | 9323.6807 | 9678.3358 | 9943.6992 | 10236.2512 | 10389.5871 | 10522.395 | 10851.1518 | 10652.8839 | 11189.007 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 | 11888.3368 |  | 6971.7859 | 7297.1587 | 8227.0671 | 9046.199 | 9473.4804 | 9819.9733 | 10149.4816 | 10430.2142 | 10722.6276 | 10850.7939 | 11025.724 | 11350.0303 | 11243.991 | 11667.5753 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077 | 11911.9077
30% | 2020.5283 | 2117.2029 | 2406.2908 | 2649.7518 | 2781.0947 | 2876.001 | 2985.3986 | 3067.2531 | 3157.4943 | 3204.7926 | 3245.7588 | 3347.1678 | 3286.0096 | 3451.3832 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 | 3667.0999 |  | 2150.5309 | 2250.896 | 2537.7374 | 2790.4084 | 2922.2085 | 3029.0884 | 3130.7292 | 3217.3245 | 3307.5229 | 3347.0574 | 3401.0166 | 3501.0528 | 3468.3437 | 3599.0034 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706 | 3674.3706
25% | 1487.2137 | 1558.3712 | 1771.1549 | 1950.3549 | 2047.03 | 2116.886 | 2197.4083 | 2257.6575 | 2324.0797 | 2358.8937 | 2389.0469 | 2463.6892 | 2418.6736 | 2540.3972 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 | 2699.1758 |  | 1582.9023 | 1656.7763 | 1867.9064 | 2053.8854 | 2150.8971 | 2229.5663 | 2304.3791 | 2368.1178 | 2434.5085 | 2463.6079 | 2503.3248 | 2576.9566 | 2552.881 | 2649.0533 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275 | 2704.5275
20% | 1183.1045 | 1239.7116 | 1408.9847 | 1551.5414 | 1628.4482 | 1684.0199 | 1748.0768 | 1796.006 | 1848.8461 | 1876.5412 | 1900.5286 | 1959.9079 | 1924.0972 | 2020.9304 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 | 2147.2416 |  | 1259.2265 | 1317.9945 | 1485.9523 | 1633.9018 | 1711.0763 | 1773.659 | 1833.1739 | 1883.8792 | 1936.6941 | 1959.8432 | 1991.4387 | 2050.014 | 2030.8615 | 2107.3682 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989 | 2151.4989
15% | 928.0573 | 972.4613 | 1105.2435 | 1217.0686 | 1277.3962 | 1320.988 | 1371.2359 | 1408.8329 | 1450.2819 | 1472.0067 | 1490.823 | 1537.4016 | 1509.3108 | 1585.2693 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 | 1684.351 |  | 987.7693 | 1033.8685 | 1165.6188 | 1281.6742 | 1342.2118 | 1391.3032 | 1437.9883 | 1477.7628 | 1519.1922 | 1537.3509 | 1562.1352 | 1608.0832 | 1593.0594 | 1653.0733 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905 | 1687.6905
10% | 651.6625 | 682.8421 | 776.079 | 854.6002 | 896.961 | 927.5703 | 962.8533 | 989.2531 | 1018.3578 | 1033.6124 | 1046.8249 | 1079.5314 | 1059.8066 | 1113.1431 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 | 1182.7162 |  | 693.591 | 725.9609 | 818.4732 | 899.9649 | 942.4732 | 976.9442 | 1009.7254 | 1037.6542 | 1066.7451 | 1079.4958 | 1096.8988 | 1129.1625 | 1118.6132 | 1160.7536 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611 | 1185.0611
5% | 67.4134 | 70.6388 | 80.284 | 88.4069 | 92.7891 | 95.9555 | 99.6055 | 102.3365 | 105.3474 | 106.9254 | 108.2922 | 111.6757 | 109.6352 | 115.1527 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 | 122.35 |  | 71.7508 | 75.0994 | 84.6696 | 93.0998 | 97.4972 | 101.0632 | 104.4544 | 107.3435 | 110.3529 | 111.672 | 113.4723 | 116.8099 | 115.7186 | 120.078 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925 | 122.5925
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 113549.1973 | 118982.0949 | 135228.1917 | 148910.1601 | 156291.3357 | 161624.858 | 167772.7617 | 172372.8029 | 177444.1564 | 180102.2155 | 182404.4242 | 188103.3826 | 184666.4331 | 193960.0608 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | 206082.8573 | E @ R (MWh) | 120855.0513 | 126495.349 | 142615.1972 | 156814.7481 | 164221.6187 | 170228.0295 | 175940.0151 | 180806.4807 | 185875.4309 | 188097.1784 | 191129.5697 | 196751.3792 | 194913.2016 | 202255.9836 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557 | 206491.4557
Option 8 Winter POE50 W E @ R (MWh) N 2 | 79484.4381 | 83287.4664 | 94659.7342 | 104237.112 | 109403.935 | 113137.4006 | 117440.9332 | 120660.962 | 124210.9095 | 126071.5508 | 127683.0969 | 131672.3678 | 129266.5031 | 135772.0426 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | 144258.0001 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 36256.5154 | 37948.6047 | 42784.5592 | 47044.4244 | 49266.4856 | 51068.4088 | 52782.0045 | 54241.9442 | 55762.6293 | 56429.1535 | 57338.8709 | 59025.4138 | 58473.9605 | 60676.7951 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367 | 61947.4367
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 48.2179 | 49.8856 | 55.197 | 58.9755 | 61.241 | 63.0547 | 64.527 | 65.9431 | 67.169 | 67.7841 | 68.6904 | 69.7274 | 70.7857 | 72.117 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249 | 72.3249
98% | 21.2169 | 21.8618 | 24.4836 | 26.3751 | 27.3701 | 28.2614 | 28.8274 | 29.4735 | 29.9898 | 30.3263 | 31.1277 | 31.6819 | 31.9736 | 32.5145 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 | 32.3571 |  | 23.8667 | 24.6921 | 27.3211 | 29.1914 | 30.3128 | 31.2105 | 31.9392 | 32.6402 | 33.247 | 33.5514 | 34 | 34.5133 | 35.0372 | 35.6961 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799 | 35.799
97% | 21.0015 | 21.6398 | 24.235 | 26.1073 | 27.0922 | 27.9744 | 28.5347 | 29.1743 | 29.6853 | 30.0184 | 30.8116 | 31.3603 | 31.649 | 32.1844 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 | 32.0286 |  | 47.2487 | 48.8828 | 54.0875 | 57.79 | 60.01 | 61.7873 | 63.23 | 64.6176 | 65.8189 | 66.4216 | 67.3097 | 68.3258 | 69.3629 | 70.6674 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711 | 70.8711
95% | 62.0353 | 63.9208 | 71.5864 | 77.1171 | 80.0263 | 82.6322 | 84.2871 | 86.1763 | 87.6859 | 88.6697 | 91.0129 | 92.6334 | 93.4862 | 95.0677 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 | 94.6075 |  | 93.0436 | 96.2616 | 106.5109 | 113.8019 | 118.1736 | 121.6735 | 124.5144 | 127.247 | 129.6126 | 130.7994 | 132.5484 | 134.5493 | 136.5916 | 139.1605 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616 | 139.5616
90% | 139.4716 | 143.7108 | 160.9452 | 173.3796 | 179.9203 | 185.779 | 189.4997 | 193.7472 | 197.1411 | 199.353 | 204.6209 | 208.2644 | 210.1817 | 213.7374 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 | 212.7025 |  | 336.1928 | 347.8201 | 384.8537 | 411.1982 | 426.9943 | 439.6404 | 449.9056 | 459.7791 | 468.3268 | 472.615 | 478.9346 | 486.1645 | 493.5438 | 502.826 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752 | 504.2752
85% | 226.1702 | 233.0445 | 260.9922 | 281.1561 | 291.7627 | 301.2632 | 307.2968 | 314.1846 | 319.6883 | 323.2751 | 331.8177 | 337.7261 | 340.8353 | 346.6011 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 | 344.923 |  | 402.8257 | 416.7575 | 461.131 | 492.697 | 511.6238 | 526.7764 | 539.076 | 550.9064 | 561.1483 | 566.2865 | 573.8586 | 582.5214 | 591.3633 | 602.4853 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216 | 604.2216
80% | 870.7553 | 897.2214 | 1004.8201 | 1082.4508 | 1123.2863 | 1159.8635 | 1183.0927 | 1209.6107 | 1230.7998 | 1244.6091 | 1277.4981 | 1300.2454 | 1312.2158 | 1334.4144 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 | 1327.9536 |  | 459.7664 | 475.6675 | 526.3134 | 562.3413 | 583.9436 | 601.238 | 615.2763 | 628.7789 | 640.4685 | 646.333 | 654.9755 | 664.8628 | 674.9545 | 687.6486 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303 | 689.6303
75% | 1318.7877 | 1358.8714 | 1521.8333 | 1639.4076 | 1701.2542 | 1756.6516 | 1791.8331 | 1831.9954 | 1864.087 | 1885.0017 | 1934.8132 | 1969.2646 | 1987.3942 | 2021.0147 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 | 2011.2297 |  | 394.3451 | 407.9836 | 451.423 | 482.3244 | 500.8528 | 515.6864 | 527.7271 | 539.3084 | 549.3346 | 554.3647 | 561.7774 | 570.2578 | 578.9136 | 589.8014 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011 | 591.5011
70% | 2014.5303 | 2075.7608 | 2324.6951 | 2504.2972 | 2598.7718 | 2683.3948 | 2737.1366 | 2798.487 | 2847.509 | 2879.4575 | 2955.5476 | 3008.1743 | 3035.8684 | 3087.2258 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 | 3072.2786 |  | 421.604 | 436.1853 | 482.6273 | 515.6648 | 535.474 | 551.3329 | 564.2059 | 576.5878 | 587.3071 | 592.6848 | 600.6099 | 609.6765 | 618.9306 | 630.571 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883 | 632.3883
65% | 3678.4968 | 3790.3025 | 4244.8522 | 4572.8025 | 4745.3114 | 4899.8315 | 4997.9632 | 5109.9879 | 5199.5012 | 5257.8386 | 5396.7777 | 5492.8733 | 5543.4421 | 5637.2199 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 | 5609.9265 |  | 1112.1622 | 1150.6266 | 1273.1376 | 1360.2882 | 1412.5434 | 1454.3781 | 1488.3362 | 1520.9988 | 1549.2756 | 1563.4617 | 1584.3676 | 1608.2847 | 1632.6964 | 1663.4029 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967 | 1668.1967
60% | 7148.594 | 7365.8712 | 8249.2187 | 8886.5398 | 9221.7843 | 9522.0704 | 9712.7743 | 9930.4771 | 10104.4324 | 10217.8023 | 10487.8092 | 10674.5561 | 10772.8288 | 10955.0715 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 | 10902.0311 |  | 1241.7934 | 1284.7411 | 1421.5316 | 1518.8403 | 1577.1863 | 1623.8971 | 1661.8133 | 1698.283 | 1729.8556 | 1745.6952 | 1769.0379 | 1795.7427 | 1822.9997 | 1857.2854 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638 | 1862.638
55% | 8285.907 | 8537.7521 | 9561.6368 | 10300.3531 | 10688.9337 | 11036.9942 | 11258.0382 | 11510.3768 | 11712.0077 | 11843.4143 | 12156.3781 | 12372.8358 | 12486.7433 | 12697.9801 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 | 12636.5011 |  | 2020.1858 | 2090.0544 | 2312.5892 | 2470.8938 | 2565.8128 | 2641.8033 | 2703.4866 | 2762.8165 | 2814.1798 | 2839.948 | 2877.9226 | 2921.3668 | 2965.7093 | 3021.4862 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194 | 3030.194
50% | 9747.9358 | 10044.2184 | 11248.7651 | 12117.8262 | 12574.971 | 12984.4459 | 13244.4926 | 13541.3557 | 13778.5639 | 13933.1569 | 14301.3425 | 14555.9936 | 14689.9998 | 14938.5089 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 | 14866.1821 |  | 3523.6644 | 3645.5311 | 4033.6826 | 4309.8019 | 4475.3622 | 4607.9071 | 4715.4967 | 4818.9816 | 4908.5708 | 4953.5166 | 5019.7528 | 5095.5294 | 5172.8729 | 5270.1605 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488 | 5285.3488
45% | 17342.4082 | 17869.5202 | 20012.5113 | 21558.6451 | 22371.9445 | 23100.4353 | 23563.0806 | 24091.2253 | 24513.2389 | 24788.273 | 25443.3065 | 25896.3525 | 26134.7609 | 26576.8798 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 | 26448.2043 |  | 7020.6756 | 7263.4873 | 8036.8544 | 8587.0043 | 8916.8725 | 9180.9598 | 9395.3251 | 9601.5122 | 9780.0131 | 9869.5646 | 10001.536 | 10152.516 | 10306.618 | 10500.4574 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719 | 10530.719
40% | 19856.1284 | 20459.6435 | 22913.2535 | 24683.4938 | 25614.6782 | 26448.7611 | 26978.4652 | 27583.1626 | 28066.3455 | 28381.2448 | 29131.2231 | 29649.9365 | 29922.9014 | 30429.1038 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 | 30281.7773 |  | 11955.7442 | 12369.2363 | 13686.2291 | 14623.0978 | 15184.8415 | 15634.5645 | 15999.6145 | 16350.7374 | 16654.7125 | 16807.2128 | 17031.9514 | 17289.0602 | 17551.4858 | 17881.5813 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149 | 17933.1149
35% | 12043.5634 | 12409.6202 | 13897.8362 | 14971.5602 | 15536.362 | 16042.2678 | 16363.5553 | 16730.3293 | 17023.3997 | 17214.3992 | 17669.292 | 17983.9131 | 18149.4777 | 18456.5104 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 | 18367.1507 |  | 14474.4645 | 14975.0672 | 16569.5112 | 17703.7504 | 18383.8369 | 18928.3031 | 19370.2583 | 19795.3524 | 20163.3661 | 20347.9936 | 20620.078 | 20931.352 | 21249.0628 | 21648.6997 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898 | 21711.0898
30% | 4991.361 | 5143.0704 | 5759.8499 | 6204.8465 | 6438.9242 | 6648.5929 | 6781.748 | 6933.7546 | 7055.2154 | 7134.3736 | 7322.9004 | 7453.2927 | 7521.9096 | 7649.1569 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 | 7612.1225 |  | 22112.4023 | 22877.1648 | 25312.9708 | 27045.7294 | 28084.6864 | 28916.4586 | 29591.6263 | 30241.0355 | 30803.244 | 31085.2964 | 31500.9553 | 31976.4835 | 32461.8451 | 33072.3638 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762 | 33167.6762
25% | 2979.5232 | 3070.084 | 3438.2619 | 3703.8964 | 3843.6258 | 3968.7846 | 4048.2697 | 4139.0079 | 4211.5122 | 4258.7646 | 4371.3031 | 4449.1389 | 4490.0988 | 4566.0573 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 | 4543.9501 |  | 18803.7802 | 19454.1133 | 21525.4559 | 22998.9462 | 23882.4467 | 24589.763 | 25163.9071 | 25716.1468 | 26194.2335 | 26434.0832 | 26787.548 | 27191.9242 | 27604.6624 | 28123.8307 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818 | 28204.8818
20% | 3169.6139 | 3265.9524 | 3657.6197 | 3940.2014 | 4088.8454 | 4221.9892 | 4306.5453 | 4403.0726 | 4480.2026 | 4530.4696 | 4650.1879 | 4732.9896 | 4776.5627 | 4857.3673 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 | 4833.8497 |  | 4988.3748 | 5160.8989 | 5710.3965 | 6101.2925 | 6335.6726 | 6523.3135 | 6675.6258 | 6822.1271 | 6948.9567 | 7012.5854 | 7106.3546 | 7213.6298 | 7323.1233 | 7460.8513 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353 | 7482.353
15% | 3283.2375 | 3383.0295 | 3788.7372 | 4081.4488 | 4235.4214 | 4373.3381 | 4460.9254 | 4560.9129 | 4640.8079 | 4692.8769 | 4816.8868 | 4902.6568 | 4947.7919 | 5031.4931 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 | 5007.1325 |  | 3091.1568 | 3198.0652 | 3538.5736 | 3780.8009 | 3926.0397 | 4042.3156 | 4136.6992 | 4227.482 | 4306.0748 | 4345.5037 | 4403.6099 | 4470.0853 | 4537.9355 | 4623.2816 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056 | 4636.6056
10% | 2189.0045 | 2255.5379 | 2526.0319 | 2721.189 | 2823.8458 | 2915.7978 | 2974.1942 | 3040.858 | 3094.1256 | 3128.8412 | 3211.5212 | 3268.7059 | 3298.7984 | 3354.6038 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 | 3338.3621 |  | 884.3992 | 914.9863 | 1012.4079 | 1081.7106 | 1123.2644 | 1156.5316 | 1183.5353 | 1209.5089 | 1231.9947 | 1243.2756 | 1259.9001 | 1278.9192 | 1298.3315 | 1322.7496 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617 | 1326.5617
5% | 174.4742 | 179.7772 | 201.3369 | 216.8918 | 225.0741 | 232.4031 | 237.0575 | 242.371 | 246.6167 | 249.3836 | 255.9736 | 260.5315 | 262.9301 | 267.378 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 | 266.0835 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 99564.2165 | 102590.4109 | 114893.5021 | 123769.9854 | 128439.2058 | 132621.532 | 135277.6178 | 138309.7405 | 140732.5559 | 142311.5495 | 146072.1518 | 148673.1266 | 150041.8495 | 152580.0908 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | 151841.354 | E @ R (MWh) | 93455.9144 | 96688.1086 | 106982.8055 | 114306.1407 | 118697.1912 | 122212.5953 | 125066.1259 | 127810.7907 | 130186.91 | 131378.9772 | 133135.7188 | 135145.4924 | 137196.8262 | 139777.1238 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523 | 140179.9523
Option 8 Summer POE50 W E @ R (MWh) N 2 | 69694.9516 | 71813.2876 | 80425.4515 | 86638.9898 | 89907.444 | 92835.0724 | 94694.3324 | 96816.8184 | 98512.7891 | 99618.0846 | 102250.5063 | 104071.1886 | 105029.2947 | 106806.0636 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | 106288.9478 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 28036.7743 | 29006.4326 | 32094.8416 | 34291.8422 | 35609.1573 | 36663.7786 | 37519.8378 | 38343.2372 | 39056.073 | 39413.6932 | 39940.7156 | 40543.6477 | 41159.0479 | 41933.1371 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857 | 42053.9857

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-OFR-TRNFMR-9000014181 | 0.2863% | 0.2863% | 0.3164% | 0.3483% | 0.3821% | 0.4177% | 0.4553% | 0.4947% | 0.5362% | 0.5797% | 0.6252% | 0.6728% | 0.7225% | 0.7743% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283%
Tx 2 Pof | DS-OFR-TRNFMR-9000016122 | 0.2863% | 0.2863% | 0.3164% | 0.3483% | 0.3821% | 0.4177% | 0.4553% | 0.4947% | 0.5362% | 0.5797% | 0.6252% | 0.6728% | 0.7225% | 0.7743% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283% | 0.8283%
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.5727% | 0.5727% | 0.6329% | 0.6966% | 0.7641% | 0.8354% | 0.9105% | 0.9895% | 1.072% | 1.159% | 1.25% | 1.346% | 1.445% | 1.549% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657% | 1.657%
N-1 Risk |  | 0.2209% | 0.2209% | 0.2442% | 0.2688% | 0.2948% | 0.3223% | 0.3513% | 0.3817% | 0.4137% | 0.4473% | 0.4824% | 0.5192% | 0.5575% | 0.5975% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391% | 0.6391%
N-2 Risk |  | 0.0001922% | 0.0001922% | 0.0002347% | 0.0002844% | 0.0003422% | 0.000409% | 0.0004858% | 0.0005738% | 0.000674% | 0.0007877% | 0.0009163% | 0.001061% | 0.001224% | 0.001406% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608% | 0.001608%
N Risk |  | 99.78% | 99.78% | 99.76% | 99.73% | 99.7% | 99.68% | 99.65% | 99.62% | 99.59% | 99.55% | 99.52% | 99.48% | 99.44% | 99.4% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36% | 99.36%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11841 | 0.90411 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.56306 | 0.96672 | 5.4201 | 15.1939 | 24.5795 | 34.9865 | 47.8695 | 61.9252 | 78.9401 | 92.41 | 110.1897 | 137.7391 | 141.9215 | 185.4141 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.50118 | 0.52101 | 0.71574 | 0.94359 | 1.1847 | 1.4632 | 1.7887 | 2.1654 | 2.6038 | 3.0811 | 3.6487 | 4.3276 | 4.9752 | 5.9004 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206
Total EUE (MWh) - Option 1 | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 25.7643 | 36.4498 | 49.6582 | 64.0905 | 81.5439 | 95.4911 | 113.8383 | 142.0667 | 147.015 | 192.2187 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137
Cost of EUE ($) - Option 1 | 46015.5335 | 64326.6602 | 265300.2016 | 697750.8459 | 1113994.5614 | 1576012.9747 | 2147118.6735 | 2771143.2766 | 3525791.6387 | 4128838.1387 | 4922136.099 | 6142673.3665 | 6356629.9087 | 8311142.6869 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125
Hours at Risk pA. (Hrs) (N) | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 1.6479 | 2.7824 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951 | 4.2951
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.56306 | 0.96672 | 5.4201 | 15.1939 | 1.8925 | 3.7991 | 6.9487 | 10.9758 | 16.6559 | 21.0416 | 27.1642 | 38.8288 | 38.0519 | 59.0022 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604 | 86.3604
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.50118 | 0.52101 | 0.71574 | 0.94359 | 0.94881 | 1.1813 | 1.4538 | 1.7698 | 2.1392 | 2.538 | 3.0169 | 3.596 | 4.1315 | 4.9314 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117 | 5.8117
Total EUE (MWh) - Option 2 | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 2.8413 | 4.9804 | 8.4024 | 12.7456 | 18.795 | 23.5796 | 30.1811 | 42.4247 | 42.1834 | 63.9336 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721 | 92.1721
Cost of EUE ($) - Option 2 | 46015.5335 | 64326.6602 | 265300.2016 | 697750.8459 | 122853.6019 | 215340.761 | 363304.6625 | 551091.6157 | 812657.939 | 1019531.9577 | 1304968.557 | 1834358.5874 | 1823925.8129 | 2764356.8966 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683 | 3985334.3683
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.56306 | 0.96672 | 5.4201 | 4.5409 | 0.29316 | 0.57223 | 1.153 | 2.1936 | 4.0588 | 5.6428 | 8.1314 | 13.6871 | 12.7356 | 23.8545 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.50118 | 0.52101 | 0.71574 | 0.84555 | 0.83086 | 1.0403 | 1.2863 | 1.572 | 1.9068 | 2.2664 | 2.701 | 3.2302 | 3.7097 | 4.4469 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573
Total EUE (MWh) - Option 3 | 1.0642 | 1.4877 | 6.1358 | 5.3865 | 1.124 | 1.6125 | 2.4393 | 3.7656 | 5.9656 | 7.9092 | 10.8325 | 16.9173 | 16.4453 | 28.3014 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371
Cost of EUE ($) - Option 3 | 46015.5335 | 64326.6602 | 265300.2016 | 232900.6742 | 48600.2259 | 69722.006 | 105469.2274 | 162816.5545 | 257940.0832 | 341978.1054 | 468373.8808 | 731468.7932 | 711060.9645 | 1223694.0784 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.56306 | 0.96672 | 5.4201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00061378 | 0.0036219 | 0.010097 | 0.024337 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974 | 0.028974
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.50118 | 0.52101 | 0.71574 | 0.022622 | 0.038328 | 0.057828 | 0.084394 | 0.11655 | 0.15866 | 0.19932 | 0.2535 | 0.33706 | 0.37296 | 0.51574 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303 | 0.69303
Total EUE (MWh) - Option 4 | 1.0642 | 1.4877 | 6.1358 | 0.022622 | 0.038328 | 0.057828 | 0.084394 | 0.11655 | 0.15866 | 0.19932 | 0.25412 | 0.34068 | 0.38305 | 0.54007 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722 | 0.722
Cost of EUE ($) - Option 4 | 46015.5335 | 64326.6602 | 265300.2016 | 978.1186 | 1657.2044 | 2500.3858 | 3649.0161 | 5039.5821 | 6860.0271 | 8618.101 | 10987.5186 | 14730.3464 | 16562.3778 | 23351.7314 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165 | 31217.9165
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.56306 | 0.96672 | 5.4201 | 4.5409 | 0.29316 | 0.57223 | 1.153 | 2.1936 | 4.0588 | 5.6428 | 8.1314 | 13.6871 | 12.7356 | 23.8545 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798 | 40.9798
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.50118 | 0.52101 | 0.71574 | 0.84555 | 0.83086 | 1.0403 | 1.2863 | 1.572 | 1.9068 | 2.2664 | 2.701 | 3.2302 | 3.7097 | 4.4469 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573 | 5.2573
Total EUE (MWh) - Option 5 | 1.0642 | 1.4877 | 6.1358 | 5.3865 | 1.124 | 1.6125 | 2.4393 | 3.7656 | 5.9656 | 7.9092 | 10.8325 | 16.9173 | 16.4453 | 28.3014 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371 | 46.2371
Cost of EUE ($) - Option 5 | 46015.5335 | 64326.6602 | 265300.2016 | 232900.6742 | 48600.2259 | 69722.006 | 105469.2274 | 162816.5545 | 257940.0832 | 341978.1054 | 468373.8808 | 731468.7932 | 711060.9645 | 1223694.0784 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956 | 1999198.8956
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11841 | 0.90411 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.56306 | 0.96672 | 5.4201 | 15.1939 | 24.5795 | 34.9865 | 47.8695 | 61.9252 | 78.9401 | 92.41 | 110.1897 | 137.7391 | 141.9215 | 185.4141 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.50118 | 0.52101 | 0.71574 | 0.94359 | 1.1847 | 1.4632 | 1.7887 | 2.1654 | 2.6038 | 3.0811 | 3.6487 | 4.3276 | 4.9752 | 5.9004 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206
Total EUE (MWh) - Option 6 | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 25.7643 | 36.4498 | 49.6582 | 64.0905 | 81.5439 | 95.4911 | 113.8383 | 142.0667 | 147.015 | 192.2187 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137
Cost of EUE ($) - Option 6 | 46015.5335 | 64326.6602 | 265300.2016 | 697750.8459 | 1113994.5614 | 1576012.9747 | 2147118.6735 | 2771143.2766 | 3525791.6387 | 4128838.1387 | 4922136.099 | 6142673.3665 | 6356629.9087 | 8311142.6869 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11841 | 0.90411 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.56306 | 0.96672 | 5.4201 | 15.1939 | 24.5795 | 34.9865 | 47.8695 | 61.9252 | 78.9401 | 92.41 | 110.1897 | 137.7391 | 141.9215 | 185.4141 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.50118 | 0.52101 | 0.71574 | 0.94359 | 1.1847 | 1.4632 | 1.7887 | 2.1654 | 2.6038 | 3.0811 | 3.6487 | 4.3276 | 4.9752 | 5.9004 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206
Total EUE (MWh) - Option 7 | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 25.7643 | 36.4498 | 49.6582 | 64.0905 | 81.5439 | 95.4911 | 113.8383 | 142.0667 | 147.015 | 192.2187 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137
Cost of EUE ($) - Option 7 | 46015.5335 | 64326.6602 | 265300.2016 | 697750.8459 | 1113994.5614 | 1576012.9747 | 2147118.6735 | 2771143.2766 | 3525791.6387 | 4128838.1387 | 4922136.099 | 6142673.3665 | 6356629.9087 | 8311142.6869 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11841 | 0.90411 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984 | 1.0984
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.56306 | 0.96672 | 5.4201 | 15.1939 | 24.5795 | 34.9865 | 47.8695 | 61.9252 | 78.9401 | 92.41 | 110.1897 | 137.7391 | 141.9215 | 185.4141 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948 | 234.4948
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.50118 | 0.52101 | 0.71574 | 0.94359 | 1.1847 | 1.4632 | 1.7887 | 2.1654 | 2.6038 | 3.0811 | 3.6487 | 4.3276 | 4.9752 | 5.9004 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206 | 6.9206
Total EUE (MWh) - Option 8 | 1.0642 | 1.4877 | 6.1358 | 16.1375 | 25.7643 | 36.4498 | 49.6582 | 64.0905 | 81.5439 | 95.4911 | 113.8383 | 142.0667 | 147.015 | 192.2187 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137 | 242.5137
Cost of EUE ($) - Option 8 | 46015.5335 | 64326.6602 | 265300.2016 | 697750.8459 | 1113994.5614 | 1576012.9747 | 2147118.6735 | 2771143.2766 | 3525791.6387 | 4128838.1387 | 4922136.099 | 6142673.3665 | 6356629.9087 | 8311142.6869 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125 | 10485796.4125