## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 105212961.6203 | 61.5% | 30.2784
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 59818974.1027 | 34.97% | 12.0256
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 2268426.58 | 1.326% | 0.44409
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 3766583.5488 | 2.202% | 0.4899
[5 empty] | 171066945.8518 |  | 43.238
Customer No. and Vol per Feeder | [6 empty] | 43237.9539 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 59818974.1027 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 14.0402 | E@R MWh | 14.0402
RESIDENTL | 105212961.6203 | [14 empty] | cost of EUE ($) | 607070.7247 | cost of EUE ($M) | 0.60707
FARM | 3766583.5488
INDUSTRIAL | 2268426.58
Forecast (FCT)
Forecast | 2031
Summer POE50 | 72.4055
Summer POE10 | 79.9243
Winter POE50 | 69.7836
Winter POE10 | 73.0466
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 3.06 |  | Summer POE50 | 69.3455 |  |  | 100% | 0 | 69.3455 | 100% |  | 0% |  | 0%
|  |  | Summer POE10 | 76.8643 |  |  | 99% | 0 | 68.6521 | 99% |  | 0% | 0 | 0% | 0
Embedded Generation |  |  | Winter POE50 | 66.7236 |  |  | 98% | 0.37816 | 67.9586 | 98% |  | 0% | 8.7376 | 0% | 25.8306
|  |  | Winter POE10 | 69.9866 |  |  | 97% | 0.75633 | 67.2652 | 97% |  | 0% | 8.4754 | 0% | 25.5684
Year | 2031 | [5 empty] | 95% | 1.8908 | 65.8783 | 95% |  | 0% | 24.2461 | 0% | 75.5251
Capacity | 0 | [5 empty] | 90% | 4.538 | 62.411 | 90% |  | 0% | 50.1493 | 0% | 169.8005
[7 empty] | 85% | 9.0759 | 58.9437 | 85% |  | 0% | 70.2358 | 0% | 275.3521
Demand Mangement | [6 empty] | 80% | 27.606 | 55.4764 | 80% |  | 0% | 222.5473 | 0% | 1060.1055
[7 empty] | 75% | 57.481 | 52.0092 | 75% |  | 0% | 255.2159 | 0% | 1605.5649
Year | 2031 | [5 empty] | 70% | 106.2642 | 48.5419 | 70% |  | 0% | 247.6001 | 0% | 2452.6004
Capacity | 0 | [5 empty] | 65% | 201.9397 | 45.0746 | 65% |  | 0% | 154.0865 | 0% | 4478.4051
[7 empty] | 60% | 402.745 | 41.6073 | 60% |  | 0% |  | 0% | 8703.0928
LDC | [6 empty] | 55% | 655.7369 | 38.14 | 55% |  | 0% |  | 0% | 10087.7205
[7 empty] | 50% | 981.7145 | 34.6728 | 50% |  | 0% |  | 0% | 11867.6751
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 1622.7029 | 31.2055 | 45% |  | 0% |  | 0% | 21113.6049
100% | 0% | 0 |  |  |  |  | 40% | 2442.9413 | 27.7382 | 40% |  | 0% |  | 0% | 24173.9467
99% | 0% | 0 |  |  |  |  | 35% | 3006.7842 | 24.2709 | 35% |  | 0% |  | 0% | 14662.4988
98% | 0.00861% | 0.37816 |  |  |  |  | 30% | 3276.4154 | 20.8037 | 30% |  | 0% |  | 0% | 6076.7584
97% | 0.01722% | 0.75633 |  |  |  |  | 25% | 3466.632 | 17.3364 | 25% |  | 0% |  | 0% | 3627.436
95% | 0.04305% | 1.8908 |  |  |  |  | 20% | 3713.9514 | 13.8691 | 20% |  | 0% |  | 0% | 3858.8629
90% | 0.1033% | 4.538 |  |  |  |  | 15% | 4043.3325 | 10.4018 | 15% |  | 0% |  | 0% | 3997.1945
85% | 0.2066% | 9.0759 |  |  |  |  | 10% | 4350.7801 | 6.9346 | 10% |  | 0% |  | 0% | 2665.0149
80% | 0.6286% | 27.606 |  |  |  |  | 5% | 4391.6218 | 3.4673 | 5% |  | 0% |  | 0% | 212.4145
75% | 1.309% | 57.481 |  |  |  |  | 9.992e-14% | 4391.6218 | 6.929e-14 | 9.992e-14% |  | 0% |  | 0% | 0
70% | 2.419% | 106.2642 | [7 empty] | Total E@R | 0 | Total E@R | 1041.2939 | Total E@R | 121214.9726
65% | 4.598% | 201.9397 | [7 empty] | Total WE@R | 0 | Total WE@R | 2.2703 | Total WE@R | 0.24366
60% | 9.17% | 402.745 |  |  |  |  | MD Weighted LDC
55% | 14.93% | 655.7369
50% | 22.35% | 981.7145 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 36.95% | 1622.7029 |  |  |  |  | 100% | 0 | 76.8643 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 55.62% | 2442.9413 |  |  |  |  | 99% | 0.75633 | 76.0957
35% | 68.46% | 3006.7842 |  |  |  |  | 98% | 1.1345 | 75.327 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 74.6% | 3276.4154 |  |  |  |  | 97% | 1.8908 | 74.5584 | 100% |  | 0% |  | 0%
25% | 78.93% | 3466.632 |  |  |  |  | 95% | 3.4035 | 73.0211 | 99% |  | 0% | 23.658 | 0% | 57.844
20% | 84.56% | 3713.9514 |  |  |  |  | 90% | 9.0759 | 69.1779 | 98% |  | 0% | 11.5383 | 0% | 28.6313
15% | 92.06% | 4043.3325 |  |  |  |  | 85% | 16.2611 | 65.3347 | 97% |  | 0% | 22.4953 | 0% | 56.6813
10% | 99.06% | 4350.7801 |  |  |  |  | 80% | 24.9588 | 61.4915 | 95% |  | 0% | 43.2465 | 0% | 111.6186
5% | 99.99% | 4391.6218 |  |  |  |  | 75% | 32.9003 | 57.6482 | 90% |  | 0% | 146.914 | 0% | 403.3094
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 41.9762 | 53.805 | 85% |  | 0% | 158.4771 | 0% | 483.2446
[7 empty] | 65% | 67.6914 | 49.9618 | 80% |  | 0% | 158.4133 | 0% | 551.5529
[7 empty] | 60% | 98.7009 | 46.1186 | 75% |  | 0% | 114.1175 | 0% | 473.071
[7 empty] | 55% | 153.5347 | 42.2754 | 70% |  | 0% | 95.5392 | 0% | 505.7718
LDC | [6 empty] | 50% | 258.2862 | 38.4322 | 65% |  | 0% | 171.8654 | 0% | 1334.1911
[7 empty] | 45% | 488.9664 | 34.5889 | 60% |  | 0% | 88.0733 | 0% | 1489.7014
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 928.0152 | 30.7457 | 55% |  | 0% | 6.0197 | 0% | 2423.4899
100% | 0% | 0 |  |  |  |  | 35% | 1530.4309 | 26.9025 | 50% |  | 0% |  | 0% | 4227.1187
99% | 0.01722% | 0.75633 |  |  |  |  | 30% | 2592.3162 | 23.0593 | 45% |  | 0% |  | 0% | 8422.2633
98% | 0.02583% | 1.1345 |  |  |  |  | 25% | 3659.4958 | 19.2161 | 40% |  | 0% |  | 0% | 14342.5548
97% | 0.04305% | 1.8908 |  |  |  |  | 20% | 4005.5161 | 15.3729 | 35% |  | 0% |  | 0% | 17364.1053
95% | 0.07749% | 3.4035 |  |  |  |  | 15% | 4281.1979 | 11.5296 | 30% |  | 0% |  | 0% | 26526.8592
90% | 0.2066% | 9.0759 |  |  |  |  | 10% | 4391.6218 | 7.6864 | 25% |  | 0% |  | 0% | 22557.7132
85% | 0.3702% | 16.2611 |  |  |  |  | 5% | 4391.6218 | 3.8432 | 20% |  | 0% |  | 0% | 5984.2397
80% | 0.5683% | 24.9588 |  |  |  |  | 9.992e-14% | 4391.6218 | 7.6803e-14 | 15% |  | 0% |  | 0% | 3708.2666
75% | 0.7491% | 32.9003 | [7 empty] | 10% |  | 0% |  | 0% | 1060.9581
70% | 0.9557% | 41.9762 | [7 empty] | 5% |  | 0% |  | 0% | 0
65% | 1.541% | 67.6914 | [7 empty] | 9.992e-14% |  | 0% |  | 0% | 0
60% | 2.247% | 98.7009 | [7 empty] | Total E@R | 0 | Total E@R | 1040.3576 | Total E@R | 112113.1862
55% | 3.496% | 153.5347 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.97209 | Total WE@R | 0.096584
50% | 5.881% | 258.2862
45% | 11.13% | 488.9664 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 21.13% | 928.0152 |  |  |  |  | 100% | 0 | 66.7236
35% | 34.85% | 1530.4309 |  |  |  |  | 99% | 0.8916 | 66.0564 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 59.02% | 2592.3162 |  |  |  |  | 98% | 3.5664 | 65.3891
25% | 83.32% | 3659.4958 |  |  |  |  | 97% | 4.7552 | 64.7219 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 91.2% | 4005.5161 |  |  |  |  | 95% | 7.7272 | 63.3874 | 100% |  | 0% |  | 0%
15% | 97.48% | 4281.1979 |  |  |  |  | 90% | 39.2302 | 60.0513 | 99% |  | 0% | 16.3964 | 0% | 59.193
10% | 99.99% | 4391.6218 |  |  |  |  | 85% | 117.6906 | 56.7151 | 98% |  | 0% | 47.4046 | 0% | 175.7944
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 268.3703 | 53.3789 | 97% |  | 0% | 20.2755 | 0% | 77.3376
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 455.9026 | 50.0427 | 95% |  | 0% | 47.7142 | 0% | 190.3695
[7 empty] | 70% | 690.9866 | 46.7065 | 90% |  | 0% | 432.201 | 0% | 1944.3472
[7 empty] | 65% | 967.6784 | 43.3703 | 85% |  | 0% | 814.6671 | 0% | 4580.767
[7 empty] | 60% | 1292.8136 | 40.0342 | 80% |  | 0% | 1061.8366 | 0% | 8294.4602
LDC | [6 empty] | 55% | 1647.0743 | 36.698 | 75% |  | 0% | 695.8947 | 0% | 9697.4441
[7 empty] | 50% | 2104.1657 | 33.3618 | 70% |  | 0% | 147.0134 | 0% | 11372.1011
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 2736.0097 | 30.0256 | 65% |  | 0% |  | 0% | 12461.7684
100% | 0% | 0 |  |  |  |  | 40% | 3483.7613 | 26.6894 | 60% |  | 0% |  | 0% | 13558.872
99% | 0.0203% | 0.8916 |  |  |  |  | 35% | 3830.2948 | 23.3533 | 55% |  | 0% |  | 0% | 13591.5918
98% | 0.0812% | 3.5664 |  |  |  |  | 30% | 3953.6322 | 20.0171 | 50% |  | 0% |  | 0% | 16011.8628
97% | 0.1083% | 4.7552 |  |  |  |  | 25% | 4060.9208 | 16.6809 | 45% |  | 0% |  | 0% | 20025.4872
95% | 0.1759% | 7.7272 |  |  |  |  | 20% | 4165.2375 | 13.3447 | 40% |  | 0% |  | 0% | 21204.3902
90% | 0.8932% | 39.2302 |  |  |  |  | 15% | 4270.4458 | 10.0085 | 35% |  | 0% |  | 0% | 8670.7375
85% | 2.68% | 117.6906 |  |  |  |  | 10% | 4373.8709 | 6.6724 | 30% |  | 0% |  | 0% | 2674.5928
80% | 6.11% | 268.3703 |  |  |  |  | 5% | 4391.7028 | 3.3362 | 25% |  | 0% |  | 0% | 1968.6391
75% | 10.38% | 455.9026 |  |  |  |  | 9.992e-14% | 4391.7028 | 6.667e-14 | 20% |  | 0% |  | 0% | 1566.0869
70% | 15.73% | 690.9866 | [7 empty] | 15% |  | 0% |  | 0% | 1228.4784
65% | 22.03% | 967.6784 | [7 empty] | 10% |  | 0% |  | 0% | 862.612
60% | 29.44% | 1292.8136 | [7 empty] | 5% |  | 0% |  | 0% | 89.2357
55% | 37.5% | 1647.0743 | [7 empty] | 9.992e-14% |  | 0% |  | 0% | 0
50% | 47.91% | 2104.1657 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 3283.4036 | Total E@R | 150306.169
45% | 62.3% | 2736.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 6.0821 | Total WE@R | 0.2567
40% | 79.32% | 3483.7613 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 87.21% | 3830.2948 |  |  |  |  | 100% | 0 | 69.9866 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 90.02% | 3953.6322 |  |  |  |  | 99% | 0.8916 | 69.2868
25% | 92.46% | 4060.9208 |  |  |  |  | 98% | 3.5664 | 68.5869 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 94.84% | 4165.2375 |  |  |  |  | 97% | 4.7552 | 67.887 | 100% |  | 100% |  | 100%
15% | 97.23% | 4270.4458 |  |  |  |  | 95% | 7.7272 | 66.4873 | 99% |  | 99% | 19.2912 | 99% | 62.0878
10% | 99.59% | 4373.8709 |  |  |  |  | 90% | 39.2302 | 62.988 | 98% |  | 98% | 56.0016 | 98% | 184.3914
5% | 99.99% | 4391.7028 |  |  |  |  | 85% | 117.6906 | 59.4886 | 97% |  | 97% | 24.0576 | 97% | 81.1197
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 268.3703 | 55.9893 | 95% |  | 95% | 57.024 | 95% | 199.6793
[7 empty] | 75% | 455.9026 | 52.49 | 90% |  | 90% | 527.2868 | 90% | 2039.433
[7 empty] | 70% | 690.9866 | 48.9907 | 85% |  | 85% | 1038.6836 | 85% | 4804.7835
[7 empty] | 65% | 967.6784 | 45.4913 | 80% |  | 80% | 1467.4664 | 80% | 8700.09
LDC | [6 empty] | 60% | 1292.8136 | 41.992 | 75% |  | 75% | 1170.1356 | 75% | 10171.685
[7 empty] | 55% | 1647.0743 | 38.4927 | 70% |  | 70% | 644.2048 | 70% | 11928.2389
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 2104.1657 | 34.9933 | 65% |  | 65% | 38.7992 | 65% | 13071.195
100% | 0% | 0 |  |  |  |  | 45% | 2736.0097 | 31.494 | 60% |  | 60% |  | 60% | 14221.951
99% | 0.0203% | 0.8916 |  |  |  |  | 40% | 3483.7613 | 27.9947 | 55% |  | 55% |  | 55% | 14256.2709
98% | 0.0812% | 3.5664 |  |  |  |  | 35% | 3830.2948 | 24.4953 | 50% |  | 50% |  | 50% | 16794.9022
97% | 0.1083% | 4.7552 |  |  |  |  | 30% | 3953.6322 | 20.996 | 45% |  | 45% |  | 45% | 21004.8077
95% | 0.1759% | 7.7272 |  |  |  |  | 25% | 4060.9208 | 17.4967 | 40% |  | 40% |  | 40% | 22241.3634
90% | 0.8932% | 39.2302 |  |  |  |  | 20% | 4165.2375 | 13.9973 | 35% |  | 35% |  | 35% | 9094.7687
85% | 2.68% | 117.6906 |  |  |  |  | 15% | 4270.4458 | 10.498 | 30% |  | 30% |  | 30% | 2805.3903
80% | 6.11% | 268.3703 |  |  |  |  | 10% | 4373.8709 | 6.9987 | 25% |  | 25% |  | 25% | 2064.9129
75% | 10.38% | 455.9026 |  |  |  |  | 5% | 4391.7028 | 3.4993 | 20% |  | 20% |  | 20% | 1642.6743
70% | 15.73% | 690.9866 |  |  |  |  | 9.992e-14% | 4391.7028 | 6.9931e-14 | 15% |  | 15% |  | 15% | 1288.5556
65% | 22.03% | 967.6784 | [7 empty] | 10% |  | 10% |  | 10% | 904.7969
60% | 29.44% | 1292.8136 | [7 empty] | 5% |  | 5% |  | 5% | 93.5997
55% | 37.5% | 1647.0743 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0 | 9.992e-14% | 0
50% | 47.91% | 2104.1657 | [7 empty] | Total E@R | 0 | Total E@R | 5042.9508 | Total E@R | 157656.6971
45% | 62.3% | 2736.0097 | [7 empty] | Total WE@R | 0 | Total WE@R | 4.0035 | Total WE@R | 0.1154
40% | 79.32% | 3483.7613
35% | 87.21% | 3830.2948
30% | 90.02% | 3953.6322
25% | 92.46% | 4060.9208
20% | 94.84% | 4165.2375
15% | 97.23% | 4270.4458
10% | 99.59% | 4373.8709
5% | 99.99% | 4391.7028
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 93.2 |  |  | Year | 2031
SCR (N-1) | 45.2 |  |  | SCR (N) | 93.2
SCR (N-2) | 0 |  |  | SCR (N-1) | 45.2
WCR (N) | 93.2 |  |  | SCR (N-2) | 0
WCR (N-1) | 48 |  |  | WCR (N) | 93.2
WCR (N-2) | 0 |  |  | WCR (N-1) | 48
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.013196 | 0.015196 | 0.045845 | 0.14835 | 0.26925 | 0.41424 | 0.60707 | 0.82412 | 1.1004 | 1.3183 | 1.6088 | 2.092 | 2.1294 | 2.9276 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799
Total EUE (MWh) | 0.3052 | 0.35146 | 1.0603 | 3.431 | 6.2272 | 9.5806 | 14.0402 | 19.0601 | 25.4503 | 30.4883 | 37.2088 | 48.3835 | 49.2485 | 67.7097 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341
Residual Values
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.013196 | 0.015196 | 0.045845 | 0.14835 | 0.022909 | 0.033138 | 0.050148 | 0.077189 | 0.12283 | 0.16254 | 0.2236 | 0.353 | 0.34207 | 0.59791 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358 | 0.99358
Total EUE (MWh) | 0.3052 | 0.35146 | 1.0603 | 3.431 | 0.52985 | 0.76641 | 1.1598 | 1.7852 | 2.8408 | 3.7593 | 5.1713 | 8.1641 | 7.9113 | 13.8283 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.013196 | 0.015196 | 0.045845 | 0.035184 | 0.014573 | 0.019194 | 0.024844 | 0.032161 | 0.041788 | 0.051736 | 0.066886 | 0.097534 | 0.10417 | 0.17521 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992
Total EUE (MWh) | 0.3052 | 0.35146 | 1.0603 | 0.81374 | 0.33704 | 0.44392 | 0.57459 | 0.74382 | 0.96648 | 1.1965 | 1.5469 | 2.2558 | 2.4092 | 4.0522 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.013196 | 0.015196 | 0.045845 | 0.00015592 | 0.00029885 | 0.00048523 | 0.00075478 | 0.0010878 | 0.0015432 | 0.0019756 | 0.0025584 | 0.0035244 | 0.003837 | 0.0055628 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798 | 0.007798
Total EUE (MWh) | 0.3052 | 0.35146 | 1.0603 | 0.0036061 | 0.0069116 | 0.011222 | 0.017456 | 0.025158 | 0.03569 | 0.045691 | 0.05917 | 0.081513 | 0.08874 | 0.12865 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.013196 | 0.015196 | 0.045845 | 0.035184 | 0.014573 | 0.019194 | 0.024844 | 0.032161 | 0.041788 | 0.051736 | 0.066886 | 0.097534 | 0.10417 | 0.17521 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992 | 0.32992
Total EUE (MWh) | 0.3052 | 0.35146 | 1.0603 | 0.81374 | 0.33704 | 0.44392 | 0.57459 | 0.74382 | 0.96648 | 1.1965 | 1.5469 | 2.2558 | 2.4092 | 4.0522 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.013196 | 0.015196 | 0.045845 | 0.14835 | 0.26925 | 0.41424 | 0.60707 | 0.82412 | 1.1004 | 1.3183 | 1.6088 | 2.092 | 2.1294 | 2.9276 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799
Total EUE (MWh) | 0.3052 | 0.35146 | 1.0603 | 3.431 | 6.2272 | 9.5806 | 14.0402 | 19.0601 | 25.4503 | 30.4883 | 37.2088 | 48.3835 | 49.2485 | 67.7097 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.013196 | 0.015196 | 0.045845 | 0.14835 | 0.26925 | 0.41424 | 0.60707 | 0.82412 | 1.1004 | 1.3183 | 1.6088 | 2.092 | 2.1294 | 2.9276 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799
Total EUE (MWh) | 0.3052 | 0.35146 | 1.0603 | 3.431 | 6.2272 | 9.5806 | 14.0402 | 19.0601 | 25.4503 | 30.4883 | 37.2088 | 48.3835 | 49.2485 | 67.7097 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.013196 | 0.015196 | 0.045845 | 0.14835 | 0.26925 | 0.41424 | 0.60707 | 0.82412 | 1.1004 | 1.3183 | 1.6088 | 2.092 | 2.1294 | 2.9276 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799 | 3.8799
Total EUE (MWh) | 0.3052 | 0.35146 | 1.0603 | 3.431 | 6.2272 | 9.5806 | 14.0402 | 19.0601 | 25.4503 | 30.4883 | 37.2088 | 48.3835 | 49.2485 | 67.7097 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341

## Key Model Assumption & Inputs
Select ZSS & Region | OFR | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
Low | 90% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1B New PHS ZSS + Three new feeders | 1B New PHS ZSS + Three new feeders
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Option 6 -
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N |  |  |  | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Added Capacity (MVA) Option 4 N-1 |  |  |  | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Added Capacity (MVA) Option 4 N-2 |  |  |  | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Transfers (MVA) Option 3 |  |  |  | 7.25 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Transfers (MVA) Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Transfers (MVA) Option 5 |  |  |  | 7.25 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN_Old | 2 | 66 | 87.3 | 95.3 | 44.6 | 48.9 | 0 | 0 | Loss of T1 |  | 22 | 12
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
CRE | 2 | 66 | 84.3 | 93.8 | 41.1 | 46.3 | 0 | 0 | Loss of T2 or T3 |  | 22 | 12
EPG | 3 | 99 | 123.1 | 139.9 | 87.8 | 98.1 | 43.9 | 49.05 | Loss of T3 | Using Highest value | 22
KLO | 2 | 66 | 97.5 | 97.5 | 49.1 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22.44 | 6
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12
WGI | 3 | 40.5 | 55.8 | 56.8 | 35.3 | 36.1 | 17.65 | 18.05

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | cre | 1
zone_sub | cyn | 1
zone_sub | epg | 1
zone_sub | klo | 0.99
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1
zone_sub | wgi | 0.99

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | OFR
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 56.9594 | 61.9907 | 68.9791 | 74.0072 | 76.6284 | 78.9811 | 80.4506 | 82.1352 | 83.4813 | 84.3346 | 86.446 | 87.894 | 88.627 | 90.0391 | 89.5765
Summer POE10 | 10 |  |  | 64.073 | 69.589 | 76.597 | 81.5678 | 84.5283 | 86.8984 | 88.8048 | 90.6365 | 92.2256 | 92.9929 | 94.1573 | 95.4952 | 96.8516 | 98.5806 | 98.8168
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 50.4065 | 56.1183 | 63.2802 | 69.3039 | 72.5305 | 74.8582 | 77.5373 | 79.5294 | 81.7407 | 82.8706 | 83.8526 | 86.3425 | 84.7668 | 88.8524 | 94.1939
Winter POE10 | 10 |  |  | 53.6497 | 59.4536 | 66.5595 | 72.8129 | 76.0509 | 78.6773 | 81.1629 | 83.2732 | 85.4834 | 86.4197 | 87.7259 | 90.1815 | 89.3155 | 92.5351 | 94.3753
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | OFR | 0 | 3.3 | 3.25 | 3.2 | 3.15 | 3.11 | 3.06 | 3.01 | 2.97 | 2.92 | 2.88 | 2.84 | 2.79 | 2.75 | 2.71
|  | PowerFactor | 1

## Load Duration Curves
Station
OFR
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.0203% | 0.8916 | 0.01722% | 0.75633 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.0812% | 3.5664 | 0.02583% | 1.1345 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.1083% | 4.7552 | 0.04305% | 1.8908 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.1759% | 7.7272 | 0.07749% | 3.4035 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 0.8932% | 39.2302 | 0.2066% | 9.0759 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 2.68% | 117.6906 | 0.3702% | 16.2611 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 6.11% | 268.3703 | 0.5683% | 24.9588 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 10.38% | 455.9026 | 0.7491% | 32.9003 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 15.73% | 690.9866 | 0.9557% | 41.9762 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 22.03% | 967.6784 | 1.541% | 67.6914 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 29.44% | 1292.8136 | 2.247% | 98.7009 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 37.5% | 1647.0743 | 3.496% | 153.5347 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 47.91% | 2104.1657 | 5.881% | 258.2862 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 62.3% | 2736.0097 | 11.13% | 488.9664 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 79.32% | 3483.7613 | 21.13% | 928.0152 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 87.21% | 3830.2948 | 34.85% | 1530.4309 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 90.02% | 3953.6322 | 59.02% | 2592.3162 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 92.46% | 4060.9208 | 83.32% | 3659.4958 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 94.84% | 4165.2375 | 91.2% | 4005.5161 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 97.23% | 4270.4458 | 97.48% | 4281.1979 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.59% | 4373.8709 | 99.99% | 4391.6218 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.0203% | 0.8916 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.0812% | 3.5664 | 0.00861% | 0.37816 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.1083% | 4.7552 | 0.01722% | 0.75633 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.1759% | 7.7272 | 0.04305% | 1.8908 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 0.8932% | 39.2302 | 0.1033% | 4.538 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 2.68% | 117.6906 | 0.2066% | 9.0759 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 6.11% | 268.3703 | 0.6286% | 27.606 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 10.38% | 455.9026 | 1.309% | 57.481 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 15.73% | 690.9866 | 2.419% | 106.2642 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 22.03% | 967.6784 | 4.598% | 201.9397 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 29.44% | 1292.8136 | 9.17% | 402.745 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 37.5% | 1647.0743 | 14.93% | 655.7369 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 47.91% | 2104.1657 | 22.35% | 981.7145 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 62.3% | 2736.0097 | 36.95% | 1622.7029 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 79.32% | 3483.7613 | 55.62% | 2442.9413 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 87.21% | 3830.2948 | 68.46% | 3006.7842 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 90.02% | 3953.6322 | 74.6% | 3276.4154 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 92.46% | 4060.9208 | 78.93% | 3466.632 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 94.84% | 4165.2375 | 84.56% | 3713.9514 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 97.23% | 4270.4458 | 92.06% | 4043.3325 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.59% | 4373.8709 | 99.06% | 4350.7801 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 1 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 3 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 93.2 | 93.2 | 93.2 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4
SCR N Rating (MVA) - Option 4 | 93.2 | 93.2 | 93.2 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4
Capacity Added (MVA) | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 5 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 6 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 7 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N Rating (MVA) - Option 8 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 1 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 3 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 48 | 48 | 48 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2 | 93.2
SCR N-1 Rating (MVA) - Option 4 | 45.2 | 45.2 | 45.2 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4
Capacity Added (MVA) | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 5 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 6 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 7 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
SCR N-1 Rating (MVA) - Option 8 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Capacity Added (MVA) | 0 | 0 | 0 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 45.3659 | 50.5065 | 56.9522 | 62.3735 | 65.2775 | 67.3724 | 69.7836 | 71.5764 | 73.5666 | 74.5836 | 75.4673 | 77.7082 | 76.2901 | 79.9671 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745 | 84.7745
Maximum Demand (MVA) - P10 | 48.2848 | 53.5082 | 59.9035 | 65.5316 | 68.4458 | 70.8096 | 73.0466 | 74.9459 | 76.9351 | 77.7777 | 78.9533 | 81.1633 | 80.3839 | 83.2816 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377 | 84.9377
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 3.3 | 3.25 | 3.2 | 3.15 | 3.11 | 3.06 | 3.01 | 2.97 | 2.92 | 2.88 | 2.84 | 2.79 | 2.75 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 51.2635 | 55.7916 | 62.0812 | 66.6065 | 68.9656 | 71.083 | 72.4055 | 73.9217 | 75.1332 | 75.9012 | 77.8014 | 79.1046 | 79.7643 | 81.0352 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189 | 80.6189
Maximum Demand (MVA) - P10 | 57.6657 | 62.6301 | 68.9373 | 73.411 | 76.0755 | 78.2086 | 79.9243 | 81.5729 | 83.003 | 83.6936 | 84.7416 | 85.9457 | 87.1664 | 88.7226 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351 | 88.9351
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 0 | 3.3 | 3.25 | 3.2 | 3.15 | 3.11 | 3.06 | 3.01 | 2.97 | 2.92 | 2.88 | 2.84 | 2.79 | 2.75 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71 | 2.71
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251
Option 2 - 1B New PHS ZSS + Three new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 47.6275 | 49.7624 | 52.2236 | 54.0664 | 56.0966 | 57.1636 | 58.0873 | 60.3682 | 59.0001 | 62.7171 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 50.7958 | 53.1996 | 55.4866 | 57.4359 | 59.4651 | 60.3577 | 61.5733 | 63.8233 | 63.0939 | 66.0316 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 51.3156 | 53.473 | 54.8455 | 56.4117 | 57.6632 | 58.4812 | 60.4214 | 61.7646 | 62.4743 | 63.7852 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 58.4255 | 60.5986 | 62.3643 | 64.0629 | 65.533 | 66.2736 | 67.3616 | 68.6057 | 69.8764 | 71.4726 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 7.25 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 45.3659 | 47.2065 | 53.7022 | 51.9235 | 40.3775 | 42.5124 | 44.9736 | 46.8164 | 48.8466 | 49.9136 | 50.8373 | 53.1182 | 51.7501 | 55.4671 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 48.2848 | 50.2082 | 56.6535 | 55.0816 | 43.5458 | 45.9496 | 48.2366 | 50.1859 | 52.2151 | 53.1077 | 54.3233 | 56.5733 | 55.8439 | 58.7816 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 51.2635 | 52.4916 | 58.8312 | 56.1565 | 44.0656 | 46.223 | 47.5955 | 49.1617 | 50.4132 | 51.2312 | 53.1714 | 54.5146 | 55.2243 | 56.5352 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 57.6657 | 59.3301 | 65.6873 | 62.961 | 51.1755 | 53.3486 | 55.1143 | 56.8129 | 58.283 | 59.0236 | 60.1116 | 61.3557 | 62.6264 | 64.2226 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 7.25 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75 | 21.75
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 45.3659 | 47.2065 | 53.7022 | 51.9235 | 40.3775 | 42.5124 | 44.9736 | 46.8164 | 48.8466 | 49.9136 | 50.8373 | 53.1182 | 51.7501 | 55.4671 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 48.2848 | 50.2082 | 56.6535 | 55.0816 | 43.5458 | 45.9496 | 48.2366 | 50.1859 | 52.2151 | 53.1077 | 54.3233 | 56.5733 | 55.8439 | 58.7816 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 51.2635 | 52.4916 | 58.8312 | 56.1565 | 44.0656 | 46.223 | 47.5955 | 49.1617 | 50.4132 | 51.2312 | 53.1714 | 54.5146 | 55.2243 | 56.5352 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 57.6657 | 59.3301 | 65.6873 | 62.961 | 51.1755 | 53.3486 | 55.1143 | 56.8129 | 58.283 | 59.0236 | 60.1116 | 61.3557 | 62.6264 | 64.2226 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751
Option 6 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 100% | 0 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
99% | 0.8916 | 44.9122 | 46.7344 | 53.1652 | 58.5818 | 61.5062 | 63.6197 | 66.0564 | 67.8808 | 69.8906 | 70.9469 | 71.8615 | 74.1195 | 72.7651 | 76.445 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 99% | 0.8916 | 47.8019 | 49.7061 | 56.087 | 61.7083 | 64.6429 | 67.0226 | 69.2868 | 71.2166 | 73.2255 | 74.1092 | 75.3125 | 77.5401 | 76.818 | 79.7262 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055
98% | 3.5664 | 44.4586 | 46.2623 | 52.6282 | 57.99 | 60.8849 | 62.9771 | 65.3891 | 67.1951 | 69.1847 | 70.2303 | 71.1356 | 73.3709 | 72.0301 | 75.6728 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 98% | 3.5664 | 47.3191 | 49.204 | 55.5204 | 61.085 | 63.9899 | 66.3456 | 68.5869 | 70.4972 | 72.4858 | 73.3606 | 74.5518 | 76.7569 | 76.0421 | 78.9209 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832
97% | 4.7552 | 44.0049 | 45.7903 | 52.0911 | 57.3983 | 60.2637 | 62.3345 | 64.7219 | 66.5095 | 68.4787 | 69.5136 | 70.4097 | 72.6222 | 71.2951 | 74.9006 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 97% | 4.7552 | 46.8362 | 48.702 | 54.9539 | 60.4617 | 63.337 | 65.6686 | 67.887 | 69.7778 | 71.7461 | 72.612 | 73.7911 | 75.9736 | 75.2661 | 78.1156 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609
95% | 7.7272 | 43.0976 | 44.8461 | 51.0171 | 56.2148 | 59.0211 | 61.0492 | 63.3874 | 65.1381 | 67.0668 | 68.0804 | 68.958 | 71.1248 | 69.8251 | 73.3563 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 95% | 7.7272 | 45.8705 | 47.6978 | 53.8208 | 59.215 | 62.031 | 64.3146 | 66.4873 | 68.3391 | 70.2668 | 71.1149 | 72.2696 | 74.4072 | 73.7142 | 76.505 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164
90% | 39.2302 | 40.8293 | 42.4858 | 48.332 | 53.2562 | 55.9147 | 57.8361 | 60.0513 | 61.7098 | 63.5369 | 64.4972 | 65.3286 | 67.3814 | 66.1501 | 69.4954 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 90% | 39.2302 | 43.4563 | 45.1874 | 50.9882 | 56.0984 | 58.7663 | 60.9296 | 62.988 | 64.7423 | 66.5686 | 67.372 | 68.4659 | 70.491 | 69.8345 | 72.4784 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005
85% | 117.6906 | 38.561 | 40.1255 | 45.6469 | 50.2975 | 52.8084 | 54.623 | 56.7151 | 58.2815 | 60.0071 | 60.914 | 61.6992 | 63.638 | 62.4751 | 65.6346 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 85% | 117.6906 | 41.042 | 42.677 | 48.1555 | 52.9819 | 55.5015 | 57.5446 | 59.4886 | 61.1455 | 62.8703 | 63.6291 | 64.6623 | 66.5748 | 65.9548 | 68.4518 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936
80% | 268.3703 | 36.2927 | 37.7652 | 42.9618 | 47.3388 | 49.702 | 51.4099 | 53.3789 | 54.8532 | 56.4773 | 57.3308 | 58.0699 | 59.8946 | 58.8001 | 61.7737 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 80% | 268.3703 | 38.6278 | 40.1666 | 45.3228 | 49.8653 | 52.2367 | 54.1596 | 55.9893 | 57.5487 | 59.1721 | 59.8862 | 60.8586 | 62.6587 | 62.0751 | 64.4253 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822
75% | 455.9026 | 34.0244 | 35.4048 | 40.2767 | 44.3801 | 46.5956 | 48.1968 | 50.0427 | 51.4248 | 52.9474 | 53.7477 | 54.4405 | 56.1512 | 55.1251 | 57.9128 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 75% | 455.9026 | 36.2136 | 37.6562 | 42.4901 | 46.7487 | 48.9719 | 50.7747 | 52.49 | 53.9519 | 55.4738 | 56.1433 | 57.055 | 58.7425 | 58.1954 | 60.3987 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708
70% | 690.9866 | 31.7561 | 33.0445 | 37.5915 | 41.4215 | 43.4892 | 44.9837 | 46.7065 | 47.9965 | 49.4176 | 50.1645 | 50.8111 | 52.4078 | 51.4501 | 54.052 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 70% | 690.9866 | 33.7993 | 35.1457 | 39.6575 | 43.6321 | 45.7071 | 47.3897 | 48.9907 | 50.3551 | 51.7756 | 52.4004 | 53.2513 | 54.8263 | 54.3158 | 56.3721 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594
65% | 967.6784 | 29.4878 | 30.6842 | 34.9064 | 38.4628 | 40.3829 | 41.7705 | 43.3703 | 44.5682 | 45.8878 | 46.5813 | 47.1818 | 48.6643 | 47.775 | 50.1911 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 65% | 967.6784 | 31.3851 | 32.6353 | 36.8248 | 40.5155 | 42.4423 | 44.0047 | 45.4913 | 46.7584 | 48.0773 | 48.6575 | 49.4476 | 50.9102 | 50.4361 | 52.3455 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448
60% | 1292.8136 | 27.2195 | 28.3239 | 32.2213 | 35.5041 | 37.2765 | 38.5574 | 40.0342 | 41.1399 | 42.358 | 42.9981 | 43.5524 | 44.9209 | 44.1 | 46.3303 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 60% | 1292.8136 | 28.9709 | 30.1249 | 33.9921 | 37.399 | 39.1775 | 40.6197 | 41.992 | 43.1616 | 44.3791 | 44.9146 | 45.644 | 46.994 | 46.5564 | 48.3189 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366
55% | 1647.0743 | 24.9512 | 25.9636 | 29.5362 | 32.5454 | 34.1701 | 35.3443 | 36.698 | 37.7115 | 38.8281 | 39.415 | 39.923 | 41.1775 | 40.425 | 42.4694 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 55% | 1647.0743 | 26.5566 | 27.6145 | 31.1594 | 34.2824 | 35.9127 | 37.2348 | 38.4927 | 39.5648 | 40.6808 | 41.1718 | 41.8403 | 43.0778 | 42.6767 | 44.2924 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253
50% | 2104.1657 | 22.6829 | 23.6032 | 26.8511 | 29.5868 | 31.0637 | 32.1312 | 33.3618 | 34.2832 | 35.2983 | 35.8318 | 36.2937 | 37.4341 | 36.75 | 38.6086 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 50% | 2104.1657 | 24.1424 | 25.1041 | 28.3268 | 31.1658 | 32.6479 | 33.8498 | 34.9933 | 35.968 | 36.9826 | 37.4289 | 38.0366 | 39.1617 | 38.797 | 40.2658 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139
45% | 2736.0097 | 20.4146 | 21.2429 | 24.166 | 26.6281 | 27.9574 | 28.9181 | 30.0256 | 30.8549 | 31.7685 | 32.2486 | 32.6643 | 33.6907 | 33.075 | 34.7477 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 45% | 2736.0097 | 21.7281 | 22.5937 | 25.4941 | 28.0492 | 29.3831 | 30.4648 | 31.494 | 32.3712 | 33.2843 | 33.686 | 34.233 | 35.2455 | 34.9173 | 36.2392 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025
40% | 3483.7613 | 18.1464 | 18.8826 | 21.4809 | 23.6694 | 24.851 | 25.7049 | 26.6894 | 27.4266 | 28.2386 | 28.6654 | 29.0349 | 29.9473 | 29.4 | 30.8868 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 40% | 3483.7613 | 19.3139 | 20.0833 | 22.6614 | 24.9326 | 26.1183 | 27.0798 | 27.9947 | 28.7744 | 29.586 | 29.9431 | 30.4293 | 31.3293 | 31.0376 | 32.2126 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911
35% | 3830.2948 | 15.8781 | 16.5223 | 18.7958 | 20.7107 | 21.7446 | 22.4918 | 23.3533 | 23.9983 | 24.7088 | 25.0822 | 25.4056 | 26.2039 | 25.725 | 27.026 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 35% | 3830.2948 | 16.8997 | 17.5729 | 19.8287 | 21.8161 | 22.8535 | 23.6948 | 24.4953 | 25.1776 | 25.8878 | 26.2002 | 26.6256 | 27.4132 | 27.1579 | 28.186 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797
30% | 3953.6322 | 13.6098 | 14.1619 | 16.1107 | 17.7521 | 18.6382 | 19.2787 | 20.0171 | 20.5699 | 21.179 | 21.4991 | 21.7762 | 22.4605 | 22.05 | 23.1651 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 30% | 3953.6322 | 14.4854 | 15.0625 | 16.9961 | 18.6995 | 19.5888 | 20.3099 | 20.996 | 21.5808 | 22.1895 | 22.4573 | 22.822 | 23.497 | 23.2782 | 24.1595 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683
25% | 4060.9208 | 11.3415 | 11.8016 | 13.4256 | 14.7934 | 15.5319 | 16.0656 | 16.6809 | 17.1416 | 17.6491 | 17.9159 | 18.1468 | 18.7171 | 18.375 | 19.3043 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 25% | 4060.9208 | 12.0712 | 12.5521 | 14.1634 | 15.5829 | 16.324 | 16.9249 | 17.4967 | 17.984 | 18.4913 | 18.7144 | 19.0183 | 19.5808 | 19.3985 | 20.1329 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569
20% | 4165.2375 | 9.0732 | 9.4413 | 10.7404 | 11.8347 | 12.4255 | 12.8525 | 13.3447 | 13.7133 | 14.1193 | 14.3327 | 14.5175 | 14.9736 | 14.7 | 15.4434 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 20% | 4165.2375 | 9.657 | 10.0416 | 11.3307 | 12.4663 | 13.0592 | 13.5399 | 13.9973 | 14.3872 | 14.793 | 14.9715 | 15.2147 | 15.6647 | 15.5188 | 16.1063 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455
15% | 4270.4458 | 6.8049 | 7.081 | 8.0553 | 8.876 | 9.3191 | 9.6394 | 10.0085 | 10.285 | 10.5895 | 10.7495 | 10.8881 | 11.2302 | 11.025 | 11.5826 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 15% | 4270.4458 | 7.2427 | 7.5312 | 8.498 | 9.3497 | 9.7944 | 10.1549 | 10.498 | 10.7904 | 11.0948 | 11.2287 | 11.411 | 11.7485 | 11.6391 | 12.0797 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342
10% | 4373.8709 | 4.5366 | 4.7206 | 5.3702 | 5.9174 | 6.2127 | 6.4262 | 6.6724 | 6.8566 | 7.0597 | 7.1664 | 7.2587 | 7.4868 | 7.35 | 7.7217 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 10% | 4373.8709 | 4.8285 | 5.0208 | 5.6654 | 6.2332 | 6.5296 | 6.77 | 6.9987 | 7.1936 | 7.3965 | 7.4858 | 7.6073 | 7.8323 | 7.7594 | 8.0532 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228
5% | 4391.7028 | 2.2683 | 2.3603 | 2.6851 | 2.9587 | 3.1064 | 3.2131 | 3.3362 | 3.4283 | 3.5298 | 3.5832 | 3.6294 | 3.7434 | 3.675 | 3.8609 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 5% | 4391.7028 | 2.4142 | 2.5104 | 2.8327 | 3.1166 | 3.2648 | 3.385 | 3.4993 | 3.5968 | 3.6983 | 3.7429 | 3.8037 | 3.9162 | 3.8797 | 4.0266 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114
9.992e-14% | 4391.7028 | 4.533e-14 | 4.7169e-14 | 5.3659e-14 | 5.9126e-14 | 6.2078e-14 | 6.4211e-14 | 6.667e-14 | 6.8512e-14 | 7.054e-14 | 7.1606e-14 | 7.2529e-14 | 7.4808e-14 | 7.3441e-14 | 7.7155e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 9.992e-14% | 4391.7028 | 4.8246e-14 | 5.0168e-14 | 5.6608e-14 | 6.2282e-14 | 6.5244e-14 | 6.7645e-14 | 6.9931e-14 | 7.1878e-14 | 7.3906e-14 | 7.4798e-14 | 7.6012e-14 | 7.8261e-14 | 7.7532e-14 | 8.0467e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 100% | 0 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251
99% | 0 | 50.7508 | 51.9667 | 58.2429 | 62.7724 | 65.1574 | 67.2933 | 68.6521 | 70.2026 | 71.4415 | 72.2514 | 74.1722 | 75.502 | 76.2046 | 77.5024 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 99% | 0.75633 | 57.089 | 58.7368 | 65.0304 | 69.5089 | 72.1962 | 74.3476 | 76.0957 | 77.7773 | 79.2327 | 79.9659 | 81.0429 | 82.2746 | 83.5326 | 85.1128 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629
98% | 0.37816 | 50.2382 | 51.4418 | 57.6546 | 62.1384 | 64.4993 | 66.6135 | 67.9586 | 69.4935 | 70.7199 | 71.5215 | 73.423 | 74.7393 | 75.4348 | 76.7195 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 98% | 1.1345 | 56.5124 | 58.1435 | 64.3735 | 68.8068 | 71.467 | 73.5966 | 75.327 | 76.9916 | 78.4324 | 79.1581 | 80.2243 | 81.4436 | 82.6889 | 84.2531 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006
97% | 0.75633 | 49.7256 | 50.9169 | 57.0663 | 61.5043 | 63.8411 | 65.9338 | 67.2652 | 68.7844 | 69.9983 | 70.7917 | 72.6738 | 73.9767 | 74.6651 | 75.9367 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 97% | 1.8908 | 55.9357 | 57.5502 | 63.7166 | 68.1047 | 70.7377 | 72.8456 | 74.5584 | 76.206 | 77.6321 | 78.3504 | 79.4057 | 80.6125 | 81.8451 | 83.3934 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384
95% | 1.8908 | 48.7003 | 49.867 | 55.8896 | 60.2362 | 62.5248 | 64.5743 | 65.8783 | 67.3661 | 68.555 | 69.3321 | 71.1753 | 72.4514 | 73.1256 | 74.371 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 95% | 3.4035 | 54.7824 | 56.3636 | 62.4029 | 66.7005 | 69.2792 | 71.3437 | 73.0211 | 74.6347 | 76.0314 | 76.7349 | 77.7685 | 78.9504 | 80.1576 | 81.6739 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139
90% | 4.538 | 46.1371 | 47.2424 | 52.9481 | 57.0659 | 59.234 | 61.1757 | 62.411 | 63.8205 | 64.9469 | 65.683 | 67.4293 | 68.6381 | 69.2769 | 70.4567 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 90% | 9.0759 | 51.8991 | 53.3971 | 59.1185 | 63.1899 | 65.6329 | 67.5887 | 69.1779 | 70.7066 | 72.0297 | 72.6962 | 73.6754 | 74.7951 | 75.9388 | 77.3753 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026
85% | 9.0759 | 43.574 | 44.6179 | 50.0065 | 53.8955 | 55.9433 | 57.777 | 58.9437 | 60.275 | 61.3387 | 62.034 | 63.6832 | 64.8249 | 65.4282 | 66.5424 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 85% | 16.2611 | 49.0158 | 50.4306 | 55.8342 | 59.6794 | 61.9866 | 63.8338 | 65.3347 | 66.7785 | 68.0281 | 68.6576 | 69.5823 | 70.6398 | 71.72 | 73.0767 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913
80% | 27.606 | 41.0108 | 41.9933 | 47.065 | 50.7252 | 52.6525 | 54.3784 | 55.4764 | 56.7294 | 57.7305 | 58.3849 | 59.9371 | 61.0117 | 61.5795 | 62.6282 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 80% | 24.9588 | 46.1325 | 47.4641 | 52.5498 | 56.1688 | 58.3404 | 60.0789 | 61.4915 | 62.8503 | 64.0264 | 64.6189 | 65.4893 | 66.4845 | 67.5011 | 68.778 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801
75% | 57.481 | 38.4476 | 39.3687 | 44.1234 | 47.5549 | 49.3617 | 50.9797 | 52.0092 | 53.1838 | 54.1224 | 54.7359 | 56.1911 | 57.1985 | 57.7307 | 58.7139 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 75% | 32.9003 | 43.2493 | 44.4976 | 49.2655 | 52.6583 | 54.6941 | 56.324 | 57.6482 | 58.9222 | 60.0248 | 60.5802 | 61.3962 | 62.3292 | 63.2823 | 64.4794 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688
70% | 106.2642 | 35.8844 | 36.7441 | 41.1818 | 44.3846 | 46.0709 | 47.5811 | 48.5419 | 49.6382 | 50.5142 | 51.0868 | 52.445 | 53.3852 | 53.882 | 54.7997 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 70% | 41.9762 | 40.366 | 41.531 | 45.9811 | 49.1477 | 51.0478 | 52.569 | 53.805 | 54.994 | 56.0231 | 56.5415 | 57.3031 | 58.174 | 59.0635 | 60.1808 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576
65% | 201.9397 | 33.3213 | 34.1195 | 38.2403 | 41.2142 | 42.7801 | 44.1824 | 45.0746 | 46.0926 | 46.9061 | 47.4378 | 48.6989 | 49.572 | 50.0333 | 50.8854 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 65% | 67.6914 | 37.4827 | 38.5645 | 42.6967 | 45.6372 | 47.4016 | 48.8141 | 49.9618 | 51.0659 | 52.0215 | 52.5028 | 53.21 | 54.0187 | 54.8447 | 55.8822 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463
60% | 402.745 | 30.7581 | 31.495 | 35.2987 | 38.0439 | 39.4894 | 40.7838 | 41.6073 | 42.547 | 43.2979 | 43.7887 | 44.9529 | 45.7588 | 46.1846 | 46.9711 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 60% | 98.7009 | 34.5994 | 35.598 | 39.4124 | 42.1266 | 43.7553 | 45.0592 | 46.1186 | 47.1377 | 48.0198 | 48.4642 | 49.1169 | 49.8634 | 50.6258 | 51.5835 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351
55% | 655.7369 | 28.1949 | 28.8704 | 32.3572 | 34.8736 | 36.1986 | 37.3851 | 38.14 | 39.0014 | 39.6897 | 40.1396 | 41.2068 | 41.9455 | 42.3359 | 43.0569 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 55% | 153.5347 | 31.7161 | 32.6315 | 36.128 | 38.6161 | 40.109 | 41.3042 | 42.2754 | 43.2096 | 44.0182 | 44.4255 | 45.0239 | 45.7081 | 46.407 | 47.2849 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238
50% | 981.7145 | 25.6317 | 26.2458 | 29.4156 | 31.7033 | 32.9078 | 33.9865 | 34.6728 | 35.4559 | 36.0816 | 36.4906 | 37.4607 | 38.1323 | 38.4872 | 39.1426 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 50% | 258.2862 | 28.8328 | 29.665 | 32.8436 | 35.1055 | 36.4627 | 37.5493 | 38.4322 | 39.2814 | 40.0165 | 40.3868 | 40.9308 | 41.5528 | 42.1882 | 42.9863 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126
45% | 1622.7029 | 23.0686 | 23.6212 | 26.474 | 28.5329 | 29.617 | 30.5878 | 31.2055 | 31.9103 | 32.4734 | 32.8415 | 33.7146 | 34.3191 | 34.6384 | 35.2283 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 45% | 488.9664 | 25.9496 | 26.6985 | 29.5593 | 31.595 | 32.8165 | 33.7944 | 34.5889 | 35.3533 | 36.0149 | 36.3481 | 36.8377 | 37.3975 | 37.9694 | 38.6876 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013
40% | 2442.9413 | 20.5054 | 20.9966 | 23.5325 | 25.3626 | 26.3262 | 27.1892 | 27.7382 | 28.3647 | 28.8653 | 29.1925 | 29.9686 | 30.5058 | 30.7897 | 31.3141 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 40% | 928.0152 | 23.0663 | 23.732 | 26.2749 | 28.0844 | 29.1702 | 30.0394 | 30.7457 | 31.4252 | 32.0132 | 32.3094 | 32.7446 | 33.2423 | 33.7506 | 34.389 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49
35% | 3006.7842 | 17.9422 | 18.3721 | 20.5909 | 22.1923 | 23.0355 | 23.7905 | 24.2709 | 24.8191 | 25.2571 | 25.5434 | 26.2225 | 26.6926 | 26.941 | 27.3998 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 35% | 1530.4309 | 20.183 | 20.7655 | 22.9905 | 24.5739 | 25.5239 | 26.2845 | 26.9025 | 27.497 | 28.0116 | 28.2708 | 28.6515 | 29.087 | 29.5317 | 30.0904 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788
30% | 3276.4154 | 15.379 | 15.7475 | 17.6494 | 19.022 | 19.7447 | 20.3919 | 20.8037 | 21.2735 | 21.649 | 21.8943 | 22.4764 | 22.8794 | 23.0923 | 23.4856 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 30% | 2592.3162 | 17.2997 | 17.799 | 19.7062 | 21.0633 | 21.8776 | 22.5296 | 23.0593 | 23.5689 | 24.0099 | 24.2321 | 24.5585 | 24.9317 | 25.3129 | 25.7918 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675
25% | 3466.632 | 12.8159 | 13.1229 | 14.7078 | 15.8516 | 16.4539 | 16.9932 | 17.3364 | 17.7279 | 18.0408 | 18.2453 | 18.7304 | 19.0662 | 19.2436 | 19.5713 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 25% | 3659.4958 | 14.4164 | 14.8325 | 16.4218 | 17.5528 | 18.2314 | 18.7747 | 19.2161 | 19.6407 | 20.0083 | 20.1934 | 20.4654 | 20.7764 | 21.0941 | 21.4931 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563
20% | 3713.9514 | 10.2527 | 10.4983 | 11.7662 | 12.6813 | 13.1631 | 13.5946 | 13.8691 | 14.1823 | 14.4326 | 14.5962 | 14.9843 | 15.2529 | 15.3949 | 15.657 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 20% | 4005.5161 | 11.5331 | 11.866 | 13.1375 | 14.0422 | 14.5851 | 15.0197 | 15.3729 | 15.7126 | 16.0066 | 16.1547 | 16.3723 | 16.6211 | 16.8753 | 17.1945 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245
15% | 4043.3325 | 7.6895 | 7.8737 | 8.8247 | 9.511 | 9.8723 | 10.1959 | 10.4018 | 10.6368 | 10.8245 | 10.9472 | 11.2382 | 11.4397 | 11.5461 | 11.7428 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 15% | 4281.1979 | 8.6499 | 8.8995 | 9.8531 | 10.5317 | 10.9388 | 11.2648 | 11.5296 | 11.7844 | 12.005 | 12.116 | 12.2792 | 12.4658 | 12.6565 | 12.8959 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338
10% | 4350.7801 | 5.1263 | 5.2492 | 5.8831 | 6.3407 | 6.5816 | 6.7973 | 6.9346 | 7.0912 | 7.2163 | 7.2981 | 7.4921 | 7.6265 | 7.6974 | 7.8285 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 10% | 4391.6218 | 5.7666 | 5.933 | 6.5687 | 7.0211 | 7.2925 | 7.5099 | 7.6864 | 7.8563 | 8.0033 | 8.0774 | 8.1862 | 8.3106 | 8.4376 | 8.5973 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225
5% | 4391.6218 | 2.5632 | 2.6246 | 2.9416 | 3.1703 | 3.2908 | 3.3986 | 3.4673 | 3.5456 | 3.6082 | 3.6491 | 3.7461 | 3.8132 | 3.8487 | 3.9143 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 5% | 4391.6218 | 2.8833 | 2.9665 | 3.2844 | 3.5106 | 3.6463 | 3.7549 | 3.8432 | 3.9281 | 4.0017 | 4.0387 | 4.0931 | 4.1553 | 4.2188 | 4.2986 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113
9.992e-14% | 4391.6218 | 5.1223e-14 | 5.245e-14 | 5.8784e-14 | 6.3356e-14 | 6.5763e-14 | 6.7919e-14 | 6.929e-14 | 7.0855e-14 | 7.2105e-14 | 7.2923e-14 | 7.4862e-14 | 7.6204e-14 | 7.6913e-14 | 7.8223e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 9.992e-14% | 4391.6218 | 5.762e-14 | 5.9283e-14 | 6.5635e-14 | 7.0155e-14 | 7.2867e-14 | 7.5039e-14 | 7.6803e-14 | 7.85e-14 | 7.9969e-14 | 8.0709e-14 | 8.1796e-14 | 8.3039e-14 | 8.4309e-14 | 8.5904e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 47.6275 | 49.7624 | 52.2236 | 54.0664 | 56.0966 | 57.1636 | 58.0873 | 60.3682 | 59.0001 | 62.7171 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 67.5645 | 100% | 0 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 50.7958 | 53.1996 | 55.4866 | 57.4359 | 59.4651 | 60.3577 | 61.5733 | 63.8233 | 63.0939 | 66.0316 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277 | 67.7277
99% | 0.8916 | 44.9122 | 46.7344 | 53.1652 | 58.5818 | 47.1512 | 49.2647 | 51.7014 | 53.5258 | 55.5356 | 56.5919 | 57.5065 | 59.7645 | 58.4101 | 62.09 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 66.8889 | 99% | 0.8916 | 47.8019 | 49.7061 | 56.087 | 61.7083 | 50.2879 | 52.6676 | 54.9318 | 56.8616 | 58.8705 | 59.7542 | 60.9575 | 63.1851 | 62.463 | 65.3712 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505 | 67.0505
98% | 3.5664 | 44.4586 | 46.2623 | 52.6282 | 57.99 | 46.6749 | 48.7671 | 51.1791 | 52.9851 | 54.9747 | 56.0203 | 56.9256 | 59.1609 | 57.8201 | 61.4628 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 66.2132 | 98% | 3.5664 | 47.3191 | 49.204 | 55.5204 | 61.085 | 49.7799 | 52.1356 | 54.3769 | 56.2872 | 58.2758 | 59.1506 | 60.3418 | 62.5469 | 61.8321 | 64.7109 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732 | 66.3732
97% | 4.7552 | 44.0049 | 45.7903 | 52.0911 | 57.3983 | 46.1987 | 48.2695 | 50.6569 | 52.4445 | 54.4137 | 55.4486 | 56.3447 | 58.5572 | 57.2301 | 60.8356 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 65.5376 | 97% | 4.7552 | 46.8362 | 48.702 | 54.9539 | 60.4617 | 49.272 | 51.6036 | 53.822 | 55.7128 | 57.6811 | 58.547 | 59.7261 | 61.9086 | 61.2011 | 64.0506 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959 | 65.6959
95% | 7.7272 | 43.0976 | 44.8461 | 51.0171 | 56.2148 | 45.2461 | 47.2742 | 49.6124 | 51.3631 | 53.2918 | 54.3054 | 55.183 | 57.3498 | 56.0501 | 59.5813 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 64.1863 | 95% | 7.7272 | 45.8705 | 47.6978 | 53.8208 | 59.215 | 48.256 | 50.5396 | 52.7123 | 54.5641 | 56.4918 | 57.3399 | 58.4946 | 60.6322 | 59.9392 | 62.73 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414 | 64.3414
90% | 39.2302 | 40.8293 | 42.4858 | 48.332 | 53.2562 | 42.8647 | 44.7861 | 47.0013 | 48.6598 | 50.4869 | 51.4472 | 52.2786 | 54.3314 | 53.1001 | 56.4454 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 60.808 | 90% | 39.2302 | 43.4563 | 45.1874 | 50.9882 | 56.0984 | 45.7163 | 47.8796 | 49.938 | 51.6923 | 53.5186 | 54.322 | 55.4159 | 57.441 | 56.7845 | 59.4284 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955 | 60.955
85% | 117.6906 | 38.561 | 40.1255 | 45.6469 | 50.2975 | 40.4834 | 42.298 | 44.3901 | 45.9565 | 47.6821 | 48.589 | 49.3742 | 51.313 | 50.1501 | 53.3096 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 57.4298 | 85% | 117.6906 | 41.042 | 42.677 | 48.1555 | 52.9819 | 43.1765 | 45.2196 | 47.1636 | 48.8205 | 50.5453 | 51.3041 | 52.3373 | 54.2498 | 53.6298 | 56.1268 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686 | 57.5686
80% | 268.3703 | 36.2927 | 37.7652 | 42.9618 | 47.3388 | 38.102 | 39.8099 | 41.7789 | 43.2532 | 44.8773 | 45.7308 | 46.4699 | 48.2946 | 47.2001 | 50.1737 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 54.0516 | 80% | 268.3703 | 38.6278 | 40.1666 | 45.3228 | 49.8653 | 40.6367 | 42.5596 | 44.3893 | 45.9487 | 47.5721 | 48.2862 | 49.2586 | 51.0587 | 50.4751 | 52.8253 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822 | 54.1822
75% | 455.9026 | 34.0244 | 35.4048 | 40.2767 | 44.3801 | 35.7206 | 37.3218 | 39.1677 | 40.5498 | 42.0724 | 42.8727 | 43.5655 | 45.2762 | 44.2501 | 47.0378 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 50.6734 | 75% | 455.9026 | 36.2136 | 37.6562 | 42.4901 | 46.7487 | 38.0969 | 39.8997 | 41.615 | 43.0769 | 44.5988 | 45.2683 | 46.18 | 47.8675 | 47.3204 | 49.5237 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958 | 50.7958
70% | 690.9866 | 31.7561 | 33.0445 | 37.5915 | 41.4215 | 33.3392 | 34.8337 | 36.5565 | 37.8465 | 39.2676 | 40.0145 | 40.6611 | 42.2578 | 41.3001 | 43.902 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 47.2951 | 70% | 690.9866 | 33.7993 | 35.1457 | 39.6575 | 43.6321 | 35.5571 | 37.2397 | 38.8407 | 40.2051 | 41.6256 | 42.2504 | 43.1013 | 44.6763 | 44.1658 | 46.2221 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094 | 47.4094
65% | 967.6784 | 29.4878 | 30.6842 | 34.9064 | 38.4628 | 30.9579 | 32.3455 | 33.9453 | 35.1432 | 36.4628 | 37.1563 | 37.7568 | 39.2393 | 38.35 | 40.7661 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 43.9169 | 65% | 967.6784 | 31.3851 | 32.6353 | 36.8248 | 40.5155 | 33.0173 | 34.5797 | 36.0663 | 37.3334 | 38.6523 | 39.2325 | 40.0226 | 41.4852 | 41.0111 | 42.9205 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023 | 44.023
60% | 1292.8136 | 27.2195 | 28.3239 | 32.2213 | 35.5041 | 28.5765 | 29.8574 | 31.3342 | 32.4399 | 33.658 | 34.2981 | 34.8524 | 36.2209 | 35.4 | 37.6303 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 40.5387 | 60% | 1292.8136 | 28.9709 | 30.1249 | 33.9921 | 37.399 | 30.4775 | 31.9197 | 33.292 | 34.4616 | 35.6791 | 36.2146 | 36.944 | 38.294 | 37.8564 | 39.6189 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366 | 40.6366
55% | 1647.0743 | 24.9512 | 25.9636 | 29.5362 | 32.5454 | 26.1951 | 27.3693 | 28.723 | 29.7365 | 30.8531 | 31.44 | 31.948 | 33.2025 | 32.45 | 34.4944 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 37.1605 | 55% | 1647.0743 | 26.5566 | 27.6145 | 31.1594 | 34.2824 | 27.9377 | 29.2598 | 30.5177 | 31.5898 | 32.7058 | 33.1968 | 33.8653 | 35.1028 | 34.7017 | 36.3174 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503 | 37.2503
50% | 2104.1657 | 22.6829 | 23.6032 | 26.8511 | 29.5868 | 23.8137 | 24.8812 | 26.1118 | 27.0332 | 28.0483 | 28.5818 | 29.0437 | 30.1841 | 29.5 | 31.3586 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 33.7822 | 50% | 2104.1657 | 24.1424 | 25.1041 | 28.3268 | 31.1658 | 25.3979 | 26.5998 | 27.7433 | 28.718 | 29.7326 | 30.1789 | 30.7866 | 31.9117 | 31.547 | 33.0158 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639 | 33.8639
45% | 2736.0097 | 20.4146 | 21.2429 | 24.166 | 26.6281 | 21.4324 | 22.3931 | 23.5006 | 24.3299 | 25.2435 | 25.7236 | 26.1393 | 27.1657 | 26.55 | 28.2227 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 30.404 | 45% | 2736.0097 | 21.7281 | 22.5937 | 25.4941 | 28.0492 | 22.8581 | 23.9398 | 24.969 | 25.8462 | 26.7593 | 27.161 | 27.708 | 28.7205 | 28.3923 | 29.7142 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775 | 30.4775
40% | 3483.7613 | 18.1464 | 18.8826 | 21.4809 | 23.6694 | 19.051 | 19.9049 | 20.8894 | 21.6266 | 22.4386 | 22.8654 | 23.2349 | 24.1473 | 23.6 | 25.0868 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 27.0258 | 40% | 3483.7613 | 19.3139 | 20.0833 | 22.6614 | 24.9326 | 20.3183 | 21.2798 | 22.1947 | 22.9744 | 23.786 | 24.1431 | 24.6293 | 25.5293 | 25.2376 | 26.4126 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911 | 27.0911
35% | 3830.2948 | 15.8781 | 16.5223 | 18.7958 | 20.7107 | 16.6696 | 17.4168 | 18.2783 | 18.9233 | 19.6338 | 20.0072 | 20.3306 | 21.1289 | 20.65 | 21.951 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 23.6476 | 35% | 3830.2948 | 16.8997 | 17.5729 | 19.8287 | 21.8161 | 17.7785 | 18.6198 | 19.4203 | 20.1026 | 20.8128 | 21.1252 | 21.5506 | 22.3382 | 22.0829 | 23.111 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047 | 23.7047
30% | 3953.6322 | 13.6098 | 14.1619 | 16.1107 | 17.7521 | 14.2882 | 14.9287 | 15.6671 | 16.2199 | 16.829 | 17.1491 | 17.4262 | 18.1105 | 17.7 | 18.8151 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 20.2693 | 30% | 3953.6322 | 14.4854 | 15.0625 | 16.9961 | 18.6995 | 15.2388 | 15.9599 | 16.646 | 17.2308 | 17.8395 | 18.1073 | 18.472 | 19.147 | 18.9282 | 19.8095 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183 | 20.3183
25% | 4060.9208 | 11.3415 | 11.8016 | 13.4256 | 14.7934 | 11.9069 | 12.4406 | 13.0559 | 13.5166 | 14.0241 | 14.2909 | 14.5218 | 15.0921 | 14.75 | 15.6793 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 16.8911 | 25% | 4060.9208 | 12.0712 | 12.5521 | 14.1634 | 15.5829 | 12.699 | 13.2999 | 13.8717 | 14.359 | 14.8663 | 15.0894 | 15.3933 | 15.9558 | 15.7735 | 16.5079 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319 | 16.9319
20% | 4165.2375 | 9.0732 | 9.4413 | 10.7404 | 11.8347 | 9.5255 | 9.9525 | 10.4447 | 10.8133 | 11.2193 | 11.4327 | 11.6175 | 12.0736 | 11.8 | 12.5434 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 13.5129 | 20% | 4165.2375 | 9.657 | 10.0416 | 11.3307 | 12.4663 | 10.1592 | 10.6399 | 11.0973 | 11.4872 | 11.893 | 12.0715 | 12.3147 | 12.7647 | 12.6188 | 13.2063 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455 | 13.5455
15% | 4270.4458 | 6.8049 | 7.081 | 8.0553 | 8.876 | 7.1441 | 7.4644 | 7.8335 | 8.11 | 8.4145 | 8.5745 | 8.7131 | 9.0552 | 8.85 | 9.4076 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 10.1347 | 15% | 4270.4458 | 7.2427 | 7.5312 | 8.498 | 9.3497 | 7.6194 | 7.9799 | 8.323 | 8.6154 | 8.9198 | 9.0537 | 9.236 | 9.5735 | 9.4641 | 9.9047 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592 | 10.1592
10% | 4373.8709 | 4.5366 | 4.7206 | 5.3702 | 5.9174 | 4.7627 | 4.9762 | 5.2224 | 5.4066 | 5.6097 | 5.7164 | 5.8087 | 6.0368 | 5.9 | 6.2717 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 6.7564 | 10% | 4373.8709 | 4.8285 | 5.0208 | 5.6654 | 6.2332 | 5.0796 | 5.32 | 5.5487 | 5.7436 | 5.9465 | 6.0358 | 6.1573 | 6.3823 | 6.3094 | 6.6032 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728 | 6.7728
5% | 4391.7028 | 2.2683 | 2.3603 | 2.6851 | 2.9587 | 2.3814 | 2.4881 | 2.6112 | 2.7033 | 2.8048 | 2.8582 | 2.9044 | 3.0184 | 2.95 | 3.1359 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 3.3782 | 5% | 4391.7028 | 2.4142 | 2.5104 | 2.8327 | 3.1166 | 2.5398 | 2.66 | 2.7743 | 2.8718 | 2.9733 | 3.0179 | 3.0787 | 3.1912 | 3.1547 | 3.3016 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864 | 3.3864
9.992e-14% | 4391.7028 | 4.533e-14 | 4.7169e-14 | 5.3659e-14 | 5.9126e-14 | 4.7589e-14 | 4.9723e-14 | 5.2182e-14 | 5.4023e-14 | 5.6052e-14 | 5.7118e-14 | 5.8041e-14 | 6.032e-14 | 5.8953e-14 | 6.2667e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 6.751e-14 | 9.992e-14% | 4391.7028 | 4.8246e-14 | 5.0168e-14 | 5.6608e-14 | 6.2282e-14 | 5.0755e-14 | 5.3157e-14 | 5.5442e-14 | 5.739e-14 | 5.9418e-14 | 6.031e-14 | 6.1524e-14 | 6.3772e-14 | 6.3043e-14 | 6.5979e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14 | 6.7674e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 51.3156 | 53.473 | 54.8455 | 56.4117 | 57.6632 | 58.4812 | 60.4214 | 61.7646 | 62.4743 | 63.7852 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 63.4089 | 100% | 0 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 58.4255 | 60.5986 | 62.3643 | 64.0629 | 65.533 | 66.2736 | 67.3616 | 68.6057 | 69.8764 | 71.4726 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251 | 71.7251
99% | 0 | 50.7508 | 51.9667 | 58.2429 | 62.7724 | 50.8024 | 52.9383 | 54.2971 | 55.8476 | 57.0865 | 57.8964 | 59.8172 | 61.147 | 61.8496 | 63.1474 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 62.7748 | 99% | 0.75633 | 57.089 | 58.7368 | 65.0304 | 69.5089 | 57.8412 | 59.9926 | 61.7407 | 63.4223 | 64.8777 | 65.6109 | 66.6879 | 67.9196 | 69.1776 | 70.7578 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079 | 71.0079
98% | 0.37816 | 50.2382 | 51.4418 | 57.6546 | 62.1384 | 50.2893 | 52.4035 | 53.7486 | 55.2835 | 56.5099 | 57.3115 | 59.213 | 60.5293 | 61.2248 | 62.5095 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 62.1407 | 98% | 1.1345 | 56.5124 | 58.1435 | 64.3735 | 68.8068 | 57.257 | 59.3866 | 61.117 | 62.7816 | 64.2224 | 64.9481 | 66.0143 | 67.2336 | 68.4789 | 70.0431 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906 | 70.2906
97% | 0.75633 | 49.7256 | 50.9169 | 57.0663 | 61.5043 | 49.7761 | 51.8688 | 53.2002 | 54.7194 | 55.9333 | 56.7267 | 58.6088 | 59.9117 | 60.6001 | 61.8717 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 61.5066 | 97% | 1.8908 | 55.9357 | 57.5502 | 63.7166 | 68.1047 | 56.6727 | 58.7806 | 60.4934 | 62.141 | 63.5671 | 64.2854 | 65.3407 | 66.5475 | 67.7801 | 69.3284 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734 | 69.5734
95% | 1.8908 | 48.7003 | 49.867 | 55.8896 | 60.2362 | 48.7498 | 50.7993 | 52.1033 | 53.5911 | 54.78 | 55.5571 | 57.4003 | 58.6764 | 59.3506 | 60.596 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 60.2384 | 95% | 3.4035 | 54.7824 | 56.3636 | 62.4029 | 66.7005 | 55.5042 | 57.5687 | 59.2461 | 60.8597 | 62.2564 | 62.9599 | 63.9935 | 65.1754 | 66.3826 | 67.8989 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389 | 68.1389
90% | 4.538 | 46.1371 | 47.2424 | 52.9481 | 57.0659 | 46.184 | 48.1257 | 49.361 | 50.7705 | 51.8969 | 52.633 | 54.3793 | 55.5881 | 56.2269 | 57.4067 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 90% | 9.0759 | 51.8991 | 53.3971 | 59.1185 | 63.1899 | 52.5829 | 54.5387 | 56.1279 | 57.6566 | 58.9797 | 59.6462 | 60.6254 | 61.7451 | 62.8888 | 64.3253 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526 | 64.5526
85% | 9.0759 | 43.574 | 44.6179 | 50.0065 | 53.8955 | 43.6183 | 45.452 | 46.6187 | 47.95 | 49.0137 | 49.709 | 51.3582 | 52.4999 | 53.1032 | 54.2174 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 53.8975 | 85% | 16.2611 | 49.0158 | 50.4306 | 55.8342 | 59.6794 | 49.6616 | 51.5088 | 53.0097 | 54.4535 | 55.7031 | 56.3326 | 57.2573 | 58.3148 | 59.395 | 60.7517 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663 | 60.9663
80% | 27.606 | 41.0108 | 41.9933 | 47.065 | 50.7252 | 41.0525 | 42.7784 | 43.8764 | 45.1294 | 46.1305 | 46.7849 | 48.3371 | 49.4117 | 49.9795 | 51.0282 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 50.7271 | 80% | 24.9588 | 46.1325 | 47.4641 | 52.5498 | 56.1688 | 46.7404 | 48.4789 | 49.8915 | 51.2503 | 52.4264 | 53.0189 | 53.8893 | 54.8845 | 55.9011 | 57.178 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801 | 57.3801
75% | 57.481 | 38.4476 | 39.3687 | 44.1234 | 47.5549 | 38.4867 | 40.1047 | 41.1342 | 42.3088 | 43.2474 | 43.8609 | 45.3161 | 46.3235 | 46.8557 | 47.8389 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 47.5566 | 75% | 32.9003 | 43.2493 | 44.4976 | 49.2655 | 52.6583 | 43.8191 | 45.449 | 46.7732 | 48.0472 | 49.1498 | 49.7052 | 50.5212 | 51.4542 | 52.4073 | 53.6044 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938 | 53.7938
70% | 106.2642 | 35.8844 | 36.7441 | 41.1818 | 44.3846 | 35.9209 | 37.4311 | 38.3919 | 39.4882 | 40.3642 | 40.9368 | 42.295 | 43.2352 | 43.732 | 44.6497 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 44.3862 | 70% | 41.9762 | 40.366 | 41.531 | 45.9811 | 49.1477 | 40.8978 | 42.419 | 43.655 | 44.844 | 45.8731 | 46.3915 | 47.1531 | 48.024 | 48.9135 | 50.0308 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076 | 50.2076
65% | 201.9397 | 33.3213 | 34.1195 | 38.2403 | 41.2142 | 33.3551 | 34.7574 | 35.6496 | 36.6676 | 37.4811 | 38.0128 | 39.2739 | 40.147 | 40.6083 | 41.4604 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 41.2158 | 65% | 67.6914 | 37.4827 | 38.5645 | 42.6967 | 45.6372 | 37.9766 | 39.3891 | 40.5368 | 41.6409 | 42.5965 | 43.0778 | 43.785 | 44.5937 | 45.4197 | 46.4572 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213 | 46.6213
60% | 402.745 | 30.7581 | 31.495 | 35.2987 | 38.0439 | 30.7894 | 32.0838 | 32.9073 | 33.847 | 34.5979 | 35.0887 | 36.2529 | 37.0588 | 37.4846 | 38.2711 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 38.0453 | 60% | 98.7009 | 34.5994 | 35.598 | 39.4124 | 42.1266 | 35.0553 | 36.3592 | 37.4186 | 38.4377 | 39.3198 | 39.7642 | 40.4169 | 41.1634 | 41.9258 | 42.8835 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351 | 43.0351
55% | 655.7369 | 28.1949 | 28.8704 | 32.3572 | 34.8736 | 28.2236 | 29.4101 | 30.165 | 31.0264 | 31.7147 | 32.1646 | 33.2318 | 33.9705 | 34.3609 | 35.0819 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 34.8749 | 55% | 153.5347 | 31.7161 | 32.6315 | 36.128 | 38.6161 | 32.134 | 33.3292 | 34.3004 | 35.2346 | 36.0432 | 36.4505 | 37.0489 | 37.7331 | 38.432 | 39.3099 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488 | 39.4488
50% | 981.7145 | 25.6317 | 26.2458 | 29.4156 | 31.7033 | 25.6578 | 26.7365 | 27.4228 | 28.2059 | 28.8316 | 29.2406 | 30.2107 | 30.8823 | 31.2372 | 31.8926 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 31.7044 | 50% | 258.2862 | 28.8328 | 29.665 | 32.8436 | 35.1055 | 29.2127 | 30.2993 | 31.1822 | 32.0314 | 32.7665 | 33.1368 | 33.6808 | 34.3028 | 34.9382 | 35.7363 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626 | 35.8626
45% | 1622.7029 | 23.0686 | 23.6212 | 26.474 | 28.5329 | 23.092 | 24.0628 | 24.6805 | 25.3853 | 25.9484 | 26.3165 | 27.1896 | 27.7941 | 28.1134 | 28.7033 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 28.534 | 45% | 488.9664 | 25.9496 | 26.6985 | 29.5593 | 31.595 | 26.2915 | 27.2694 | 28.0639 | 28.8283 | 29.4899 | 29.8231 | 30.3127 | 30.8725 | 31.4444 | 32.1626 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763 | 32.2763
40% | 2442.9413 | 20.5054 | 20.9966 | 23.5325 | 25.3626 | 20.5262 | 21.3892 | 21.9382 | 22.5647 | 23.0653 | 23.3925 | 24.1686 | 24.7058 | 24.9897 | 25.5141 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 25.3635 | 40% | 928.0152 | 23.0663 | 23.732 | 26.2749 | 28.0844 | 23.3702 | 24.2394 | 24.9457 | 25.6252 | 26.2132 | 26.5094 | 26.9446 | 27.4423 | 27.9506 | 28.589 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69 | 28.69
35% | 3006.7842 | 17.9422 | 18.3721 | 20.5909 | 22.1923 | 17.9605 | 18.7155 | 19.1959 | 19.7441 | 20.1821 | 20.4684 | 21.1475 | 21.6176 | 21.866 | 22.3248 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 22.1931 | 35% | 1530.4309 | 20.183 | 20.7655 | 22.9905 | 24.5739 | 20.4489 | 21.2095 | 21.8275 | 22.422 | 22.9366 | 23.1958 | 23.5765 | 24.012 | 24.4567 | 25.0154 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038 | 25.1038
30% | 3276.4154 | 15.379 | 15.7475 | 17.6494 | 19.022 | 15.3947 | 16.0419 | 16.4537 | 16.9235 | 17.299 | 17.5443 | 18.1264 | 18.5294 | 18.7423 | 19.1356 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 19.0227 | 30% | 2592.3162 | 17.2997 | 17.799 | 19.7062 | 21.0633 | 17.5276 | 18.1796 | 18.7093 | 19.2189 | 19.6599 | 19.8821 | 20.2085 | 20.5817 | 20.9629 | 21.4418 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175 | 21.5175
25% | 3466.632 | 12.8159 | 13.1229 | 14.7078 | 15.8516 | 12.8289 | 13.3682 | 13.7114 | 14.1029 | 14.4158 | 14.6203 | 15.1054 | 15.4412 | 15.6186 | 15.9463 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 15.8522 | 25% | 3659.4958 | 14.4164 | 14.8325 | 16.4218 | 17.5528 | 14.6064 | 15.1497 | 15.5911 | 16.0157 | 16.3833 | 16.5684 | 16.8404 | 17.1514 | 17.4691 | 17.8681 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313 | 17.9313
20% | 3713.9514 | 10.2527 | 10.4983 | 11.7662 | 12.6813 | 10.2631 | 10.6946 | 10.9691 | 11.2823 | 11.5326 | 11.6962 | 12.0843 | 12.3529 | 12.4949 | 12.757 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 12.6818 | 20% | 4005.5161 | 11.5331 | 11.866 | 13.1375 | 14.0422 | 11.6851 | 12.1197 | 12.4729 | 12.8126 | 13.1066 | 13.2547 | 13.4723 | 13.7211 | 13.9753 | 14.2945 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345 | 14.345
15% | 4043.3325 | 7.6895 | 7.8737 | 8.8247 | 9.511 | 7.6973 | 8.0209 | 8.2268 | 8.4618 | 8.6495 | 8.7722 | 9.0632 | 9.2647 | 9.3711 | 9.5678 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 9.5113 | 15% | 4281.1979 | 8.6499 | 8.8995 | 9.8531 | 10.5317 | 8.7638 | 9.0898 | 9.3546 | 9.6094 | 9.83 | 9.941 | 10.1042 | 10.2908 | 10.4815 | 10.7209 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588 | 10.7588
10% | 4350.7801 | 5.1263 | 5.2492 | 5.8831 | 6.3407 | 5.1316 | 5.3473 | 5.4846 | 5.6412 | 5.7663 | 5.8481 | 6.0421 | 6.1765 | 6.2474 | 6.3785 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 6.3409 | 10% | 4391.6218 | 5.7666 | 5.933 | 6.5687 | 7.0211 | 5.8425 | 6.0599 | 6.2364 | 6.4063 | 6.5533 | 6.6274 | 6.7362 | 6.8606 | 6.9876 | 7.1473 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725 | 7.1725
5% | 4391.6218 | 2.5632 | 2.6246 | 2.9416 | 3.1703 | 2.5658 | 2.6736 | 2.7423 | 2.8206 | 2.8832 | 2.9241 | 3.0211 | 3.0882 | 3.1237 | 3.1893 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 3.1704 | 5% | 4391.6218 | 2.8833 | 2.9665 | 3.2844 | 3.5106 | 2.9213 | 3.0299 | 3.1182 | 3.2031 | 3.2767 | 3.3137 | 3.3681 | 3.4303 | 3.4938 | 3.5736 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863 | 3.5863
9.992e-14% | 4391.6218 | 5.1223e-14 | 5.245e-14 | 5.8784e-14 | 6.3356e-14 | 5.1275e-14 | 5.343e-14 | 5.4802e-14 | 5.6367e-14 | 5.7617e-14 | 5.8434e-14 | 6.0373e-14 | 6.1715e-14 | 6.2424e-14 | 6.3734e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 6.3358e-14 | 9.992e-14% | 4391.6218 | 5.762e-14 | 5.9283e-14 | 6.5635e-14 | 7.0155e-14 | 5.8379e-14 | 6.055e-14 | 6.2314e-14 | 6.4012e-14 | 6.5481e-14 | 6.6221e-14 | 6.7308e-14 | 6.8551e-14 | 6.9821e-14 | 7.1415e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14 | 7.1668e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.3659 | 47.2065 | 53.7022 | 51.9235 | 40.3775 | 42.5124 | 44.9736 | 46.8164 | 48.8466 | 49.9136 | 50.8373 | 53.1182 | 51.7501 | 55.4671 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 100% | 0 | 48.2848 | 50.2082 | 56.6535 | 55.0816 | 43.5458 | 45.9496 | 48.2366 | 50.1859 | 52.2151 | 53.1077 | 54.3233 | 56.5733 | 55.8439 | 58.7816 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777
99% | 0.8916 | 44.9122 | 46.7344 | 53.1652 | 51.4043 | 39.9737 | 42.0872 | 44.5239 | 46.3483 | 48.3581 | 49.4144 | 50.329 | 52.587 | 51.2326 | 54.9125 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 99% | 0.8916 | 47.8019 | 49.7061 | 56.087 | 54.5308 | 43.1104 | 45.4901 | 47.7543 | 49.6841 | 51.693 | 52.5767 | 53.78 | 56.0076 | 55.2855 | 58.1937 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873
98% | 3.5664 | 44.4586 | 46.2623 | 52.6282 | 50.885 | 39.5699 | 41.6621 | 44.0741 | 45.8801 | 47.8697 | 48.9153 | 49.8206 | 52.0559 | 50.7151 | 54.3578 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 98% | 3.5664 | 47.3191 | 49.204 | 55.5204 | 53.98 | 42.6749 | 45.0306 | 47.2719 | 49.1822 | 51.1708 | 52.0456 | 53.2368 | 55.4419 | 54.7271 | 57.6059 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682
97% | 4.7552 | 44.0049 | 45.7903 | 52.0911 | 50.3658 | 39.1662 | 41.237 | 43.6244 | 45.412 | 47.3812 | 48.4161 | 49.3122 | 51.5247 | 50.1976 | 53.8031 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 97% | 4.7552 | 46.8362 | 48.702 | 54.9539 | 53.4292 | 42.2395 | 44.5711 | 46.7895 | 48.6803 | 50.6486 | 51.5145 | 52.6936 | 54.8761 | 54.1686 | 57.0181 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634
95% | 7.7272 | 43.0976 | 44.8461 | 51.0171 | 49.3273 | 38.3586 | 40.3867 | 42.7249 | 44.4756 | 46.4043 | 47.4179 | 48.2955 | 50.4623 | 49.1626 | 52.6938 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 95% | 7.7272 | 45.8705 | 47.6978 | 53.8208 | 52.3275 | 41.3685 | 43.6521 | 45.8248 | 47.6766 | 49.6043 | 50.4524 | 51.6071 | 53.7447 | 53.0517 | 55.8425 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539
90% | 39.2302 | 40.8293 | 42.4858 | 48.332 | 46.7312 | 36.3397 | 38.2611 | 40.4763 | 42.1348 | 43.9619 | 44.9222 | 45.7536 | 47.8064 | 46.5751 | 49.9204 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 90% | 39.2302 | 43.4563 | 45.1874 | 50.9882 | 49.5734 | 39.1913 | 41.3546 | 43.413 | 45.1673 | 46.9936 | 47.797 | 48.8909 | 50.916 | 50.2595 | 52.9034 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43
85% | 117.6906 | 38.561 | 40.1255 | 45.6469 | 44.135 | 34.3209 | 36.1355 | 38.2276 | 39.794 | 41.5196 | 42.4265 | 43.2117 | 45.1505 | 43.9876 | 47.1471 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 85% | 117.6906 | 41.042 | 42.677 | 48.1555 | 46.8194 | 37.014 | 39.0571 | 41.0011 | 42.658 | 44.3828 | 45.1416 | 46.1748 | 48.0873 | 47.4673 | 49.9643 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061
80% | 268.3703 | 36.2927 | 37.7652 | 42.9618 | 41.5388 | 32.302 | 34.0099 | 35.9789 | 37.4532 | 39.0773 | 39.9308 | 40.6699 | 42.4946 | 41.4001 | 44.3737 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 80% | 268.3703 | 38.6278 | 40.1666 | 45.3228 | 44.0653 | 34.8367 | 36.7596 | 38.5893 | 40.1487 | 41.7721 | 42.4862 | 43.4586 | 45.2587 | 44.6751 | 47.0253 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822
75% | 455.9026 | 34.0244 | 35.4048 | 40.2767 | 38.9426 | 30.2831 | 31.8843 | 33.7302 | 35.1123 | 36.6349 | 37.4352 | 38.128 | 39.8387 | 38.8126 | 41.6003 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 75% | 455.9026 | 36.2136 | 37.6562 | 42.4901 | 41.3112 | 32.6594 | 34.4622 | 36.1775 | 37.6394 | 39.1613 | 39.8308 | 40.7425 | 42.43 | 41.8829 | 44.0862 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583
70% | 690.9866 | 31.7561 | 33.0445 | 37.5915 | 36.3465 | 28.2642 | 29.7587 | 31.4815 | 32.7715 | 34.1926 | 34.9395 | 35.5861 | 37.1828 | 36.2251 | 38.827 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 70% | 690.9866 | 33.7993 | 35.1457 | 39.6575 | 38.5571 | 30.4821 | 32.1647 | 33.7657 | 35.1301 | 36.5506 | 37.1754 | 38.0263 | 39.6013 | 39.0908 | 41.1471 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344
65% | 967.6784 | 29.4878 | 30.6842 | 34.9064 | 33.7503 | 26.2454 | 27.633 | 29.2328 | 30.4307 | 31.7503 | 32.4438 | 33.0443 | 34.5268 | 33.6375 | 36.0536 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 65% | 967.6784 | 31.3851 | 32.6353 | 36.8248 | 35.803 | 28.3048 | 29.8672 | 31.3538 | 32.6209 | 33.9398 | 34.52 | 35.3101 | 36.7727 | 36.2986 | 38.208 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105
60% | 1292.8136 | 27.2195 | 28.3239 | 32.2213 | 31.1541 | 24.2265 | 25.5074 | 26.9842 | 28.0899 | 29.308 | 29.9481 | 30.5024 | 31.8709 | 31.05 | 33.2803 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 60% | 1292.8136 | 28.9709 | 30.1249 | 33.9921 | 33.049 | 26.1275 | 27.5697 | 28.942 | 30.1116 | 31.3291 | 31.8646 | 32.594 | 33.944 | 33.5064 | 35.2689 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866
55% | 1647.0743 | 24.9512 | 25.9636 | 29.5362 | 28.5579 | 22.2076 | 23.3818 | 24.7355 | 25.749 | 26.8656 | 27.4525 | 27.9605 | 29.215 | 28.4625 | 30.5069 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 55% | 1647.0743 | 26.5566 | 27.6145 | 31.1594 | 30.2949 | 23.9502 | 25.2723 | 26.5302 | 27.6023 | 28.7183 | 29.2093 | 29.8778 | 31.1153 | 30.7142 | 32.3299 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628
50% | 2104.1657 | 22.6829 | 23.6032 | 26.8511 | 25.9618 | 20.1887 | 21.2562 | 22.4868 | 23.4082 | 24.4233 | 24.9568 | 25.4187 | 26.5591 | 25.875 | 27.7336 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 50% | 2104.1657 | 24.1424 | 25.1041 | 28.3268 | 27.5408 | 21.7729 | 22.9748 | 24.1183 | 25.093 | 26.1076 | 26.5539 | 27.1616 | 28.2867 | 27.922 | 29.3908 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389
45% | 2736.0097 | 20.4146 | 21.2429 | 24.166 | 23.3656 | 18.1699 | 19.1306 | 20.2381 | 21.0674 | 21.981 | 22.4611 | 22.8768 | 23.9032 | 23.2875 | 24.9602 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 45% | 2736.0097 | 21.7281 | 22.5937 | 25.4941 | 24.7867 | 19.5956 | 20.6773 | 21.7065 | 22.5837 | 23.4968 | 23.8985 | 24.4455 | 25.458 | 25.1298 | 26.4517 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215
40% | 3483.7613 | 18.1464 | 18.8826 | 21.4809 | 20.7694 | 16.151 | 17.0049 | 17.9894 | 18.7266 | 19.5386 | 19.9654 | 20.3349 | 21.2473 | 20.7 | 22.1868 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 40% | 3483.7613 | 19.3139 | 20.0833 | 22.6614 | 22.0326 | 17.4183 | 18.3798 | 19.2947 | 20.0744 | 20.886 | 21.2431 | 21.7293 | 22.6293 | 22.3376 | 23.5126 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911
35% | 3830.2948 | 15.8781 | 16.5223 | 18.7958 | 18.1732 | 14.1321 | 14.8793 | 15.7408 | 16.3858 | 17.0963 | 17.4697 | 17.7931 | 18.5914 | 18.1125 | 19.4135 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 35% | 3830.2948 | 16.8997 | 17.5729 | 19.8287 | 19.2786 | 15.241 | 16.0823 | 16.8828 | 17.5651 | 18.2753 | 18.5877 | 19.0131 | 19.8007 | 19.5454 | 20.5735 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672
30% | 3953.6322 | 13.6098 | 14.1619 | 16.1107 | 15.5771 | 12.1132 | 12.7537 | 13.4921 | 14.0449 | 14.654 | 14.9741 | 15.2512 | 15.9355 | 15.525 | 16.6401 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 30% | 3953.6322 | 14.4854 | 15.0625 | 16.9961 | 16.5245 | 13.0638 | 13.7849 | 14.471 | 15.0558 | 15.6645 | 15.9323 | 16.297 | 16.972 | 16.7532 | 17.6345 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433
25% | 4060.9208 | 11.3415 | 11.8016 | 13.4256 | 12.9809 | 10.0944 | 10.6281 | 11.2434 | 11.7041 | 12.2116 | 12.4784 | 12.7093 | 13.2796 | 12.9375 | 13.8668 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 25% | 4060.9208 | 12.0712 | 12.5521 | 14.1634 | 13.7704 | 10.8865 | 11.4874 | 12.0592 | 12.5465 | 13.0538 | 13.2769 | 13.5808 | 14.1433 | 13.961 | 14.6954 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194
20% | 4165.2375 | 9.0732 | 9.4413 | 10.7404 | 10.3847 | 8.0755 | 8.5025 | 8.9947 | 9.3633 | 9.7693 | 9.9827 | 10.1675 | 10.6236 | 10.35 | 11.0934 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 20% | 4165.2375 | 9.657 | 10.0416 | 11.3307 | 11.0163 | 8.7092 | 9.1899 | 9.6473 | 10.0372 | 10.443 | 10.6215 | 10.8647 | 11.3147 | 11.1688 | 11.7563 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955
15% | 4270.4458 | 6.8049 | 7.081 | 8.0553 | 7.7885 | 6.0566 | 6.3769 | 6.746 | 7.0225 | 7.327 | 7.487 | 7.6256 | 7.9677 | 7.7625 | 8.3201 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 15% | 4270.4458 | 7.2427 | 7.5312 | 8.498 | 8.2622 | 6.5319 | 6.8924 | 7.2355 | 7.5279 | 7.8323 | 7.9662 | 8.1485 | 8.486 | 8.3766 | 8.8172 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717
10% | 4373.8709 | 4.5366 | 4.7206 | 5.3702 | 5.1924 | 4.0377 | 4.2512 | 4.4974 | 4.6816 | 4.8847 | 4.9914 | 5.0837 | 5.3118 | 5.175 | 5.5467 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 10% | 4373.8709 | 4.8285 | 5.0208 | 5.6654 | 5.5082 | 4.3546 | 4.595 | 4.8237 | 5.0186 | 5.2215 | 5.3108 | 5.4323 | 5.6573 | 5.5844 | 5.8782 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478
5% | 4391.7028 | 2.2683 | 2.3603 | 2.6851 | 2.5962 | 2.0189 | 2.1256 | 2.2487 | 2.3408 | 2.4423 | 2.4957 | 2.5419 | 2.6559 | 2.5875 | 2.7734 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 5% | 4391.7028 | 2.4142 | 2.5104 | 2.8327 | 2.7541 | 2.1773 | 2.2975 | 2.4118 | 2.5093 | 2.6108 | 2.6554 | 2.7162 | 2.8287 | 2.7922 | 2.9391 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239
9.992e-14% | 4391.7028 | 4.533e-14 | 4.7169e-14 | 5.3659e-14 | 5.1882e-14 | 4.0345e-14 | 4.2478e-14 | 4.4938e-14 | 4.6779e-14 | 4.8808e-14 | 4.9874e-14 | 5.0797e-14 | 5.3076e-14 | 5.1709e-14 | 5.5423e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 9.992e-14% | 4391.7028 | 4.8246e-14 | 5.0168e-14 | 5.6608e-14 | 5.5038e-14 | 4.3511e-14 | 4.5913e-14 | 4.8198e-14 | 5.0146e-14 | 5.2173e-14 | 5.3065e-14 | 5.428e-14 | 5.6528e-14 | 5.5799e-14 | 5.8735e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.2635 | 52.4916 | 58.8312 | 56.1565 | 44.0656 | 46.223 | 47.5955 | 49.1617 | 50.4132 | 51.2312 | 53.1714 | 54.5146 | 55.2243 | 56.5352 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 100% | 0 | 57.6657 | 59.3301 | 65.6873 | 62.961 | 51.1755 | 53.3486 | 55.1143 | 56.8129 | 58.283 | 59.0236 | 60.1116 | 61.3557 | 62.6264 | 64.2226 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751
99% | 0 | 50.7508 | 51.9667 | 58.2429 | 55.5949 | 43.6249 | 45.7608 | 47.1196 | 48.6701 | 49.909 | 50.7189 | 52.6397 | 53.9695 | 54.6721 | 55.9699 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 99% | 0.75633 | 57.089 | 58.7368 | 65.0304 | 62.3314 | 50.6637 | 52.8151 | 54.5632 | 56.2448 | 57.7002 | 58.4334 | 59.5104 | 60.7421 | 62.0001 | 63.5803 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304
98% | 0.37816 | 50.2382 | 51.4418 | 57.6546 | 55.0334 | 43.1843 | 45.2985 | 46.6436 | 48.1785 | 49.4049 | 50.2065 | 52.108 | 53.4243 | 54.1198 | 55.4045 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 98% | 1.1345 | 56.5124 | 58.1435 | 64.3735 | 61.7018 | 50.152 | 52.2816 | 54.012 | 55.6766 | 57.1174 | 57.8431 | 58.9093 | 60.1286 | 61.3739 | 62.9381 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856
97% | 0.75633 | 49.7256 | 50.9169 | 57.0663 | 54.4718 | 42.7436 | 44.8363 | 46.1677 | 47.6869 | 48.9008 | 49.6942 | 51.5763 | 52.8792 | 53.5676 | 54.8392 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 97% | 1.8908 | 55.9357 | 57.5502 | 63.7166 | 61.0722 | 49.6402 | 51.7481 | 53.4609 | 55.1085 | 56.5346 | 57.2529 | 58.3082 | 59.515 | 60.7476 | 62.2959 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409
95% | 1.8908 | 48.7003 | 49.867 | 55.8896 | 53.3487 | 41.8623 | 43.9118 | 45.2158 | 46.7036 | 47.8925 | 48.6696 | 50.5128 | 51.7889 | 52.4631 | 53.7085 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 95% | 3.4035 | 54.7824 | 56.3636 | 62.4029 | 59.813 | 48.6167 | 50.6812 | 52.3586 | 53.9722 | 55.3689 | 56.0724 | 57.106 | 58.2879 | 59.4951 | 61.0114 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514
90% | 4.538 | 46.1371 | 47.2424 | 52.9481 | 50.5409 | 39.659 | 41.6007 | 42.836 | 44.2455 | 45.3719 | 46.108 | 47.8543 | 49.0631 | 49.7019 | 50.8817 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 90% | 9.0759 | 51.8991 | 53.3971 | 59.1185 | 56.6649 | 46.0579 | 48.0137 | 49.6029 | 51.1316 | 52.4547 | 53.1212 | 54.1004 | 55.2201 | 56.3638 | 57.8003 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276
85% | 9.0759 | 43.574 | 44.6179 | 50.0065 | 47.733 | 37.4558 | 39.2895 | 40.4562 | 41.7875 | 42.8512 | 43.5465 | 45.1957 | 46.3374 | 46.9407 | 48.0549 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 85% | 16.2611 | 49.0158 | 50.4306 | 55.8342 | 53.5169 | 43.4991 | 45.3463 | 46.8472 | 48.291 | 49.5406 | 50.1701 | 51.0948 | 52.1523 | 53.2325 | 54.5892 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038
80% | 27.606 | 41.0108 | 41.9933 | 47.065 | 44.9252 | 35.2525 | 36.9784 | 38.0764 | 39.3294 | 40.3305 | 40.9849 | 42.5371 | 43.6117 | 44.1795 | 45.2282 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 80% | 24.9588 | 46.1325 | 47.4641 | 52.5498 | 50.3688 | 40.9404 | 42.6789 | 44.0915 | 45.4503 | 46.6264 | 47.2189 | 48.0893 | 49.0845 | 50.1011 | 51.378 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801
75% | 57.481 | 38.4476 | 39.3687 | 44.1234 | 42.1174 | 33.0492 | 34.6672 | 35.6967 | 36.8713 | 37.8099 | 38.4234 | 39.8786 | 40.886 | 41.4182 | 42.4014 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 75% | 32.9003 | 43.2493 | 44.4976 | 49.2655 | 47.2208 | 38.3816 | 40.0115 | 41.3357 | 42.6097 | 43.7123 | 44.2677 | 45.0837 | 46.0167 | 46.9698 | 48.1669 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563
70% | 106.2642 | 35.8844 | 36.7441 | 41.1818 | 39.3096 | 30.8459 | 32.3561 | 33.3169 | 34.4132 | 35.2892 | 35.8618 | 37.22 | 38.1602 | 38.657 | 39.5747 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 70% | 41.9762 | 40.366 | 41.531 | 45.9811 | 44.0727 | 35.8228 | 37.344 | 38.58 | 39.769 | 40.7981 | 41.3165 | 42.0781 | 42.949 | 43.8385 | 44.9558 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326
65% | 201.9397 | 33.3213 | 34.1195 | 38.2403 | 36.5017 | 28.6426 | 30.0449 | 30.9371 | 31.9551 | 32.7686 | 33.3003 | 34.5614 | 35.4345 | 35.8958 | 36.7479 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 65% | 67.6914 | 37.4827 | 38.5645 | 42.6967 | 40.9247 | 33.2641 | 34.6766 | 35.8243 | 36.9284 | 37.884 | 38.3653 | 39.0725 | 39.8812 | 40.7072 | 41.7447 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088
60% | 402.745 | 30.7581 | 31.495 | 35.2987 | 33.6939 | 26.4394 | 27.7338 | 28.5573 | 29.497 | 30.2479 | 30.7387 | 31.9029 | 32.7088 | 33.1346 | 33.9211 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 60% | 98.7009 | 34.5994 | 35.598 | 39.4124 | 37.7766 | 30.7053 | 32.0092 | 33.0686 | 34.0877 | 34.9698 | 35.4142 | 36.0669 | 36.8134 | 37.5758 | 38.5335 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851
55% | 655.7369 | 28.1949 | 28.8704 | 32.3572 | 30.8861 | 24.2361 | 25.4226 | 26.1775 | 27.0389 | 27.7272 | 28.1771 | 29.2443 | 29.983 | 30.3734 | 31.0944 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 55% | 153.5347 | 31.7161 | 32.6315 | 36.128 | 34.6286 | 28.1465 | 29.3417 | 30.3129 | 31.2471 | 32.0557 | 32.463 | 33.0614 | 33.7456 | 34.4445 | 35.3224 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613
50% | 981.7145 | 25.6317 | 26.2458 | 29.4156 | 28.0783 | 22.0328 | 23.1115 | 23.7978 | 24.5809 | 25.2066 | 25.6156 | 26.5857 | 27.2573 | 27.6122 | 28.2676 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 50% | 258.2862 | 28.8328 | 29.665 | 32.8436 | 31.4805 | 25.5877 | 26.6743 | 27.5572 | 28.4064 | 29.1415 | 29.5118 | 30.0558 | 30.6778 | 31.3132 | 32.1113 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376
45% | 1622.7029 | 23.0686 | 23.6212 | 26.474 | 25.2704 | 19.8295 | 20.8003 | 21.418 | 22.1228 | 22.6859 | 23.054 | 23.9271 | 24.5316 | 24.8509 | 25.4408 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 45% | 488.9664 | 25.9496 | 26.6985 | 29.5593 | 28.3325 | 23.029 | 24.0069 | 24.8014 | 25.5658 | 26.2274 | 26.5606 | 27.0502 | 27.61 | 28.1819 | 28.9001 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138
40% | 2442.9413 | 20.5054 | 20.9966 | 23.5325 | 22.4626 | 17.6262 | 18.4892 | 19.0382 | 19.6647 | 20.1653 | 20.4925 | 21.2686 | 21.8058 | 22.0897 | 22.6141 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 40% | 928.0152 | 23.0663 | 23.732 | 26.2749 | 25.1844 | 20.4702 | 21.3394 | 22.0457 | 22.7252 | 23.3132 | 23.6094 | 24.0446 | 24.5423 | 25.0506 | 25.689 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79
35% | 3006.7842 | 17.9422 | 18.3721 | 20.5909 | 19.6548 | 15.423 | 16.178 | 16.6584 | 17.2066 | 17.6446 | 17.9309 | 18.61 | 19.0801 | 19.3285 | 19.7873 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 35% | 1530.4309 | 20.183 | 20.7655 | 22.9905 | 22.0364 | 17.9114 | 18.672 | 19.29 | 19.8845 | 20.3991 | 20.6583 | 21.039 | 21.4745 | 21.9192 | 22.4779 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663
30% | 3276.4154 | 15.379 | 15.7475 | 17.6494 | 16.847 | 13.2197 | 13.8669 | 14.2787 | 14.7485 | 15.124 | 15.3693 | 15.9514 | 16.3544 | 16.5673 | 16.9606 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 30% | 2592.3162 | 17.2997 | 17.799 | 19.7062 | 18.8883 | 15.3526 | 16.0046 | 16.5343 | 17.0439 | 17.4849 | 17.7071 | 18.0335 | 18.4067 | 18.7879 | 19.2668 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425
25% | 3466.632 | 12.8159 | 13.1229 | 14.7078 | 14.0391 | 11.0164 | 11.5557 | 11.8989 | 12.2904 | 12.6033 | 12.8078 | 13.2929 | 13.6287 | 13.8061 | 14.1338 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 25% | 3659.4958 | 14.4164 | 14.8325 | 16.4218 | 15.7403 | 12.7939 | 13.3372 | 13.7786 | 14.2032 | 14.5708 | 14.7559 | 15.0279 | 15.3389 | 15.6566 | 16.0556 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188
20% | 3713.9514 | 10.2527 | 10.4983 | 11.7662 | 11.2313 | 8.8131 | 9.2446 | 9.5191 | 9.8323 | 10.0826 | 10.2462 | 10.6343 | 10.9029 | 11.0449 | 11.307 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 20% | 4005.5161 | 11.5331 | 11.866 | 13.1375 | 12.5922 | 10.2351 | 10.6697 | 11.0229 | 11.3626 | 11.6566 | 11.8047 | 12.0223 | 12.2711 | 12.5253 | 12.8445 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895
15% | 4043.3325 | 7.6895 | 7.8737 | 8.8247 | 8.4235 | 6.6098 | 6.9334 | 7.1393 | 7.3743 | 7.562 | 7.6847 | 7.9757 | 8.1772 | 8.2836 | 8.4803 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 15% | 4281.1979 | 8.6499 | 8.8995 | 9.8531 | 9.4442 | 7.6763 | 8.0023 | 8.2671 | 8.5219 | 8.7425 | 8.8535 | 9.0167 | 9.2033 | 9.394 | 9.6334 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713
10% | 4350.7801 | 5.1263 | 5.2492 | 5.8831 | 5.6157 | 4.4066 | 4.6223 | 4.7596 | 4.9162 | 5.0413 | 5.1231 | 5.3171 | 5.4515 | 5.5224 | 5.6535 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 10% | 4391.6218 | 5.7666 | 5.933 | 6.5687 | 6.2961 | 5.1175 | 5.3349 | 5.5114 | 5.6813 | 5.8283 | 5.9024 | 6.0112 | 6.1356 | 6.2626 | 6.4223 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475
5% | 4391.6218 | 2.5632 | 2.6246 | 2.9416 | 2.8078 | 2.2033 | 2.3111 | 2.3798 | 2.4581 | 2.5207 | 2.5616 | 2.6586 | 2.7257 | 2.7612 | 2.8268 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 5% | 4391.6218 | 2.8833 | 2.9665 | 3.2844 | 3.1481 | 2.5588 | 2.6674 | 2.7557 | 2.8406 | 2.9142 | 2.9512 | 3.0056 | 3.0678 | 3.1313 | 3.2111 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238
9.992e-14% | 4391.6218 | 5.1223e-14 | 5.245e-14 | 5.8784e-14 | 5.6112e-14 | 4.403e-14 | 4.6186e-14 | 4.7558e-14 | 4.9122e-14 | 5.0373e-14 | 5.119e-14 | 5.3129e-14 | 5.4471e-14 | 5.518e-14 | 5.649e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 9.992e-14% | 4391.6218 | 5.762e-14 | 5.9283e-14 | 6.5635e-14 | 6.2911e-14 | 5.1135e-14 | 5.3306e-14 | 5.507e-14 | 5.6767e-14 | 5.8236e-14 | 5.8976e-14 | 6.0064e-14 | 6.1307e-14 | 6.2576e-14 | 6.4171e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 100% | 0 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
99% | 0.8916 | 44.9122 | 46.7344 | 53.1652 | 58.5818 | 61.5062 | 63.6197 | 66.0564 | 67.8808 | 69.8906 | 70.9469 | 71.8615 | 74.1195 | 72.7651 | 76.445 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 99% | 0.8916 | 47.8019 | 49.7061 | 56.087 | 61.7083 | 64.6429 | 67.0226 | 69.2868 | 71.2166 | 73.2255 | 74.1092 | 75.3125 | 77.5401 | 76.818 | 79.7262 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055
98% | 3.5664 | 44.4586 | 46.2623 | 52.6282 | 57.99 | 60.8849 | 62.9771 | 65.3891 | 67.1951 | 69.1847 | 70.2303 | 71.1356 | 73.3709 | 72.0301 | 75.6728 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 98% | 3.5664 | 47.3191 | 49.204 | 55.5204 | 61.085 | 63.9899 | 66.3456 | 68.5869 | 70.4972 | 72.4858 | 73.3606 | 74.5518 | 76.7569 | 76.0421 | 78.9209 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832
97% | 4.7552 | 44.0049 | 45.7903 | 52.0911 | 57.3983 | 60.2637 | 62.3345 | 64.7219 | 66.5095 | 68.4787 | 69.5136 | 70.4097 | 72.6222 | 71.2951 | 74.9006 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 97% | 4.7552 | 46.8362 | 48.702 | 54.9539 | 60.4617 | 63.337 | 65.6686 | 67.887 | 69.7778 | 71.7461 | 72.612 | 73.7911 | 75.9736 | 75.2661 | 78.1156 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609
95% | 7.7272 | 43.0976 | 44.8461 | 51.0171 | 56.2148 | 59.0211 | 61.0492 | 63.3874 | 65.1381 | 67.0668 | 68.0804 | 68.958 | 71.1248 | 69.8251 | 73.3563 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 95% | 7.7272 | 45.8705 | 47.6978 | 53.8208 | 59.215 | 62.031 | 64.3146 | 66.4873 | 68.3391 | 70.2668 | 71.1149 | 72.2696 | 74.4072 | 73.7142 | 76.505 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164
90% | 39.2302 | 40.8293 | 42.4858 | 48.332 | 53.2562 | 55.9147 | 57.8361 | 60.0513 | 61.7098 | 63.5369 | 64.4972 | 65.3286 | 67.3814 | 66.1501 | 69.4954 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 90% | 39.2302 | 43.4563 | 45.1874 | 50.9882 | 56.0984 | 58.7663 | 60.9296 | 62.988 | 64.7423 | 66.5686 | 67.372 | 68.4659 | 70.491 | 69.8345 | 72.4784 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005
85% | 117.6906 | 38.561 | 40.1255 | 45.6469 | 50.2975 | 52.8084 | 54.623 | 56.7151 | 58.2815 | 60.0071 | 60.914 | 61.6992 | 63.638 | 62.4751 | 65.6346 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 85% | 117.6906 | 41.042 | 42.677 | 48.1555 | 52.9819 | 55.5015 | 57.5446 | 59.4886 | 61.1455 | 62.8703 | 63.6291 | 64.6623 | 66.5748 | 65.9548 | 68.4518 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936
80% | 268.3703 | 36.2927 | 37.7652 | 42.9618 | 47.3388 | 49.702 | 51.4099 | 53.3789 | 54.8532 | 56.4773 | 57.3308 | 58.0699 | 59.8946 | 58.8001 | 61.7737 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 80% | 268.3703 | 38.6278 | 40.1666 | 45.3228 | 49.8653 | 52.2367 | 54.1596 | 55.9893 | 57.5487 | 59.1721 | 59.8862 | 60.8586 | 62.6587 | 62.0751 | 64.4253 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822
75% | 455.9026 | 34.0244 | 35.4048 | 40.2767 | 44.3801 | 46.5956 | 48.1968 | 50.0427 | 51.4248 | 52.9474 | 53.7477 | 54.4405 | 56.1512 | 55.1251 | 57.9128 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 75% | 455.9026 | 36.2136 | 37.6562 | 42.4901 | 46.7487 | 48.9719 | 50.7747 | 52.49 | 53.9519 | 55.4738 | 56.1433 | 57.055 | 58.7425 | 58.1954 | 60.3987 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708
70% | 690.9866 | 31.7561 | 33.0445 | 37.5915 | 41.4215 | 43.4892 | 44.9837 | 46.7065 | 47.9965 | 49.4176 | 50.1645 | 50.8111 | 52.4078 | 51.4501 | 54.052 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 70% | 690.9866 | 33.7993 | 35.1457 | 39.6575 | 43.6321 | 45.7071 | 47.3897 | 48.9907 | 50.3551 | 51.7756 | 52.4004 | 53.2513 | 54.8263 | 54.3158 | 56.3721 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594
65% | 967.6784 | 29.4878 | 30.6842 | 34.9064 | 38.4628 | 40.3829 | 41.7705 | 43.3703 | 44.5682 | 45.8878 | 46.5813 | 47.1818 | 48.6643 | 47.775 | 50.1911 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 65% | 967.6784 | 31.3851 | 32.6353 | 36.8248 | 40.5155 | 42.4423 | 44.0047 | 45.4913 | 46.7584 | 48.0773 | 48.6575 | 49.4476 | 50.9102 | 50.4361 | 52.3455 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448
60% | 1292.8136 | 27.2195 | 28.3239 | 32.2213 | 35.5041 | 37.2765 | 38.5574 | 40.0342 | 41.1399 | 42.358 | 42.9981 | 43.5524 | 44.9209 | 44.1 | 46.3303 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 60% | 1292.8136 | 28.9709 | 30.1249 | 33.9921 | 37.399 | 39.1775 | 40.6197 | 41.992 | 43.1616 | 44.3791 | 44.9146 | 45.644 | 46.994 | 46.5564 | 48.3189 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366
55% | 1647.0743 | 24.9512 | 25.9636 | 29.5362 | 32.5454 | 34.1701 | 35.3443 | 36.698 | 37.7115 | 38.8281 | 39.415 | 39.923 | 41.1775 | 40.425 | 42.4694 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 55% | 1647.0743 | 26.5566 | 27.6145 | 31.1594 | 34.2824 | 35.9127 | 37.2348 | 38.4927 | 39.5648 | 40.6808 | 41.1718 | 41.8403 | 43.0778 | 42.6767 | 44.2924 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253
50% | 2104.1657 | 22.6829 | 23.6032 | 26.8511 | 29.5868 | 31.0637 | 32.1312 | 33.3618 | 34.2832 | 35.2983 | 35.8318 | 36.2937 | 37.4341 | 36.75 | 38.6086 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 50% | 2104.1657 | 24.1424 | 25.1041 | 28.3268 | 31.1658 | 32.6479 | 33.8498 | 34.9933 | 35.968 | 36.9826 | 37.4289 | 38.0366 | 39.1617 | 38.797 | 40.2658 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139
45% | 2736.0097 | 20.4146 | 21.2429 | 24.166 | 26.6281 | 27.9574 | 28.9181 | 30.0256 | 30.8549 | 31.7685 | 32.2486 | 32.6643 | 33.6907 | 33.075 | 34.7477 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 45% | 2736.0097 | 21.7281 | 22.5937 | 25.4941 | 28.0492 | 29.3831 | 30.4648 | 31.494 | 32.3712 | 33.2843 | 33.686 | 34.233 | 35.2455 | 34.9173 | 36.2392 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025
40% | 3483.7613 | 18.1464 | 18.8826 | 21.4809 | 23.6694 | 24.851 | 25.7049 | 26.6894 | 27.4266 | 28.2386 | 28.6654 | 29.0349 | 29.9473 | 29.4 | 30.8868 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 40% | 3483.7613 | 19.3139 | 20.0833 | 22.6614 | 24.9326 | 26.1183 | 27.0798 | 27.9947 | 28.7744 | 29.586 | 29.9431 | 30.4293 | 31.3293 | 31.0376 | 32.2126 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911
35% | 3830.2948 | 15.8781 | 16.5223 | 18.7958 | 20.7107 | 21.7446 | 22.4918 | 23.3533 | 23.9983 | 24.7088 | 25.0822 | 25.4056 | 26.2039 | 25.725 | 27.026 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 35% | 3830.2948 | 16.8997 | 17.5729 | 19.8287 | 21.8161 | 22.8535 | 23.6948 | 24.4953 | 25.1776 | 25.8878 | 26.2002 | 26.6256 | 27.4132 | 27.1579 | 28.186 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797
30% | 3953.6322 | 13.6098 | 14.1619 | 16.1107 | 17.7521 | 18.6382 | 19.2787 | 20.0171 | 20.5699 | 21.179 | 21.4991 | 21.7762 | 22.4605 | 22.05 | 23.1651 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 30% | 3953.6322 | 14.4854 | 15.0625 | 16.9961 | 18.6995 | 19.5888 | 20.3099 | 20.996 | 21.5808 | 22.1895 | 22.4573 | 22.822 | 23.497 | 23.2782 | 24.1595 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683
25% | 4060.9208 | 11.3415 | 11.8016 | 13.4256 | 14.7934 | 15.5319 | 16.0656 | 16.6809 | 17.1416 | 17.6491 | 17.9159 | 18.1468 | 18.7171 | 18.375 | 19.3043 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 25% | 4060.9208 | 12.0712 | 12.5521 | 14.1634 | 15.5829 | 16.324 | 16.9249 | 17.4967 | 17.984 | 18.4913 | 18.7144 | 19.0183 | 19.5808 | 19.3985 | 20.1329 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569
20% | 4165.2375 | 9.0732 | 9.4413 | 10.7404 | 11.8347 | 12.4255 | 12.8525 | 13.3447 | 13.7133 | 14.1193 | 14.3327 | 14.5175 | 14.9736 | 14.7 | 15.4434 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 20% | 4165.2375 | 9.657 | 10.0416 | 11.3307 | 12.4663 | 13.0592 | 13.5399 | 13.9973 | 14.3872 | 14.793 | 14.9715 | 15.2147 | 15.6647 | 15.5188 | 16.1063 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455
15% | 4270.4458 | 6.8049 | 7.081 | 8.0553 | 8.876 | 9.3191 | 9.6394 | 10.0085 | 10.285 | 10.5895 | 10.7495 | 10.8881 | 11.2302 | 11.025 | 11.5826 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 15% | 4270.4458 | 7.2427 | 7.5312 | 8.498 | 9.3497 | 9.7944 | 10.1549 | 10.498 | 10.7904 | 11.0948 | 11.2287 | 11.411 | 11.7485 | 11.6391 | 12.0797 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342
10% | 4373.8709 | 4.5366 | 4.7206 | 5.3702 | 5.9174 | 6.2127 | 6.4262 | 6.6724 | 6.8566 | 7.0597 | 7.1664 | 7.2587 | 7.4868 | 7.35 | 7.7217 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 10% | 4373.8709 | 4.8285 | 5.0208 | 5.6654 | 6.2332 | 6.5296 | 6.77 | 6.9987 | 7.1936 | 7.3965 | 7.4858 | 7.6073 | 7.8323 | 7.7594 | 8.0532 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228
5% | 4391.7028 | 2.2683 | 2.3603 | 2.6851 | 2.9587 | 3.1064 | 3.2131 | 3.3362 | 3.4283 | 3.5298 | 3.5832 | 3.6294 | 3.7434 | 3.675 | 3.8609 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 5% | 4391.7028 | 2.4142 | 2.5104 | 2.8327 | 3.1166 | 3.2648 | 3.385 | 3.4993 | 3.5968 | 3.6983 | 3.7429 | 3.8037 | 3.9162 | 3.8797 | 4.0266 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114
9.992e-14% | 4391.7028 | 4.533e-14 | 4.7169e-14 | 5.3659e-14 | 5.9126e-14 | 6.2078e-14 | 6.4211e-14 | 6.667e-14 | 6.8512e-14 | 7.054e-14 | 7.1606e-14 | 7.2529e-14 | 7.4808e-14 | 7.3441e-14 | 7.7155e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 9.992e-14% | 4391.7028 | 4.8246e-14 | 5.0168e-14 | 5.6608e-14 | 6.2282e-14 | 6.5244e-14 | 6.7645e-14 | 6.9931e-14 | 7.1878e-14 | 7.3906e-14 | 7.4798e-14 | 7.6012e-14 | 7.8261e-14 | 7.7532e-14 | 8.0467e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 100% | 0 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251
99% | 0 | 50.7508 | 51.9667 | 58.2429 | 62.7724 | 65.1574 | 67.2933 | 68.6521 | 70.2026 | 71.4415 | 72.2514 | 74.1722 | 75.502 | 76.2046 | 77.5024 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 99% | 0.75633 | 57.089 | 58.7368 | 65.0304 | 69.5089 | 72.1962 | 74.3476 | 76.0957 | 77.7773 | 79.2327 | 79.9659 | 81.0429 | 82.2746 | 83.5326 | 85.1128 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629
98% | 0.37816 | 50.2382 | 51.4418 | 57.6546 | 62.1384 | 64.4993 | 66.6135 | 67.9586 | 69.4935 | 70.7199 | 71.5215 | 73.423 | 74.7393 | 75.4348 | 76.7195 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 98% | 1.1345 | 56.5124 | 58.1435 | 64.3735 | 68.8068 | 71.467 | 73.5966 | 75.327 | 76.9916 | 78.4324 | 79.1581 | 80.2243 | 81.4436 | 82.6889 | 84.2531 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006
97% | 0.75633 | 49.7256 | 50.9169 | 57.0663 | 61.5043 | 63.8411 | 65.9338 | 67.2652 | 68.7844 | 69.9983 | 70.7917 | 72.6738 | 73.9767 | 74.6651 | 75.9367 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 97% | 1.8908 | 55.9357 | 57.5502 | 63.7166 | 68.1047 | 70.7377 | 72.8456 | 74.5584 | 76.206 | 77.6321 | 78.3504 | 79.4057 | 80.6125 | 81.8451 | 83.3934 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384
95% | 1.8908 | 48.7003 | 49.867 | 55.8896 | 60.2362 | 62.5248 | 64.5743 | 65.8783 | 67.3661 | 68.555 | 69.3321 | 71.1753 | 72.4514 | 73.1256 | 74.371 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 95% | 3.4035 | 54.7824 | 56.3636 | 62.4029 | 66.7005 | 69.2792 | 71.3437 | 73.0211 | 74.6347 | 76.0314 | 76.7349 | 77.7685 | 78.9504 | 80.1576 | 81.6739 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139
90% | 4.538 | 46.1371 | 47.2424 | 52.9481 | 57.0659 | 59.234 | 61.1757 | 62.411 | 63.8205 | 64.9469 | 65.683 | 67.4293 | 68.6381 | 69.2769 | 70.4567 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 90% | 9.0759 | 51.8991 | 53.3971 | 59.1185 | 63.1899 | 65.6329 | 67.5887 | 69.1779 | 70.7066 | 72.0297 | 72.6962 | 73.6754 | 74.7951 | 75.9388 | 77.3753 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026
85% | 9.0759 | 43.574 | 44.6179 | 50.0065 | 53.8955 | 55.9433 | 57.777 | 58.9437 | 60.275 | 61.3387 | 62.034 | 63.6832 | 64.8249 | 65.4282 | 66.5424 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 85% | 16.2611 | 49.0158 | 50.4306 | 55.8342 | 59.6794 | 61.9866 | 63.8338 | 65.3347 | 66.7785 | 68.0281 | 68.6576 | 69.5823 | 70.6398 | 71.72 | 73.0767 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913
80% | 27.606 | 41.0108 | 41.9933 | 47.065 | 50.7252 | 52.6525 | 54.3784 | 55.4764 | 56.7294 | 57.7305 | 58.3849 | 59.9371 | 61.0117 | 61.5795 | 62.6282 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 80% | 24.9588 | 46.1325 | 47.4641 | 52.5498 | 56.1688 | 58.3404 | 60.0789 | 61.4915 | 62.8503 | 64.0264 | 64.6189 | 65.4893 | 66.4845 | 67.5011 | 68.778 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801
75% | 57.481 | 38.4476 | 39.3687 | 44.1234 | 47.5549 | 49.3617 | 50.9797 | 52.0092 | 53.1838 | 54.1224 | 54.7359 | 56.1911 | 57.1985 | 57.7307 | 58.7139 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 75% | 32.9003 | 43.2493 | 44.4976 | 49.2655 | 52.6583 | 54.6941 | 56.324 | 57.6482 | 58.9222 | 60.0248 | 60.5802 | 61.3962 | 62.3292 | 63.2823 | 64.4794 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688
70% | 106.2642 | 35.8844 | 36.7441 | 41.1818 | 44.3846 | 46.0709 | 47.5811 | 48.5419 | 49.6382 | 50.5142 | 51.0868 | 52.445 | 53.3852 | 53.882 | 54.7997 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 70% | 41.9762 | 40.366 | 41.531 | 45.9811 | 49.1477 | 51.0478 | 52.569 | 53.805 | 54.994 | 56.0231 | 56.5415 | 57.3031 | 58.174 | 59.0635 | 60.1808 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576
65% | 201.9397 | 33.3213 | 34.1195 | 38.2403 | 41.2142 | 42.7801 | 44.1824 | 45.0746 | 46.0926 | 46.9061 | 47.4378 | 48.6989 | 49.572 | 50.0333 | 50.8854 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 65% | 67.6914 | 37.4827 | 38.5645 | 42.6967 | 45.6372 | 47.4016 | 48.8141 | 49.9618 | 51.0659 | 52.0215 | 52.5028 | 53.21 | 54.0187 | 54.8447 | 55.8822 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463
60% | 402.745 | 30.7581 | 31.495 | 35.2987 | 38.0439 | 39.4894 | 40.7838 | 41.6073 | 42.547 | 43.2979 | 43.7887 | 44.9529 | 45.7588 | 46.1846 | 46.9711 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 60% | 98.7009 | 34.5994 | 35.598 | 39.4124 | 42.1266 | 43.7553 | 45.0592 | 46.1186 | 47.1377 | 48.0198 | 48.4642 | 49.1169 | 49.8634 | 50.6258 | 51.5835 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351
55% | 655.7369 | 28.1949 | 28.8704 | 32.3572 | 34.8736 | 36.1986 | 37.3851 | 38.14 | 39.0014 | 39.6897 | 40.1396 | 41.2068 | 41.9455 | 42.3359 | 43.0569 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 55% | 153.5347 | 31.7161 | 32.6315 | 36.128 | 38.6161 | 40.109 | 41.3042 | 42.2754 | 43.2096 | 44.0182 | 44.4255 | 45.0239 | 45.7081 | 46.407 | 47.2849 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238
50% | 981.7145 | 25.6317 | 26.2458 | 29.4156 | 31.7033 | 32.9078 | 33.9865 | 34.6728 | 35.4559 | 36.0816 | 36.4906 | 37.4607 | 38.1323 | 38.4872 | 39.1426 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 50% | 258.2862 | 28.8328 | 29.665 | 32.8436 | 35.1055 | 36.4627 | 37.5493 | 38.4322 | 39.2814 | 40.0165 | 40.3868 | 40.9308 | 41.5528 | 42.1882 | 42.9863 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126
45% | 1622.7029 | 23.0686 | 23.6212 | 26.474 | 28.5329 | 29.617 | 30.5878 | 31.2055 | 31.9103 | 32.4734 | 32.8415 | 33.7146 | 34.3191 | 34.6384 | 35.2283 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 45% | 488.9664 | 25.9496 | 26.6985 | 29.5593 | 31.595 | 32.8165 | 33.7944 | 34.5889 | 35.3533 | 36.0149 | 36.3481 | 36.8377 | 37.3975 | 37.9694 | 38.6876 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013
40% | 2442.9413 | 20.5054 | 20.9966 | 23.5325 | 25.3626 | 26.3262 | 27.1892 | 27.7382 | 28.3647 | 28.8653 | 29.1925 | 29.9686 | 30.5058 | 30.7897 | 31.3141 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 40% | 928.0152 | 23.0663 | 23.732 | 26.2749 | 28.0844 | 29.1702 | 30.0394 | 30.7457 | 31.4252 | 32.0132 | 32.3094 | 32.7446 | 33.2423 | 33.7506 | 34.389 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49
35% | 3006.7842 | 17.9422 | 18.3721 | 20.5909 | 22.1923 | 23.0355 | 23.7905 | 24.2709 | 24.8191 | 25.2571 | 25.5434 | 26.2225 | 26.6926 | 26.941 | 27.3998 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 35% | 1530.4309 | 20.183 | 20.7655 | 22.9905 | 24.5739 | 25.5239 | 26.2845 | 26.9025 | 27.497 | 28.0116 | 28.2708 | 28.6515 | 29.087 | 29.5317 | 30.0904 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788
30% | 3276.4154 | 15.379 | 15.7475 | 17.6494 | 19.022 | 19.7447 | 20.3919 | 20.8037 | 21.2735 | 21.649 | 21.8943 | 22.4764 | 22.8794 | 23.0923 | 23.4856 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 30% | 2592.3162 | 17.2997 | 17.799 | 19.7062 | 21.0633 | 21.8776 | 22.5296 | 23.0593 | 23.5689 | 24.0099 | 24.2321 | 24.5585 | 24.9317 | 25.3129 | 25.7918 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675
25% | 3466.632 | 12.8159 | 13.1229 | 14.7078 | 15.8516 | 16.4539 | 16.9932 | 17.3364 | 17.7279 | 18.0408 | 18.2453 | 18.7304 | 19.0662 | 19.2436 | 19.5713 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 25% | 3659.4958 | 14.4164 | 14.8325 | 16.4218 | 17.5528 | 18.2314 | 18.7747 | 19.2161 | 19.6407 | 20.0083 | 20.1934 | 20.4654 | 20.7764 | 21.0941 | 21.4931 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563
20% | 3713.9514 | 10.2527 | 10.4983 | 11.7662 | 12.6813 | 13.1631 | 13.5946 | 13.8691 | 14.1823 | 14.4326 | 14.5962 | 14.9843 | 15.2529 | 15.3949 | 15.657 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 20% | 4005.5161 | 11.5331 | 11.866 | 13.1375 | 14.0422 | 14.5851 | 15.0197 | 15.3729 | 15.7126 | 16.0066 | 16.1547 | 16.3723 | 16.6211 | 16.8753 | 17.1945 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245
15% | 4043.3325 | 7.6895 | 7.8737 | 8.8247 | 9.511 | 9.8723 | 10.1959 | 10.4018 | 10.6368 | 10.8245 | 10.9472 | 11.2382 | 11.4397 | 11.5461 | 11.7428 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 15% | 4281.1979 | 8.6499 | 8.8995 | 9.8531 | 10.5317 | 10.9388 | 11.2648 | 11.5296 | 11.7844 | 12.005 | 12.116 | 12.2792 | 12.4658 | 12.6565 | 12.8959 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338
10% | 4350.7801 | 5.1263 | 5.2492 | 5.8831 | 6.3407 | 6.5816 | 6.7973 | 6.9346 | 7.0912 | 7.2163 | 7.2981 | 7.4921 | 7.6265 | 7.6974 | 7.8285 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 10% | 4391.6218 | 5.7666 | 5.933 | 6.5687 | 7.0211 | 7.2925 | 7.5099 | 7.6864 | 7.8563 | 8.0033 | 8.0774 | 8.1862 | 8.3106 | 8.4376 | 8.5973 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225
5% | 4391.6218 | 2.5632 | 2.6246 | 2.9416 | 3.1703 | 3.2908 | 3.3986 | 3.4673 | 3.5456 | 3.6082 | 3.6491 | 3.7461 | 3.8132 | 3.8487 | 3.9143 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 5% | 4391.6218 | 2.8833 | 2.9665 | 3.2844 | 3.5106 | 3.6463 | 3.7549 | 3.8432 | 3.9281 | 4.0017 | 4.0387 | 4.0931 | 4.1553 | 4.2188 | 4.2986 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113
9.992e-14% | 4391.6218 | 5.1223e-14 | 5.245e-14 | 5.8784e-14 | 6.3356e-14 | 6.5763e-14 | 6.7919e-14 | 6.929e-14 | 7.0855e-14 | 7.2105e-14 | 7.2923e-14 | 7.4862e-14 | 7.6204e-14 | 7.6913e-14 | 7.8223e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 9.992e-14% | 4391.6218 | 5.762e-14 | 5.9283e-14 | 6.5635e-14 | 7.0155e-14 | 7.2867e-14 | 7.5039e-14 | 7.6803e-14 | 7.85e-14 | 7.9969e-14 | 8.0709e-14 | 8.1796e-14 | 8.3039e-14 | 8.4309e-14 | 8.5904e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.3659 | 47.2065 | 53.7022 | 51.9235 | 40.3775 | 42.5124 | 44.9736 | 46.8164 | 48.8466 | 49.9136 | 50.8373 | 53.1182 | 51.7501 | 55.4671 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 60.3145 | 100% | 0 | 48.2848 | 50.2082 | 56.6535 | 55.0816 | 43.5458 | 45.9496 | 48.2366 | 50.1859 | 52.2151 | 53.1077 | 54.3233 | 56.5733 | 55.8439 | 58.7816 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777 | 60.4777
99% | 0.8916 | 44.9122 | 46.7344 | 53.1652 | 51.4043 | 39.9737 | 42.0872 | 44.5239 | 46.3483 | 48.3581 | 49.4144 | 50.329 | 52.587 | 51.2326 | 54.9125 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 59.7114 | 99% | 0.8916 | 47.8019 | 49.7061 | 56.087 | 54.5308 | 43.1104 | 45.4901 | 47.7543 | 49.6841 | 51.693 | 52.5767 | 53.78 | 56.0076 | 55.2855 | 58.1937 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873 | 59.873
98% | 3.5664 | 44.4586 | 46.2623 | 52.6282 | 50.885 | 39.5699 | 41.6621 | 44.0741 | 45.8801 | 47.8697 | 48.9153 | 49.8206 | 52.0559 | 50.7151 | 54.3578 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 59.1082 | 98% | 3.5664 | 47.3191 | 49.204 | 55.5204 | 53.98 | 42.6749 | 45.0306 | 47.2719 | 49.1822 | 51.1708 | 52.0456 | 53.2368 | 55.4419 | 54.7271 | 57.6059 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682 | 59.2682
97% | 4.7552 | 44.0049 | 45.7903 | 52.0911 | 50.3658 | 39.1662 | 41.237 | 43.6244 | 45.412 | 47.3812 | 48.4161 | 49.3122 | 51.5247 | 50.1976 | 53.8031 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 58.5051 | 97% | 4.7552 | 46.8362 | 48.702 | 54.9539 | 53.4292 | 42.2395 | 44.5711 | 46.7895 | 48.6803 | 50.6486 | 51.5145 | 52.6936 | 54.8761 | 54.1686 | 57.0181 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634 | 58.6634
95% | 7.7272 | 43.0976 | 44.8461 | 51.0171 | 49.3273 | 38.3586 | 40.3867 | 42.7249 | 44.4756 | 46.4043 | 47.4179 | 48.2955 | 50.4623 | 49.1626 | 52.6938 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 57.2988 | 95% | 7.7272 | 45.8705 | 47.6978 | 53.8208 | 52.3275 | 41.3685 | 43.6521 | 45.8248 | 47.6766 | 49.6043 | 50.4524 | 51.6071 | 53.7447 | 53.0517 | 55.8425 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539 | 57.4539
90% | 39.2302 | 40.8293 | 42.4858 | 48.332 | 46.7312 | 36.3397 | 38.2611 | 40.4763 | 42.1348 | 43.9619 | 44.9222 | 45.7536 | 47.8064 | 46.5751 | 49.9204 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 54.283 | 90% | 39.2302 | 43.4563 | 45.1874 | 50.9882 | 49.5734 | 39.1913 | 41.3546 | 43.413 | 45.1673 | 46.9936 | 47.797 | 48.8909 | 50.916 | 50.2595 | 52.9034 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43 | 54.43
85% | 117.6906 | 38.561 | 40.1255 | 45.6469 | 44.135 | 34.3209 | 36.1355 | 38.2276 | 39.794 | 41.5196 | 42.4265 | 43.2117 | 45.1505 | 43.9876 | 47.1471 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 51.2673 | 85% | 117.6906 | 41.042 | 42.677 | 48.1555 | 46.8194 | 37.014 | 39.0571 | 41.0011 | 42.658 | 44.3828 | 45.1416 | 46.1748 | 48.0873 | 47.4673 | 49.9643 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061 | 51.4061
80% | 268.3703 | 36.2927 | 37.7652 | 42.9618 | 41.5388 | 32.302 | 34.0099 | 35.9789 | 37.4532 | 39.0773 | 39.9308 | 40.6699 | 42.4946 | 41.4001 | 44.3737 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 48.2516 | 80% | 268.3703 | 38.6278 | 40.1666 | 45.3228 | 44.0653 | 34.8367 | 36.7596 | 38.5893 | 40.1487 | 41.7721 | 42.4862 | 43.4586 | 45.2587 | 44.6751 | 47.0253 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822 | 48.3822
75% | 455.9026 | 34.0244 | 35.4048 | 40.2767 | 38.9426 | 30.2831 | 31.8843 | 33.7302 | 35.1123 | 36.6349 | 37.4352 | 38.128 | 39.8387 | 38.8126 | 41.6003 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 45.2359 | 75% | 455.9026 | 36.2136 | 37.6562 | 42.4901 | 41.3112 | 32.6594 | 34.4622 | 36.1775 | 37.6394 | 39.1613 | 39.8308 | 40.7425 | 42.43 | 41.8829 | 44.0862 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583 | 45.3583
70% | 690.9866 | 31.7561 | 33.0445 | 37.5915 | 36.3465 | 28.2642 | 29.7587 | 31.4815 | 32.7715 | 34.1926 | 34.9395 | 35.5861 | 37.1828 | 36.2251 | 38.827 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 42.2201 | 70% | 690.9866 | 33.7993 | 35.1457 | 39.6575 | 38.5571 | 30.4821 | 32.1647 | 33.7657 | 35.1301 | 36.5506 | 37.1754 | 38.0263 | 39.6013 | 39.0908 | 41.1471 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344 | 42.3344
65% | 967.6784 | 29.4878 | 30.6842 | 34.9064 | 33.7503 | 26.2454 | 27.633 | 29.2328 | 30.4307 | 31.7503 | 32.4438 | 33.0443 | 34.5268 | 33.6375 | 36.0536 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 39.2044 | 65% | 967.6784 | 31.3851 | 32.6353 | 36.8248 | 35.803 | 28.3048 | 29.8672 | 31.3538 | 32.6209 | 33.9398 | 34.52 | 35.3101 | 36.7727 | 36.2986 | 38.208 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105 | 39.3105
60% | 1292.8136 | 27.2195 | 28.3239 | 32.2213 | 31.1541 | 24.2265 | 25.5074 | 26.9842 | 28.0899 | 29.308 | 29.9481 | 30.5024 | 31.8709 | 31.05 | 33.2803 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 36.1887 | 60% | 1292.8136 | 28.9709 | 30.1249 | 33.9921 | 33.049 | 26.1275 | 27.5697 | 28.942 | 30.1116 | 31.3291 | 31.8646 | 32.594 | 33.944 | 33.5064 | 35.2689 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866 | 36.2866
55% | 1647.0743 | 24.9512 | 25.9636 | 29.5362 | 28.5579 | 22.2076 | 23.3818 | 24.7355 | 25.749 | 26.8656 | 27.4525 | 27.9605 | 29.215 | 28.4625 | 30.5069 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 33.173 | 55% | 1647.0743 | 26.5566 | 27.6145 | 31.1594 | 30.2949 | 23.9502 | 25.2723 | 26.5302 | 27.6023 | 28.7183 | 29.2093 | 29.8778 | 31.1153 | 30.7142 | 32.3299 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628 | 33.2628
50% | 2104.1657 | 22.6829 | 23.6032 | 26.8511 | 25.9618 | 20.1887 | 21.2562 | 22.4868 | 23.4082 | 24.4233 | 24.9568 | 25.4187 | 26.5591 | 25.875 | 27.7336 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 30.1572 | 50% | 2104.1657 | 24.1424 | 25.1041 | 28.3268 | 27.5408 | 21.7729 | 22.9748 | 24.1183 | 25.093 | 26.1076 | 26.5539 | 27.1616 | 28.2867 | 27.922 | 29.3908 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389 | 30.2389
45% | 2736.0097 | 20.4146 | 21.2429 | 24.166 | 23.3656 | 18.1699 | 19.1306 | 20.2381 | 21.0674 | 21.981 | 22.4611 | 22.8768 | 23.9032 | 23.2875 | 24.9602 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 27.1415 | 45% | 2736.0097 | 21.7281 | 22.5937 | 25.4941 | 24.7867 | 19.5956 | 20.6773 | 21.7065 | 22.5837 | 23.4968 | 23.8985 | 24.4455 | 25.458 | 25.1298 | 26.4517 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215 | 27.215
40% | 3483.7613 | 18.1464 | 18.8826 | 21.4809 | 20.7694 | 16.151 | 17.0049 | 17.9894 | 18.7266 | 19.5386 | 19.9654 | 20.3349 | 21.2473 | 20.7 | 22.1868 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 24.1258 | 40% | 3483.7613 | 19.3139 | 20.0833 | 22.6614 | 22.0326 | 17.4183 | 18.3798 | 19.2947 | 20.0744 | 20.886 | 21.2431 | 21.7293 | 22.6293 | 22.3376 | 23.5126 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911 | 24.1911
35% | 3830.2948 | 15.8781 | 16.5223 | 18.7958 | 18.1732 | 14.1321 | 14.8793 | 15.7408 | 16.3858 | 17.0963 | 17.4697 | 17.7931 | 18.5914 | 18.1125 | 19.4135 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 21.1101 | 35% | 3830.2948 | 16.8997 | 17.5729 | 19.8287 | 19.2786 | 15.241 | 16.0823 | 16.8828 | 17.5651 | 18.2753 | 18.5877 | 19.0131 | 19.8007 | 19.5454 | 20.5735 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672 | 21.1672
30% | 3953.6322 | 13.6098 | 14.1619 | 16.1107 | 15.5771 | 12.1132 | 12.7537 | 13.4921 | 14.0449 | 14.654 | 14.9741 | 15.2512 | 15.9355 | 15.525 | 16.6401 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 18.0943 | 30% | 3953.6322 | 14.4854 | 15.0625 | 16.9961 | 16.5245 | 13.0638 | 13.7849 | 14.471 | 15.0558 | 15.6645 | 15.9323 | 16.297 | 16.972 | 16.7532 | 17.6345 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433 | 18.1433
25% | 4060.9208 | 11.3415 | 11.8016 | 13.4256 | 12.9809 | 10.0944 | 10.6281 | 11.2434 | 11.7041 | 12.2116 | 12.4784 | 12.7093 | 13.2796 | 12.9375 | 13.8668 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 15.0786 | 25% | 4060.9208 | 12.0712 | 12.5521 | 14.1634 | 13.7704 | 10.8865 | 11.4874 | 12.0592 | 12.5465 | 13.0538 | 13.2769 | 13.5808 | 14.1433 | 13.961 | 14.6954 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194 | 15.1194
20% | 4165.2375 | 9.0732 | 9.4413 | 10.7404 | 10.3847 | 8.0755 | 8.5025 | 8.9947 | 9.3633 | 9.7693 | 9.9827 | 10.1675 | 10.6236 | 10.35 | 11.0934 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 12.0629 | 20% | 4165.2375 | 9.657 | 10.0416 | 11.3307 | 11.0163 | 8.7092 | 9.1899 | 9.6473 | 10.0372 | 10.443 | 10.6215 | 10.8647 | 11.3147 | 11.1688 | 11.7563 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955 | 12.0955
15% | 4270.4458 | 6.8049 | 7.081 | 8.0553 | 7.7885 | 6.0566 | 6.3769 | 6.746 | 7.0225 | 7.327 | 7.487 | 7.6256 | 7.9677 | 7.7625 | 8.3201 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 9.0472 | 15% | 4270.4458 | 7.2427 | 7.5312 | 8.498 | 8.2622 | 6.5319 | 6.8924 | 7.2355 | 7.5279 | 7.8323 | 7.9662 | 8.1485 | 8.486 | 8.3766 | 8.8172 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717 | 9.0717
10% | 4373.8709 | 4.5366 | 4.7206 | 5.3702 | 5.1924 | 4.0377 | 4.2512 | 4.4974 | 4.6816 | 4.8847 | 4.9914 | 5.0837 | 5.3118 | 5.175 | 5.5467 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 6.0314 | 10% | 4373.8709 | 4.8285 | 5.0208 | 5.6654 | 5.5082 | 4.3546 | 4.595 | 4.8237 | 5.0186 | 5.2215 | 5.3108 | 5.4323 | 5.6573 | 5.5844 | 5.8782 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478 | 6.0478
5% | 4391.7028 | 2.2683 | 2.3603 | 2.6851 | 2.5962 | 2.0189 | 2.1256 | 2.2487 | 2.3408 | 2.4423 | 2.4957 | 2.5419 | 2.6559 | 2.5875 | 2.7734 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 3.0157 | 5% | 4391.7028 | 2.4142 | 2.5104 | 2.8327 | 2.7541 | 2.1773 | 2.2975 | 2.4118 | 2.5093 | 2.6108 | 2.6554 | 2.7162 | 2.8287 | 2.7922 | 2.9391 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239 | 3.0239
9.992e-14% | 4391.7028 | 4.533e-14 | 4.7169e-14 | 5.3659e-14 | 5.1882e-14 | 4.0345e-14 | 4.2478e-14 | 4.4938e-14 | 4.6779e-14 | 4.8808e-14 | 4.9874e-14 | 5.0797e-14 | 5.3076e-14 | 5.1709e-14 | 5.5423e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 6.0266e-14 | 9.992e-14% | 4391.7028 | 4.8246e-14 | 5.0168e-14 | 5.6608e-14 | 5.5038e-14 | 4.3511e-14 | 4.5913e-14 | 4.8198e-14 | 5.0146e-14 | 5.2173e-14 | 5.3065e-14 | 5.428e-14 | 5.6528e-14 | 5.5799e-14 | 5.8735e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14 | 6.0429e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.2635 | 52.4916 | 58.8312 | 56.1565 | 44.0656 | 46.223 | 47.5955 | 49.1617 | 50.4132 | 51.2312 | 53.1714 | 54.5146 | 55.2243 | 56.5352 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 56.1589 | 100% | 0 | 57.6657 | 59.3301 | 65.6873 | 62.961 | 51.1755 | 53.3486 | 55.1143 | 56.8129 | 58.283 | 59.0236 | 60.1116 | 61.3557 | 62.6264 | 64.2226 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751 | 64.4751
99% | 0 | 50.7508 | 51.9667 | 58.2429 | 55.5949 | 43.6249 | 45.7608 | 47.1196 | 48.6701 | 49.909 | 50.7189 | 52.6397 | 53.9695 | 54.6721 | 55.9699 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 55.5973 | 99% | 0.75633 | 57.089 | 58.7368 | 65.0304 | 62.3314 | 50.6637 | 52.8151 | 54.5632 | 56.2448 | 57.7002 | 58.4334 | 59.5104 | 60.7421 | 62.0001 | 63.5803 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304 | 63.8304
98% | 0.37816 | 50.2382 | 51.4418 | 57.6546 | 55.0334 | 43.1843 | 45.2985 | 46.6436 | 48.1785 | 49.4049 | 50.2065 | 52.108 | 53.4243 | 54.1198 | 55.4045 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 55.0357 | 98% | 1.1345 | 56.5124 | 58.1435 | 64.3735 | 61.7018 | 50.152 | 52.2816 | 54.012 | 55.6766 | 57.1174 | 57.8431 | 58.9093 | 60.1286 | 61.3739 | 62.9381 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856 | 63.1856
97% | 0.75633 | 49.7256 | 50.9169 | 57.0663 | 54.4718 | 42.7436 | 44.8363 | 46.1677 | 47.6869 | 48.9008 | 49.6942 | 51.5763 | 52.8792 | 53.5676 | 54.8392 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 54.4741 | 97% | 1.8908 | 55.9357 | 57.5502 | 63.7166 | 61.0722 | 49.6402 | 51.7481 | 53.4609 | 55.1085 | 56.5346 | 57.2529 | 58.3082 | 59.515 | 60.7476 | 62.2959 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409 | 62.5409
95% | 1.8908 | 48.7003 | 49.867 | 55.8896 | 53.3487 | 41.8623 | 43.9118 | 45.2158 | 46.7036 | 47.8925 | 48.6696 | 50.5128 | 51.7889 | 52.4631 | 53.7085 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 53.3509 | 95% | 3.4035 | 54.7824 | 56.3636 | 62.4029 | 59.813 | 48.6167 | 50.6812 | 52.3586 | 53.9722 | 55.3689 | 56.0724 | 57.106 | 58.2879 | 59.4951 | 61.0114 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514 | 61.2514
90% | 4.538 | 46.1371 | 47.2424 | 52.9481 | 50.5409 | 39.659 | 41.6007 | 42.836 | 44.2455 | 45.3719 | 46.108 | 47.8543 | 49.0631 | 49.7019 | 50.8817 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 50.543 | 90% | 9.0759 | 51.8991 | 53.3971 | 59.1185 | 56.6649 | 46.0579 | 48.0137 | 49.6029 | 51.1316 | 52.4547 | 53.1212 | 54.1004 | 55.2201 | 56.3638 | 57.8003 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276 | 58.0276
85% | 9.0759 | 43.574 | 44.6179 | 50.0065 | 47.733 | 37.4558 | 39.2895 | 40.4562 | 41.7875 | 42.8512 | 43.5465 | 45.1957 | 46.3374 | 46.9407 | 48.0549 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 47.735 | 85% | 16.2611 | 49.0158 | 50.4306 | 55.8342 | 53.5169 | 43.4991 | 45.3463 | 46.8472 | 48.291 | 49.5406 | 50.1701 | 51.0948 | 52.1523 | 53.2325 | 54.5892 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038 | 54.8038
80% | 27.606 | 41.0108 | 41.9933 | 47.065 | 44.9252 | 35.2525 | 36.9784 | 38.0764 | 39.3294 | 40.3305 | 40.9849 | 42.5371 | 43.6117 | 44.1795 | 45.2282 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 44.9271 | 80% | 24.9588 | 46.1325 | 47.4641 | 52.5498 | 50.3688 | 40.9404 | 42.6789 | 44.0915 | 45.4503 | 46.6264 | 47.2189 | 48.0893 | 49.0845 | 50.1011 | 51.378 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801 | 51.5801
75% | 57.481 | 38.4476 | 39.3687 | 44.1234 | 42.1174 | 33.0492 | 34.6672 | 35.6967 | 36.8713 | 37.8099 | 38.4234 | 39.8786 | 40.886 | 41.4182 | 42.4014 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 42.1191 | 75% | 32.9003 | 43.2493 | 44.4976 | 49.2655 | 47.2208 | 38.3816 | 40.0115 | 41.3357 | 42.6097 | 43.7123 | 44.2677 | 45.0837 | 46.0167 | 46.9698 | 48.1669 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563 | 48.3563
70% | 106.2642 | 35.8844 | 36.7441 | 41.1818 | 39.3096 | 30.8459 | 32.3561 | 33.3169 | 34.4132 | 35.2892 | 35.8618 | 37.22 | 38.1602 | 38.657 | 39.5747 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 39.3112 | 70% | 41.9762 | 40.366 | 41.531 | 45.9811 | 44.0727 | 35.8228 | 37.344 | 38.58 | 39.769 | 40.7981 | 41.3165 | 42.0781 | 42.949 | 43.8385 | 44.9558 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326 | 45.1326
65% | 201.9397 | 33.3213 | 34.1195 | 38.2403 | 36.5017 | 28.6426 | 30.0449 | 30.9371 | 31.9551 | 32.7686 | 33.3003 | 34.5614 | 35.4345 | 35.8958 | 36.7479 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 36.5033 | 65% | 67.6914 | 37.4827 | 38.5645 | 42.6967 | 40.9247 | 33.2641 | 34.6766 | 35.8243 | 36.9284 | 37.884 | 38.3653 | 39.0725 | 39.8812 | 40.7072 | 41.7447 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088 | 41.9088
60% | 402.745 | 30.7581 | 31.495 | 35.2987 | 33.6939 | 26.4394 | 27.7338 | 28.5573 | 29.497 | 30.2479 | 30.7387 | 31.9029 | 32.7088 | 33.1346 | 33.9211 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 33.6953 | 60% | 98.7009 | 34.5994 | 35.598 | 39.4124 | 37.7766 | 30.7053 | 32.0092 | 33.0686 | 34.0877 | 34.9698 | 35.4142 | 36.0669 | 36.8134 | 37.5758 | 38.5335 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851 | 38.6851
55% | 655.7369 | 28.1949 | 28.8704 | 32.3572 | 30.8861 | 24.2361 | 25.4226 | 26.1775 | 27.0389 | 27.7272 | 28.1771 | 29.2443 | 29.983 | 30.3734 | 31.0944 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 30.8874 | 55% | 153.5347 | 31.7161 | 32.6315 | 36.128 | 34.6286 | 28.1465 | 29.3417 | 30.3129 | 31.2471 | 32.0557 | 32.463 | 33.0614 | 33.7456 | 34.4445 | 35.3224 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613 | 35.4613
50% | 981.7145 | 25.6317 | 26.2458 | 29.4156 | 28.0783 | 22.0328 | 23.1115 | 23.7978 | 24.5809 | 25.2066 | 25.6156 | 26.5857 | 27.2573 | 27.6122 | 28.2676 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 28.0794 | 50% | 258.2862 | 28.8328 | 29.665 | 32.8436 | 31.4805 | 25.5877 | 26.6743 | 27.5572 | 28.4064 | 29.1415 | 29.5118 | 30.0558 | 30.6778 | 31.3132 | 32.1113 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376 | 32.2376
45% | 1622.7029 | 23.0686 | 23.6212 | 26.474 | 25.2704 | 19.8295 | 20.8003 | 21.418 | 22.1228 | 22.6859 | 23.054 | 23.9271 | 24.5316 | 24.8509 | 25.4408 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 25.2715 | 45% | 488.9664 | 25.9496 | 26.6985 | 29.5593 | 28.3325 | 23.029 | 24.0069 | 24.8014 | 25.5658 | 26.2274 | 26.5606 | 27.0502 | 27.61 | 28.1819 | 28.9001 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138 | 29.0138
40% | 2442.9413 | 20.5054 | 20.9966 | 23.5325 | 22.4626 | 17.6262 | 18.4892 | 19.0382 | 19.6647 | 20.1653 | 20.4925 | 21.2686 | 21.8058 | 22.0897 | 22.6141 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 22.4635 | 40% | 928.0152 | 23.0663 | 23.732 | 26.2749 | 25.1844 | 20.4702 | 21.3394 | 22.0457 | 22.7252 | 23.3132 | 23.6094 | 24.0446 | 24.5423 | 25.0506 | 25.689 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79 | 25.79
35% | 3006.7842 | 17.9422 | 18.3721 | 20.5909 | 19.6548 | 15.423 | 16.178 | 16.6584 | 17.2066 | 17.6446 | 17.9309 | 18.61 | 19.0801 | 19.3285 | 19.7873 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 19.6556 | 35% | 1530.4309 | 20.183 | 20.7655 | 22.9905 | 22.0364 | 17.9114 | 18.672 | 19.29 | 19.8845 | 20.3991 | 20.6583 | 21.039 | 21.4745 | 21.9192 | 22.4779 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663 | 22.5663
30% | 3276.4154 | 15.379 | 15.7475 | 17.6494 | 16.847 | 13.2197 | 13.8669 | 14.2787 | 14.7485 | 15.124 | 15.3693 | 15.9514 | 16.3544 | 16.5673 | 16.9606 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 16.8477 | 30% | 2592.3162 | 17.2997 | 17.799 | 19.7062 | 18.8883 | 15.3526 | 16.0046 | 16.5343 | 17.0439 | 17.4849 | 17.7071 | 18.0335 | 18.4067 | 18.7879 | 19.2668 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425 | 19.3425
25% | 3466.632 | 12.8159 | 13.1229 | 14.7078 | 14.0391 | 11.0164 | 11.5557 | 11.8989 | 12.2904 | 12.6033 | 12.8078 | 13.2929 | 13.6287 | 13.8061 | 14.1338 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 14.0397 | 25% | 3659.4958 | 14.4164 | 14.8325 | 16.4218 | 15.7403 | 12.7939 | 13.3372 | 13.7786 | 14.2032 | 14.5708 | 14.7559 | 15.0279 | 15.3389 | 15.6566 | 16.0556 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188 | 16.1188
20% | 3713.9514 | 10.2527 | 10.4983 | 11.7662 | 11.2313 | 8.8131 | 9.2446 | 9.5191 | 9.8323 | 10.0826 | 10.2462 | 10.6343 | 10.9029 | 11.0449 | 11.307 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 11.2318 | 20% | 4005.5161 | 11.5331 | 11.866 | 13.1375 | 12.5922 | 10.2351 | 10.6697 | 11.0229 | 11.3626 | 11.6566 | 11.8047 | 12.0223 | 12.2711 | 12.5253 | 12.8445 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895 | 12.895
15% | 4043.3325 | 7.6895 | 7.8737 | 8.8247 | 8.4235 | 6.6098 | 6.9334 | 7.1393 | 7.3743 | 7.562 | 7.6847 | 7.9757 | 8.1772 | 8.2836 | 8.4803 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 8.4238 | 15% | 4281.1979 | 8.6499 | 8.8995 | 9.8531 | 9.4442 | 7.6763 | 8.0023 | 8.2671 | 8.5219 | 8.7425 | 8.8535 | 9.0167 | 9.2033 | 9.394 | 9.6334 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713 | 9.6713
10% | 4350.7801 | 5.1263 | 5.2492 | 5.8831 | 5.6157 | 4.4066 | 4.6223 | 4.7596 | 4.9162 | 5.0413 | 5.1231 | 5.3171 | 5.4515 | 5.5224 | 5.6535 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 5.6159 | 10% | 4391.6218 | 5.7666 | 5.933 | 6.5687 | 6.2961 | 5.1175 | 5.3349 | 5.5114 | 5.6813 | 5.8283 | 5.9024 | 6.0112 | 6.1356 | 6.2626 | 6.4223 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475 | 6.4475
5% | 4391.6218 | 2.5632 | 2.6246 | 2.9416 | 2.8078 | 2.2033 | 2.3111 | 2.3798 | 2.4581 | 2.5207 | 2.5616 | 2.6586 | 2.7257 | 2.7612 | 2.8268 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 2.8079 | 5% | 4391.6218 | 2.8833 | 2.9665 | 3.2844 | 3.1481 | 2.5588 | 2.6674 | 2.7557 | 2.8406 | 2.9142 | 2.9512 | 3.0056 | 3.0678 | 3.1313 | 3.2111 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238 | 3.2238
9.992e-14% | 4391.6218 | 5.1223e-14 | 5.245e-14 | 5.8784e-14 | 5.6112e-14 | 4.403e-14 | 4.6186e-14 | 4.7558e-14 | 4.9122e-14 | 5.0373e-14 | 5.119e-14 | 5.3129e-14 | 5.4471e-14 | 5.518e-14 | 5.649e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 5.6114e-14 | 9.992e-14% | 4391.6218 | 5.762e-14 | 5.9283e-14 | 6.5635e-14 | 6.2911e-14 | 5.1135e-14 | 5.3306e-14 | 5.507e-14 | 5.6767e-14 | 5.8236e-14 | 5.8976e-14 | 6.0064e-14 | 6.1307e-14 | 6.2576e-14 | 6.4171e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14 | 6.4424e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 100% | 0 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
99% | 0.8916 | 44.9122 | 46.7344 | 53.1652 | 58.5818 | 61.5062 | 63.6197 | 66.0564 | 67.8808 | 69.8906 | 70.9469 | 71.8615 | 74.1195 | 72.7651 | 76.445 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 99% | 0.8916 | 47.8019 | 49.7061 | 56.087 | 61.7083 | 64.6429 | 67.0226 | 69.2868 | 71.2166 | 73.2255 | 74.1092 | 75.3125 | 77.5401 | 76.818 | 79.7262 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055
98% | 3.5664 | 44.4586 | 46.2623 | 52.6282 | 57.99 | 60.8849 | 62.9771 | 65.3891 | 67.1951 | 69.1847 | 70.2303 | 71.1356 | 73.3709 | 72.0301 | 75.6728 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 98% | 3.5664 | 47.3191 | 49.204 | 55.5204 | 61.085 | 63.9899 | 66.3456 | 68.5869 | 70.4972 | 72.4858 | 73.3606 | 74.5518 | 76.7569 | 76.0421 | 78.9209 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832
97% | 4.7552 | 44.0049 | 45.7903 | 52.0911 | 57.3983 | 60.2637 | 62.3345 | 64.7219 | 66.5095 | 68.4787 | 69.5136 | 70.4097 | 72.6222 | 71.2951 | 74.9006 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 97% | 4.7552 | 46.8362 | 48.702 | 54.9539 | 60.4617 | 63.337 | 65.6686 | 67.887 | 69.7778 | 71.7461 | 72.612 | 73.7911 | 75.9736 | 75.2661 | 78.1156 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609
95% | 7.7272 | 43.0976 | 44.8461 | 51.0171 | 56.2148 | 59.0211 | 61.0492 | 63.3874 | 65.1381 | 67.0668 | 68.0804 | 68.958 | 71.1248 | 69.8251 | 73.3563 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 95% | 7.7272 | 45.8705 | 47.6978 | 53.8208 | 59.215 | 62.031 | 64.3146 | 66.4873 | 68.3391 | 70.2668 | 71.1149 | 72.2696 | 74.4072 | 73.7142 | 76.505 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164
90% | 39.2302 | 40.8293 | 42.4858 | 48.332 | 53.2562 | 55.9147 | 57.8361 | 60.0513 | 61.7098 | 63.5369 | 64.4972 | 65.3286 | 67.3814 | 66.1501 | 69.4954 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 90% | 39.2302 | 43.4563 | 45.1874 | 50.9882 | 56.0984 | 58.7663 | 60.9296 | 62.988 | 64.7423 | 66.5686 | 67.372 | 68.4659 | 70.491 | 69.8345 | 72.4784 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005
85% | 117.6906 | 38.561 | 40.1255 | 45.6469 | 50.2975 | 52.8084 | 54.623 | 56.7151 | 58.2815 | 60.0071 | 60.914 | 61.6992 | 63.638 | 62.4751 | 65.6346 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 85% | 117.6906 | 41.042 | 42.677 | 48.1555 | 52.9819 | 55.5015 | 57.5446 | 59.4886 | 61.1455 | 62.8703 | 63.6291 | 64.6623 | 66.5748 | 65.9548 | 68.4518 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936
80% | 268.3703 | 36.2927 | 37.7652 | 42.9618 | 47.3388 | 49.702 | 51.4099 | 53.3789 | 54.8532 | 56.4773 | 57.3308 | 58.0699 | 59.8946 | 58.8001 | 61.7737 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 80% | 268.3703 | 38.6278 | 40.1666 | 45.3228 | 49.8653 | 52.2367 | 54.1596 | 55.9893 | 57.5487 | 59.1721 | 59.8862 | 60.8586 | 62.6587 | 62.0751 | 64.4253 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822
75% | 455.9026 | 34.0244 | 35.4048 | 40.2767 | 44.3801 | 46.5956 | 48.1968 | 50.0427 | 51.4248 | 52.9474 | 53.7477 | 54.4405 | 56.1512 | 55.1251 | 57.9128 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 75% | 455.9026 | 36.2136 | 37.6562 | 42.4901 | 46.7487 | 48.9719 | 50.7747 | 52.49 | 53.9519 | 55.4738 | 56.1433 | 57.055 | 58.7425 | 58.1954 | 60.3987 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708
70% | 690.9866 | 31.7561 | 33.0445 | 37.5915 | 41.4215 | 43.4892 | 44.9837 | 46.7065 | 47.9965 | 49.4176 | 50.1645 | 50.8111 | 52.4078 | 51.4501 | 54.052 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 70% | 690.9866 | 33.7993 | 35.1457 | 39.6575 | 43.6321 | 45.7071 | 47.3897 | 48.9907 | 50.3551 | 51.7756 | 52.4004 | 53.2513 | 54.8263 | 54.3158 | 56.3721 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594
65% | 967.6784 | 29.4878 | 30.6842 | 34.9064 | 38.4628 | 40.3829 | 41.7705 | 43.3703 | 44.5682 | 45.8878 | 46.5813 | 47.1818 | 48.6643 | 47.775 | 50.1911 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 65% | 967.6784 | 31.3851 | 32.6353 | 36.8248 | 40.5155 | 42.4423 | 44.0047 | 45.4913 | 46.7584 | 48.0773 | 48.6575 | 49.4476 | 50.9102 | 50.4361 | 52.3455 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448
60% | 1292.8136 | 27.2195 | 28.3239 | 32.2213 | 35.5041 | 37.2765 | 38.5574 | 40.0342 | 41.1399 | 42.358 | 42.9981 | 43.5524 | 44.9209 | 44.1 | 46.3303 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 60% | 1292.8136 | 28.9709 | 30.1249 | 33.9921 | 37.399 | 39.1775 | 40.6197 | 41.992 | 43.1616 | 44.3791 | 44.9146 | 45.644 | 46.994 | 46.5564 | 48.3189 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366
55% | 1647.0743 | 24.9512 | 25.9636 | 29.5362 | 32.5454 | 34.1701 | 35.3443 | 36.698 | 37.7115 | 38.8281 | 39.415 | 39.923 | 41.1775 | 40.425 | 42.4694 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 55% | 1647.0743 | 26.5566 | 27.6145 | 31.1594 | 34.2824 | 35.9127 | 37.2348 | 38.4927 | 39.5648 | 40.6808 | 41.1718 | 41.8403 | 43.0778 | 42.6767 | 44.2924 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253
50% | 2104.1657 | 22.6829 | 23.6032 | 26.8511 | 29.5868 | 31.0637 | 32.1312 | 33.3618 | 34.2832 | 35.2983 | 35.8318 | 36.2937 | 37.4341 | 36.75 | 38.6086 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 50% | 2104.1657 | 24.1424 | 25.1041 | 28.3268 | 31.1658 | 32.6479 | 33.8498 | 34.9933 | 35.968 | 36.9826 | 37.4289 | 38.0366 | 39.1617 | 38.797 | 40.2658 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139
45% | 2736.0097 | 20.4146 | 21.2429 | 24.166 | 26.6281 | 27.9574 | 28.9181 | 30.0256 | 30.8549 | 31.7685 | 32.2486 | 32.6643 | 33.6907 | 33.075 | 34.7477 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 45% | 2736.0097 | 21.7281 | 22.5937 | 25.4941 | 28.0492 | 29.3831 | 30.4648 | 31.494 | 32.3712 | 33.2843 | 33.686 | 34.233 | 35.2455 | 34.9173 | 36.2392 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025
40% | 3483.7613 | 18.1464 | 18.8826 | 21.4809 | 23.6694 | 24.851 | 25.7049 | 26.6894 | 27.4266 | 28.2386 | 28.6654 | 29.0349 | 29.9473 | 29.4 | 30.8868 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 40% | 3483.7613 | 19.3139 | 20.0833 | 22.6614 | 24.9326 | 26.1183 | 27.0798 | 27.9947 | 28.7744 | 29.586 | 29.9431 | 30.4293 | 31.3293 | 31.0376 | 32.2126 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911
35% | 3830.2948 | 15.8781 | 16.5223 | 18.7958 | 20.7107 | 21.7446 | 22.4918 | 23.3533 | 23.9983 | 24.7088 | 25.0822 | 25.4056 | 26.2039 | 25.725 | 27.026 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 35% | 3830.2948 | 16.8997 | 17.5729 | 19.8287 | 21.8161 | 22.8535 | 23.6948 | 24.4953 | 25.1776 | 25.8878 | 26.2002 | 26.6256 | 27.4132 | 27.1579 | 28.186 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797
30% | 3953.6322 | 13.6098 | 14.1619 | 16.1107 | 17.7521 | 18.6382 | 19.2787 | 20.0171 | 20.5699 | 21.179 | 21.4991 | 21.7762 | 22.4605 | 22.05 | 23.1651 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 30% | 3953.6322 | 14.4854 | 15.0625 | 16.9961 | 18.6995 | 19.5888 | 20.3099 | 20.996 | 21.5808 | 22.1895 | 22.4573 | 22.822 | 23.497 | 23.2782 | 24.1595 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683
25% | 4060.9208 | 11.3415 | 11.8016 | 13.4256 | 14.7934 | 15.5319 | 16.0656 | 16.6809 | 17.1416 | 17.6491 | 17.9159 | 18.1468 | 18.7171 | 18.375 | 19.3043 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 25% | 4060.9208 | 12.0712 | 12.5521 | 14.1634 | 15.5829 | 16.324 | 16.9249 | 17.4967 | 17.984 | 18.4913 | 18.7144 | 19.0183 | 19.5808 | 19.3985 | 20.1329 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569
20% | 4165.2375 | 9.0732 | 9.4413 | 10.7404 | 11.8347 | 12.4255 | 12.8525 | 13.3447 | 13.7133 | 14.1193 | 14.3327 | 14.5175 | 14.9736 | 14.7 | 15.4434 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 20% | 4165.2375 | 9.657 | 10.0416 | 11.3307 | 12.4663 | 13.0592 | 13.5399 | 13.9973 | 14.3872 | 14.793 | 14.9715 | 15.2147 | 15.6647 | 15.5188 | 16.1063 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455
15% | 4270.4458 | 6.8049 | 7.081 | 8.0553 | 8.876 | 9.3191 | 9.6394 | 10.0085 | 10.285 | 10.5895 | 10.7495 | 10.8881 | 11.2302 | 11.025 | 11.5826 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 15% | 4270.4458 | 7.2427 | 7.5312 | 8.498 | 9.3497 | 9.7944 | 10.1549 | 10.498 | 10.7904 | 11.0948 | 11.2287 | 11.411 | 11.7485 | 11.6391 | 12.0797 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342
10% | 4373.8709 | 4.5366 | 4.7206 | 5.3702 | 5.9174 | 6.2127 | 6.4262 | 6.6724 | 6.8566 | 7.0597 | 7.1664 | 7.2587 | 7.4868 | 7.35 | 7.7217 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 10% | 4373.8709 | 4.8285 | 5.0208 | 5.6654 | 6.2332 | 6.5296 | 6.77 | 6.9987 | 7.1936 | 7.3965 | 7.4858 | 7.6073 | 7.8323 | 7.7594 | 8.0532 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228
5% | 4391.7028 | 2.2683 | 2.3603 | 2.6851 | 2.9587 | 3.1064 | 3.2131 | 3.3362 | 3.4283 | 3.5298 | 3.5832 | 3.6294 | 3.7434 | 3.675 | 3.8609 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 5% | 4391.7028 | 2.4142 | 2.5104 | 2.8327 | 3.1166 | 3.2648 | 3.385 | 3.4993 | 3.5968 | 3.6983 | 3.7429 | 3.8037 | 3.9162 | 3.8797 | 4.0266 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114
9.992e-14% | 4391.7028 | 4.533e-14 | 4.7169e-14 | 5.3659e-14 | 5.9126e-14 | 6.2078e-14 | 6.4211e-14 | 6.667e-14 | 6.8512e-14 | 7.054e-14 | 7.1606e-14 | 7.2529e-14 | 7.4808e-14 | 7.3441e-14 | 7.7155e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 9.992e-14% | 4391.7028 | 4.8246e-14 | 5.0168e-14 | 5.6608e-14 | 6.2282e-14 | 6.5244e-14 | 6.7645e-14 | 6.9931e-14 | 7.1878e-14 | 7.3906e-14 | 7.4798e-14 | 7.6012e-14 | 7.8261e-14 | 7.7532e-14 | 8.0467e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 100% | 0 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251
99% | 0 | 50.7508 | 51.9667 | 58.2429 | 62.7724 | 65.1574 | 67.2933 | 68.6521 | 70.2026 | 71.4415 | 72.2514 | 74.1722 | 75.502 | 76.2046 | 77.5024 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 99% | 0.75633 | 57.089 | 58.7368 | 65.0304 | 69.5089 | 72.1962 | 74.3476 | 76.0957 | 77.7773 | 79.2327 | 79.9659 | 81.0429 | 82.2746 | 83.5326 | 85.1128 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629
98% | 0.37816 | 50.2382 | 51.4418 | 57.6546 | 62.1384 | 64.4993 | 66.6135 | 67.9586 | 69.4935 | 70.7199 | 71.5215 | 73.423 | 74.7393 | 75.4348 | 76.7195 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 98% | 1.1345 | 56.5124 | 58.1435 | 64.3735 | 68.8068 | 71.467 | 73.5966 | 75.327 | 76.9916 | 78.4324 | 79.1581 | 80.2243 | 81.4436 | 82.6889 | 84.2531 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006
97% | 0.75633 | 49.7256 | 50.9169 | 57.0663 | 61.5043 | 63.8411 | 65.9338 | 67.2652 | 68.7844 | 69.9983 | 70.7917 | 72.6738 | 73.9767 | 74.6651 | 75.9367 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 97% | 1.8908 | 55.9357 | 57.5502 | 63.7166 | 68.1047 | 70.7377 | 72.8456 | 74.5584 | 76.206 | 77.6321 | 78.3504 | 79.4057 | 80.6125 | 81.8451 | 83.3934 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384
95% | 1.8908 | 48.7003 | 49.867 | 55.8896 | 60.2362 | 62.5248 | 64.5743 | 65.8783 | 67.3661 | 68.555 | 69.3321 | 71.1753 | 72.4514 | 73.1256 | 74.371 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 95% | 3.4035 | 54.7824 | 56.3636 | 62.4029 | 66.7005 | 69.2792 | 71.3437 | 73.0211 | 74.6347 | 76.0314 | 76.7349 | 77.7685 | 78.9504 | 80.1576 | 81.6739 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139
90% | 4.538 | 46.1371 | 47.2424 | 52.9481 | 57.0659 | 59.234 | 61.1757 | 62.411 | 63.8205 | 64.9469 | 65.683 | 67.4293 | 68.6381 | 69.2769 | 70.4567 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 90% | 9.0759 | 51.8991 | 53.3971 | 59.1185 | 63.1899 | 65.6329 | 67.5887 | 69.1779 | 70.7066 | 72.0297 | 72.6962 | 73.6754 | 74.7951 | 75.9388 | 77.3753 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026
85% | 9.0759 | 43.574 | 44.6179 | 50.0065 | 53.8955 | 55.9433 | 57.777 | 58.9437 | 60.275 | 61.3387 | 62.034 | 63.6832 | 64.8249 | 65.4282 | 66.5424 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 85% | 16.2611 | 49.0158 | 50.4306 | 55.8342 | 59.6794 | 61.9866 | 63.8338 | 65.3347 | 66.7785 | 68.0281 | 68.6576 | 69.5823 | 70.6398 | 71.72 | 73.0767 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913
80% | 27.606 | 41.0108 | 41.9933 | 47.065 | 50.7252 | 52.6525 | 54.3784 | 55.4764 | 56.7294 | 57.7305 | 58.3849 | 59.9371 | 61.0117 | 61.5795 | 62.6282 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 80% | 24.9588 | 46.1325 | 47.4641 | 52.5498 | 56.1688 | 58.3404 | 60.0789 | 61.4915 | 62.8503 | 64.0264 | 64.6189 | 65.4893 | 66.4845 | 67.5011 | 68.778 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801
75% | 57.481 | 38.4476 | 39.3687 | 44.1234 | 47.5549 | 49.3617 | 50.9797 | 52.0092 | 53.1838 | 54.1224 | 54.7359 | 56.1911 | 57.1985 | 57.7307 | 58.7139 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 75% | 32.9003 | 43.2493 | 44.4976 | 49.2655 | 52.6583 | 54.6941 | 56.324 | 57.6482 | 58.9222 | 60.0248 | 60.5802 | 61.3962 | 62.3292 | 63.2823 | 64.4794 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688
70% | 106.2642 | 35.8844 | 36.7441 | 41.1818 | 44.3846 | 46.0709 | 47.5811 | 48.5419 | 49.6382 | 50.5142 | 51.0868 | 52.445 | 53.3852 | 53.882 | 54.7997 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 70% | 41.9762 | 40.366 | 41.531 | 45.9811 | 49.1477 | 51.0478 | 52.569 | 53.805 | 54.994 | 56.0231 | 56.5415 | 57.3031 | 58.174 | 59.0635 | 60.1808 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576
65% | 201.9397 | 33.3213 | 34.1195 | 38.2403 | 41.2142 | 42.7801 | 44.1824 | 45.0746 | 46.0926 | 46.9061 | 47.4378 | 48.6989 | 49.572 | 50.0333 | 50.8854 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 65% | 67.6914 | 37.4827 | 38.5645 | 42.6967 | 45.6372 | 47.4016 | 48.8141 | 49.9618 | 51.0659 | 52.0215 | 52.5028 | 53.21 | 54.0187 | 54.8447 | 55.8822 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463
60% | 402.745 | 30.7581 | 31.495 | 35.2987 | 38.0439 | 39.4894 | 40.7838 | 41.6073 | 42.547 | 43.2979 | 43.7887 | 44.9529 | 45.7588 | 46.1846 | 46.9711 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 60% | 98.7009 | 34.5994 | 35.598 | 39.4124 | 42.1266 | 43.7553 | 45.0592 | 46.1186 | 47.1377 | 48.0198 | 48.4642 | 49.1169 | 49.8634 | 50.6258 | 51.5835 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351
55% | 655.7369 | 28.1949 | 28.8704 | 32.3572 | 34.8736 | 36.1986 | 37.3851 | 38.14 | 39.0014 | 39.6897 | 40.1396 | 41.2068 | 41.9455 | 42.3359 | 43.0569 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 55% | 153.5347 | 31.7161 | 32.6315 | 36.128 | 38.6161 | 40.109 | 41.3042 | 42.2754 | 43.2096 | 44.0182 | 44.4255 | 45.0239 | 45.7081 | 46.407 | 47.2849 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238
50% | 981.7145 | 25.6317 | 26.2458 | 29.4156 | 31.7033 | 32.9078 | 33.9865 | 34.6728 | 35.4559 | 36.0816 | 36.4906 | 37.4607 | 38.1323 | 38.4872 | 39.1426 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 50% | 258.2862 | 28.8328 | 29.665 | 32.8436 | 35.1055 | 36.4627 | 37.5493 | 38.4322 | 39.2814 | 40.0165 | 40.3868 | 40.9308 | 41.5528 | 42.1882 | 42.9863 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126
45% | 1622.7029 | 23.0686 | 23.6212 | 26.474 | 28.5329 | 29.617 | 30.5878 | 31.2055 | 31.9103 | 32.4734 | 32.8415 | 33.7146 | 34.3191 | 34.6384 | 35.2283 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 45% | 488.9664 | 25.9496 | 26.6985 | 29.5593 | 31.595 | 32.8165 | 33.7944 | 34.5889 | 35.3533 | 36.0149 | 36.3481 | 36.8377 | 37.3975 | 37.9694 | 38.6876 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013
40% | 2442.9413 | 20.5054 | 20.9966 | 23.5325 | 25.3626 | 26.3262 | 27.1892 | 27.7382 | 28.3647 | 28.8653 | 29.1925 | 29.9686 | 30.5058 | 30.7897 | 31.3141 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 40% | 928.0152 | 23.0663 | 23.732 | 26.2749 | 28.0844 | 29.1702 | 30.0394 | 30.7457 | 31.4252 | 32.0132 | 32.3094 | 32.7446 | 33.2423 | 33.7506 | 34.389 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49
35% | 3006.7842 | 17.9422 | 18.3721 | 20.5909 | 22.1923 | 23.0355 | 23.7905 | 24.2709 | 24.8191 | 25.2571 | 25.5434 | 26.2225 | 26.6926 | 26.941 | 27.3998 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 35% | 1530.4309 | 20.183 | 20.7655 | 22.9905 | 24.5739 | 25.5239 | 26.2845 | 26.9025 | 27.497 | 28.0116 | 28.2708 | 28.6515 | 29.087 | 29.5317 | 30.0904 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788
30% | 3276.4154 | 15.379 | 15.7475 | 17.6494 | 19.022 | 19.7447 | 20.3919 | 20.8037 | 21.2735 | 21.649 | 21.8943 | 22.4764 | 22.8794 | 23.0923 | 23.4856 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 30% | 2592.3162 | 17.2997 | 17.799 | 19.7062 | 21.0633 | 21.8776 | 22.5296 | 23.0593 | 23.5689 | 24.0099 | 24.2321 | 24.5585 | 24.9317 | 25.3129 | 25.7918 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675
25% | 3466.632 | 12.8159 | 13.1229 | 14.7078 | 15.8516 | 16.4539 | 16.9932 | 17.3364 | 17.7279 | 18.0408 | 18.2453 | 18.7304 | 19.0662 | 19.2436 | 19.5713 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 25% | 3659.4958 | 14.4164 | 14.8325 | 16.4218 | 17.5528 | 18.2314 | 18.7747 | 19.2161 | 19.6407 | 20.0083 | 20.1934 | 20.4654 | 20.7764 | 21.0941 | 21.4931 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563
20% | 3713.9514 | 10.2527 | 10.4983 | 11.7662 | 12.6813 | 13.1631 | 13.5946 | 13.8691 | 14.1823 | 14.4326 | 14.5962 | 14.9843 | 15.2529 | 15.3949 | 15.657 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 20% | 4005.5161 | 11.5331 | 11.866 | 13.1375 | 14.0422 | 14.5851 | 15.0197 | 15.3729 | 15.7126 | 16.0066 | 16.1547 | 16.3723 | 16.6211 | 16.8753 | 17.1945 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245
15% | 4043.3325 | 7.6895 | 7.8737 | 8.8247 | 9.511 | 9.8723 | 10.1959 | 10.4018 | 10.6368 | 10.8245 | 10.9472 | 11.2382 | 11.4397 | 11.5461 | 11.7428 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 15% | 4281.1979 | 8.6499 | 8.8995 | 9.8531 | 10.5317 | 10.9388 | 11.2648 | 11.5296 | 11.7844 | 12.005 | 12.116 | 12.2792 | 12.4658 | 12.6565 | 12.8959 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338
10% | 4350.7801 | 5.1263 | 5.2492 | 5.8831 | 6.3407 | 6.5816 | 6.7973 | 6.9346 | 7.0912 | 7.2163 | 7.2981 | 7.4921 | 7.6265 | 7.6974 | 7.8285 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 10% | 4391.6218 | 5.7666 | 5.933 | 6.5687 | 7.0211 | 7.2925 | 7.5099 | 7.6864 | 7.8563 | 8.0033 | 8.0774 | 8.1862 | 8.3106 | 8.4376 | 8.5973 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225
5% | 4391.6218 | 2.5632 | 2.6246 | 2.9416 | 3.1703 | 3.2908 | 3.3986 | 3.4673 | 3.5456 | 3.6082 | 3.6491 | 3.7461 | 3.8132 | 3.8487 | 3.9143 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 5% | 4391.6218 | 2.8833 | 2.9665 | 3.2844 | 3.5106 | 3.6463 | 3.7549 | 3.8432 | 3.9281 | 4.0017 | 4.0387 | 4.0931 | 4.1553 | 4.2188 | 4.2986 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113
9.992e-14% | 4391.6218 | 5.1223e-14 | 5.245e-14 | 5.8784e-14 | 6.3356e-14 | 6.5763e-14 | 6.7919e-14 | 6.929e-14 | 7.0855e-14 | 7.2105e-14 | 7.2923e-14 | 7.4862e-14 | 7.6204e-14 | 7.6913e-14 | 7.8223e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 9.992e-14% | 4391.6218 | 5.762e-14 | 5.9283e-14 | 6.5635e-14 | 7.0155e-14 | 7.2867e-14 | 7.5039e-14 | 7.6803e-14 | 7.85e-14 | 7.9969e-14 | 8.0709e-14 | 8.1796e-14 | 8.3039e-14 | 8.4309e-14 | 8.5904e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 100% | 0 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
99% | 0.8916 | 44.9122 | 46.7344 | 53.1652 | 58.5818 | 61.5062 | 63.6197 | 66.0564 | 67.8808 | 69.8906 | 70.9469 | 71.8615 | 74.1195 | 72.7651 | 76.445 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 99% | 0.8916 | 47.8019 | 49.7061 | 56.087 | 61.7083 | 64.6429 | 67.0226 | 69.2868 | 71.2166 | 73.2255 | 74.1092 | 75.3125 | 77.5401 | 76.818 | 79.7262 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055
98% | 3.5664 | 44.4586 | 46.2623 | 52.6282 | 57.99 | 60.8849 | 62.9771 | 65.3891 | 67.1951 | 69.1847 | 70.2303 | 71.1356 | 73.3709 | 72.0301 | 75.6728 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 98% | 3.5664 | 47.3191 | 49.204 | 55.5204 | 61.085 | 63.9899 | 66.3456 | 68.5869 | 70.4972 | 72.4858 | 73.3606 | 74.5518 | 76.7569 | 76.0421 | 78.9209 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832
97% | 4.7552 | 44.0049 | 45.7903 | 52.0911 | 57.3983 | 60.2637 | 62.3345 | 64.7219 | 66.5095 | 68.4787 | 69.5136 | 70.4097 | 72.6222 | 71.2951 | 74.9006 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 97% | 4.7552 | 46.8362 | 48.702 | 54.9539 | 60.4617 | 63.337 | 65.6686 | 67.887 | 69.7778 | 71.7461 | 72.612 | 73.7911 | 75.9736 | 75.2661 | 78.1156 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609
95% | 7.7272 | 43.0976 | 44.8461 | 51.0171 | 56.2148 | 59.0211 | 61.0492 | 63.3874 | 65.1381 | 67.0668 | 68.0804 | 68.958 | 71.1248 | 69.8251 | 73.3563 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 95% | 7.7272 | 45.8705 | 47.6978 | 53.8208 | 59.215 | 62.031 | 64.3146 | 66.4873 | 68.3391 | 70.2668 | 71.1149 | 72.2696 | 74.4072 | 73.7142 | 76.505 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164
90% | 39.2302 | 40.8293 | 42.4858 | 48.332 | 53.2562 | 55.9147 | 57.8361 | 60.0513 | 61.7098 | 63.5369 | 64.4972 | 65.3286 | 67.3814 | 66.1501 | 69.4954 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 90% | 39.2302 | 43.4563 | 45.1874 | 50.9882 | 56.0984 | 58.7663 | 60.9296 | 62.988 | 64.7423 | 66.5686 | 67.372 | 68.4659 | 70.491 | 69.8345 | 72.4784 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005
85% | 117.6906 | 38.561 | 40.1255 | 45.6469 | 50.2975 | 52.8084 | 54.623 | 56.7151 | 58.2815 | 60.0071 | 60.914 | 61.6992 | 63.638 | 62.4751 | 65.6346 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 85% | 117.6906 | 41.042 | 42.677 | 48.1555 | 52.9819 | 55.5015 | 57.5446 | 59.4886 | 61.1455 | 62.8703 | 63.6291 | 64.6623 | 66.5748 | 65.9548 | 68.4518 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936
80% | 268.3703 | 36.2927 | 37.7652 | 42.9618 | 47.3388 | 49.702 | 51.4099 | 53.3789 | 54.8532 | 56.4773 | 57.3308 | 58.0699 | 59.8946 | 58.8001 | 61.7737 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 80% | 268.3703 | 38.6278 | 40.1666 | 45.3228 | 49.8653 | 52.2367 | 54.1596 | 55.9893 | 57.5487 | 59.1721 | 59.8862 | 60.8586 | 62.6587 | 62.0751 | 64.4253 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822
75% | 455.9026 | 34.0244 | 35.4048 | 40.2767 | 44.3801 | 46.5956 | 48.1968 | 50.0427 | 51.4248 | 52.9474 | 53.7477 | 54.4405 | 56.1512 | 55.1251 | 57.9128 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 75% | 455.9026 | 36.2136 | 37.6562 | 42.4901 | 46.7487 | 48.9719 | 50.7747 | 52.49 | 53.9519 | 55.4738 | 56.1433 | 57.055 | 58.7425 | 58.1954 | 60.3987 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708
70% | 690.9866 | 31.7561 | 33.0445 | 37.5915 | 41.4215 | 43.4892 | 44.9837 | 46.7065 | 47.9965 | 49.4176 | 50.1645 | 50.8111 | 52.4078 | 51.4501 | 54.052 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 70% | 690.9866 | 33.7993 | 35.1457 | 39.6575 | 43.6321 | 45.7071 | 47.3897 | 48.9907 | 50.3551 | 51.7756 | 52.4004 | 53.2513 | 54.8263 | 54.3158 | 56.3721 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594
65% | 967.6784 | 29.4878 | 30.6842 | 34.9064 | 38.4628 | 40.3829 | 41.7705 | 43.3703 | 44.5682 | 45.8878 | 46.5813 | 47.1818 | 48.6643 | 47.775 | 50.1911 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 65% | 967.6784 | 31.3851 | 32.6353 | 36.8248 | 40.5155 | 42.4423 | 44.0047 | 45.4913 | 46.7584 | 48.0773 | 48.6575 | 49.4476 | 50.9102 | 50.4361 | 52.3455 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448
60% | 1292.8136 | 27.2195 | 28.3239 | 32.2213 | 35.5041 | 37.2765 | 38.5574 | 40.0342 | 41.1399 | 42.358 | 42.9981 | 43.5524 | 44.9209 | 44.1 | 46.3303 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 60% | 1292.8136 | 28.9709 | 30.1249 | 33.9921 | 37.399 | 39.1775 | 40.6197 | 41.992 | 43.1616 | 44.3791 | 44.9146 | 45.644 | 46.994 | 46.5564 | 48.3189 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366
55% | 1647.0743 | 24.9512 | 25.9636 | 29.5362 | 32.5454 | 34.1701 | 35.3443 | 36.698 | 37.7115 | 38.8281 | 39.415 | 39.923 | 41.1775 | 40.425 | 42.4694 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 55% | 1647.0743 | 26.5566 | 27.6145 | 31.1594 | 34.2824 | 35.9127 | 37.2348 | 38.4927 | 39.5648 | 40.6808 | 41.1718 | 41.8403 | 43.0778 | 42.6767 | 44.2924 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253
50% | 2104.1657 | 22.6829 | 23.6032 | 26.8511 | 29.5868 | 31.0637 | 32.1312 | 33.3618 | 34.2832 | 35.2983 | 35.8318 | 36.2937 | 37.4341 | 36.75 | 38.6086 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 50% | 2104.1657 | 24.1424 | 25.1041 | 28.3268 | 31.1658 | 32.6479 | 33.8498 | 34.9933 | 35.968 | 36.9826 | 37.4289 | 38.0366 | 39.1617 | 38.797 | 40.2658 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139
45% | 2736.0097 | 20.4146 | 21.2429 | 24.166 | 26.6281 | 27.9574 | 28.9181 | 30.0256 | 30.8549 | 31.7685 | 32.2486 | 32.6643 | 33.6907 | 33.075 | 34.7477 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 45% | 2736.0097 | 21.7281 | 22.5937 | 25.4941 | 28.0492 | 29.3831 | 30.4648 | 31.494 | 32.3712 | 33.2843 | 33.686 | 34.233 | 35.2455 | 34.9173 | 36.2392 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025
40% | 3483.7613 | 18.1464 | 18.8826 | 21.4809 | 23.6694 | 24.851 | 25.7049 | 26.6894 | 27.4266 | 28.2386 | 28.6654 | 29.0349 | 29.9473 | 29.4 | 30.8868 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 40% | 3483.7613 | 19.3139 | 20.0833 | 22.6614 | 24.9326 | 26.1183 | 27.0798 | 27.9947 | 28.7744 | 29.586 | 29.9431 | 30.4293 | 31.3293 | 31.0376 | 32.2126 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911
35% | 3830.2948 | 15.8781 | 16.5223 | 18.7958 | 20.7107 | 21.7446 | 22.4918 | 23.3533 | 23.9983 | 24.7088 | 25.0822 | 25.4056 | 26.2039 | 25.725 | 27.026 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 35% | 3830.2948 | 16.8997 | 17.5729 | 19.8287 | 21.8161 | 22.8535 | 23.6948 | 24.4953 | 25.1776 | 25.8878 | 26.2002 | 26.6256 | 27.4132 | 27.1579 | 28.186 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797
30% | 3953.6322 | 13.6098 | 14.1619 | 16.1107 | 17.7521 | 18.6382 | 19.2787 | 20.0171 | 20.5699 | 21.179 | 21.4991 | 21.7762 | 22.4605 | 22.05 | 23.1651 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 30% | 3953.6322 | 14.4854 | 15.0625 | 16.9961 | 18.6995 | 19.5888 | 20.3099 | 20.996 | 21.5808 | 22.1895 | 22.4573 | 22.822 | 23.497 | 23.2782 | 24.1595 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683
25% | 4060.9208 | 11.3415 | 11.8016 | 13.4256 | 14.7934 | 15.5319 | 16.0656 | 16.6809 | 17.1416 | 17.6491 | 17.9159 | 18.1468 | 18.7171 | 18.375 | 19.3043 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 25% | 4060.9208 | 12.0712 | 12.5521 | 14.1634 | 15.5829 | 16.324 | 16.9249 | 17.4967 | 17.984 | 18.4913 | 18.7144 | 19.0183 | 19.5808 | 19.3985 | 20.1329 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569
20% | 4165.2375 | 9.0732 | 9.4413 | 10.7404 | 11.8347 | 12.4255 | 12.8525 | 13.3447 | 13.7133 | 14.1193 | 14.3327 | 14.5175 | 14.9736 | 14.7 | 15.4434 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 20% | 4165.2375 | 9.657 | 10.0416 | 11.3307 | 12.4663 | 13.0592 | 13.5399 | 13.9973 | 14.3872 | 14.793 | 14.9715 | 15.2147 | 15.6647 | 15.5188 | 16.1063 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455
15% | 4270.4458 | 6.8049 | 7.081 | 8.0553 | 8.876 | 9.3191 | 9.6394 | 10.0085 | 10.285 | 10.5895 | 10.7495 | 10.8881 | 11.2302 | 11.025 | 11.5826 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 15% | 4270.4458 | 7.2427 | 7.5312 | 8.498 | 9.3497 | 9.7944 | 10.1549 | 10.498 | 10.7904 | 11.0948 | 11.2287 | 11.411 | 11.7485 | 11.6391 | 12.0797 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342
10% | 4373.8709 | 4.5366 | 4.7206 | 5.3702 | 5.9174 | 6.2127 | 6.4262 | 6.6724 | 6.8566 | 7.0597 | 7.1664 | 7.2587 | 7.4868 | 7.35 | 7.7217 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 10% | 4373.8709 | 4.8285 | 5.0208 | 5.6654 | 6.2332 | 6.5296 | 6.77 | 6.9987 | 7.1936 | 7.3965 | 7.4858 | 7.6073 | 7.8323 | 7.7594 | 8.0532 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228
5% | 4391.7028 | 2.2683 | 2.3603 | 2.6851 | 2.9587 | 3.1064 | 3.2131 | 3.3362 | 3.4283 | 3.5298 | 3.5832 | 3.6294 | 3.7434 | 3.675 | 3.8609 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 5% | 4391.7028 | 2.4142 | 2.5104 | 2.8327 | 3.1166 | 3.2648 | 3.385 | 3.4993 | 3.5968 | 3.6983 | 3.7429 | 3.8037 | 3.9162 | 3.8797 | 4.0266 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114
9.992e-14% | 4391.7028 | 4.533e-14 | 4.7169e-14 | 5.3659e-14 | 5.9126e-14 | 6.2078e-14 | 6.4211e-14 | 6.667e-14 | 6.8512e-14 | 7.054e-14 | 7.1606e-14 | 7.2529e-14 | 7.4808e-14 | 7.3441e-14 | 7.7155e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 9.992e-14% | 4391.7028 | 4.8246e-14 | 5.0168e-14 | 5.6608e-14 | 6.2282e-14 | 6.5244e-14 | 6.7645e-14 | 6.9931e-14 | 7.1878e-14 | 7.3906e-14 | 7.4798e-14 | 7.6012e-14 | 7.8261e-14 | 7.7532e-14 | 8.0467e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 100% | 0 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251
99% | 0 | 50.7508 | 51.9667 | 58.2429 | 62.7724 | 65.1574 | 67.2933 | 68.6521 | 70.2026 | 71.4415 | 72.2514 | 74.1722 | 75.502 | 76.2046 | 77.5024 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 99% | 0.75633 | 57.089 | 58.7368 | 65.0304 | 69.5089 | 72.1962 | 74.3476 | 76.0957 | 77.7773 | 79.2327 | 79.9659 | 81.0429 | 82.2746 | 83.5326 | 85.1128 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629
98% | 0.37816 | 50.2382 | 51.4418 | 57.6546 | 62.1384 | 64.4993 | 66.6135 | 67.9586 | 69.4935 | 70.7199 | 71.5215 | 73.423 | 74.7393 | 75.4348 | 76.7195 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 98% | 1.1345 | 56.5124 | 58.1435 | 64.3735 | 68.8068 | 71.467 | 73.5966 | 75.327 | 76.9916 | 78.4324 | 79.1581 | 80.2243 | 81.4436 | 82.6889 | 84.2531 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006
97% | 0.75633 | 49.7256 | 50.9169 | 57.0663 | 61.5043 | 63.8411 | 65.9338 | 67.2652 | 68.7844 | 69.9983 | 70.7917 | 72.6738 | 73.9767 | 74.6651 | 75.9367 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 97% | 1.8908 | 55.9357 | 57.5502 | 63.7166 | 68.1047 | 70.7377 | 72.8456 | 74.5584 | 76.206 | 77.6321 | 78.3504 | 79.4057 | 80.6125 | 81.8451 | 83.3934 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384
95% | 1.8908 | 48.7003 | 49.867 | 55.8896 | 60.2362 | 62.5248 | 64.5743 | 65.8783 | 67.3661 | 68.555 | 69.3321 | 71.1753 | 72.4514 | 73.1256 | 74.371 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 95% | 3.4035 | 54.7824 | 56.3636 | 62.4029 | 66.7005 | 69.2792 | 71.3437 | 73.0211 | 74.6347 | 76.0314 | 76.7349 | 77.7685 | 78.9504 | 80.1576 | 81.6739 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139
90% | 4.538 | 46.1371 | 47.2424 | 52.9481 | 57.0659 | 59.234 | 61.1757 | 62.411 | 63.8205 | 64.9469 | 65.683 | 67.4293 | 68.6381 | 69.2769 | 70.4567 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 90% | 9.0759 | 51.8991 | 53.3971 | 59.1185 | 63.1899 | 65.6329 | 67.5887 | 69.1779 | 70.7066 | 72.0297 | 72.6962 | 73.6754 | 74.7951 | 75.9388 | 77.3753 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026
85% | 9.0759 | 43.574 | 44.6179 | 50.0065 | 53.8955 | 55.9433 | 57.777 | 58.9437 | 60.275 | 61.3387 | 62.034 | 63.6832 | 64.8249 | 65.4282 | 66.5424 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 85% | 16.2611 | 49.0158 | 50.4306 | 55.8342 | 59.6794 | 61.9866 | 63.8338 | 65.3347 | 66.7785 | 68.0281 | 68.6576 | 69.5823 | 70.6398 | 71.72 | 73.0767 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913
80% | 27.606 | 41.0108 | 41.9933 | 47.065 | 50.7252 | 52.6525 | 54.3784 | 55.4764 | 56.7294 | 57.7305 | 58.3849 | 59.9371 | 61.0117 | 61.5795 | 62.6282 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 80% | 24.9588 | 46.1325 | 47.4641 | 52.5498 | 56.1688 | 58.3404 | 60.0789 | 61.4915 | 62.8503 | 64.0264 | 64.6189 | 65.4893 | 66.4845 | 67.5011 | 68.778 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801
75% | 57.481 | 38.4476 | 39.3687 | 44.1234 | 47.5549 | 49.3617 | 50.9797 | 52.0092 | 53.1838 | 54.1224 | 54.7359 | 56.1911 | 57.1985 | 57.7307 | 58.7139 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 75% | 32.9003 | 43.2493 | 44.4976 | 49.2655 | 52.6583 | 54.6941 | 56.324 | 57.6482 | 58.9222 | 60.0248 | 60.5802 | 61.3962 | 62.3292 | 63.2823 | 64.4794 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688
70% | 106.2642 | 35.8844 | 36.7441 | 41.1818 | 44.3846 | 46.0709 | 47.5811 | 48.5419 | 49.6382 | 50.5142 | 51.0868 | 52.445 | 53.3852 | 53.882 | 54.7997 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 70% | 41.9762 | 40.366 | 41.531 | 45.9811 | 49.1477 | 51.0478 | 52.569 | 53.805 | 54.994 | 56.0231 | 56.5415 | 57.3031 | 58.174 | 59.0635 | 60.1808 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576
65% | 201.9397 | 33.3213 | 34.1195 | 38.2403 | 41.2142 | 42.7801 | 44.1824 | 45.0746 | 46.0926 | 46.9061 | 47.4378 | 48.6989 | 49.572 | 50.0333 | 50.8854 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 65% | 67.6914 | 37.4827 | 38.5645 | 42.6967 | 45.6372 | 47.4016 | 48.8141 | 49.9618 | 51.0659 | 52.0215 | 52.5028 | 53.21 | 54.0187 | 54.8447 | 55.8822 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463
60% | 402.745 | 30.7581 | 31.495 | 35.2987 | 38.0439 | 39.4894 | 40.7838 | 41.6073 | 42.547 | 43.2979 | 43.7887 | 44.9529 | 45.7588 | 46.1846 | 46.9711 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 60% | 98.7009 | 34.5994 | 35.598 | 39.4124 | 42.1266 | 43.7553 | 45.0592 | 46.1186 | 47.1377 | 48.0198 | 48.4642 | 49.1169 | 49.8634 | 50.6258 | 51.5835 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351
55% | 655.7369 | 28.1949 | 28.8704 | 32.3572 | 34.8736 | 36.1986 | 37.3851 | 38.14 | 39.0014 | 39.6897 | 40.1396 | 41.2068 | 41.9455 | 42.3359 | 43.0569 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 55% | 153.5347 | 31.7161 | 32.6315 | 36.128 | 38.6161 | 40.109 | 41.3042 | 42.2754 | 43.2096 | 44.0182 | 44.4255 | 45.0239 | 45.7081 | 46.407 | 47.2849 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238
50% | 981.7145 | 25.6317 | 26.2458 | 29.4156 | 31.7033 | 32.9078 | 33.9865 | 34.6728 | 35.4559 | 36.0816 | 36.4906 | 37.4607 | 38.1323 | 38.4872 | 39.1426 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 50% | 258.2862 | 28.8328 | 29.665 | 32.8436 | 35.1055 | 36.4627 | 37.5493 | 38.4322 | 39.2814 | 40.0165 | 40.3868 | 40.9308 | 41.5528 | 42.1882 | 42.9863 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126
45% | 1622.7029 | 23.0686 | 23.6212 | 26.474 | 28.5329 | 29.617 | 30.5878 | 31.2055 | 31.9103 | 32.4734 | 32.8415 | 33.7146 | 34.3191 | 34.6384 | 35.2283 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 45% | 488.9664 | 25.9496 | 26.6985 | 29.5593 | 31.595 | 32.8165 | 33.7944 | 34.5889 | 35.3533 | 36.0149 | 36.3481 | 36.8377 | 37.3975 | 37.9694 | 38.6876 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013
40% | 2442.9413 | 20.5054 | 20.9966 | 23.5325 | 25.3626 | 26.3262 | 27.1892 | 27.7382 | 28.3647 | 28.8653 | 29.1925 | 29.9686 | 30.5058 | 30.7897 | 31.3141 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 40% | 928.0152 | 23.0663 | 23.732 | 26.2749 | 28.0844 | 29.1702 | 30.0394 | 30.7457 | 31.4252 | 32.0132 | 32.3094 | 32.7446 | 33.2423 | 33.7506 | 34.389 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49
35% | 3006.7842 | 17.9422 | 18.3721 | 20.5909 | 22.1923 | 23.0355 | 23.7905 | 24.2709 | 24.8191 | 25.2571 | 25.5434 | 26.2225 | 26.6926 | 26.941 | 27.3998 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 35% | 1530.4309 | 20.183 | 20.7655 | 22.9905 | 24.5739 | 25.5239 | 26.2845 | 26.9025 | 27.497 | 28.0116 | 28.2708 | 28.6515 | 29.087 | 29.5317 | 30.0904 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788
30% | 3276.4154 | 15.379 | 15.7475 | 17.6494 | 19.022 | 19.7447 | 20.3919 | 20.8037 | 21.2735 | 21.649 | 21.8943 | 22.4764 | 22.8794 | 23.0923 | 23.4856 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 30% | 2592.3162 | 17.2997 | 17.799 | 19.7062 | 21.0633 | 21.8776 | 22.5296 | 23.0593 | 23.5689 | 24.0099 | 24.2321 | 24.5585 | 24.9317 | 25.3129 | 25.7918 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675
25% | 3466.632 | 12.8159 | 13.1229 | 14.7078 | 15.8516 | 16.4539 | 16.9932 | 17.3364 | 17.7279 | 18.0408 | 18.2453 | 18.7304 | 19.0662 | 19.2436 | 19.5713 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 25% | 3659.4958 | 14.4164 | 14.8325 | 16.4218 | 17.5528 | 18.2314 | 18.7747 | 19.2161 | 19.6407 | 20.0083 | 20.1934 | 20.4654 | 20.7764 | 21.0941 | 21.4931 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563
20% | 3713.9514 | 10.2527 | 10.4983 | 11.7662 | 12.6813 | 13.1631 | 13.5946 | 13.8691 | 14.1823 | 14.4326 | 14.5962 | 14.9843 | 15.2529 | 15.3949 | 15.657 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 20% | 4005.5161 | 11.5331 | 11.866 | 13.1375 | 14.0422 | 14.5851 | 15.0197 | 15.3729 | 15.7126 | 16.0066 | 16.1547 | 16.3723 | 16.6211 | 16.8753 | 17.1945 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245
15% | 4043.3325 | 7.6895 | 7.8737 | 8.8247 | 9.511 | 9.8723 | 10.1959 | 10.4018 | 10.6368 | 10.8245 | 10.9472 | 11.2382 | 11.4397 | 11.5461 | 11.7428 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 15% | 4281.1979 | 8.6499 | 8.8995 | 9.8531 | 10.5317 | 10.9388 | 11.2648 | 11.5296 | 11.7844 | 12.005 | 12.116 | 12.2792 | 12.4658 | 12.6565 | 12.8959 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338
10% | 4350.7801 | 5.1263 | 5.2492 | 5.8831 | 6.3407 | 6.5816 | 6.7973 | 6.9346 | 7.0912 | 7.2163 | 7.2981 | 7.4921 | 7.6265 | 7.6974 | 7.8285 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 10% | 4391.6218 | 5.7666 | 5.933 | 6.5687 | 7.0211 | 7.2925 | 7.5099 | 7.6864 | 7.8563 | 8.0033 | 8.0774 | 8.1862 | 8.3106 | 8.4376 | 8.5973 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225
5% | 4391.6218 | 2.5632 | 2.6246 | 2.9416 | 3.1703 | 3.2908 | 3.3986 | 3.4673 | 3.5456 | 3.6082 | 3.6491 | 3.7461 | 3.8132 | 3.8487 | 3.9143 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 5% | 4391.6218 | 2.8833 | 2.9665 | 3.2844 | 3.5106 | 3.6463 | 3.7549 | 3.8432 | 3.9281 | 4.0017 | 4.0387 | 4.0931 | 4.1553 | 4.2188 | 4.2986 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113
9.992e-14% | 4391.6218 | 5.1223e-14 | 5.245e-14 | 5.8784e-14 | 6.3356e-14 | 6.5763e-14 | 6.7919e-14 | 6.929e-14 | 7.0855e-14 | 7.2105e-14 | 7.2923e-14 | 7.4862e-14 | 7.6204e-14 | 7.6913e-14 | 7.8223e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 9.992e-14% | 4391.6218 | 5.762e-14 | 5.9283e-14 | 6.5635e-14 | 7.0155e-14 | 7.2867e-14 | 7.5039e-14 | 7.6803e-14 | 7.85e-14 | 7.9969e-14 | 8.0709e-14 | 8.1796e-14 | 8.3039e-14 | 8.4309e-14 | 8.5904e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 45.3659 | 47.2065 | 53.7022 | 59.1735 | 62.1275 | 64.2624 | 66.7236 | 68.5664 | 70.5966 | 71.6636 | 72.5873 | 74.8682 | 73.5001 | 77.2171 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 82.0645 | 100% | 0 | 48.2848 | 50.2082 | 56.6535 | 62.3316 | 65.2958 | 67.6996 | 69.9866 | 71.9359 | 73.9651 | 74.8577 | 76.0733 | 78.3233 | 77.5939 | 80.5316 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277 | 82.2277
99% | 0.8916 | 44.9122 | 46.7344 | 53.1652 | 58.5818 | 61.5062 | 63.6197 | 66.0564 | 67.8808 | 69.8906 | 70.9469 | 71.8615 | 74.1195 | 72.7651 | 76.445 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 81.2439 | 99% | 0.8916 | 47.8019 | 49.7061 | 56.087 | 61.7083 | 64.6429 | 67.0226 | 69.2868 | 71.2166 | 73.2255 | 74.1092 | 75.3125 | 77.5401 | 76.818 | 79.7262 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055 | 81.4055
98% | 3.5664 | 44.4586 | 46.2623 | 52.6282 | 57.99 | 60.8849 | 62.9771 | 65.3891 | 67.1951 | 69.1847 | 70.2303 | 71.1356 | 73.3709 | 72.0301 | 75.6728 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 80.4232 | 98% | 3.5664 | 47.3191 | 49.204 | 55.5204 | 61.085 | 63.9899 | 66.3456 | 68.5869 | 70.4972 | 72.4858 | 73.3606 | 74.5518 | 76.7569 | 76.0421 | 78.9209 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832 | 80.5832
97% | 4.7552 | 44.0049 | 45.7903 | 52.0911 | 57.3983 | 60.2637 | 62.3345 | 64.7219 | 66.5095 | 68.4787 | 69.5136 | 70.4097 | 72.6222 | 71.2951 | 74.9006 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 79.6026 | 97% | 4.7552 | 46.8362 | 48.702 | 54.9539 | 60.4617 | 63.337 | 65.6686 | 67.887 | 69.7778 | 71.7461 | 72.612 | 73.7911 | 75.9736 | 75.2661 | 78.1156 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609 | 79.7609
95% | 7.7272 | 43.0976 | 44.8461 | 51.0171 | 56.2148 | 59.0211 | 61.0492 | 63.3874 | 65.1381 | 67.0668 | 68.0804 | 68.958 | 71.1248 | 69.8251 | 73.3563 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 77.9613 | 95% | 7.7272 | 45.8705 | 47.6978 | 53.8208 | 59.215 | 62.031 | 64.3146 | 66.4873 | 68.3391 | 70.2668 | 71.1149 | 72.2696 | 74.4072 | 73.7142 | 76.505 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164 | 78.1164
90% | 39.2302 | 40.8293 | 42.4858 | 48.332 | 53.2562 | 55.9147 | 57.8361 | 60.0513 | 61.7098 | 63.5369 | 64.4972 | 65.3286 | 67.3814 | 66.1501 | 69.4954 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 73.858 | 90% | 39.2302 | 43.4563 | 45.1874 | 50.9882 | 56.0984 | 58.7663 | 60.9296 | 62.988 | 64.7423 | 66.5686 | 67.372 | 68.4659 | 70.491 | 69.8345 | 72.4784 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005 | 74.005
85% | 117.6906 | 38.561 | 40.1255 | 45.6469 | 50.2975 | 52.8084 | 54.623 | 56.7151 | 58.2815 | 60.0071 | 60.914 | 61.6992 | 63.638 | 62.4751 | 65.6346 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 69.7548 | 85% | 117.6906 | 41.042 | 42.677 | 48.1555 | 52.9819 | 55.5015 | 57.5446 | 59.4886 | 61.1455 | 62.8703 | 63.6291 | 64.6623 | 66.5748 | 65.9548 | 68.4518 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936 | 69.8936
80% | 268.3703 | 36.2927 | 37.7652 | 42.9618 | 47.3388 | 49.702 | 51.4099 | 53.3789 | 54.8532 | 56.4773 | 57.3308 | 58.0699 | 59.8946 | 58.8001 | 61.7737 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 65.6516 | 80% | 268.3703 | 38.6278 | 40.1666 | 45.3228 | 49.8653 | 52.2367 | 54.1596 | 55.9893 | 57.5487 | 59.1721 | 59.8862 | 60.8586 | 62.6587 | 62.0751 | 64.4253 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822 | 65.7822
75% | 455.9026 | 34.0244 | 35.4048 | 40.2767 | 44.3801 | 46.5956 | 48.1968 | 50.0427 | 51.4248 | 52.9474 | 53.7477 | 54.4405 | 56.1512 | 55.1251 | 57.9128 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 61.5484 | 75% | 455.9026 | 36.2136 | 37.6562 | 42.4901 | 46.7487 | 48.9719 | 50.7747 | 52.49 | 53.9519 | 55.4738 | 56.1433 | 57.055 | 58.7425 | 58.1954 | 60.3987 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708 | 61.6708
70% | 690.9866 | 31.7561 | 33.0445 | 37.5915 | 41.4215 | 43.4892 | 44.9837 | 46.7065 | 47.9965 | 49.4176 | 50.1645 | 50.8111 | 52.4078 | 51.4501 | 54.052 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 57.4451 | 70% | 690.9866 | 33.7993 | 35.1457 | 39.6575 | 43.6321 | 45.7071 | 47.3897 | 48.9907 | 50.3551 | 51.7756 | 52.4004 | 53.2513 | 54.8263 | 54.3158 | 56.3721 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594 | 57.5594
65% | 967.6784 | 29.4878 | 30.6842 | 34.9064 | 38.4628 | 40.3829 | 41.7705 | 43.3703 | 44.5682 | 45.8878 | 46.5813 | 47.1818 | 48.6643 | 47.775 | 50.1911 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 53.3419 | 65% | 967.6784 | 31.3851 | 32.6353 | 36.8248 | 40.5155 | 42.4423 | 44.0047 | 45.4913 | 46.7584 | 48.0773 | 48.6575 | 49.4476 | 50.9102 | 50.4361 | 52.3455 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448 | 53.448
60% | 1292.8136 | 27.2195 | 28.3239 | 32.2213 | 35.5041 | 37.2765 | 38.5574 | 40.0342 | 41.1399 | 42.358 | 42.9981 | 43.5524 | 44.9209 | 44.1 | 46.3303 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 49.2387 | 60% | 1292.8136 | 28.9709 | 30.1249 | 33.9921 | 37.399 | 39.1775 | 40.6197 | 41.992 | 43.1616 | 44.3791 | 44.9146 | 45.644 | 46.994 | 46.5564 | 48.3189 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366 | 49.3366
55% | 1647.0743 | 24.9512 | 25.9636 | 29.5362 | 32.5454 | 34.1701 | 35.3443 | 36.698 | 37.7115 | 38.8281 | 39.415 | 39.923 | 41.1775 | 40.425 | 42.4694 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 45.1355 | 55% | 1647.0743 | 26.5566 | 27.6145 | 31.1594 | 34.2824 | 35.9127 | 37.2348 | 38.4927 | 39.5648 | 40.6808 | 41.1718 | 41.8403 | 43.0778 | 42.6767 | 44.2924 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253 | 45.2253
50% | 2104.1657 | 22.6829 | 23.6032 | 26.8511 | 29.5868 | 31.0637 | 32.1312 | 33.3618 | 34.2832 | 35.2983 | 35.8318 | 36.2937 | 37.4341 | 36.75 | 38.6086 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 41.0322 | 50% | 2104.1657 | 24.1424 | 25.1041 | 28.3268 | 31.1658 | 32.6479 | 33.8498 | 34.9933 | 35.968 | 36.9826 | 37.4289 | 38.0366 | 39.1617 | 38.797 | 40.2658 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139 | 41.1139
45% | 2736.0097 | 20.4146 | 21.2429 | 24.166 | 26.6281 | 27.9574 | 28.9181 | 30.0256 | 30.8549 | 31.7685 | 32.2486 | 32.6643 | 33.6907 | 33.075 | 34.7477 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 36.929 | 45% | 2736.0097 | 21.7281 | 22.5937 | 25.4941 | 28.0492 | 29.3831 | 30.4648 | 31.494 | 32.3712 | 33.2843 | 33.686 | 34.233 | 35.2455 | 34.9173 | 36.2392 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025 | 37.0025
40% | 3483.7613 | 18.1464 | 18.8826 | 21.4809 | 23.6694 | 24.851 | 25.7049 | 26.6894 | 27.4266 | 28.2386 | 28.6654 | 29.0349 | 29.9473 | 29.4 | 30.8868 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 32.8258 | 40% | 3483.7613 | 19.3139 | 20.0833 | 22.6614 | 24.9326 | 26.1183 | 27.0798 | 27.9947 | 28.7744 | 29.586 | 29.9431 | 30.4293 | 31.3293 | 31.0376 | 32.2126 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911 | 32.8911
35% | 3830.2948 | 15.8781 | 16.5223 | 18.7958 | 20.7107 | 21.7446 | 22.4918 | 23.3533 | 23.9983 | 24.7088 | 25.0822 | 25.4056 | 26.2039 | 25.725 | 27.026 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 28.7226 | 35% | 3830.2948 | 16.8997 | 17.5729 | 19.8287 | 21.8161 | 22.8535 | 23.6948 | 24.4953 | 25.1776 | 25.8878 | 26.2002 | 26.6256 | 27.4132 | 27.1579 | 28.186 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797 | 28.7797
30% | 3953.6322 | 13.6098 | 14.1619 | 16.1107 | 17.7521 | 18.6382 | 19.2787 | 20.0171 | 20.5699 | 21.179 | 21.4991 | 21.7762 | 22.4605 | 22.05 | 23.1651 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 24.6193 | 30% | 3953.6322 | 14.4854 | 15.0625 | 16.9961 | 18.6995 | 19.5888 | 20.3099 | 20.996 | 21.5808 | 22.1895 | 22.4573 | 22.822 | 23.497 | 23.2782 | 24.1595 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683 | 24.6683
25% | 4060.9208 | 11.3415 | 11.8016 | 13.4256 | 14.7934 | 15.5319 | 16.0656 | 16.6809 | 17.1416 | 17.6491 | 17.9159 | 18.1468 | 18.7171 | 18.375 | 19.3043 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 20.5161 | 25% | 4060.9208 | 12.0712 | 12.5521 | 14.1634 | 15.5829 | 16.324 | 16.9249 | 17.4967 | 17.984 | 18.4913 | 18.7144 | 19.0183 | 19.5808 | 19.3985 | 20.1329 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569 | 20.5569
20% | 4165.2375 | 9.0732 | 9.4413 | 10.7404 | 11.8347 | 12.4255 | 12.8525 | 13.3447 | 13.7133 | 14.1193 | 14.3327 | 14.5175 | 14.9736 | 14.7 | 15.4434 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 16.4129 | 20% | 4165.2375 | 9.657 | 10.0416 | 11.3307 | 12.4663 | 13.0592 | 13.5399 | 13.9973 | 14.3872 | 14.793 | 14.9715 | 15.2147 | 15.6647 | 15.5188 | 16.1063 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455 | 16.4455
15% | 4270.4458 | 6.8049 | 7.081 | 8.0553 | 8.876 | 9.3191 | 9.6394 | 10.0085 | 10.285 | 10.5895 | 10.7495 | 10.8881 | 11.2302 | 11.025 | 11.5826 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 12.3097 | 15% | 4270.4458 | 7.2427 | 7.5312 | 8.498 | 9.3497 | 9.7944 | 10.1549 | 10.498 | 10.7904 | 11.0948 | 11.2287 | 11.411 | 11.7485 | 11.6391 | 12.0797 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342 | 12.3342
10% | 4373.8709 | 4.5366 | 4.7206 | 5.3702 | 5.9174 | 6.2127 | 6.4262 | 6.6724 | 6.8566 | 7.0597 | 7.1664 | 7.2587 | 7.4868 | 7.35 | 7.7217 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 8.2064 | 10% | 4373.8709 | 4.8285 | 5.0208 | 5.6654 | 6.2332 | 6.5296 | 6.77 | 6.9987 | 7.1936 | 7.3965 | 7.4858 | 7.6073 | 7.8323 | 7.7594 | 8.0532 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228 | 8.2228
5% | 4391.7028 | 2.2683 | 2.3603 | 2.6851 | 2.9587 | 3.1064 | 3.2131 | 3.3362 | 3.4283 | 3.5298 | 3.5832 | 3.6294 | 3.7434 | 3.675 | 3.8609 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 4.1032 | 5% | 4391.7028 | 2.4142 | 2.5104 | 2.8327 | 3.1166 | 3.2648 | 3.385 | 3.4993 | 3.5968 | 3.6983 | 3.7429 | 3.8037 | 3.9162 | 3.8797 | 4.0266 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114 | 4.1114
9.992e-14% | 4391.7028 | 4.533e-14 | 4.7169e-14 | 5.3659e-14 | 5.9126e-14 | 6.2078e-14 | 6.4211e-14 | 6.667e-14 | 6.8512e-14 | 7.054e-14 | 7.1606e-14 | 7.2529e-14 | 7.4808e-14 | 7.3441e-14 | 7.7155e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 8.1999e-14 | 9.992e-14% | 4391.7028 | 4.8246e-14 | 5.0168e-14 | 5.6608e-14 | 6.2282e-14 | 6.5244e-14 | 6.7645e-14 | 6.9931e-14 | 7.1878e-14 | 7.3906e-14 | 7.4798e-14 | 7.6012e-14 | 7.8261e-14 | 7.7532e-14 | 8.0467e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14 | 8.2162e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 51.2635 | 52.4916 | 58.8312 | 63.4065 | 65.8156 | 67.973 | 69.3455 | 70.9117 | 72.1632 | 72.9812 | 74.9214 | 76.2646 | 76.9743 | 78.2852 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 77.9089 | 100% | 0 | 57.6657 | 59.3301 | 65.6873 | 70.211 | 72.9255 | 75.0986 | 76.8643 | 78.5629 | 80.033 | 80.7736 | 81.8616 | 83.1057 | 84.3764 | 85.9726 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251 | 86.2251
99% | 0 | 50.7508 | 51.9667 | 58.2429 | 62.7724 | 65.1574 | 67.2933 | 68.6521 | 70.2026 | 71.4415 | 72.2514 | 74.1722 | 75.502 | 76.2046 | 77.5024 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 77.1298 | 99% | 0.75633 | 57.089 | 58.7368 | 65.0304 | 69.5089 | 72.1962 | 74.3476 | 76.0957 | 77.7773 | 79.2327 | 79.9659 | 81.0429 | 82.2746 | 83.5326 | 85.1128 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629 | 85.3629
98% | 0.37816 | 50.2382 | 51.4418 | 57.6546 | 62.1384 | 64.4993 | 66.6135 | 67.9586 | 69.4935 | 70.7199 | 71.5215 | 73.423 | 74.7393 | 75.4348 | 76.7195 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 76.3507 | 98% | 1.1345 | 56.5124 | 58.1435 | 64.3735 | 68.8068 | 71.467 | 73.5966 | 75.327 | 76.9916 | 78.4324 | 79.1581 | 80.2243 | 81.4436 | 82.6889 | 84.2531 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006 | 84.5006
97% | 0.75633 | 49.7256 | 50.9169 | 57.0663 | 61.5043 | 63.8411 | 65.9338 | 67.2652 | 68.7844 | 69.9983 | 70.7917 | 72.6738 | 73.9767 | 74.6651 | 75.9367 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 75.5716 | 97% | 1.8908 | 55.9357 | 57.5502 | 63.7166 | 68.1047 | 70.7377 | 72.8456 | 74.5584 | 76.206 | 77.6321 | 78.3504 | 79.4057 | 80.6125 | 81.8451 | 83.3934 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384 | 83.6384
95% | 1.8908 | 48.7003 | 49.867 | 55.8896 | 60.2362 | 62.5248 | 64.5743 | 65.8783 | 67.3661 | 68.555 | 69.3321 | 71.1753 | 72.4514 | 73.1256 | 74.371 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 74.0134 | 95% | 3.4035 | 54.7824 | 56.3636 | 62.4029 | 66.7005 | 69.2792 | 71.3437 | 73.0211 | 74.6347 | 76.0314 | 76.7349 | 77.7685 | 78.9504 | 80.1576 | 81.6739 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139 | 81.9139
90% | 4.538 | 46.1371 | 47.2424 | 52.9481 | 57.0659 | 59.234 | 61.1757 | 62.411 | 63.8205 | 64.9469 | 65.683 | 67.4293 | 68.6381 | 69.2769 | 70.4567 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 70.118 | 90% | 9.0759 | 51.8991 | 53.3971 | 59.1185 | 63.1899 | 65.6329 | 67.5887 | 69.1779 | 70.7066 | 72.0297 | 72.6962 | 73.6754 | 74.7951 | 75.9388 | 77.3753 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026 | 77.6026
85% | 9.0759 | 43.574 | 44.6179 | 50.0065 | 53.8955 | 55.9433 | 57.777 | 58.9437 | 60.275 | 61.3387 | 62.034 | 63.6832 | 64.8249 | 65.4282 | 66.5424 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 66.2225 | 85% | 16.2611 | 49.0158 | 50.4306 | 55.8342 | 59.6794 | 61.9866 | 63.8338 | 65.3347 | 66.7785 | 68.0281 | 68.6576 | 69.5823 | 70.6398 | 71.72 | 73.0767 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913 | 73.2913
80% | 27.606 | 41.0108 | 41.9933 | 47.065 | 50.7252 | 52.6525 | 54.3784 | 55.4764 | 56.7294 | 57.7305 | 58.3849 | 59.9371 | 61.0117 | 61.5795 | 62.6282 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 62.3271 | 80% | 24.9588 | 46.1325 | 47.4641 | 52.5498 | 56.1688 | 58.3404 | 60.0789 | 61.4915 | 62.8503 | 64.0264 | 64.6189 | 65.4893 | 66.4845 | 67.5011 | 68.778 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801 | 68.9801
75% | 57.481 | 38.4476 | 39.3687 | 44.1234 | 47.5549 | 49.3617 | 50.9797 | 52.0092 | 53.1838 | 54.1224 | 54.7359 | 56.1911 | 57.1985 | 57.7307 | 58.7139 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 58.4316 | 75% | 32.9003 | 43.2493 | 44.4976 | 49.2655 | 52.6583 | 54.6941 | 56.324 | 57.6482 | 58.9222 | 60.0248 | 60.5802 | 61.3962 | 62.3292 | 63.2823 | 64.4794 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688 | 64.6688
70% | 106.2642 | 35.8844 | 36.7441 | 41.1818 | 44.3846 | 46.0709 | 47.5811 | 48.5419 | 49.6382 | 50.5142 | 51.0868 | 52.445 | 53.3852 | 53.882 | 54.7997 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 54.5362 | 70% | 41.9762 | 40.366 | 41.531 | 45.9811 | 49.1477 | 51.0478 | 52.569 | 53.805 | 54.994 | 56.0231 | 56.5415 | 57.3031 | 58.174 | 59.0635 | 60.1808 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576 | 60.3576
65% | 201.9397 | 33.3213 | 34.1195 | 38.2403 | 41.2142 | 42.7801 | 44.1824 | 45.0746 | 46.0926 | 46.9061 | 47.4378 | 48.6989 | 49.572 | 50.0333 | 50.8854 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 50.6408 | 65% | 67.6914 | 37.4827 | 38.5645 | 42.6967 | 45.6372 | 47.4016 | 48.8141 | 49.9618 | 51.0659 | 52.0215 | 52.5028 | 53.21 | 54.0187 | 54.8447 | 55.8822 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463 | 56.0463
60% | 402.745 | 30.7581 | 31.495 | 35.2987 | 38.0439 | 39.4894 | 40.7838 | 41.6073 | 42.547 | 43.2979 | 43.7887 | 44.9529 | 45.7588 | 46.1846 | 46.9711 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 46.7453 | 60% | 98.7009 | 34.5994 | 35.598 | 39.4124 | 42.1266 | 43.7553 | 45.0592 | 46.1186 | 47.1377 | 48.0198 | 48.4642 | 49.1169 | 49.8634 | 50.6258 | 51.5835 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351 | 51.7351
55% | 655.7369 | 28.1949 | 28.8704 | 32.3572 | 34.8736 | 36.1986 | 37.3851 | 38.14 | 39.0014 | 39.6897 | 40.1396 | 41.2068 | 41.9455 | 42.3359 | 43.0569 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 42.8499 | 55% | 153.5347 | 31.7161 | 32.6315 | 36.128 | 38.6161 | 40.109 | 41.3042 | 42.2754 | 43.2096 | 44.0182 | 44.4255 | 45.0239 | 45.7081 | 46.407 | 47.2849 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238 | 47.4238
50% | 981.7145 | 25.6317 | 26.2458 | 29.4156 | 31.7033 | 32.9078 | 33.9865 | 34.6728 | 35.4559 | 36.0816 | 36.4906 | 37.4607 | 38.1323 | 38.4872 | 39.1426 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 38.9544 | 50% | 258.2862 | 28.8328 | 29.665 | 32.8436 | 35.1055 | 36.4627 | 37.5493 | 38.4322 | 39.2814 | 40.0165 | 40.3868 | 40.9308 | 41.5528 | 42.1882 | 42.9863 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126 | 43.1126
45% | 1622.7029 | 23.0686 | 23.6212 | 26.474 | 28.5329 | 29.617 | 30.5878 | 31.2055 | 31.9103 | 32.4734 | 32.8415 | 33.7146 | 34.3191 | 34.6384 | 35.2283 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 35.059 | 45% | 488.9664 | 25.9496 | 26.6985 | 29.5593 | 31.595 | 32.8165 | 33.7944 | 34.5889 | 35.3533 | 36.0149 | 36.3481 | 36.8377 | 37.3975 | 37.9694 | 38.6876 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013 | 38.8013
40% | 2442.9413 | 20.5054 | 20.9966 | 23.5325 | 25.3626 | 26.3262 | 27.1892 | 27.7382 | 28.3647 | 28.8653 | 29.1925 | 29.9686 | 30.5058 | 30.7897 | 31.3141 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 31.1635 | 40% | 928.0152 | 23.0663 | 23.732 | 26.2749 | 28.0844 | 29.1702 | 30.0394 | 30.7457 | 31.4252 | 32.0132 | 32.3094 | 32.7446 | 33.2423 | 33.7506 | 34.389 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49 | 34.49
35% | 3006.7842 | 17.9422 | 18.3721 | 20.5909 | 22.1923 | 23.0355 | 23.7905 | 24.2709 | 24.8191 | 25.2571 | 25.5434 | 26.2225 | 26.6926 | 26.941 | 27.3998 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 27.2681 | 35% | 1530.4309 | 20.183 | 20.7655 | 22.9905 | 24.5739 | 25.5239 | 26.2845 | 26.9025 | 27.497 | 28.0116 | 28.2708 | 28.6515 | 29.087 | 29.5317 | 30.0904 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788 | 30.1788
30% | 3276.4154 | 15.379 | 15.7475 | 17.6494 | 19.022 | 19.7447 | 20.3919 | 20.8037 | 21.2735 | 21.649 | 21.8943 | 22.4764 | 22.8794 | 23.0923 | 23.4856 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 23.3727 | 30% | 2592.3162 | 17.2997 | 17.799 | 19.7062 | 21.0633 | 21.8776 | 22.5296 | 23.0593 | 23.5689 | 24.0099 | 24.2321 | 24.5585 | 24.9317 | 25.3129 | 25.7918 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675 | 25.8675
25% | 3466.632 | 12.8159 | 13.1229 | 14.7078 | 15.8516 | 16.4539 | 16.9932 | 17.3364 | 17.7279 | 18.0408 | 18.2453 | 18.7304 | 19.0662 | 19.2436 | 19.5713 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 19.4772 | 25% | 3659.4958 | 14.4164 | 14.8325 | 16.4218 | 17.5528 | 18.2314 | 18.7747 | 19.2161 | 19.6407 | 20.0083 | 20.1934 | 20.4654 | 20.7764 | 21.0941 | 21.4931 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563 | 21.5563
20% | 3713.9514 | 10.2527 | 10.4983 | 11.7662 | 12.6813 | 13.1631 | 13.5946 | 13.8691 | 14.1823 | 14.4326 | 14.5962 | 14.9843 | 15.2529 | 15.3949 | 15.657 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 15.5818 | 20% | 4005.5161 | 11.5331 | 11.866 | 13.1375 | 14.0422 | 14.5851 | 15.0197 | 15.3729 | 15.7126 | 16.0066 | 16.1547 | 16.3723 | 16.6211 | 16.8753 | 17.1945 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245 | 17.245
15% | 4043.3325 | 7.6895 | 7.8737 | 8.8247 | 9.511 | 9.8723 | 10.1959 | 10.4018 | 10.6368 | 10.8245 | 10.9472 | 11.2382 | 11.4397 | 11.5461 | 11.7428 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 11.6863 | 15% | 4281.1979 | 8.6499 | 8.8995 | 9.8531 | 10.5317 | 10.9388 | 11.2648 | 11.5296 | 11.7844 | 12.005 | 12.116 | 12.2792 | 12.4658 | 12.6565 | 12.8959 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338 | 12.9338
10% | 4350.7801 | 5.1263 | 5.2492 | 5.8831 | 6.3407 | 6.5816 | 6.7973 | 6.9346 | 7.0912 | 7.2163 | 7.2981 | 7.4921 | 7.6265 | 7.6974 | 7.8285 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 7.7909 | 10% | 4391.6218 | 5.7666 | 5.933 | 6.5687 | 7.0211 | 7.2925 | 7.5099 | 7.6864 | 7.8563 | 8.0033 | 8.0774 | 8.1862 | 8.3106 | 8.4376 | 8.5973 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225 | 8.6225
5% | 4391.6218 | 2.5632 | 2.6246 | 2.9416 | 3.1703 | 3.2908 | 3.3986 | 3.4673 | 3.5456 | 3.6082 | 3.6491 | 3.7461 | 3.8132 | 3.8487 | 3.9143 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 3.8954 | 5% | 4391.6218 | 2.8833 | 2.9665 | 3.2844 | 3.5106 | 3.6463 | 3.7549 | 3.8432 | 3.9281 | 4.0017 | 4.0387 | 4.0931 | 4.1553 | 4.2188 | 4.2986 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113 | 4.3113
9.992e-14% | 4391.6218 | 5.1223e-14 | 5.245e-14 | 5.8784e-14 | 6.3356e-14 | 6.5763e-14 | 6.7919e-14 | 6.929e-14 | 7.0855e-14 | 7.2105e-14 | 7.2923e-14 | 7.4862e-14 | 7.6204e-14 | 7.6913e-14 | 7.8223e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 7.7847e-14 | 9.992e-14% | 4391.6218 | 5.762e-14 | 5.9283e-14 | 6.5635e-14 | 7.0155e-14 | 7.2867e-14 | 7.5039e-14 | 7.6803e-14 | 7.85e-14 | 7.9969e-14 | 8.0709e-14 | 8.1796e-14 | 8.3039e-14 | 8.4309e-14 | 8.5904e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14 | 8.6156e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 105212961.6203 | 61.5% | 30.2784
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 59818974.1027 | 34.97% | 12.0256
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 2268426.58 | 1.326% | 0.44409
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 3766583.5488 | 2.202% | 0.4899
|  | 171066945.8518 |  | 43.238 | KW/h
|  |  |  | 43237.9539 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  |  | 4.8447 | 9.6985 | 12.319 | 14.213 | 16.3964 | 18.0313 | 19.8323 | 20.7788 | 21.5984 | 23.6218 | 22.4081 | 25.7056 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 |  | 0.074865 | 1.745 | 7.4629 | 12.5001 | 15.1298 | 17.2622 | 19.2912 | 21.0205 | 22.8206 | 23.6125 | 24.6909 | 26.687 | 26.0399 | 28.646 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507
98% |  |  | 13.0976 | 27.5126 | 35.2953 | 40.92 | 47.4046 | 52.2599 | 57.6086 | 60.4197 | 62.8536 | 68.8629 | 65.2583 | 75.0515 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 |  |  | 3.892 | 20.8732 | 35.8331 | 43.6429 | 49.9759 | 56.0016 | 61.1373 | 66.4835 | 68.8353 | 72.0378 | 77.966 | 76.0442 | 83.7839 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528
97% |  |  | 5.1827 | 11.5244 | 14.9482 | 17.4227 | 20.2755 | 22.4115 | 24.7646 | 26.0013 | 27.072 | 29.7157 | 28.1299 | 32.4383 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 |  |  | 1.1329 | 8.6035 | 15.1848 | 18.6206 | 21.4067 | 24.0576 | 26.317 | 28.6689 | 29.7036 | 31.1125 | 33.7204 | 32.875 | 36.2799 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459
95% |  |  | 10.5628 | 26.173 | 34.601 | 40.692 | 47.7142 | 52.972 | 58.7642 | 61.8084 | 64.4441 | 70.9517 | 67.0482 | 77.6533 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 |  |  | 0.72918 | 18.9832 | 35.1834 | 43.6406 | 50.4987 | 57.024 | 62.5855 | 68.375 | 70.9218 | 74.3898 | 80.8095 | 78.7284 | 87.1098 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492
90% |  |  | 52.7531 | 212.1886 | 298.2683 | 360.4795 | 432.201 | 485.9019 | 545.0608 | 576.1524 | 603.0721 | 669.5377 | 629.6694 | 737.9853 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 |  |  |  | 138.755 | 304.2164 | 390.5952 | 460.6403 | 527.2868 | 584.0895 | 643.2204 | 669.2324 | 704.653 | 770.2205 | 748.9655 | 834.5691 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964
85% |  |  | 1.6102 | 296.3309 | 499.1296 | 645.6954 | 814.6671 | 941.1831 | 1080.558 | 1153.8081 | 1217.2291 | 1373.8183 | 1279.8908 | 1535.0767 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 |  |  |  | 123.3255 | 513.1428 | 716.6463 | 881.6684 | 1038.6836 | 1172.5073 | 1311.8162 | 1373.0989 | 1456.5478 | 1611.0209 | 1560.9455 | 1762.6224 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702
80% |  |  |  | 134.4101 | 490.4883 | 755.877 | 1061.8366 | 1290.921 | 1543.289 | 1675.9241 | 1790.7614 | 2074.2996 | 1904.2237 | 2366.2926 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 |  |  |  | 0.64295 | 515.8623 | 884.3489 | 1183.1569 | 1467.4664 | 1709.7829 | 1962.0315 | 2072.997 | 2224.0991 | 2503.8057 | 2413.1335 | 2778.3128 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664
75% |  |  |  |  | 87.4388 | 338.183 | 695.8947 | 963.7281 | 1258.7834 | 1413.8533 | 1548.115 | 1879.6129 | 1680.7692 | 2220.9957 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 |  |  |  |  | 104.678 | 488.3855 | 837.736 | 1170.1356 | 1453.4392 | 1748.355 | 1878.09 | 2054.7506 | 2381.7687 | 2275.7595 | 2702.7079 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268
70% | [5 empty] | 1.4164 | 147.0134 | 402.153 | 748.1612 | 930.0102 | 1087.4577 | 1476.2021 | 1243.02 | 1876.5385 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | [5 empty] | 34.0065 | 267.3371 | 644.2048 | 976.4323 | 1322.2772 | 1474.4162 | 1681.5844 | 2065.0755 | 1940.7595 | 2441.4379 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282
65% | [8 empty] | 78.7639 | 180.8872 | 301.2318 | 701.7054 | 448.0849 | 1140.4017 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | [7 empty] | 38.7992 | 213.3471 | 533.0315 | 699.7484 | 926.7673 | 1347.0043 | 1210.7764 | 1759.4294 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203
60% | [11 empty] | 19.1672 |  | 202.1562 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | [9 empty] | 0.26278 | 18.7788 | 89.5662 | 351.5667 | 248.6624 | 758.289 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693
55% | FY39: 66.2368; FY40: 66.2368; FY41: 66.2368; FY42: 66.2368; FY43: 66.2368; FY44: 66.2368; FY45: 66.2368; FY46: 66.2368; FY47: 66.2368; FY48: 66.2368; FY49: 66.2368; FY50: 66.2368; FY51: 66.2368; FY52: 66.2368; FY53: 66.2368; FY54: 66.2368 | [14 empty] | 4.4747 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 88.051 | 717.8381 | 1472.4887 | 2214.8991 | 3283.4036 | 4229.5618 | 5415.5859 | 6099.6435 | 6723.8351 | 8387.4954 | 7368.5024 | 10290.2954 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | E @ R (MWh) | 0.074865 | 7.4991 | 318.6462 | 1536.6009 | 2635.0164 | 3769.6822 | 5042.9508 | 6280.6584 | 7707.3424 | 8379.4347 | 9340.1993 | 11249.6452 | 10612.6898 | 13277.663 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 61.6357 | 502.4866 | 1030.7421 | 1550.4293 | 2298.3825 | 2960.6933 | 3790.9101 | 4269.7505 | 4706.6846 | 5871.2468 | 5157.9517 | 7203.2068 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 0.02246 | 2.2497 | 95.5939 | 460.9803 | 790.5049 | 1130.9047 | 1512.8853 | 1884.1975 | 2312.2027 | 2513.8304 | 2802.0598 | 3374.8936 | 3183.807 | 3983.2989 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.2101 | 10.4626 | 15.2467 | 18.651 | 20.6938 | 22.3292 | 23.658 | 24.9362 | 26.0426 | 26.5999 | 27.4186 | 28.3549 | 29.3112 | 30.5123 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024
98% | 2.0022 | 2.4597 | 4.8211 | 6.5254 | 7.4227 | 8.2264 | 8.7376 | 9.321 | 9.7872 | 10.0919 | 10.8146 | 11.3149 | 11.5793 | 12.0676 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 |  | 4.387 | 5.0069 | 7.3749 | 9.06 | 10.0711 | 10.8806 | 11.5383 | 12.171 | 12.7186 | 12.9945 | 13.3997 | 13.8632 | 14.3365 | 14.931 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251
97% | 1.8083 | 2.2612 | 4.5986 | 6.2856 | 7.1739 | 7.9693 | 8.4754 | 9.0528 | 9.5143 | 9.8159 | 10.5313 | 11.0265 | 11.2882 | 11.7715 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 |  | 8.3378 | 9.5651 | 14.2531 | 17.589 | 19.5907 | 21.1932 | 22.4953 | 23.7478 | 24.8319 | 25.378 | 26.1803 | 27.0978 | 28.0348 | 29.2119 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981
95% | 4.5527 | 5.8902 | 12.7948 | 17.7778 | 20.4016 | 22.7512 | 24.2461 | 25.9518 | 27.3148 | 28.2057 | 30.3188 | 31.7817 | 32.5547 | 33.9824 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 |  | 15.3672 | 17.7841 | 27.0157 | 33.5849 | 37.5267 | 40.6824 | 43.2465 | 45.7131 | 47.8479 | 48.9233 | 50.5032 | 52.3099 | 54.1552 | 56.473 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398
90% | 5.8733 | 8.8805 | 24.4037 | 35.6069 | 41.5058 | 46.7884 | 50.1493 | 53.9842 | 57.0486 | 59.0515 | 63.8024 | 67.0914 | 68.8292 | 72.0391 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 |  | 46.1782 | 54.9112 | 88.2676 | 112.004 | 126.2467 | 137.6492 | 146.914 | 155.8264 | 163.5403 | 167.426 | 173.1346 | 179.6625 | 186.3301 | 194.7051 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303
85% | 0.77742 | 3.6064 | 28.4862 | 46.6535 | 56.2193 | 64.7857 | 70.2358 | 76.4546 | 81.4238 | 84.6718 | 92.376 | 97.7095 | 100.5276 | 105.7328 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 |  | 37.7756 | 48.2395 | 88.2071 | 116.6479 | 133.7136 | 147.376 | 158.4771 | 169.1559 | 178.3987 | 183.0546 | 189.8946 | 197.7163 | 205.7054 | 215.7403 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282
80% |  |  | 61.8114 | 131.7556 | 168.5839 | 201.5645 | 222.5473 | 246.4899 | 265.6212 | 278.1261 | 307.7873 | 328.321 | 339.1708 | 359.2107 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 |  | 20.6502 | 32.5932 | 78.2104 | 110.6714 | 130.1493 | 145.743 | 158.4133 | 170.6016 | 181.1509 | 186.4648 | 194.2718 | 203.199 | 212.3175 | 223.7708 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831
75% |  |  | 17.662 | 117.7088 | 173.4865 | 223.4368 | 255.2159 | 291.4777 | 320.4528 | 339.3918 | 384.3147 | 415.4137 | 431.846 | 462.1971 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 |  | 1.1976 | 6.8612 | 45.3269 | 73.1689 | 89.8753 | 103.2501 | 114.1175 | 124.5715 | 133.6197 | 138.1775 | 144.8736 | 152.5306 | 160.3515 | 170.1752 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296
70% |  |  |  | 42.6654 | 122.7534 | 199.0556 | 247.6001 | 302.9923 | 347.2535 | 376.184 | 444.8066 | 492.3121 | 517.4136 | 563.7768 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 |  |  |  | 21.9935 | 51.7601 | 69.6212 | 83.9206 | 95.5392 | 106.7158 | 116.3895 | 121.2623 | 128.4213 | 136.6075 | 144.9691 | 155.4718 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337
65% |  |  |  |  | 11.0262 | 79.8024 | 154.0865 | 255.0147 | 335.835 | 388.6616 | 513.9651 | 600.7094 | 646.5443 | 731.2026 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 |  |  |  | 2.3884 | 56.3791 | 103.4956 | 141.2163 | 171.8654 | 201.3485 | 226.867 | 239.7213 | 258.606 | 280.2009 | 302.2582 | 329.9635 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474
60% | [7 empty] | 22.5626 | 80.9935 | 137.7814 | 328.1238 | 495.0609 | 584.1339 | 748.6544 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 |  |  |  |  | 0.84409 | 20.6098 | 53.9337 | 88.0733 | 120.9929 | 149.4858 | 163.8383 | 184.9243 | 209.0361 | 233.6644 | 264.599 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938
55% | [11 empty] | 10.3571 | 31.8625 | 101.3744 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | [7 empty] | 6.0197 | 26.2071 | 54.4783 | 72.3303 | 102.7689 | 141.787 | 181.853 | 232.1783 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414
50% | [42 empty] | 3.2543 | 18.0873 | 52.963 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0139 | 23.0979 | 154.5779 | 404.9789 | 608.5733 | 854.3803 | 1041.2939 | 1293.3017 | 1535.2447 | 1711.9817 | 2186.8407 | 2561.0983 | 2775.75 | 3202.0092 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | E @ R (MWh) | 143.1036 | 185.424 | 388.2843 | 600.3605 | 761.5938 | 908.1742 | 1040.3576 | 1181.9879 | 1315.3714 | 1386.1709 | 1494.397 | 1625.6198 | 1771.3742 | 1970.6952 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317
Option 1 Summer POE50 W E @ R (MWh) N 1 | 10.5097 | 16.1685 | 108.2045 | 283.4852 | 426.0013 | 598.0662 | 728.9057 | 905.3112 | 1074.6713 | 1198.3872 | 1530.7885 | 1792.7688 | 1943.025 | 2241.4064 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 42.9311 | 55.6272 | 116.4853 | 180.1082 | 228.4781 | 272.4523 | 312.1073 | 354.5964 | 394.6114 | 415.8513 | 448.3191 | 487.6859 | 531.4123 | 591.2086 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  |  | 4.8447 | 9.6985 |  | 1.3495 | 3.5329 | 5.1678 | 6.9688 | 7.9153 | 8.7349 | 10.7583 | 9.5446 | 12.8421 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 | 17.1424 |  | 0.074865 | 1.745 | 7.4629 | 12.5001 | 2.2663 | 4.3987 | 6.4277 | 8.157 | 9.9571 | 10.749 | 11.8274 | 13.8235 | 13.1764 | 15.7825 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872 | 17.2872
98% |  |  | 13.0976 | 27.5126 |  | 2.7174 | 9.202 | 14.0572 | 19.406 | 22.217 | 24.6509 | 30.6603 | 27.0557 | 36.8488 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 | 49.6201 |  |  | 3.892 | 20.8732 | 35.8331 | 5.4402 | 11.7732 | 17.799 | 22.9347 | 28.2809 | 30.6327 | 33.8352 | 39.7633 | 37.8416 | 45.5813 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502 | 50.0502
97% |  |  | 5.1827 | 11.5244 |  | 0.61616 | 3.4689 | 5.6049 | 7.958 | 9.1947 | 10.2654 | 12.9091 | 11.3234 | 15.6317 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 | 21.2502 |  |  | 1.1329 | 8.6035 | 15.1848 | 1.814 | 4.6001 | 7.251 | 9.5104 | 11.8624 | 12.897 | 14.3059 | 16.9139 | 16.0684 | 19.4734 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394 | 21.4394
95% |  |  | 10.5628 | 26.173 |  | 0.10844 | 6.3442 | 11.602 | 17.3942 | 20.4384 | 23.0741 | 29.5817 | 25.6782 | 36.2833 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 | 50.1134 |  |  | 0.72918 | 18.9832 | 35.1834 | 2.2706 | 9.1287 | 15.654 | 21.2155 | 27.0049 | 29.5518 | 33.0198 | 39.4394 | 37.3584 | 45.7397 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791 | 50.5791
90% |  |  | 52.7531 | 212.1886 |  |  | 15.6837 | 63.3673 | 122.5262 | 153.6179 | 180.5375 | 247.0031 | 207.1348 | 315.4507 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 | 456.7047 |  |  |  | 138.755 | 304.2164 | 0.40659 | 38.1916 | 104.7522 | 161.5549 | 220.6858 | 246.6978 | 282.1184 | 347.6859 | 326.4309 | 412.0345 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618 | 461.4618
85% |  |  | 1.6102 | 296.3309 |  |  |  | 6.3176 | 86.505 | 158.3416 | 221.7626 | 378.3518 | 284.4243 | 539.6102 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 | 872.3964 |  |  |  | 123.3255 | 513.1428 |  |  | 53.1081 | 177.0408 | 316.3497 | 377.6324 | 461.0813 | 615.5544 | 565.479 | 767.1559 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037 | 883.6037
80% |  |  |  | 134.4101 | [5 empty] | 9.1452 | 48.9892 | 271.7942 | 118.0607 | 563.7872 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 | 1166.3678 |  |  |  | 0.64295 | 515.8623 |  |  |  | 17.6631 | 164.166 | 270.4916 | 421.5937 | 701.3003 | 610.628 | 975.8074 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661 | 1186.661
75% | [11 empty] | 2.6958 |  | 141.2827 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 | 818.1071 |  |  |  |  | 104.678 | [5 empty] | 2.545 | 48.2469 | 274.8906 | 182.0913 | 595.3139 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328 | 841.8328
70% | FY39: 248.6704; FY40: 248.6704; FY41: 248.6704; FY42: 248.6704; FY43: 248.6704; FY44: 248.6704; FY45: 248.6704; FY46: 248.6704; FY47: 248.6704; FY48: 248.6704; FY49: 248.6704; FY50: 248.6704; FY51: 248.6704; FY52: 248.6704; FY53: 248.6704; FY54: 248.6704 | [14 empty] | 82.6522 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135 | 271.3135
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 88.051 | 717.8381 | 0 | 4.7915 | 38.2317 | 106.1168 | 260.7581 | 380.8701 | 518.0146 | 983.7543 | 683.2215 | 1661.7368 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | 3700.3725 | E @ R (MWh) | 0.074865 | 7.4991 | 318.6462 | 1536.6009 | 12.1978 | 68.0924 | 204.992 | 418.0762 | 778.3067 | 981.1972 | 1306.0285 | 2049.3713 | 1789.074 | 2959.5409 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287 | 3784.2287
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 61.6357 | 502.4866 | 0 | 3.354 | 26.7622 | 74.2818 | 182.5307 | 266.6091 | 362.6102 | 688.628 | 478.2551 | 1163.2157 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | 2590.2607 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 0.02246 | 2.2497 | 95.5939 | 460.9803 | 3.6593 | 20.4277 | 61.4976 | 125.4229 | 233.492 | 294.3591 | 391.8086 | 614.8114 | 536.7222 | 887.8623 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686 | 1135.2686
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.2101 | 10.4626 | 15.2467 | 18.651 | 9.7819 | 11.4172 | 12.746 | 14.0243 | 15.1306 | 15.6879 | 16.5067 | 17.4429 | 18.3992 | 19.6004 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905 | 19.7905
98% | 2.0022 | 2.4597 | 4.8211 | 6.5254 | 2.0216 | 2.8252 | 3.3365 | 3.9199 | 4.386 | 4.6907 | 5.4135 | 5.9138 | 6.1782 | 6.6664 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 | 6.5263 |  | 4.387 | 5.0069 | 7.3749 | 9.06 | 4.67 | 5.4795 | 6.1372 | 6.7699 | 7.3175 | 7.5933 | 7.9986 | 8.462 | 8.9354 | 9.5299 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624 | 9.624
97% | 1.8083 | 2.2612 | 4.5986 | 6.2856 | 1.8276 | 2.623 | 3.1291 | 3.7065 | 4.168 | 4.4696 | 5.185 | 5.6802 | 5.9419 | 6.4252 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 | 6.2865 |  | 8.3378 | 9.5651 | 14.2531 | 17.589 | 8.8981 | 10.5006 | 11.8027 | 13.0552 | 14.1393 | 14.6854 | 15.4877 | 16.4052 | 17.3422 | 18.5193 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055 | 18.7055
95% | 4.5527 | 5.8902 | 12.7948 | 17.7778 | 4.6094 | 6.9591 | 8.4539 | 10.1597 | 11.5226 | 12.4135 | 14.5267 | 15.9896 | 16.7625 | 18.1902 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 | 17.7803 |  | 15.3672 | 17.7841 | 27.0157 | 33.5849 | 16.4705 | 19.6262 | 22.1903 | 24.6569 | 26.7918 | 27.8671 | 29.447 | 31.2537 | 33.099 | 35.4168 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836 | 35.7836
90% | 5.8733 | 8.8805 | 24.4037 | 35.6069 | 6.0009 | 11.2835 | 14.6444 | 18.4793 | 21.5437 | 23.5466 | 28.2975 | 31.5865 | 33.3243 | 36.5342 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 | 35.6126 |  | 46.1782 | 54.9112 | 88.2676 | 112.004 | 50.1648 | 61.5673 | 70.8321 | 79.7445 | 87.4584 | 91.3441 | 97.0527 | 103.5806 | 110.2482 | 118.6232 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484 | 119.9484
85% | 0.77742 | 3.6064 | 28.4862 | 46.6535 | 0.85631 | 7.2102 | 12.6603 | 18.8791 | 23.8483 | 27.0963 | 34.8005 | 40.134 | 42.9521 | 48.1573 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 | 46.6628 |  | 37.7756 | 48.2395 | 88.2071 | 116.6479 | 42.5523 | 56.2148 | 67.3159 | 77.9947 | 87.2375 | 91.8933 | 98.7334 | 106.555 | 114.5442 | 124.5791 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669 | 126.1669
80% |  |  | 61.8114 | 131.7556 |  | 0.22012 | 6.8002 | 24.8405 | 43.9555 | 56.4604 | 86.1216 | 106.6553 | 117.505 | 137.5449 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 | 131.7914 |  | 20.6502 | 32.5932 | 78.2104 | 110.6714 | 26.1021 | 41.6958 | 54.3661 | 66.5544 | 77.1037 | 82.4176 | 90.2246 | 99.1518 | 108.2703 | 119.7237 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359 | 121.5359
75% |  |  | 17.662 | 117.7088 |  |  |  |  | 4.4862 | 12.8326 | 48.5946 | 79.6936 | 96.1259 | 126.477 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 | 117.7631 |  | 1.1976 | 6.8612 | 45.3269 | 73.1689 | 3.2252 | 14.008 | 24.8755 | 35.3294 | 44.3777 | 48.9355 | 55.6315 | 63.2885 | 71.1095 | 80.9331 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875 | 82.4875
70% |  |  |  | 42.6654 | [6 empty] | 0.10876 | 9.9688 | 21.4071 | 53.2599 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 | 42.7276 |  |  |  | 21.9935 | 51.7601 |  | 0.092823 | 3.6021 | 11.4845 | 20.9786 | 25.8515 | 33.0104 | 41.1967 | 49.5583 | 60.061 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228 | 61.7228
65% | [33 empty] | 2.3884 | 56.3791 |  |  |  |  | 1.778 | 5.5087 | 14.5621 | 29.8916 | 50.5709 | 78.2763 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601 | 82.6601
60% | [34 empty] | 0.84409 | [8 empty] | 0.21414 | 6.857 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339 | 8.7339
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0139 | 23.0979 | 154.5779 | 404.9789 | 15.3158 | 31.1211 | 49.0244 | 79.9851 | 113.9104 | 141.5097 | 223.0482 | 295.6216 | 340.1971 | 433.2552 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | 405.1506 | E @ R (MWh) | 143.1036 | 185.424 | 388.2843 | 600.3605 | 161.8648 | 220.6022 | 273.8678 | 329.6138 | 382.3132 | 411.7846 | 458.6548 | 517.228 | 582.2914 | 672.1197 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592 | 687.1592
Option 2 Summer POE50 W E @ R (MWh) N 1 | 10.5097 | 16.1685 | 108.2045 | 283.4852 | 10.721 | 21.7848 | 34.3171 | 55.9896 | 79.7372 | 99.0568 | 156.1337 | 206.9351 | 238.138 | 303.2787 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | 283.6054 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 42.9311 | 55.6272 | 116.4853 | 180.1082 | 48.5594 | 66.1807 | 82.1603 | 98.8841 | 114.6939 | 123.5354 | 137.5964 | 155.1684 | 174.6874 | 201.6359 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477 | 206.1477
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  |  | 4.8447 | 3.2667 |  |  |  |  | 0.53706 | 1.4836 | 2.3031 | 4.3266 | 3.1129 | 6.4104 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 |  | 0.074865 | 1.745 | 7.4629 | 6.0684 |  |  | 0.051755 | 1.7252 | 3.5254 | 4.3173 | 5.3956 | 7.3917 | 6.7447 | 9.3507 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555
98% |  |  | 13.0976 | 8.4113 |  |  |  |  | 0.35115 | 3.1157 | 5.5496 | 11.559 | 7.9543 | 17.7475 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 |  |  | 3.892 | 20.8732 | 16.7318 |  |  |  | 3.8333 | 9.1795 | 11.5314 | 14.7338 | 20.662 | 18.7403 | 26.48 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488
97% |  |  | 5.1827 | 3.1211 | [5 empty] | 0.7914 | 1.8621 | 4.5059 | 2.9201 | 7.2284 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 |  |  | 1.1329 | 8.6035 | 6.7815 |  |  |  | 1.1071 | 3.4591 | 4.4937 | 5.9026 | 8.5106 | 7.6651 | 11.0701 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361
95% |  |  | 10.5628 | 5.488 | [5 empty] | 0.25779 | 2.389 | 8.8966 | 4.9932 | 15.5983 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 |  |  | 0.72918 | 18.9832 | 14.4983 |  |  |  | 0.68528 | 6.3199 | 8.8667 | 12.3347 | 18.7544 | 16.6733 | 25.0547 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941
90% |  |  | 52.7531 | 10.6893 | [6 empty] | 0.54103 | 35.9581 | 8.2278 | 104.1834 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 |  |  |  | 138.755 | 92.9491 |  |  |  |  | 15.5294 | 35.675 | 70.8511 | 136.4186 | 115.1636 | 200.7672 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945
85% |  |  | 1.6102 | [10 empty] | 52.168 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 |  |  |  | 123.3255 | 35.265 | [6 empty] | 11.4647 | 117.8211 | 71.7321 | 269.4227 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704
80% | FY39: 265.1151; FY40: 265.1151; FY41: 265.1151; FY42: 265.1151; FY43: 265.1151; FY44: 265.1151; FY45: 265.1151; FY46: 265.1151; FY47: 265.1151; FY48: 265.1151; FY49: 265.1151; FY50: 265.1151; FY51: 265.1151; FY52: 265.1151; FY53: 265.1151; FY54: 265.1151 |  |  |  | 0.64295 | [8 empty] | 0.20313 |  | 98.9103 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083
75% | FY39: 1.9682; FY40: 1.9682; FY41: 1.9682; FY42: 1.9682; FY43: 1.9682; FY44: 1.9682; FY45: 1.9682; FY46: 1.9682; FY47: 1.9682; FY48: 1.9682; FY49: 1.9682; FY50: 1.9682; FY51: 1.9682; FY52: 1.9682; FY53: 1.9682; FY54: 1.9682 | [15 empty] | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 88.051 | 30.9763 | 0 | 0 | 0 | 0 | 0.8882 | 5.6485 | 12.6449 | 65.2462 | 27.2082 | 203.336 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | E @ R (MWh) | 0.074865 | 7.4991 | 318.6462 | 172.2941 | 0 | 0 | 0.051755 | 7.3509 | 38.0133 | 64.8841 | 120.6826 | 309.7615 | 236.7191 | 641.0557 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 61.6357 | 21.6834 | 0 | 0 | 0 | 0 | 0.62174 | 3.954 | 8.8515 | 45.6723 | 19.0457 | 142.3352 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 0.02246 | 2.2497 | 95.5939 | 51.6882 | 0 | 0 | 0.015527 | 2.2053 | 11.404 | 19.4652 | 36.2048 | 92.9285 | 71.0157 | 192.3167 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.2101 | 10.4626 | 15.2467 | 13.1951 | 4.3259 | 5.9613 | 7.2901 | 8.5683 | 9.6747 | 10.232 | 11.0507 | 11.987 | 12.9433 | 14.1444 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345
98% | 2.0022 | 2.4597 | 4.8211 | 3.8248 |  | 0.12466 | 0.63593 | 1.2193 | 1.6855 | 1.9902 | 2.7129 | 3.2132 | 3.4776 | 3.9659 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 |  | 4.387 | 5.0069 | 7.3749 | 6.3594 | 1.9694 | 2.7789 | 3.4366 | 4.0693 | 4.6169 | 4.8928 | 5.298 | 5.7615 | 6.2348 | 6.8293 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234
97% | 1.8083 | 2.2612 | 4.5986 | 3.6125 |  | 0.0039708 | 0.45594 | 1.0334 | 1.4948 | 1.7964 | 2.5118 | 3.0071 | 3.2687 | 3.7521 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 |  | 8.3378 | 9.5651 | 14.2531 | 12.2427 | 3.5518 | 5.1543 | 6.4564 | 7.7089 | 8.793 | 9.3391 | 10.1414 | 11.0589 | 11.9959 | 13.173 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592
95% | 4.5527 | 5.8902 | 12.7948 | 9.8817 |  |  | 0.55786 | 2.2636 | 3.6266 | 4.5175 | 6.6306 | 8.0935 | 8.8665 | 10.2942 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 |  | 15.3672 | 17.7841 | 27.0157 | 23.0568 | 5.9424 | 9.0981 | 11.6622 | 14.1288 | 16.2637 | 17.3391 | 18.919 | 20.7256 | 22.5709 | 24.8887 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555
90% | 5.8733 | 8.8805 | 24.4037 | 17.8544 |  |  | 0.00013828 | 1.2174 | 3.7912 | 5.7942 | 10.5451 | 13.834 | 15.5719 | 18.7817 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 |  | 46.1782 | 54.9112 | 88.2676 | 73.963 | 12.1238 | 23.5263 | 32.7911 | 41.7035 | 49.4174 | 53.3031 | 59.0118 | 65.5396 | 72.2073 | 80.5822 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074
85% | 0.77742 | 3.6064 | 28.4862 | 17.8658 |  |  |  |  | 0.026586 | 0.73038 | 6.0128 | 11.3462 | 14.1643 | 19.3695 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 |  | 37.7756 | 48.2395 | 88.2071 | 71.0673 | 1.0334 | 10.6342 | 21.7353 | 32.4141 | 41.6569 | 46.3127 | 53.1528 | 60.9744 | 68.9636 | 78.9985 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863
80% |  |  | 61.8114 | 21.1719 | [7 empty] | 4.3975 | 10.1668 | 26.7121 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 |  | 20.6502 | 32.5932 | 78.2104 | 58.6478 |  | 0.034901 | 4.2818 | 14.5308 | 25.0801 | 30.3941 | 38.201 | 47.1283 | 56.2467 | 67.7001 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124
75% | FY27: 17.662; FY38: 0.0041946 |  | 1.1976 | 6.8612 | 45.3269 | 28.5479 |  |  |  | 0.087582 | 2.7724 | 5.4839 | 11.0284 | 18.6675 | 26.4885 | 36.3121 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665
70% | [33 empty] | 21.9935 | 5.8865 | [7 empty] | 0.98677 | 4.5393 | 12.4398 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238
65% | [33 empty] | 2.3884
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0139 | 23.0979 | 154.5779 | 74.211 | 0 | 0.12863 | 1.6499 | 5.7337 | 10.6247 | 14.8286 | 28.4132 | 43.8915 | 55.5158 | 82.8796 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | E @ R (MWh) | 143.1036 | 185.424 | 388.2843 | 292.9666 | 28.9467 | 57.1879 | 87.6535 | 123.2113 | 158.2752 | 177.2968 | 206.8031 | 242.8294 | 282.1902 | 335.0682 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769
Option 3 Summer POE50 W E @ R (MWh) N 1 | 10.5097 | 16.1685 | 108.2045 | 51.9477 | 0 | 0.09004 | 1.1549 | 4.0136 | 7.4373 | 10.38 | 19.8892 | 30.724 | 38.8611 | 58.0157 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 42.9311 | 55.6272 | 116.4853 | 87.89 | 8.684 | 17.1564 | 26.2961 | 36.9634 | 47.4826 | 53.189 | 62.0409 | 72.8488 | 84.6571 | 100.5205 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY27: 4.8447 |  | 0.074865 | 1.745 | 7.4629
98% | FY27: 13.0976 |  |  | 3.892 | 20.8732
97% | FY27: 5.1827 |  |  | 1.1329 | 8.6035
95% | FY27: 10.5628 |  |  | 0.72918 | 18.9832
90% | FY27: 52.7531 |  |  |  | 138.755
85% | FY27: 1.6102 |  |  |  | 123.3255
80% | [33 empty] | 0.64295
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 88.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0.074865 | 7.4991 | 318.6462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 61.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 0.02246 | 2.2497 | 95.5939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 9.2101 | 10.4626 | 15.2467
98% | FY25: 2.0022; FY26: 2.4597; FY27: 4.8211 |  | 4.387 | 5.0069 | 7.3749
97% | FY25: 1.8083; FY26: 2.2612; FY27: 4.5986 |  | 8.3378 | 9.5651 | 14.2531
95% | FY25: 4.5527; FY26: 5.8902; FY27: 12.7948 |  | 15.3672 | 17.7841 | 27.0157
90% | FY25: 5.8733; FY26: 8.8805; FY27: 24.4037 |  | 46.1782 | 54.9112 | 88.2676
85% | FY25: 0.77742; FY26: 3.6064; FY27: 28.4862 |  | 37.7756 | 48.2395 | 88.2071
80% | FY27: 61.8114 |  | 20.6502 | 32.5932 | 78.2104
75% | FY27: 17.662 |  | 1.1976 | 6.8612 | 45.3269
70% | [33 empty] | 21.9935
65% | [33 empty] | 2.3884
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0139 | 23.0979 | 154.5779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 143.1036 | 185.424 | 388.2843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) N 1 | 10.5097 | 16.1685 | 108.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 42.9311 | 55.6272 | 116.4853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  |  | 4.8447 | 3.2667 |  |  |  |  | 0.53706 | 1.4836 | 2.3031 | 4.3266 | 3.1129 | 6.4104 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 | 10.7107 |  | 0.074865 | 1.745 | 7.4629 | 6.0684 |  |  | 0.051755 | 1.7252 | 3.5254 | 4.3173 | 5.3956 | 7.3917 | 6.7447 | 9.3507 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555 | 10.8555
98% |  |  | 13.0976 | 8.4113 |  |  |  |  | 0.35115 | 3.1157 | 5.5496 | 11.559 | 7.9543 | 17.7475 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 | 30.5187 |  |  | 3.892 | 20.8732 | 16.7318 |  |  |  | 3.8333 | 9.1795 | 11.5314 | 14.7338 | 20.662 | 18.7403 | 26.48 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488 | 30.9488
97% |  |  | 5.1827 | 3.1211 | [5 empty] | 0.7914 | 1.8621 | 4.5059 | 2.9201 | 7.2284 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 | 12.8469 |  |  | 1.1329 | 8.6035 | 6.7815 |  |  |  | 1.1071 | 3.4591 | 4.4937 | 5.9026 | 8.5106 | 7.6651 | 11.0701 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361 | 13.0361
95% |  |  | 10.5628 | 5.488 | [5 empty] | 0.25779 | 2.389 | 8.8966 | 4.9932 | 15.5983 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 | 29.4284 |  |  | 0.72918 | 18.9832 | 14.4983 |  |  |  | 0.68528 | 6.3199 | 8.8667 | 12.3347 | 18.7544 | 16.6733 | 25.0547 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941 | 29.8941
90% |  |  | 52.7531 | 10.6893 | [6 empty] | 0.54103 | 35.9581 | 8.2278 | 104.1834 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 | 245.4374 |  |  |  | 138.755 | 92.9491 |  |  |  |  | 15.5294 | 35.675 | 70.8511 | 136.4186 | 115.1636 | 200.7672 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945 | 250.1945
85% |  |  | 1.6102 | [10 empty] | 52.168 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 | 374.6631 |  |  |  | 123.3255 | 35.265 | [6 empty] | 11.4647 | 117.8211 | 71.7321 | 269.4227 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704 | 385.8704
80% | FY39: 265.1151; FY40: 265.1151; FY41: 265.1151; FY42: 265.1151; FY43: 265.1151; FY44: 265.1151; FY45: 265.1151; FY46: 265.1151; FY47: 265.1151; FY48: 265.1151; FY49: 265.1151; FY50: 265.1151; FY51: 265.1151; FY52: 265.1151; FY53: 265.1151; FY54: 265.1151 |  |  |  | 0.64295 | [8 empty] | 0.20313 |  | 98.9103 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083 | 285.4083
75% | FY39: 1.9682; FY40: 1.9682; FY41: 1.9682; FY42: 1.9682; FY43: 1.9682; FY44: 1.9682; FY45: 1.9682; FY46: 1.9682; FY47: 1.9682; FY48: 1.9682; FY49: 1.9682; FY50: 1.9682; FY51: 1.9682; FY52: 1.9682; FY53: 1.9682; FY54: 1.9682 | [15 empty] | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295 | 4.5295
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 88.051 | 30.9763 | 0 | 0 | 0 | 0 | 0.8882 | 5.6485 | 12.6449 | 65.2462 | 27.2082 | 203.336 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | 970.6885 | E @ R (MWh) | 0.074865 | 7.4991 | 318.6462 | 172.2941 | 0 | 0 | 0.051755 | 7.3509 | 38.0133 | 64.8841 | 120.6826 | 309.7615 | 236.7191 | 641.0557 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373 | 1010.7373
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 61.6357 | 21.6834 | 0 | 0 | 0 | 0 | 0.62174 | 3.954 | 8.8515 | 45.6723 | 19.0457 | 142.3352 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | 679.482 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 0.02246 | 2.2497 | 95.5939 | 51.6882 | 0 | 0 | 0.015527 | 2.2053 | 11.404 | 19.4652 | 36.2048 | 92.9285 | 71.0157 | 192.3167 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212 | 303.2212
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.2101 | 10.4626 | 15.2467 | 13.1951 | 4.3259 | 5.9613 | 7.2901 | 8.5683 | 9.6747 | 10.232 | 11.0507 | 11.987 | 12.9433 | 14.1444 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345 | 14.3345
98% | 2.0022 | 2.4597 | 4.8211 | 3.8248 |  | 0.12466 | 0.63593 | 1.2193 | 1.6855 | 1.9902 | 2.7129 | 3.2132 | 3.4776 | 3.9659 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 | 3.8257 |  | 4.387 | 5.0069 | 7.3749 | 6.3594 | 1.9694 | 2.7789 | 3.4366 | 4.0693 | 4.6169 | 4.8928 | 5.298 | 5.7615 | 6.2348 | 6.8293 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234 | 6.9234
97% | 1.8083 | 2.2612 | 4.5986 | 3.6125 |  | 0.0039708 | 0.45594 | 1.0334 | 1.4948 | 1.7964 | 2.5118 | 3.0071 | 3.2687 | 3.7521 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 | 3.6133 |  | 8.3378 | 9.5651 | 14.2531 | 12.2427 | 3.5518 | 5.1543 | 6.4564 | 7.7089 | 8.793 | 9.3391 | 10.1414 | 11.0589 | 11.9959 | 13.173 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592 | 13.3592
95% | 4.5527 | 5.8902 | 12.7948 | 9.8817 |  |  | 0.55786 | 2.2636 | 3.6266 | 4.5175 | 6.6306 | 8.0935 | 8.8665 | 10.2942 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 | 9.8843 |  | 15.3672 | 17.7841 | 27.0157 | 23.0568 | 5.9424 | 9.0981 | 11.6622 | 14.1288 | 16.2637 | 17.3391 | 18.919 | 20.7256 | 22.5709 | 24.8887 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555 | 25.2555
90% | 5.8733 | 8.8805 | 24.4037 | 17.8544 |  |  | 0.00013828 | 1.2174 | 3.7912 | 5.7942 | 10.5451 | 13.834 | 15.5719 | 18.7817 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 | 17.8602 |  | 46.1782 | 54.9112 | 88.2676 | 73.963 | 12.1238 | 23.5263 | 32.7911 | 41.7035 | 49.4174 | 53.3031 | 59.0118 | 65.5396 | 72.2073 | 80.5822 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074 | 81.9074
85% | 0.77742 | 3.6064 | 28.4862 | 17.8658 |  |  |  |  | 0.026586 | 0.73038 | 6.0128 | 11.3462 | 14.1643 | 19.3695 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 | 17.8751 |  | 37.7756 | 48.2395 | 88.2071 | 71.0673 | 1.0334 | 10.6342 | 21.7353 | 32.4141 | 41.6569 | 46.3127 | 53.1528 | 60.9744 | 68.9636 | 78.9985 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863 | 80.5863
80% |  |  | 61.8114 | 21.1719 | [7 empty] | 4.3975 | 10.1668 | 26.7121 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 | 21.2043 |  | 20.6502 | 32.5932 | 78.2104 | 58.6478 |  | 0.034901 | 4.2818 | 14.5308 | 25.0801 | 30.3941 | 38.201 | 47.1283 | 56.2467 | 67.7001 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124 | 69.5124
75% | FY27: 17.662; FY38: 0.0041946 |  | 1.1976 | 6.8612 | 45.3269 | 28.5479 |  |  |  | 0.087582 | 2.7724 | 5.4839 | 11.0284 | 18.6675 | 26.4885 | 36.3121 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665 | 37.8665
70% | [33 empty] | 21.9935 | 5.8865 | [7 empty] | 0.98677 | 4.5393 | 12.4398 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238 | 14.0238
65% | [33 empty] | 2.3884
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0139 | 23.0979 | 154.5779 | 74.211 | 0 | 0.12863 | 1.6499 | 5.7337 | 10.6247 | 14.8286 | 28.4132 | 43.8915 | 55.5158 | 82.8796 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | 74.2628 | E @ R (MWh) | 143.1036 | 185.424 | 388.2843 | 292.9666 | 28.9467 | 57.1879 | 87.6535 | 123.2113 | 158.2752 | 177.2968 | 206.8031 | 242.8294 | 282.1902 | 335.0682 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769 | 343.769
Option 5 Summer POE50 W E @ R (MWh) N 1 | 10.5097 | 16.1685 | 108.2045 | 51.9477 | 0 | 0.09004 | 1.1549 | 4.0136 | 7.4373 | 10.38 | 19.8892 | 30.724 | 38.8611 | 58.0157 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | 51.984 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 42.9311 | 55.6272 | 116.4853 | 87.89 | 8.684 | 17.1564 | 26.2961 | 36.9634 | 47.4826 | 53.189 | 62.0409 | 72.8488 | 84.6571 | 100.5205 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307 | 103.1307
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  |  | 4.8447 | 9.6985 | 12.319 | 14.213 | 16.3964 | 18.0313 | 19.8323 | 20.7788 | 21.5984 | 23.6218 | 22.4081 | 25.7056 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 |  | 0.074865 | 1.745 | 7.4629 | 12.5001 | 15.1298 | 17.2622 | 19.2912 | 21.0205 | 22.8206 | 23.6125 | 24.6909 | 26.687 | 26.0399 | 28.646 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507
98% |  |  | 13.0976 | 27.5126 | 35.2953 | 40.92 | 47.4046 | 52.2599 | 57.6086 | 60.4197 | 62.8536 | 68.8629 | 65.2583 | 75.0515 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 |  |  | 3.892 | 20.8732 | 35.8331 | 43.6429 | 49.9759 | 56.0016 | 61.1373 | 66.4835 | 68.8353 | 72.0378 | 77.966 | 76.0442 | 83.7839 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528
97% |  |  | 5.1827 | 11.5244 | 14.9482 | 17.4227 | 20.2755 | 22.4115 | 24.7646 | 26.0013 | 27.072 | 29.7157 | 28.1299 | 32.4383 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 |  |  | 1.1329 | 8.6035 | 15.1848 | 18.6206 | 21.4067 | 24.0576 | 26.317 | 28.6689 | 29.7036 | 31.1125 | 33.7204 | 32.875 | 36.2799 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459
95% |  |  | 10.5628 | 26.173 | 34.601 | 40.692 | 47.7142 | 52.972 | 58.7642 | 61.8084 | 64.4441 | 70.9517 | 67.0482 | 77.6533 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 |  |  | 0.72918 | 18.9832 | 35.1834 | 43.6406 | 50.4987 | 57.024 | 62.5855 | 68.375 | 70.9218 | 74.3898 | 80.8095 | 78.7284 | 87.1098 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492
90% |  |  | 52.7531 | 212.1886 | 298.2683 | 360.4795 | 432.201 | 485.9019 | 545.0608 | 576.1524 | 603.0721 | 669.5377 | 629.6694 | 737.9853 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 |  |  |  | 138.755 | 304.2164 | 390.5952 | 460.6403 | 527.2868 | 584.0895 | 643.2204 | 669.2324 | 704.653 | 770.2205 | 748.9655 | 834.5691 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964
85% |  |  | 1.6102 | 296.3309 | 499.1296 | 645.6954 | 814.6671 | 941.1831 | 1080.558 | 1153.8081 | 1217.2291 | 1373.8183 | 1279.8908 | 1535.0767 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 |  |  |  | 123.3255 | 513.1428 | 716.6463 | 881.6684 | 1038.6836 | 1172.5073 | 1311.8162 | 1373.0989 | 1456.5478 | 1611.0209 | 1560.9455 | 1762.6224 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702
80% |  |  |  | 134.4101 | 490.4883 | 755.877 | 1061.8366 | 1290.921 | 1543.289 | 1675.9241 | 1790.7614 | 2074.2996 | 1904.2237 | 2366.2926 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 |  |  |  | 0.64295 | 515.8623 | 884.3489 | 1183.1569 | 1467.4664 | 1709.7829 | 1962.0315 | 2072.997 | 2224.0991 | 2503.8057 | 2413.1335 | 2778.3128 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664
75% |  |  |  |  | 87.4388 | 338.183 | 695.8947 | 963.7281 | 1258.7834 | 1413.8533 | 1548.115 | 1879.6129 | 1680.7692 | 2220.9957 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 |  |  |  |  | 104.678 | 488.3855 | 837.736 | 1170.1356 | 1453.4392 | 1748.355 | 1878.09 | 2054.7506 | 2381.7687 | 2275.7595 | 2702.7079 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268
70% | [5 empty] | 1.4164 | 147.0134 | 402.153 | 748.1612 | 930.0102 | 1087.4577 | 1476.2021 | 1243.02 | 1876.5385 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | [5 empty] | 34.0065 | 267.3371 | 644.2048 | 976.4323 | 1322.2772 | 1474.4162 | 1681.5844 | 2065.0755 | 1940.7595 | 2441.4379 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282
65% | [8 empty] | 78.7639 | 180.8872 | 301.2318 | 701.7054 | 448.0849 | 1140.4017 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | [7 empty] | 38.7992 | 213.3471 | 533.0315 | 699.7484 | 926.7673 | 1347.0043 | 1210.7764 | 1759.4294 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203
60% | [11 empty] | 19.1672 |  | 202.1562 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | [9 empty] | 0.26278 | 18.7788 | 89.5662 | 351.5667 | 248.6624 | 758.289 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693
55% | FY39: 66.2368; FY40: 66.2368; FY41: 66.2368; FY42: 66.2368; FY43: 66.2368; FY44: 66.2368; FY45: 66.2368; FY46: 66.2368; FY47: 66.2368; FY48: 66.2368; FY49: 66.2368; FY50: 66.2368; FY51: 66.2368; FY52: 66.2368; FY53: 66.2368; FY54: 66.2368 | [14 empty] | 4.4747 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 88.051 | 717.8381 | 1472.4887 | 2214.8991 | 3283.4036 | 4229.5618 | 5415.5859 | 6099.6435 | 6723.8351 | 8387.4954 | 7368.5024 | 10290.2954 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | E @ R (MWh) | 0.074865 | 7.4991 | 318.6462 | 1536.6009 | 2635.0164 | 3769.6822 | 5042.9508 | 6280.6584 | 7707.3424 | 8379.4347 | 9340.1993 | 11249.6452 | 10612.6898 | 13277.663 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 61.6357 | 502.4866 | 1030.7421 | 1550.4293 | 2298.3825 | 2960.6933 | 3790.9101 | 4269.7505 | 4706.6846 | 5871.2468 | 5157.9517 | 7203.2068 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 0.02246 | 2.2497 | 95.5939 | 460.9803 | 790.5049 | 1130.9047 | 1512.8853 | 1884.1975 | 2312.2027 | 2513.8304 | 2802.0598 | 3374.8936 | 3183.807 | 3983.2989 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.2101 | 10.4626 | 15.2467 | 18.651 | 20.6938 | 22.3292 | 23.658 | 24.9362 | 26.0426 | 26.5999 | 27.4186 | 28.3549 | 29.3112 | 30.5123 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024
98% | 2.0022 | 2.4597 | 4.8211 | 6.5254 | 7.4227 | 8.2264 | 8.7376 | 9.321 | 9.7872 | 10.0919 | 10.8146 | 11.3149 | 11.5793 | 12.0676 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 |  | 4.387 | 5.0069 | 7.3749 | 9.06 | 10.0711 | 10.8806 | 11.5383 | 12.171 | 12.7186 | 12.9945 | 13.3997 | 13.8632 | 14.3365 | 14.931 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251
97% | 1.8083 | 2.2612 | 4.5986 | 6.2856 | 7.1739 | 7.9693 | 8.4754 | 9.0528 | 9.5143 | 9.8159 | 10.5313 | 11.0265 | 11.2882 | 11.7715 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 |  | 8.3378 | 9.5651 | 14.2531 | 17.589 | 19.5907 | 21.1932 | 22.4953 | 23.7478 | 24.8319 | 25.378 | 26.1803 | 27.0978 | 28.0348 | 29.2119 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981
95% | 4.5527 | 5.8902 | 12.7948 | 17.7778 | 20.4016 | 22.7512 | 24.2461 | 25.9518 | 27.3148 | 28.2057 | 30.3188 | 31.7817 | 32.5547 | 33.9824 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 |  | 15.3672 | 17.7841 | 27.0157 | 33.5849 | 37.5267 | 40.6824 | 43.2465 | 45.7131 | 47.8479 | 48.9233 | 50.5032 | 52.3099 | 54.1552 | 56.473 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398
90% | 5.8733 | 8.8805 | 24.4037 | 35.6069 | 41.5058 | 46.7884 | 50.1493 | 53.9842 | 57.0486 | 59.0515 | 63.8024 | 67.0914 | 68.8292 | 72.0391 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 |  | 46.1782 | 54.9112 | 88.2676 | 112.004 | 126.2467 | 137.6492 | 146.914 | 155.8264 | 163.5403 | 167.426 | 173.1346 | 179.6625 | 186.3301 | 194.7051 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303
85% | 0.77742 | 3.6064 | 28.4862 | 46.6535 | 56.2193 | 64.7857 | 70.2358 | 76.4546 | 81.4238 | 84.6718 | 92.376 | 97.7095 | 100.5276 | 105.7328 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 |  | 37.7756 | 48.2395 | 88.2071 | 116.6479 | 133.7136 | 147.376 | 158.4771 | 169.1559 | 178.3987 | 183.0546 | 189.8946 | 197.7163 | 205.7054 | 215.7403 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282
80% |  |  | 61.8114 | 131.7556 | 168.5839 | 201.5645 | 222.5473 | 246.4899 | 265.6212 | 278.1261 | 307.7873 | 328.321 | 339.1708 | 359.2107 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 |  | 20.6502 | 32.5932 | 78.2104 | 110.6714 | 130.1493 | 145.743 | 158.4133 | 170.6016 | 181.1509 | 186.4648 | 194.2718 | 203.199 | 212.3175 | 223.7708 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831
75% |  |  | 17.662 | 117.7088 | 173.4865 | 223.4368 | 255.2159 | 291.4777 | 320.4528 | 339.3918 | 384.3147 | 415.4137 | 431.846 | 462.1971 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 |  | 1.1976 | 6.8612 | 45.3269 | 73.1689 | 89.8753 | 103.2501 | 114.1175 | 124.5715 | 133.6197 | 138.1775 | 144.8736 | 152.5306 | 160.3515 | 170.1752 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296
70% |  |  |  | 42.6654 | 122.7534 | 199.0556 | 247.6001 | 302.9923 | 347.2535 | 376.184 | 444.8066 | 492.3121 | 517.4136 | 563.7768 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 |  |  |  | 21.9935 | 51.7601 | 69.6212 | 83.9206 | 95.5392 | 106.7158 | 116.3895 | 121.2623 | 128.4213 | 136.6075 | 144.9691 | 155.4718 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337
65% |  |  |  |  | 11.0262 | 79.8024 | 154.0865 | 255.0147 | 335.835 | 388.6616 | 513.9651 | 600.7094 | 646.5443 | 731.2026 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 |  |  |  | 2.3884 | 56.3791 | 103.4956 | 141.2163 | 171.8654 | 201.3485 | 226.867 | 239.7213 | 258.606 | 280.2009 | 302.2582 | 329.9635 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474
60% | [7 empty] | 22.5626 | 80.9935 | 137.7814 | 328.1238 | 495.0609 | 584.1339 | 748.6544 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 |  |  |  |  | 0.84409 | 20.6098 | 53.9337 | 88.0733 | 120.9929 | 149.4858 | 163.8383 | 184.9243 | 209.0361 | 233.6644 | 264.599 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938
55% | [11 empty] | 10.3571 | 31.8625 | 101.3744 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | [7 empty] | 6.0197 | 26.2071 | 54.4783 | 72.3303 | 102.7689 | 141.787 | 181.853 | 232.1783 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414
50% | [42 empty] | 3.2543 | 18.0873 | 52.963 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0139 | 23.0979 | 154.5779 | 404.9789 | 608.5733 | 854.3803 | 1041.2939 | 1293.3017 | 1535.2447 | 1711.9817 | 2186.8407 | 2561.0983 | 2775.75 | 3202.0092 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | E @ R (MWh) | 143.1036 | 185.424 | 388.2843 | 600.3605 | 761.5938 | 908.1742 | 1040.3576 | 1181.9879 | 1315.3714 | 1386.1709 | 1494.397 | 1625.6198 | 1771.3742 | 1970.6952 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317
Option 6 Summer POE50 W E @ R (MWh) N 1 | 10.5097 | 16.1685 | 108.2045 | 283.4852 | 426.0013 | 598.0662 | 728.9057 | 905.3112 | 1074.6713 | 1198.3872 | 1530.7885 | 1792.7688 | 1943.025 | 2241.4064 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 42.9311 | 55.6272 | 116.4853 | 180.1082 | 228.4781 | 272.4523 | 312.1073 | 354.5964 | 394.6114 | 415.8513 | 448.3191 | 487.6859 | 531.4123 | 591.2086 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  |  | 4.8447 | 9.6985 | 12.319 | 14.213 | 16.3964 | 18.0313 | 19.8323 | 20.7788 | 21.5984 | 23.6218 | 22.4081 | 25.7056 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 |  | 0.074865 | 1.745 | 7.4629 | 12.5001 | 15.1298 | 17.2622 | 19.2912 | 21.0205 | 22.8206 | 23.6125 | 24.6909 | 26.687 | 26.0399 | 28.646 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507
98% |  |  | 13.0976 | 27.5126 | 35.2953 | 40.92 | 47.4046 | 52.2599 | 57.6086 | 60.4197 | 62.8536 | 68.8629 | 65.2583 | 75.0515 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 |  |  | 3.892 | 20.8732 | 35.8331 | 43.6429 | 49.9759 | 56.0016 | 61.1373 | 66.4835 | 68.8353 | 72.0378 | 77.966 | 76.0442 | 83.7839 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528
97% |  |  | 5.1827 | 11.5244 | 14.9482 | 17.4227 | 20.2755 | 22.4115 | 24.7646 | 26.0013 | 27.072 | 29.7157 | 28.1299 | 32.4383 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 |  |  | 1.1329 | 8.6035 | 15.1848 | 18.6206 | 21.4067 | 24.0576 | 26.317 | 28.6689 | 29.7036 | 31.1125 | 33.7204 | 32.875 | 36.2799 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459
95% |  |  | 10.5628 | 26.173 | 34.601 | 40.692 | 47.7142 | 52.972 | 58.7642 | 61.8084 | 64.4441 | 70.9517 | 67.0482 | 77.6533 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 |  |  | 0.72918 | 18.9832 | 35.1834 | 43.6406 | 50.4987 | 57.024 | 62.5855 | 68.375 | 70.9218 | 74.3898 | 80.8095 | 78.7284 | 87.1098 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492
90% |  |  | 52.7531 | 212.1886 | 298.2683 | 360.4795 | 432.201 | 485.9019 | 545.0608 | 576.1524 | 603.0721 | 669.5377 | 629.6694 | 737.9853 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 |  |  |  | 138.755 | 304.2164 | 390.5952 | 460.6403 | 527.2868 | 584.0895 | 643.2204 | 669.2324 | 704.653 | 770.2205 | 748.9655 | 834.5691 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964
85% |  |  | 1.6102 | 296.3309 | 499.1296 | 645.6954 | 814.6671 | 941.1831 | 1080.558 | 1153.8081 | 1217.2291 | 1373.8183 | 1279.8908 | 1535.0767 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 |  |  |  | 123.3255 | 513.1428 | 716.6463 | 881.6684 | 1038.6836 | 1172.5073 | 1311.8162 | 1373.0989 | 1456.5478 | 1611.0209 | 1560.9455 | 1762.6224 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702
80% |  |  |  | 134.4101 | 490.4883 | 755.877 | 1061.8366 | 1290.921 | 1543.289 | 1675.9241 | 1790.7614 | 2074.2996 | 1904.2237 | 2366.2926 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 |  |  |  | 0.64295 | 515.8623 | 884.3489 | 1183.1569 | 1467.4664 | 1709.7829 | 1962.0315 | 2072.997 | 2224.0991 | 2503.8057 | 2413.1335 | 2778.3128 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664
75% |  |  |  |  | 87.4388 | 338.183 | 695.8947 | 963.7281 | 1258.7834 | 1413.8533 | 1548.115 | 1879.6129 | 1680.7692 | 2220.9957 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 |  |  |  |  | 104.678 | 488.3855 | 837.736 | 1170.1356 | 1453.4392 | 1748.355 | 1878.09 | 2054.7506 | 2381.7687 | 2275.7595 | 2702.7079 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268
70% | [5 empty] | 1.4164 | 147.0134 | 402.153 | 748.1612 | 930.0102 | 1087.4577 | 1476.2021 | 1243.02 | 1876.5385 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | [5 empty] | 34.0065 | 267.3371 | 644.2048 | 976.4323 | 1322.2772 | 1474.4162 | 1681.5844 | 2065.0755 | 1940.7595 | 2441.4379 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282
65% | [8 empty] | 78.7639 | 180.8872 | 301.2318 | 701.7054 | 448.0849 | 1140.4017 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | [7 empty] | 38.7992 | 213.3471 | 533.0315 | 699.7484 | 926.7673 | 1347.0043 | 1210.7764 | 1759.4294 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203
60% | [11 empty] | 19.1672 |  | 202.1562 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | [9 empty] | 0.26278 | 18.7788 | 89.5662 | 351.5667 | 248.6624 | 758.289 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693
55% | FY39: 66.2368; FY40: 66.2368; FY41: 66.2368; FY42: 66.2368; FY43: 66.2368; FY44: 66.2368; FY45: 66.2368; FY46: 66.2368; FY47: 66.2368; FY48: 66.2368; FY49: 66.2368; FY50: 66.2368; FY51: 66.2368; FY52: 66.2368; FY53: 66.2368; FY54: 66.2368 | [14 empty] | 4.4747 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 88.051 | 717.8381 | 1472.4887 | 2214.8991 | 3283.4036 | 4229.5618 | 5415.5859 | 6099.6435 | 6723.8351 | 8387.4954 | 7368.5024 | 10290.2954 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | E @ R (MWh) | 0.074865 | 7.4991 | 318.6462 | 1536.6009 | 2635.0164 | 3769.6822 | 5042.9508 | 6280.6584 | 7707.3424 | 8379.4347 | 9340.1993 | 11249.6452 | 10612.6898 | 13277.663 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 61.6357 | 502.4866 | 1030.7421 | 1550.4293 | 2298.3825 | 2960.6933 | 3790.9101 | 4269.7505 | 4706.6846 | 5871.2468 | 5157.9517 | 7203.2068 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 0.02246 | 2.2497 | 95.5939 | 460.9803 | 790.5049 | 1130.9047 | 1512.8853 | 1884.1975 | 2312.2027 | 2513.8304 | 2802.0598 | 3374.8936 | 3183.807 | 3983.2989 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.2101 | 10.4626 | 15.2467 | 18.651 | 20.6938 | 22.3292 | 23.658 | 24.9362 | 26.0426 | 26.5999 | 27.4186 | 28.3549 | 29.3112 | 30.5123 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024
98% | 2.0022 | 2.4597 | 4.8211 | 6.5254 | 7.4227 | 8.2264 | 8.7376 | 9.321 | 9.7872 | 10.0919 | 10.8146 | 11.3149 | 11.5793 | 12.0676 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 |  | 4.387 | 5.0069 | 7.3749 | 9.06 | 10.0711 | 10.8806 | 11.5383 | 12.171 | 12.7186 | 12.9945 | 13.3997 | 13.8632 | 14.3365 | 14.931 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251
97% | 1.8083 | 2.2612 | 4.5986 | 6.2856 | 7.1739 | 7.9693 | 8.4754 | 9.0528 | 9.5143 | 9.8159 | 10.5313 | 11.0265 | 11.2882 | 11.7715 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 |  | 8.3378 | 9.5651 | 14.2531 | 17.589 | 19.5907 | 21.1932 | 22.4953 | 23.7478 | 24.8319 | 25.378 | 26.1803 | 27.0978 | 28.0348 | 29.2119 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981
95% | 4.5527 | 5.8902 | 12.7948 | 17.7778 | 20.4016 | 22.7512 | 24.2461 | 25.9518 | 27.3148 | 28.2057 | 30.3188 | 31.7817 | 32.5547 | 33.9824 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 |  | 15.3672 | 17.7841 | 27.0157 | 33.5849 | 37.5267 | 40.6824 | 43.2465 | 45.7131 | 47.8479 | 48.9233 | 50.5032 | 52.3099 | 54.1552 | 56.473 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398
90% | 5.8733 | 8.8805 | 24.4037 | 35.6069 | 41.5058 | 46.7884 | 50.1493 | 53.9842 | 57.0486 | 59.0515 | 63.8024 | 67.0914 | 68.8292 | 72.0391 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 |  | 46.1782 | 54.9112 | 88.2676 | 112.004 | 126.2467 | 137.6492 | 146.914 | 155.8264 | 163.5403 | 167.426 | 173.1346 | 179.6625 | 186.3301 | 194.7051 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303
85% | 0.77742 | 3.6064 | 28.4862 | 46.6535 | 56.2193 | 64.7857 | 70.2358 | 76.4546 | 81.4238 | 84.6718 | 92.376 | 97.7095 | 100.5276 | 105.7328 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 |  | 37.7756 | 48.2395 | 88.2071 | 116.6479 | 133.7136 | 147.376 | 158.4771 | 169.1559 | 178.3987 | 183.0546 | 189.8946 | 197.7163 | 205.7054 | 215.7403 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282
80% |  |  | 61.8114 | 131.7556 | 168.5839 | 201.5645 | 222.5473 | 246.4899 | 265.6212 | 278.1261 | 307.7873 | 328.321 | 339.1708 | 359.2107 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 |  | 20.6502 | 32.5932 | 78.2104 | 110.6714 | 130.1493 | 145.743 | 158.4133 | 170.6016 | 181.1509 | 186.4648 | 194.2718 | 203.199 | 212.3175 | 223.7708 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831
75% |  |  | 17.662 | 117.7088 | 173.4865 | 223.4368 | 255.2159 | 291.4777 | 320.4528 | 339.3918 | 384.3147 | 415.4137 | 431.846 | 462.1971 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 |  | 1.1976 | 6.8612 | 45.3269 | 73.1689 | 89.8753 | 103.2501 | 114.1175 | 124.5715 | 133.6197 | 138.1775 | 144.8736 | 152.5306 | 160.3515 | 170.1752 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296
70% |  |  |  | 42.6654 | 122.7534 | 199.0556 | 247.6001 | 302.9923 | 347.2535 | 376.184 | 444.8066 | 492.3121 | 517.4136 | 563.7768 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 |  |  |  | 21.9935 | 51.7601 | 69.6212 | 83.9206 | 95.5392 | 106.7158 | 116.3895 | 121.2623 | 128.4213 | 136.6075 | 144.9691 | 155.4718 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337
65% |  |  |  |  | 11.0262 | 79.8024 | 154.0865 | 255.0147 | 335.835 | 388.6616 | 513.9651 | 600.7094 | 646.5443 | 731.2026 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 |  |  |  | 2.3884 | 56.3791 | 103.4956 | 141.2163 | 171.8654 | 201.3485 | 226.867 | 239.7213 | 258.606 | 280.2009 | 302.2582 | 329.9635 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474
60% | [7 empty] | 22.5626 | 80.9935 | 137.7814 | 328.1238 | 495.0609 | 584.1339 | 748.6544 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 |  |  |  |  | 0.84409 | 20.6098 | 53.9337 | 88.0733 | 120.9929 | 149.4858 | 163.8383 | 184.9243 | 209.0361 | 233.6644 | 264.599 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938
55% | [11 empty] | 10.3571 | 31.8625 | 101.3744 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | [7 empty] | 6.0197 | 26.2071 | 54.4783 | 72.3303 | 102.7689 | 141.787 | 181.853 | 232.1783 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414
50% | [42 empty] | 3.2543 | 18.0873 | 52.963 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0139 | 23.0979 | 154.5779 | 404.9789 | 608.5733 | 854.3803 | 1041.2939 | 1293.3017 | 1535.2447 | 1711.9817 | 2186.8407 | 2561.0983 | 2775.75 | 3202.0092 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | E @ R (MWh) | 143.1036 | 185.424 | 388.2843 | 600.3605 | 761.5938 | 908.1742 | 1040.3576 | 1181.9879 | 1315.3714 | 1386.1709 | 1494.397 | 1625.6198 | 1771.3742 | 1970.6952 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317
Option 7 Summer POE50 W E @ R (MWh) N 1 | 10.5097 | 16.1685 | 108.2045 | 283.4852 | 426.0013 | 598.0662 | 728.9057 | 905.3112 | 1074.6713 | 1198.3872 | 1530.7885 | 1792.7688 | 1943.025 | 2241.4064 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 42.9311 | 55.6272 | 116.4853 | 180.1082 | 228.4781 | 272.4523 | 312.1073 | 354.5964 | 394.6114 | 415.8513 | 448.3191 | 487.6859 | 531.4123 | 591.2086 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  |  | 4.8447 | 9.6985 | 12.319 | 14.213 | 16.3964 | 18.0313 | 19.8323 | 20.7788 | 21.5984 | 23.6218 | 22.4081 | 25.7056 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 | 30.0059 |  | 0.074865 | 1.745 | 7.4629 | 12.5001 | 15.1298 | 17.2622 | 19.2912 | 21.0205 | 22.8206 | 23.6125 | 24.6909 | 26.687 | 26.0399 | 28.646 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507 | 30.1507
98% |  |  | 13.0976 | 27.5126 | 35.2953 | 40.92 | 47.4046 | 52.2599 | 57.6086 | 60.4197 | 62.8536 | 68.8629 | 65.2583 | 75.0515 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 | 87.8227 |  |  | 3.892 | 20.8732 | 35.8331 | 43.6429 | 49.9759 | 56.0016 | 61.1373 | 66.4835 | 68.8353 | 72.0378 | 77.966 | 76.0442 | 83.7839 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528 | 88.2528
97% |  |  | 5.1827 | 11.5244 | 14.9482 | 17.4227 | 20.2755 | 22.4115 | 24.7646 | 26.0013 | 27.072 | 29.7157 | 28.1299 | 32.4383 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 | 38.0567 |  |  | 1.1329 | 8.6035 | 15.1848 | 18.6206 | 21.4067 | 24.0576 | 26.317 | 28.6689 | 29.7036 | 31.1125 | 33.7204 | 32.875 | 36.2799 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459 | 38.2459
95% |  |  | 10.5628 | 26.173 | 34.601 | 40.692 | 47.7142 | 52.972 | 58.7642 | 61.8084 | 64.4441 | 70.9517 | 67.0482 | 77.6533 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 | 91.4834 |  |  | 0.72918 | 18.9832 | 35.1834 | 43.6406 | 50.4987 | 57.024 | 62.5855 | 68.375 | 70.9218 | 74.3898 | 80.8095 | 78.7284 | 87.1098 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492 | 91.9492
90% |  |  | 52.7531 | 212.1886 | 298.2683 | 360.4795 | 432.201 | 485.9019 | 545.0608 | 576.1524 | 603.0721 | 669.5377 | 629.6694 | 737.9853 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 | 879.2393 |  |  |  | 138.755 | 304.2164 | 390.5952 | 460.6403 | 527.2868 | 584.0895 | 643.2204 | 669.2324 | 704.653 | 770.2205 | 748.9655 | 834.5691 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964 | 883.9964
85% |  |  | 1.6102 | 296.3309 | 499.1296 | 645.6954 | 814.6671 | 941.1831 | 1080.558 | 1153.8081 | 1217.2291 | 1373.8183 | 1279.8908 | 1535.0767 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 | 1867.8629 |  |  |  | 123.3255 | 513.1428 | 716.6463 | 881.6684 | 1038.6836 | 1172.5073 | 1311.8162 | 1373.0989 | 1456.5478 | 1611.0209 | 1560.9455 | 1762.6224 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702 | 1879.0702
80% |  |  |  | 134.4101 | 490.4883 | 755.877 | 1061.8366 | 1290.921 | 1543.289 | 1675.9241 | 1790.7614 | 2074.2996 | 1904.2237 | 2366.2926 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 | 2968.8732 |  |  |  | 0.64295 | 515.8623 | 884.3489 | 1183.1569 | 1467.4664 | 1709.7829 | 1962.0315 | 2072.997 | 2224.0991 | 2503.8057 | 2413.1335 | 2778.3128 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664 | 2989.1664
75% |  |  |  |  | 87.4388 | 338.183 | 695.8947 | 963.7281 | 1258.7834 | 1413.8533 | 1548.115 | 1879.6129 | 1680.7692 | 2220.9957 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 | 2925.5011 |  |  |  |  | 104.678 | 488.3855 | 837.736 | 1170.1356 | 1453.4392 | 1748.355 | 1878.09 | 2054.7506 | 2381.7687 | 2275.7595 | 2702.7079 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268 | 2949.2268
70% | [5 empty] | 1.4164 | 147.0134 | 402.153 | 748.1612 | 930.0102 | 1087.4577 | 1476.2021 | 1243.02 | 1876.5385 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | 2702.7053 | [5 empty] | 34.0065 | 267.3371 | 644.2048 | 976.4323 | 1322.2772 | 1474.4162 | 1681.5844 | 2065.0755 | 1940.7595 | 2441.4379 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282 | 2730.5282
65% | [8 empty] | 78.7639 | 180.8872 | 301.2318 | 701.7054 | 448.0849 | 1140.4017 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | 2045.7313 | [7 empty] | 38.7992 | 213.3471 | 533.0315 | 699.7484 | 926.7673 | 1347.0043 | 1210.7764 | 1759.4294 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203 | 2076.2203
60% | [11 empty] | 19.1672 |  | 202.1562 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | 1069.7962 | [9 empty] | 0.26278 | 18.7788 | 89.5662 | 351.5667 | 248.6624 | 758.289 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693 | 1102.9693
55% | FY39: 66.2368; FY40: 66.2368; FY41: 66.2368; FY42: 66.2368; FY43: 66.2368; FY44: 66.2368; FY45: 66.2368; FY46: 66.2368; FY47: 66.2368; FY48: 66.2368; FY49: 66.2368; FY50: 66.2368; FY51: 66.2368; FY52: 66.2368; FY53: 66.2368; FY54: 66.2368 | [14 empty] | 4.4747 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729 | 76.9729
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 88.051 | 717.8381 | 1472.4887 | 2214.8991 | 3283.4036 | 4229.5618 | 5415.5859 | 6099.6435 | 6723.8351 | 8387.4954 | 7368.5024 | 10290.2954 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | 14773.315 | E @ R (MWh) | 0.074865 | 7.4991 | 318.6462 | 1536.6009 | 2635.0164 | 3769.6822 | 5042.9508 | 6280.6584 | 7707.3424 | 8379.4347 | 9340.1993 | 11249.6452 | 10612.6898 | 13277.663 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492 | 14936.7492
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0 | 0 | 61.6357 | 502.4866 | 1030.7421 | 1550.4293 | 2298.3825 | 2960.6933 | 3790.9101 | 4269.7505 | 4706.6846 | 5871.2468 | 5157.9517 | 7203.2068 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | 10341.3205 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 0.02246 | 2.2497 | 95.5939 | 460.9803 | 790.5049 | 1130.9047 | 1512.8853 | 1884.1975 | 2312.2027 | 2513.8304 | 2802.0598 | 3374.8936 | 3183.807 | 3983.2989 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248 | 4481.0248
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.2101 | 10.4626 | 15.2467 | 18.651 | 20.6938 | 22.3292 | 23.658 | 24.9362 | 26.0426 | 26.5999 | 27.4186 | 28.3549 | 29.3112 | 30.5123 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024
98% | 2.0022 | 2.4597 | 4.8211 | 6.5254 | 7.4227 | 8.2264 | 8.7376 | 9.321 | 9.7872 | 10.0919 | 10.8146 | 11.3149 | 11.5793 | 12.0676 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 |  | 4.387 | 5.0069 | 7.3749 | 9.06 | 10.0711 | 10.8806 | 11.5383 | 12.171 | 12.7186 | 12.9945 | 13.3997 | 13.8632 | 14.3365 | 14.931 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251
97% | 1.8083 | 2.2612 | 4.5986 | 6.2856 | 7.1739 | 7.9693 | 8.4754 | 9.0528 | 9.5143 | 9.8159 | 10.5313 | 11.0265 | 11.2882 | 11.7715 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 |  | 8.3378 | 9.5651 | 14.2531 | 17.589 | 19.5907 | 21.1932 | 22.4953 | 23.7478 | 24.8319 | 25.378 | 26.1803 | 27.0978 | 28.0348 | 29.2119 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981
95% | 4.5527 | 5.8902 | 12.7948 | 17.7778 | 20.4016 | 22.7512 | 24.2461 | 25.9518 | 27.3148 | 28.2057 | 30.3188 | 31.7817 | 32.5547 | 33.9824 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 |  | 15.3672 | 17.7841 | 27.0157 | 33.5849 | 37.5267 | 40.6824 | 43.2465 | 45.7131 | 47.8479 | 48.9233 | 50.5032 | 52.3099 | 54.1552 | 56.473 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398
90% | 5.8733 | 8.8805 | 24.4037 | 35.6069 | 41.5058 | 46.7884 | 50.1493 | 53.9842 | 57.0486 | 59.0515 | 63.8024 | 67.0914 | 68.8292 | 72.0391 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 |  | 46.1782 | 54.9112 | 88.2676 | 112.004 | 126.2467 | 137.6492 | 146.914 | 155.8264 | 163.5403 | 167.426 | 173.1346 | 179.6625 | 186.3301 | 194.7051 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303
85% | 0.77742 | 3.6064 | 28.4862 | 46.6535 | 56.2193 | 64.7857 | 70.2358 | 76.4546 | 81.4238 | 84.6718 | 92.376 | 97.7095 | 100.5276 | 105.7328 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 |  | 37.7756 | 48.2395 | 88.2071 | 116.6479 | 133.7136 | 147.376 | 158.4771 | 169.1559 | 178.3987 | 183.0546 | 189.8946 | 197.7163 | 205.7054 | 215.7403 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282
80% |  |  | 61.8114 | 131.7556 | 168.5839 | 201.5645 | 222.5473 | 246.4899 | 265.6212 | 278.1261 | 307.7873 | 328.321 | 339.1708 | 359.2107 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 |  | 20.6502 | 32.5932 | 78.2104 | 110.6714 | 130.1493 | 145.743 | 158.4133 | 170.6016 | 181.1509 | 186.4648 | 194.2718 | 203.199 | 212.3175 | 223.7708 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831
75% |  |  | 17.662 | 117.7088 | 173.4865 | 223.4368 | 255.2159 | 291.4777 | 320.4528 | 339.3918 | 384.3147 | 415.4137 | 431.846 | 462.1971 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 |  | 1.1976 | 6.8612 | 45.3269 | 73.1689 | 89.8753 | 103.2501 | 114.1175 | 124.5715 | 133.6197 | 138.1775 | 144.8736 | 152.5306 | 160.3515 | 170.1752 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296
70% |  |  |  | 42.6654 | 122.7534 | 199.0556 | 247.6001 | 302.9923 | 347.2535 | 376.184 | 444.8066 | 492.3121 | 517.4136 | 563.7768 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 |  |  |  | 21.9935 | 51.7601 | 69.6212 | 83.9206 | 95.5392 | 106.7158 | 116.3895 | 121.2623 | 128.4213 | 136.6075 | 144.9691 | 155.4718 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337
65% |  |  |  |  | 11.0262 | 79.8024 | 154.0865 | 255.0147 | 335.835 | 388.6616 | 513.9651 | 600.7094 | 646.5443 | 731.2026 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 |  |  |  | 2.3884 | 56.3791 | 103.4956 | 141.2163 | 171.8654 | 201.3485 | 226.867 | 239.7213 | 258.606 | 280.2009 | 302.2582 | 329.9635 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474
60% | [7 empty] | 22.5626 | 80.9935 | 137.7814 | 328.1238 | 495.0609 | 584.1339 | 748.6544 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 |  |  |  |  | 0.84409 | 20.6098 | 53.9337 | 88.0733 | 120.9929 | 149.4858 | 163.8383 | 184.9243 | 209.0361 | 233.6644 | 264.599 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938
55% | [11 empty] | 10.3571 | 31.8625 | 101.3744 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | [7 empty] | 6.0197 | 26.2071 | 54.4783 | 72.3303 | 102.7689 | 141.787 | 181.853 | 232.1783 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414
50% | [42 empty] | 3.2543 | 18.0873 | 52.963 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 15.0139 | 23.0979 | 154.5779 | 404.9789 | 608.5733 | 854.3803 | 1041.2939 | 1293.3017 | 1535.2447 | 1711.9817 | 2186.8407 | 2561.0983 | 2775.75 | 3202.0092 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | E @ R (MWh) | 143.1036 | 185.424 | 388.2843 | 600.3605 | 761.5938 | 908.1742 | 1040.3576 | 1181.9879 | 1315.3714 | 1386.1709 | 1494.397 | 1625.6198 | 1771.3742 | 1970.6952 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317
Option 8 Summer POE50 W E @ R (MWh) N 1 | 10.5097 | 16.1685 | 108.2045 | 283.4852 | 426.0013 | 598.0662 | 728.9057 | 905.3112 | 1074.6713 | 1198.3872 | 1530.7885 | 1792.7688 | 1943.025 | 2241.4064 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 42.9311 | 55.6272 | 116.4853 | 180.1082 | 228.4781 | 272.4523 | 312.1073 | 354.5964 | 394.6114 | 415.8513 | 448.3191 | 487.6859 | 531.4123 | 591.2086 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 40.2458 | 41.8786 | 47.6412 | 52.495 | 55.1156 | 57.0096 | 59.193 | 60.8279 | 62.6289 | 63.5754 | 64.395 | 66.4184 | 65.2047 | 68.5022 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 |  | 42.8352 | 44.5416 | 50.2595 | 55.2967 | 57.9264 | 60.0588 | 62.0878 | 63.8171 | 65.6172 | 66.4091 | 67.4875 | 69.4836 | 68.8365 | 71.4426 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473
98% | 119.5239 | 124.3732 | 141.4873 | 155.9024 | 163.6851 | 169.3098 | 175.7944 | 180.6496 | 185.9984 | 188.8095 | 191.2433 | 197.2527 | 193.6481 | 203.4413 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 |  | 127.2142 | 132.2818 | 149.263 | 164.2229 | 172.0327 | 178.3657 | 184.3914 | 189.5271 | 194.8733 | 197.2251 | 200.4276 | 206.3557 | 204.434 | 212.1737 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426
97% | 52.5824 | 54.7158 | 62.2448 | 68.5865 | 72.0104 | 74.4849 | 77.3376 | 79.4736 | 81.8267 | 83.0634 | 84.1341 | 86.7778 | 85.1921 | 89.5004 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 |  | 55.9656 | 58.195 | 65.6656 | 72.247 | 75.6827 | 78.4688 | 81.1197 | 83.3791 | 85.7311 | 86.7657 | 88.1746 | 90.7826 | 89.9371 | 93.3421 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081
95% | 129.4337 | 134.685 | 153.2181 | 168.8283 | 177.2563 | 183.3473 | 190.3695 | 195.6273 | 201.4195 | 204.4637 | 207.0994 | 213.607 | 209.7035 | 220.3086 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 |  | 137.7615 | 143.2493 | 161.6385 | 177.8387 | 186.2959 | 193.154 | 199.6793 | 205.2408 | 211.0303 | 213.5771 | 217.0451 | 223.4648 | 221.3837 | 229.7651 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045
90% | 1321.9761 | 1375.6113 | 1564.8992 | 1724.3348 | 1810.4145 | 1872.6256 | 1944.3472 | 1998.0481 | 2057.2069 | 2088.2986 | 2115.2182 | 2181.6839 | 2141.8155 | 2250.1315 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 |  | 1407.0332 | 1463.083 | 1650.9011 | 1816.3625 | 1902.7414 | 1972.7865 | 2039.433 | 2096.2356 | 2155.3665 | 2181.3785 | 2216.7992 | 2282.3666 | 2261.1117 | 2346.7152 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425
85% | 3114.4974 | 3240.8588 | 3686.8101 | 4062.4308 | 4265.2295 | 4411.7952 | 4580.767 | 4707.283 | 4846.6578 | 4919.908 | 4983.329 | 5139.9182 | 5045.9907 | 5301.1766 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 |  | 3314.8869 | 3446.937 | 3889.4254 | 4279.2427 | 4482.7462 | 4647.7683 | 4804.7835 | 4938.6071 | 5077.916 | 5139.1988 | 5222.6477 | 5377.1207 | 5327.0453 | 5528.7223 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701
80% | 5639.4649 | 5868.2694 | 6675.7596 | 7355.9015 | 7723.112 | 7988.5007 | 8294.4602 | 8523.5446 | 8775.9126 | 8908.5477 | 9023.385 | 9306.9232 | 9136.8474 | 9598.9162 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 |  | 6002.313 | 6241.4181 | 7042.6381 | 7748.4859 | 8116.9725 | 8415.7805 | 8700.09 | 8942.4065 | 9194.6551 | 9305.6206 | 9456.7228 | 9736.4294 | 9645.7571 | 10010.9365 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901
75% | 6593.364 | 6860.8701 | 7804.945 | 8600.1308 | 9029.4539 | 9339.7323 | 9697.4441 | 9965.2774 | 10260.3327 | 10415.4026 | 10549.6644 | 10881.1622 | 10682.3185 | 11222.545 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 |  | 7017.5868 | 7297.1358 | 8233.8799 | 9059.1197 | 9489.9348 | 9839.2853 | 10171.685 | 10454.9886 | 10749.9043 | 10879.6393 | 11056.2999 | 11383.3181 | 11277.3089 | 11704.2572 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761
70% | 7731.9758 | 8045.6776 | 9152.7853 | 10085.2922 | 10588.7553 | 10952.6159 | 11372.1011 | 11686.1867 | 12032.1953 | 12214.0443 | 12371.4918 | 12760.2362 | 12527.0541 | 13160.5726 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 |  | 8229.4578 | 8557.2822 | 9655.7932 | 10623.5442 | 11128.757 | 11538.437 | 11928.2389 | 12260.4664 | 12606.3113 | 12758.4503 | 12965.6185 | 13349.1096 | 13224.7936 | 13725.472 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623
65% | 8472.8486 | 8816.6091 | 10029.7992 | 11051.6583 | 11603.3629 | 12002.0884 | 12461.7684 | 12805.9495 | 13185.1124 | 13384.3861 | 13556.92 | 13982.9137 | 13727.3882 | 14421.61 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 |  | 9017.9991 | 9377.2354 | 10581.005 | 11641.4852 | 12195.1072 | 12644.0425 | 13071.195 | 13435.2562 | 13814.2398 | 13980.9566 | 14207.9756 | 14628.2126 | 14491.9847 | 15040.6377 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285
60% | 9218.7775 | 9592.8018 | 10912.7982 | 12024.6193 | 12624.8946 | 13058.7229 | 13558.872 | 13933.354 | 14345.8974 | 14562.7147 | 14750.4381 | 15213.9352 | 14935.9139 | 15691.2533 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 |  | 9811.9216 | 10202.7843 | 11512.5308 | 12666.3731 | 13268.7346 | 13757.193 | 14221.951 | 14618.0633 | 15030.4117 | 15211.8059 | 15458.811 | 15916.0446 | 15767.8236 | 16364.7787 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459
55% | 9241.0239 | 9615.9508 | 10939.1325 | 12053.6366 | 12655.3606 | 13090.2357 | 13591.5918 | 13966.9774 | 14380.5164 | 14597.8569 | 14786.0333 | 15250.6489 | 14971.9567 | 15729.1189 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 |  | 9835.5994 | 10227.4053 | 11540.3124 | 12696.9392 | 13300.7542 | 13790.3914 | 14256.2709 | 14653.3391 | 15066.6825 | 15248.5144 | 15496.1157 | 15954.4526 | 15805.8739 | 16404.2696 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816
50% | 10886.5841 | 11328.2747 | 12887.077 | 14200.0421 | 14908.9158 | 15421.2297 | 16011.8628 | 16454.0938 | 16941.2722 | 17197.3148 | 17419 | 17966.3503 | 17638.031 | 18530.0219 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 |  | 11587.0364 | 12048.6116 | 13595.3097 | 14957.8983 | 15669.2355 | 16246.0629 | 16794.9022 | 17262.6768 | 17749.6247 | 17963.8357 | 18255.5276 | 18795.4812 | 18620.4449 | 19325.3975 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353
45% | 13615.4771 | 14167.8844 | 16117.4248 | 17759.5053 | 18646.0692 | 19286.8027 | 20025.4872 | 20578.5704 | 21187.8676 | 21508.0913 | 21785.3454 | 22469.8976 | 22059.2799 | 23174.8624 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 |  | 14491.5087 | 15068.7849 | 17003.1872 | 18707.33 | 19596.975 | 20318.3933 | 21004.8077 | 21589.8373 | 22198.8464 | 22466.7527 | 22831.5617 | 23506.8631 | 23287.9512 | 24169.6113 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796
40% | 14417.022 | 15001.9495 | 17066.2597 | 18805.0097 | 19743.7657 | 20422.2192 | 21204.3902 | 21790.0335 | 22435.2001 | 22774.2754 | 23067.8515 | 23792.7034 | 23357.9126 | 24539.1695 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 |  | 15344.6257 | 15955.8863 | 18004.167 | 19808.633 | 20750.6515 | 21514.5397 | 22241.3634 | 22860.8338 | 23505.6953 | 23789.3733 | 24175.6587 | 24890.7152 | 24658.9159 | 25592.4795 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166
35% | 5895.2987 | 6134.4828 | 6978.6047 | 7689.6011 | 8073.4701 | 8350.8981 | 8670.7375 | 8910.2143 | 9174.0309 | 9312.683 | 9432.7299 | 9729.1308 | 9551.3395 | 10034.37 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 |  | 6274.6073 | 6524.5593 | 7362.1266 | 8099.9951 | 8485.1981 | 8797.5615 | 9094.7687 | 9348.0778 | 9611.7696 | 9727.7691 | 9885.726 | 10178.1214 | 10083.3358 | 10465.0815 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005
30% | 1818.4755 | 1892.2547 | 2152.6342 | 2371.9496 | 2490.3586 | 2575.9346 | 2674.5928 | 2748.4623 | 2829.8397 | 2872.6086 | 2909.6385 | 3001.0669 | 2946.2251 | 3095.2216 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 |  | 1935.4778 | 2012.5785 | 2270.9361 | 2498.5405 | 2617.361 | 2713.7132 | 2805.3903 | 2883.5266 | 2964.8655 | 3000.6469 | 3049.3706 | 3139.5635 | 3110.3257 | 3228.0797 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706
25% | 1338.4923 | 1392.7977 | 1584.4505 | 1745.878 | 1833.0331 | 1896.0215 | 1968.6391 | 2023.0109 | 2082.9089 | 2114.389 | 2141.645 | 2208.941 | 2168.5746 | 2278.2438 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 |  | 1424.6121 | 1481.3622 | 1671.5269 | 1839.0555 | 1926.5135 | 1997.4338 | 2064.9129 | 2122.4252 | 2182.2949 | 2208.6319 | 2244.495 | 2310.8817 | 2289.3612 | 2376.0342 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079
20% | 1064.7941 | 1107.9949 | 1260.4581 | 1388.8765 | 1458.2099 | 1508.3183 | 1566.0869 | 1609.3406 | 1656.9905 | 1682.0335 | 1703.7161 | 1757.2512 | 1725.139 | 1812.3828 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 |  | 1133.3039 | 1178.4496 | 1329.7289 | 1463.0008 | 1532.5752 | 1588.9935 | 1642.6743 | 1688.4264 | 1736.0538 | 1757.0053 | 1785.5351 | 1838.3468 | 1821.2269 | 1890.1768 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883
15% | 835.2516 | 869.1394 | 988.7354 | 1089.4701 | 1143.857 | 1183.1633 | 1228.4784 | 1262.4077 | 1299.7855 | 1319.4299 | 1336.4382 | 1378.4326 | 1353.2429 | 1421.6792 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 |  | 888.9924 | 924.4058 | 1043.0732 | 1147.6151 | 1202.191 | 1246.447 | 1288.5556 | 1324.4446 | 1361.8048 | 1378.2397 | 1400.6191 | 1442.046 | 1428.6167 | 1482.7028 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932
10% | 586.4963 | 610.2916 | 694.2694 | 765.0032 | 803.1926 | 830.7926 | 862.612 | 886.4364 | 912.6823 | 926.4762 | 938.4191 | 967.9067 | 950.219 | 998.2735 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 |  | 624.2319 | 649.0985 | 732.4243 | 805.8314 | 844.1535 | 875.2291 | 904.7969 | 929.9974 | 956.2309 | 967.7712 | 983.4856 | 1012.5747 | 1003.1449 | 1041.123 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515
5% | 60.672 | 63.1336 | 71.821 | 79.1383 | 83.0889 | 85.9441 | 89.2357 | 91.7003 | 94.4154 | 95.8424 | 97.0778 | 100.1283 | 98.2985 | 103.2697 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 |  | 64.5757 | 67.1481 | 75.768 | 83.3619 | 87.3262 | 90.5409 | 93.5997 | 96.2066 | 98.9204 | 100.1143 | 101.7399 | 104.7491 | 103.7736 | 107.7024 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102194.2775 | 106340.5049 | 120973.2554 | 133298.2902 | 139952.6116 | 144761.7923 | 150306.169 | 154457.4695 | 159030.6983 | 161434.2148 | 163515.2133 | 168653.2865 | 165571.2953 | 173944.571 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | E @ R (MWh) | 108769.5462 | 113102.4335 | 127621.5603 | 140412.4195 | 147089.8663 | 152504.6467 | 157656.6971 | 162047.7795 | 166618.8453 | 168629.6814 | 171367.8442 | 176436.4835 | 174793.387 | 181410.9014 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837
Option 1 Winter POE50 W E @ R (MWh) N 2 | 71535.9943 | 74438.3534 | 84681.2788 | 93308.8031 | 97966.8281 | 101333.2546 | 105214.3183 | 108120.2286 | 111321.4888 | 113003.9503 | 114460.6493 | 118057.3006 | 115899.9067 | 121761.1997 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 32630.8639 | 33930.7301 | 38286.4681 | 42123.7258 | 44126.9599 | 45751.394 | 47297.0091 | 48614.3339 | 49985.6536 | 50588.9044 | 51410.3533 | 52930.9451 | 52438.0161 | 54423.2704 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43.3961 | 44.6487 | 49.4328 | 52.8371 | 54.8798 | 56.5152 | 57.844 | 59.1223 | 60.2286 | 60.7859 | 61.6047 | 62.5409 | 63.4972 | 64.6984 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884
98% | 19.0952 | 19.5527 | 21.9141 | 23.6184 | 24.5158 | 25.3194 | 25.8306 | 26.414 | 26.8802 | 27.1849 | 27.9076 | 28.4079 | 28.6723 | 29.1606 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 |  | 21.48 | 22.1 | 24.468 | 26.153 | 27.1641 | 27.9736 | 28.6313 | 29.264 | 29.8117 | 30.0875 | 30.4928 | 30.9562 | 31.4295 | 32.0241 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181
97% | 18.9014 | 19.3542 | 21.6917 | 23.3786 | 24.2669 | 25.0623 | 25.5684 | 26.1459 | 26.6073 | 26.9089 | 27.6243 | 28.1195 | 28.3812 | 28.8646 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 |  | 42.5239 | 43.7512 | 48.4391 | 51.775 | 53.7767 | 55.3792 | 56.6813 | 57.9339 | 59.018 | 59.5641 | 60.3664 | 61.2838 | 62.2209 | 63.3979 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842
95% | 55.8317 | 57.1693 | 64.0738 | 69.0569 | 71.6806 | 74.0303 | 75.5251 | 77.2309 | 78.5939 | 79.4847 | 81.5979 | 83.0608 | 83.8338 | 85.2615 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 |  | 83.7393 | 86.1562 | 95.3878 | 101.957 | 105.8988 | 109.0545 | 111.6186 | 114.0852 | 116.22 | 117.2954 | 118.8753 | 120.682 | 122.5273 | 124.8451 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119
90% | 125.5245 | 128.5317 | 144.0549 | 155.2581 | 161.157 | 166.4396 | 169.8005 | 173.6354 | 176.6997 | 178.7027 | 183.4536 | 186.7426 | 188.4804 | 191.6903 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 |  | 302.5736 | 311.3066 | 344.663 | 368.3993 | 382.6421 | 394.0446 | 403.3094 | 412.2218 | 419.9357 | 423.8214 | 429.53 | 436.0579 | 442.7255 | 451.1005 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257
85% | 203.5532 | 208.4297 | 233.6025 | 251.7698 | 261.3356 | 269.902 | 275.3521 | 281.5709 | 286.5401 | 289.7881 | 297.4924 | 302.8258 | 305.6439 | 310.8491 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 |  | 362.5431 | 373.007 | 412.9746 | 441.4154 | 458.4811 | 472.1435 | 483.2446 | 493.9234 | 503.1662 | 507.822 | 514.6621 | 522.4838 | 530.4729 | 540.5078 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957
80% | 783.6798 | 802.4544 | 899.3697 | 969.3138 | 1006.1421 | 1039.1228 | 1060.1055 | 1084.0481 | 1103.1795 | 1115.6843 | 1145.3456 | 1165.8792 | 1176.729 | 1196.7689 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 |  | 413.7898 | 425.7328 | 471.35 | 503.811 | 523.2889 | 538.8826 | 551.5529 | 563.7412 | 574.2905 | 579.6044 | 587.4113 | 596.3386 | 605.4571 | 616.9104 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227
75% | 1186.9089 | 1215.3438 | 1362.1252 | 1468.0578 | 1523.8356 | 1573.7859 | 1605.5649 | 1641.8267 | 1670.8018 | 1689.7408 | 1734.6637 | 1765.7627 | 1782.195 | 1812.5461 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 |  | 354.9106 | 365.1542 | 404.2804 | 432.1225 | 448.8288 | 462.2036 | 473.071 | 483.525 | 492.5733 | 497.1311 | 503.8271 | 511.4841 | 519.3051 | 529.1287 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831
70% | 1813.0773 | 1856.5133 | 2080.731 | 2242.5498 | 2327.7537 | 2404.0559 | 2452.6004 | 2507.9926 | 2552.2538 | 2581.1844 | 2649.8069 | 2697.3124 | 2722.4139 | 2768.7771 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 |  | 379.4436 | 390.3953 | 432.2261 | 461.9927 | 479.8539 | 494.1532 | 505.7718 | 516.9484 | 526.6221 | 531.495 | 538.6539 | 546.8402 | 555.2017 | 565.7044 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663
65% | 3310.6471 | 3389.9605 | 3799.3781 | 4094.8563 | 4250.4372 | 4389.7637 | 4478.4051 | 4579.5502 | 4660.3705 | 4713.1971 | 4838.5006 | 4925.2449 | 4971.0798 | 5055.7381 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 |  | 1000.946 | 1029.8359 | 1140.1826 | 1218.7049 | 1265.8214 | 1303.542 | 1334.1911 | 1363.6743 | 1389.1928 | 1402.047 | 1420.9318 | 1442.5266 | 1464.5839 | 1492.2892 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731
60% | 6433.7346 | 6587.868 | 7383.5083 | 7957.7247 | 8260.0724 | 8530.8319 | 8703.0928 | 8899.6529 | 9056.7147 | 9159.3751 | 9402.8833 | 9571.4576 | 9660.5305 | 9825.051 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 |  | 1117.614 | 1149.8713 | 1273.0797 | 1360.7544 | 1413.3626 | 1455.4799 | 1489.7014 | 1522.621 | 1551.1139 | 1565.4665 | 1586.5524 | 1610.6642 | 1635.2925 | 1666.2271 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219
55% | 7457.3163 | 7635.9717 | 8558.1952 | 9223.7673 | 9574.2172 | 9888.0535 | 10087.7205 | 10315.5525 | 10497.6022 | 10616.5955 | 10898.8448 | 11094.2386 | 11197.4827 | 11388.1777 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 |  | 1818.1672 | 1870.6442 | 2071.0832 | 2213.715 | 2299.2997 | 2367.8174 | 2423.4899 | 2477.0445 | 2523.3976 | 2546.7466 | 2581.0498 | 2620.2757 | 2660.3417 | 2710.667 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301
50% | 8773.1422 | 8983.321 | 10068.2687 | 10851.2793 | 11263.5653 | 11632.7773 | 11867.6751 | 12135.7075 | 12349.8795 | 12489.8688 | 12821.9204 | 13051.7909 | 13173.2522 | 13397.595 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 |  | 3171.2979 | 3262.8298 | 3612.4412 | 3861.2234 | 4010.5027 | 4130.0131 | 4227.1187 | 4320.5301 | 4401.3804 | 4442.1065 | 4501.9391 | 4570.358 | 4640.2422 | 4728.021 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104
45% | 15608.1674 | 15982.0933 | 17912.3076 | 19305.3503 | 20038.8422 | 20695.7017 | 21113.6049 | 21590.4575 | 21971.4876 | 22220.5406 | 22811.2886 | 23220.2479 | 23436.3378 | 23835.4627 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 |  | 6318.6081 | 6500.9794 | 7197.5577 | 7693.2404 | 7990.6698 | 8228.7865 | 8422.2633 | 8608.3795 | 8769.4686 | 8850.6128 | 8969.8254 | 9106.1456 | 9245.3853 | 9420.279 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528
40% | 17870.5156 | 18298.6407 | 20508.6327 | 22103.592 | 22943.401 | 23695.47 | 24173.9467 | 24719.9173 | 25156.1764 | 25441.3288 | 26117.7036 | 26585.9401 | 26833.3515 | 27290.3281 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 |  | 10760.1697 | 11070.7361 | 12256.9625 | 13101.0774 | 13607.5797 | 14013.0768 | 14342.5548 | 14659.4983 | 14933.8224 | 15072.0056 | 15275.0167 | 15507.161 | 15744.277 | 16042.1094 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359
35% | 10839.207 | 11098.8826 | 12439.3342 | 13406.743 | 13916.1219 | 14372.2829 | 14662.4988 | 14993.6526 | 15258.2617 | 15431.2184 | 15841.4678 | 16125.4726 | 16275.5378 | 16552.713 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 |  | 13027.0181 | 13403.0116 | 14839.1407 | 15861.0855 | 16474.2928 | 16965.2161 | 17364.1053 | 17747.8195 | 18079.9354 | 18247.2297 | 18493.0093 | 18774.0595 | 19061.1288 | 19421.7056 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603
30% | 4492.2249 | 4599.8454 | 5155.3852 | 5556.3202 | 5767.4283 | 5956.4807 | 6076.7584 | 6214.0025 | 6323.6677 | 6395.3483 | 6565.3729 | 6683.0765 | 6745.2698 | 6860.1429 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 |  | 19901.1621 | 20475.5611 | 22669.5121 | 24230.7204 | 25167.5072 | 25917.4827 | 26526.8592 | 27113.053 | 27620.4211 | 27875.9939 | 28251.4673 | 28680.8231 | 29119.3742 | 29670.2214 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383
25% | 2681.5709 | 2745.8134 | 3077.4351 | 3316.7677 | 3442.7857 | 3555.6379 | 3627.436 | 3709.3619 | 3774.825 | 3817.6138 | 3919.1076 | 3989.3691 | 4026.4946 | 4095.0665 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 |  | 16923.4022 | 17411.8554 | 19277.5311 | 20605.1398 | 21401.7576 | 22039.5161 | 22557.7132 | 23056.1964 | 23487.6483 | 23704.9803 | 24024.2726 | 24389.385 | 24762.3168 | 25230.7422 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862
20% | 2852.6525 | 2920.9937 | 3273.7725 | 3528.3742 | 3662.4321 | 3782.4841 | 3858.8629 | 3946.0156 | 4015.6552 | 4061.1738 | 4169.1428 | 4243.8869 | 4283.381 | 4356.3277 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 |  | 4489.5373 | 4619.117 | 5114.0541 | 5466.2498 | 5677.5811 | 5846.7694 | 5984.2397 | 6116.4802 | 6230.9382 | 6288.5933 | 6373.297 | 6470.1561 | 6569.0896 | 6693.3562 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191
15% | 2954.9137 | 3025.7048 | 3391.1299 | 3654.8586 | 3793.7221 | 3918.0777 | 3997.1945 | 4087.4715 | 4159.6075 | 4206.7578 | 4318.5973 | 4396.0208 | 4436.9307 | 4512.4923 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 |  | 2782.0412 | 2862.3381 | 3169.0368 | 3387.2827 | 3518.2388 | 3623.08 | 3708.2666 | 3790.2123 | 3861.1387 | 3896.866 | 3949.3545 | 4009.3754 | 4070.6817 | 4147.6863 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708
10% | 1970.104 | 2017.3019 | 2260.9387 | 2436.7722 | 2529.3555 | 2612.266 | 2665.0149 | 2725.2045 | 2773.2991 | 2804.7352 | 2879.301 | 2930.9209 | 2958.1963 | 3008.5749 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 |  | 795.9593 | 818.9327 | 906.6811 | 969.1226 | 1006.59 | 1036.5857 | 1060.9581 | 1084.4033 | 1104.6958 | 1114.9176 | 1129.9349 | 1147.1072 | 1164.6473 | 1186.6788 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649
5% | 157.0267 | 160.7886 | 180.2077 | 194.2224 | 201.6018 | 208.2101 | 212.4145 | 217.2119 | 221.0452 | 223.5509 | 229.4941 | 233.6085 | 235.7824 | 239.7979 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 89607.7949 | 91754.5348 | 102836.0568 | 110833.6316 | 115044.6699 | 118815.7555 | 121214.9726 | 123952.623 | 126140.1488 | 127569.9829 | 130961.5169 | 133309.3862 | 134549.9768 | 136841.3859 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | E @ R (MWh) | 84110.3229 | 86537.9646 | 95810.4847 | 102408.7793 | 106368.0177 | 109537.7157 | 112113.1862 | 114590.6774 | 116735.0192 | 117815.1726 | 119402.0743 | 121216.7049 | 123070.1983 | 125398.3005 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805
Option 1 Summer POE50 W E @ R (MWh) N 2 | 62725.4564 | 64228.1743 | 71985.2398 | 77583.5421 | 80531.2689 | 83171.0289 | 84850.4808 | 86766.8361 | 88298.1041 | 89298.9881 | 91673.0619 | 93316.5703 | 94184.9837 | 95788.9701 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 25233.0969 | 25961.3894 | 28743.1454 | 30722.6338 | 31910.4053 | 32861.3147 | 33633.9559 | 34377.2032 | 35020.5057 | 35344.5518 | 35820.6223 | 36365.0115 | 36921.0595 | 37619.4901 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041
Option 2 - 1B New PHS ZSS + Three new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 40.2458 | 41.8786 | 47.6412 | 52.495 | 42.2521 | 44.1461 | 46.3295 | 47.9644 | 49.7654 | 50.7119 | 51.5315 | 53.5549 | 52.3412 | 55.6387 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 | 59.939 |  | 42.8352 | 44.5416 | 50.2595 | 55.2967 | 45.0629 | 47.1953 | 49.2243 | 50.9536 | 52.7537 | 53.5456 | 54.624 | 56.6201 | 55.973 | 58.5791 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838 | 60.0838
98% | 119.5239 | 124.3732 | 141.4873 | 155.9024 | 125.4825 | 131.1072 | 137.5917 | 142.447 | 147.7957 | 150.6068 | 153.0407 | 159.0501 | 155.4454 | 165.2386 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 | 178.0098 |  | 127.2142 | 132.2818 | 149.263 | 164.2229 | 133.83 | 140.163 | 146.1887 | 151.3244 | 156.6706 | 159.0225 | 162.2249 | 168.1531 | 166.2314 | 173.9711 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399 | 178.4399
97% | 52.5824 | 54.7158 | 62.2448 | 68.5865 | 55.2038 | 57.6783 | 60.531 | 62.667 | 65.0201 | 66.2568 | 67.3275 | 69.9713 | 68.3855 | 72.6938 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 | 78.3123 |  | 55.9656 | 58.195 | 65.6656 | 72.247 | 58.8762 | 61.6622 | 64.3131 | 66.5725 | 68.9245 | 69.9591 | 71.368 | 73.976 | 73.1306 | 76.5355 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015 | 78.5015
95% | 129.4337 | 134.685 | 153.2181 | 168.8283 | 135.8863 | 141.9773 | 148.9995 | 154.2573 | 160.0495 | 163.0937 | 165.7294 | 172.237 | 168.3335 | 178.9386 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 | 192.7687 |  | 137.7615 | 143.2493 | 161.6385 | 177.8387 | 144.9259 | 151.784 | 158.3093 | 163.8708 | 169.6602 | 172.2071 | 175.6751 | 182.0947 | 180.0137 | 188.395 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344 | 193.2344
90% | 1321.9761 | 1375.6113 | 1564.8992 | 1724.3348 | 1387.8799 | 1450.091 | 1521.8126 | 1575.5135 | 1634.6723 | 1665.764 | 1692.6836 | 1759.1493 | 1719.2809 | 1827.5969 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 | 1968.8509 |  | 1407.0332 | 1463.083 | 1650.9011 | 1816.3625 | 1480.2068 | 1550.2519 | 1616.8984 | 1673.701 | 1732.8319 | 1758.8439 | 1794.2646 | 1859.832 | 1838.5771 | 1924.1807 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079 | 1973.6079
85% | 3114.4974 | 3240.8588 | 3686.8101 | 4062.4308 | 3269.763 | 3416.3287 | 3585.3005 | 3711.8165 | 3851.1913 | 3924.4415 | 3987.8625 | 4144.4517 | 4050.5242 | 4305.7101 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 | 4638.4963 |  | 3314.8869 | 3446.937 | 3889.4254 | 4279.2427 | 3487.2797 | 3652.3018 | 3809.317 | 3943.1406 | 4082.4495 | 4143.7323 | 4227.1812 | 4381.6542 | 4331.5788 | 4533.2558 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036 | 4649.7036
80% | 5639.4649 | 5868.2694 | 6675.7596 | 7355.9015 | 5920.6065 | 6185.9952 | 6491.9548 | 6721.0392 | 6973.4072 | 7106.0423 | 7220.8796 | 7504.4178 | 7334.3419 | 7796.4108 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 | 8398.9914 |  | 6002.313 | 6241.4181 | 7042.6381 | 7748.4859 | 6314.4671 | 6613.2751 | 6897.5846 | 7139.9011 | 7392.1497 | 7503.1152 | 7654.2173 | 7933.9239 | 7843.2517 | 8208.431 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846 | 8419.2846
75% | 6593.364 | 6860.8701 | 7804.945 | 8600.1308 | 6922.0599 | 7232.3383 | 7590.0501 | 7857.8834 | 8152.9387 | 8308.0087 | 8442.2704 | 8773.7683 | 8574.9246 | 9115.151 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 | 9819.6564 |  | 7017.5868 | 7297.1358 | 8233.8799 | 9059.1197 | 7382.5409 | 7731.8913 | 8064.291 | 8347.5946 | 8642.5103 | 8772.2453 | 8948.9059 | 9275.9241 | 9169.9149 | 9596.8633 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822 | 9843.3822
70% | 7731.9758 | 8045.6776 | 9152.7853 | 10085.2922 | 8117.4343 | 8481.2949 | 8900.7801 | 9214.8657 | 9560.8743 | 9742.7233 | 9900.1708 | 10288.9152 | 10055.7331 | 10689.2516 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 | 11515.4184 |  | 8229.4578 | 8557.2822 | 9655.7932 | 10623.5442 | 8657.436 | 9067.116 | 9456.9179 | 9789.1453 | 10134.9902 | 10287.1293 | 10494.2975 | 10877.7886 | 10753.4726 | 11254.1509 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413 | 11543.2413
65% | 8472.8486 | 8816.6091 | 10029.7992 | 11051.6583 | 8895.2416 | 9293.967 | 9753.647 | 10097.8281 | 10476.991 | 10676.2647 | 10848.7987 | 11274.7923 | 11019.2668 | 11713.4887 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 | 12618.8182 |  | 9017.9991 | 9377.2354 | 10581.005 | 11641.4852 | 9486.9858 | 9935.9211 | 10363.0736 | 10727.1349 | 11106.1184 | 11272.8353 | 11499.8542 | 11920.0912 | 11783.8633 | 12332.5163 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072 | 12649.3072
60% | 9218.7775 | 9592.8018 | 10912.7982 | 12024.6193 | 9678.3569 | 10112.1851 | 10612.3342 | 10986.8162 | 11399.3597 | 11616.1769 | 11803.9004 | 12267.3975 | 11989.3761 | 12744.7155 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 | 13729.7481 |  | 9811.9216 | 10202.7843 | 11512.5308 | 12666.3731 | 10322.1969 | 10810.6553 | 11275.4133 | 11671.5256 | 12083.8739 | 12265.2681 | 12512.2733 | 12969.5069 | 12821.2858 | 13418.2409 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212 | 13762.9212
55% | 9241.0239 | 9615.9508 | 10939.1325 | 12053.6366 | 9701.7123 | 10136.5875 | 10637.9435 | 11013.3292 | 11426.8682 | 11644.2086 | 11832.3851 | 12297.0007 | 12018.3085 | 12775.4706 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 | 13762.8803 |  | 9835.5994 | 10227.4053 | 11540.3124 | 12696.9392 | 10347.106 | 10836.7432 | 11302.6227 | 11699.6909 | 12113.0343 | 12294.8662 | 12542.4674 | 13000.8044 | 12852.2257 | 13450.6213 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334 | 13796.1334
50% | 10886.5841 | 11328.2747 | 12887.077 | 14200.0421 | 11429.3079 | 11941.6218 | 12532.2549 | 12974.4859 | 13461.6643 | 13717.7068 | 13939.3921 | 14486.7424 | 14158.4231 | 15050.414 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 | 16213.6528 |  | 11587.0364 | 12048.6116 | 13595.3097 | 14957.8983 | 12189.6276 | 12766.455 | 13315.2942 | 13783.0689 | 14270.0168 | 14484.2278 | 14775.9196 | 15315.8732 | 15140.8369 | 15845.7896 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274 | 16252.8274
45% | 13615.4771 | 14167.8844 | 16117.4248 | 17759.5053 | 14294.243 | 14934.9765 | 15673.661 | 16226.7442 | 16836.0415 | 17156.2651 | 17433.5192 | 18118.0715 | 17707.4537 | 18823.0362 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 | 20277.8591 |  | 14491.5087 | 15068.7849 | 17003.1872 | 18707.33 | 15245.1488 | 15966.5671 | 16652.9815 | 17238.0111 | 17847.0202 | 18114.9265 | 18479.7355 | 19155.037 | 18936.1251 | 19817.7851 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534 | 20326.8534
40% | 14417.022 | 15001.9495 | 17066.2597 | 18805.0097 | 15135.747 | 15814.2005 | 16596.3715 | 17182.0147 | 17827.1814 | 18166.2566 | 18459.8328 | 19184.6847 | 18749.8938 | 19931.1508 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 | 21471.6193 |  | 15344.6257 | 15955.8863 | 18004.167 | 19808.633 | 16142.6327 | 16906.5209 | 17633.3447 | 18252.8151 | 18897.6766 | 19181.3546 | 19567.6399 | 20282.6965 | 20050.8972 | 20984.4607 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979 | 21523.4979
35% | 5895.2987 | 6134.4828 | 6978.6047 | 7689.6011 | 6189.1942 | 6466.6222 | 6786.4616 | 7025.9384 | 7289.755 | 7428.4071 | 7548.454 | 7844.8549 | 7667.0636 | 8150.0941 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 | 8780.0108 |  | 6274.6073 | 6524.5593 | 7362.1266 | 8099.9951 | 6600.9222 | 6913.2856 | 7210.4928 | 7463.8019 | 7727.4938 | 7843.4932 | 8001.4501 | 8293.8455 | 8199.0599 | 8580.8056 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246 | 8801.2246
30% | 1818.4755 | 1892.2547 | 2152.6342 | 2371.9496 | 1909.1311 | 1994.7071 | 2093.3654 | 2167.2349 | 2248.6123 | 2291.3812 | 2328.4111 | 2419.8395 | 2364.9976 | 2513.9942 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 | 2708.2995 |  | 1935.4778 | 2012.5785 | 2270.9361 | 2498.5405 | 2036.1335 | 2132.4857 | 2224.1629 | 2302.2991 | 2383.638 | 2419.4194 | 2468.1431 | 2558.336 | 2529.0982 | 2646.8523 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431 | 2714.8431
25% | 1338.4923 | 1392.7977 | 1584.4505 | 1745.878 | 1405.2196 | 1468.2079 | 1540.8256 | 1595.1973 | 1655.0953 | 1686.5754 | 1713.8314 | 1781.1274 | 1740.761 | 1850.4302 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 | 1993.449 |  | 1424.6121 | 1481.3622 | 1671.5269 | 1839.0555 | 1498.7 | 1569.6202 | 1637.0993 | 1694.6116 | 1754.4813 | 1780.8183 | 1816.6814 | 1883.0681 | 1861.5476 | 1948.2206 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655 | 1998.2655
20% | 1064.7941 | 1107.9949 | 1260.4581 | 1388.8765 | 1117.8768 | 1167.9851 | 1225.7537 | 1269.0074 | 1316.6573 | 1341.7003 | 1363.3829 | 1416.918 | 1384.8058 | 1472.0496 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 | 1585.8236 |  | 1133.3039 | 1178.4496 | 1329.7289 | 1463.0008 | 1192.242 | 1248.6603 | 1302.3412 | 1348.0932 | 1395.7206 | 1416.6721 | 1445.2019 | 1498.0136 | 1480.8937 | 1549.8436 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551 | 1589.6551
15% | 835.2516 | 869.1394 | 988.7354 | 1089.4701 | 876.891 | 916.1972 | 961.5124 | 995.4417 | 1032.8195 | 1052.4639 | 1069.4722 | 1111.4666 | 1086.2769 | 1154.7132 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 | 1243.9604 |  | 888.9924 | 924.4058 | 1043.0732 | 1147.6151 | 935.225 | 979.4809 | 1021.5895 | 1057.4786 | 1094.8387 | 1111.2737 | 1133.6531 | 1175.08 | 1161.6507 | 1215.7368 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966 | 1246.966
10% | 586.4963 | 610.2916 | 694.2694 | 765.0032 | 615.7346 | 643.3346 | 675.154 | 698.9784 | 725.2243 | 739.0182 | 750.9611 | 780.4487 | 762.761 | 810.8155 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 | 873.4831 |  | 624.2319 | 649.0985 | 732.4243 | 805.8314 | 656.6955 | 687.7711 | 717.3389 | 742.5395 | 768.773 | 780.3132 | 796.0276 | 825.1167 | 815.6869 | 853.6651 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935 | 875.5935
5% | 60.672 | 63.1336 | 71.821 | 79.1383 | 63.6967 | 66.5519 | 69.8435 | 72.3081 | 75.0232 | 76.4502 | 77.6856 | 80.7361 | 78.9063 | 83.8775 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 | 90.3603 |  | 64.5757 | 67.1481 | 75.768 | 83.3619 | 67.934 | 71.1487 | 74.2075 | 76.8144 | 79.5282 | 80.7221 | 82.3477 | 85.3569 | 84.3814 | 88.3102 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786 | 90.5786
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102194.2775 | 106340.5049 | 120973.2554 | 133298.2902 | 107288.9208 | 112098.1015 | 117642.4782 | 121793.7787 | 126367.0075 | 128770.524 | 130851.5225 | 135989.5957 | 132907.6045 | 141280.8802 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | 152200.4076 | E @ R (MWh) | 108769.5462 | 113102.4335 | 127621.5603 | 140412.4195 | 114426.1755 | 119840.9559 | 124993.0063 | 129384.0887 | 133955.1545 | 135965.9906 | 138704.1534 | 143772.7927 | 142129.6962 | 148747.2106 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462 | 152568.1462
Option 2 Winter POE50 W E @ R (MWh) N 2 | 71535.9943 | 74438.3534 | 84681.2788 | 93308.8031 | 75102.2446 | 78468.6711 | 82349.7347 | 85255.6451 | 88456.9052 | 90139.3668 | 91596.0657 | 95192.717 | 93035.3231 | 98896.6161 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | 106540.2853 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 32630.8639 | 33930.7301 | 38286.4681 | 42123.7258 | 34327.8527 | 35952.2868 | 37497.9019 | 38815.2266 | 40186.5463 | 40789.7972 | 41611.246 | 43131.8378 | 42638.9089 | 44624.1632 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439 | 45770.4439
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43.3961 | 44.6487 | 49.4328 | 52.8371 | 43.9679 | 45.6033 | 46.9321 | 48.2103 | 49.3167 | 49.874 | 50.6927 | 51.629 | 52.5853 | 53.7864 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765 | 53.9765
98% | 19.0952 | 19.5527 | 21.9141 | 23.6184 | 19.1146 | 19.9182 | 20.4295 | 21.0129 | 21.4791 | 21.7838 | 22.5065 | 23.0068 | 23.2712 | 23.7595 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 | 23.6193 |  | 21.48 | 22.1 | 24.468 | 26.153 | 21.763 | 22.5725 | 23.2302 | 23.8629 | 24.4105 | 24.6864 | 25.0916 | 25.555 | 26.0284 | 26.6229 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717 | 26.717
97% | 18.9014 | 19.3542 | 21.6917 | 23.3786 | 18.9206 | 19.716 | 20.2221 | 20.7996 | 21.261 | 21.5626 | 22.278 | 22.7732 | 23.0349 | 23.5183 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 | 23.3795 |  | 42.5239 | 43.7512 | 48.4391 | 51.775 | 43.0841 | 44.6866 | 45.9887 | 47.2413 | 48.3254 | 48.8715 | 49.6738 | 50.5912 | 51.5283 | 52.7053 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916 | 52.8916
95% | 55.8317 | 57.1693 | 64.0738 | 69.0569 | 55.8885 | 58.2381 | 59.733 | 61.4387 | 62.8017 | 63.6926 | 65.8058 | 67.2686 | 68.0416 | 69.4693 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 | 69.0594 |  | 83.7393 | 86.1562 | 95.3878 | 101.957 | 84.8426 | 87.9983 | 90.5624 | 93.029 | 95.1639 | 96.2393 | 97.8192 | 99.6258 | 101.4711 | 103.7889 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557 | 104.1557
90% | 125.5245 | 128.5317 | 144.0549 | 155.2581 | 125.6521 | 130.9347 | 134.2956 | 138.1305 | 141.1948 | 143.1978 | 147.9487 | 151.2377 | 152.9755 | 156.1854 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 | 155.2638 |  | 302.5736 | 311.3066 | 344.663 | 368.3993 | 306.5602 | 317.9626 | 327.2275 | 336.1399 | 343.8538 | 347.7395 | 353.4481 | 359.976 | 366.6436 | 375.0186 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438 | 376.3438
85% | 203.5532 | 208.4297 | 233.6025 | 251.7698 | 203.7601 | 212.3265 | 217.7766 | 223.9954 | 228.9646 | 232.2126 | 239.9168 | 245.2503 | 248.0684 | 253.2736 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 | 251.7791 |  | 362.5431 | 373.007 | 412.9746 | 441.4154 | 367.3198 | 380.9823 | 392.0834 | 402.7622 | 412.005 | 416.6608 | 423.5009 | 431.3225 | 439.3117 | 449.3466 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344 | 450.9344
80% | 783.6798 | 802.4544 | 899.3697 | 969.3138 | 784.4764 | 817.4571 | 838.4398 | 862.3824 | 881.5138 | 894.0186 | 923.6798 | 944.2135 | 955.0633 | 975.1032 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 | 969.3497 |  | 413.7898 | 425.7328 | 471.35 | 503.811 | 419.2417 | 434.8354 | 447.5057 | 459.694 | 470.2433 | 475.5572 | 483.3642 | 492.2914 | 501.4099 | 512.8632 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755 | 514.6755
75% | 1186.9089 | 1215.3438 | 1362.1252 | 1468.0578 | 1188.1155 | 1238.0658 | 1269.8449 | 1306.1067 | 1335.0818 | 1354.0208 | 1398.9437 | 1430.0426 | 1446.475 | 1476.8261 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 | 1468.1122 |  | 354.9106 | 365.1542 | 404.2804 | 432.1225 | 359.5868 | 372.9616 | 383.829 | 394.283 | 403.3312 | 407.889 | 414.5851 | 422.2421 | 430.063 | 439.8867 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411 | 441.4411
70% | 1813.0773 | 1856.5133 | 2080.731 | 2242.5498 | 1814.9204 | 1891.2226 | 1939.7671 | 1995.1593 | 2039.4205 | 2068.351 | 2136.9736 | 2184.4791 | 2209.5806 | 2255.9438 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 | 2242.6327 |  | 379.4436 | 390.3953 | 432.2261 | 461.9927 | 384.443 | 398.7423 | 410.361 | 421.5376 | 431.2112 | 436.0841 | 443.243 | 451.4293 | 459.7909 | 470.2936 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554 | 471.9554
65% | 3310.6471 | 3389.9605 | 3799.3781 | 4094.8563 | 3314.0126 | 3453.3391 | 3541.9805 | 3643.1256 | 3723.9459 | 3776.7725 | 3902.076 | 3988.8204 | 4034.6552 | 4119.3135 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 | 4095.0078 |  | 1000.946 | 1029.8359 | 1140.1826 | 1218.7049 | 1014.1341 | 1051.8548 | 1082.5039 | 1111.987 | 1137.5055 | 1150.3598 | 1169.2445 | 1190.8394 | 1212.8967 | 1240.602 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859 | 1244.9859
60% | 6433.7346 | 6587.868 | 7383.5083 | 7957.7247 | 6440.2749 | 6711.0344 | 6883.2954 | 7079.8555 | 7236.9173 | 7339.5777 | 7583.0859 | 7751.6601 | 7840.7331 | 8005.2535 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 | 7958.0192 |  | 1117.614 | 1149.8713 | 1273.0797 | 1360.7544 | 1132.3393 | 1174.4566 | 1208.6781 | 1241.5977 | 1270.0906 | 1284.4431 | 1305.529 | 1329.6409 | 1354.2692 | 1385.2038 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986 | 1390.0986
55% | 7457.3163 | 7635.9717 | 8558.1952 | 9223.7673 | 7464.8972 | 7778.7335 | 7978.4005 | 8206.2325 | 8388.2822 | 8507.2755 | 8789.5248 | 8984.9186 | 9088.1627 | 9278.8577 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 | 9224.1085 |  | 1818.1672 | 1870.6442 | 2071.0832 | 2213.715 | 1842.1227 | 1910.6404 | 1966.3129 | 2019.8675 | 2066.2206 | 2089.5697 | 2123.8729 | 2163.0987 | 2203.1647 | 2253.49 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531 | 2261.4531
50% | 8773.1422 | 8983.321 | 10068.2687 | 10851.2793 | 8782.0607 | 9151.2727 | 9386.1705 | 9654.2029 | 9868.3749 | 10008.3642 | 10340.4158 | 10570.2864 | 10691.7476 | 10916.0904 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 | 10851.6808 |  | 3171.2979 | 3262.8298 | 3612.4412 | 3861.2234 | 3213.0818 | 3332.5922 | 3429.6978 | 3523.1092 | 3603.9595 | 3644.6857 | 3704.5183 | 3772.9371 | 3842.8213 | 3930.6001 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895 | 3944.4895
45% | 15608.1674 | 15982.0933 | 17912.3076 | 19305.3503 | 15624.0342 | 16280.8937 | 16698.7969 | 17175.6494 | 17556.6795 | 17805.7325 | 18396.4806 | 18805.4398 | 19021.5298 | 19420.6547 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 | 19306.0646 |  | 6318.6081 | 6500.9794 | 7197.5577 | 7693.2404 | 6401.8598 | 6639.9766 | 6833.4533 | 7019.5695 | 7180.6586 | 7261.8028 | 7381.0154 | 7517.3357 | 7656.5754 | 7831.4691 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428 | 7859.1428
40% | 17870.5156 | 18298.6407 | 20508.6327 | 22103.592 | 17888.6822 | 18640.7512 | 19119.228 | 19665.1986 | 20101.4577 | 20386.61 | 21062.9849 | 21531.2213 | 21778.6328 | 22235.6093 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 | 22104.4099 |  | 10760.1697 | 11070.7361 | 12256.9625 | 13101.0774 | 10901.9419 | 11307.439 | 11636.917 | 11953.8605 | 12228.1845 | 12366.3677 | 12569.3789 | 12801.5232 | 13038.6392 | 13336.4715 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981 | 13383.5981
35% | 10839.207 | 11098.8826 | 12439.3342 | 13406.743 | 10850.2259 | 11306.3868 | 11596.6028 | 11927.7565 | 12192.3657 | 12365.3224 | 12775.5718 | 13059.5765 | 13209.6418 | 13486.817 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 | 13407.2391 |  | 13027.0181 | 13403.0116 | 14839.1407 | 15861.0855 | 13198.6574 | 13689.5807 | 14088.4699 | 14472.1841 | 14804.3 | 14971.5943 | 15217.3739 | 15498.4241 | 15785.4934 | 16146.0702 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249 | 16203.1249
30% | 4492.2249 | 4599.8454 | 5155.3852 | 5556.3202 | 4496.7916 | 4685.8439 | 4806.1217 | 4943.3658 | 5053.031 | 5124.7115 | 5294.7362 | 5412.4397 | 5474.6331 | 5589.5062 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 | 5556.5258 |  | 19901.1621 | 20475.5611 | 22669.5121 | 24230.7204 | 20163.3727 | 20913.3481 | 21522.7247 | 22108.9185 | 22616.2866 | 22871.8593 | 23247.3327 | 23676.6886 | 24115.2396 | 24666.0869 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485 | 24753.2485
25% | 2681.5709 | 2745.8134 | 3077.4351 | 3316.7677 | 2684.2969 | 2797.149 | 2868.9472 | 2950.8731 | 3016.3362 | 3059.1249 | 3160.6188 | 3230.8803 | 3268.0057 | 3336.5776 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 | 3316.8904 |  | 16923.4022 | 17411.8554 | 19277.5311 | 20605.1398 | 17146.3789 | 17784.1374 | 18302.3345 | 18800.8177 | 19232.2696 | 19449.6016 | 19768.8939 | 20134.0063 | 20506.9381 | 20975.3635 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833 | 21049.4833
20% | 2852.6525 | 2920.9937 | 3273.7725 | 3528.3742 | 2855.5524 | 2975.6044 | 3051.9832 | 3139.1359 | 3208.7755 | 3254.2941 | 3362.2632 | 3437.0073 | 3476.5013 | 3549.448 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 | 3528.5048 |  | 4489.5373 | 4619.117 | 5114.0541 | 5466.2498 | 4548.6898 | 4717.8781 | 4855.3484 | 4987.5889 | 5102.0469 | 5159.702 | 5244.4057 | 5341.2648 | 5440.1983 | 5564.4649 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278 | 5584.1278
15% | 2954.9137 | 3025.7048 | 3391.1299 | 3654.8586 | 2957.9176 | 3082.2732 | 3161.39 | 3251.667 | 3323.803 | 3370.9533 | 3482.7928 | 3560.2163 | 3601.1261 | 3676.6878 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 | 3654.9938 |  | 2782.0412 | 2862.3381 | 3169.0368 | 3387.2827 | 2818.6963 | 2923.5376 | 3008.7241 | 3090.6698 | 3161.5963 | 3197.3235 | 3249.812 | 3309.8329 | 3371.1393 | 3448.1438 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284 | 3460.3284
10% | 1970.104 | 2017.3019 | 2260.9387 | 2436.7722 | 1972.1068 | 2055.0173 | 2107.7662 | 2167.9557 | 2216.0504 | 2247.4865 | 2322.0523 | 2373.6722 | 2400.9476 | 2451.3262 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 | 2436.8624 |  | 795.9593 | 818.9327 | 906.6811 | 969.1226 | 806.4465 | 836.4423 | 860.8147 | 884.2598 | 904.5523 | 914.7741 | 929.7914 | 946.9638 | 964.5039 | 986.5354 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214 | 990.0214
5% | 157.0267 | 160.7886 | 180.2077 | 194.2224 | 157.1864 | 163.7947 | 167.9991 | 172.7965 | 176.6298 | 179.1355 | 185.0787 | 189.1931 | 191.367 | 195.3825 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 | 194.2296 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 89607.7949 | 91754.5348 | 102836.0568 | 110833.6316 | 89698.8876 | 93469.9732 | 95869.1902 | 98606.8406 | 100794.3664 | 102224.2006 | 105615.7346 | 107963.6038 | 109204.1944 | 111495.6035 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | 110837.7323 | E @ R (MWh) | 84110.3229 | 86537.9646 | 95810.4847 | 102408.7793 | 85218.5306 | 88388.2286 | 90963.6991 | 93441.1903 | 95585.5321 | 96665.6855 | 98252.5872 | 100067.2178 | 101920.7112 | 104248.8134 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934 | 104617.1934
Option 2 Summer POE50 W E @ R (MWh) N 2 | 62725.4564 | 64228.1743 | 71985.2398 | 77583.5421 | 62789.2213 | 65428.9812 | 67108.4332 | 69024.7884 | 70556.0565 | 71556.9404 | 73931.0142 | 75574.5227 | 76442.9361 | 78046.9225 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | 77586.4126 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 25233.0969 | 25961.3894 | 28743.1454 | 30722.6338 | 25565.5592 | 26516.4686 | 27289.1097 | 28032.3571 | 28675.6596 | 28999.7056 | 29475.7762 | 30020.1654 | 30576.2134 | 31274.644 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158 | 31385.158
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 40.2458 | 41.8786 | 47.6412 | 46.0633 | 35.8204 | 37.7143 | 39.8978 | 41.5326 | 43.3336 | 44.2802 | 45.0997 | 47.1232 | 45.9094 | 49.207 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 |  | 42.8352 | 44.5416 | 50.2595 | 48.865 | 38.6312 | 40.7636 | 42.7925 | 44.5218 | 46.322 | 47.1139 | 48.1922 | 50.1883 | 49.5413 | 52.1473 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521
98% | 119.5239 | 124.3732 | 141.4873 | 136.8011 | 106.3811 | 112.0058 | 118.4904 | 123.3457 | 128.6944 | 131.5055 | 133.9394 | 139.9487 | 136.3441 | 146.1373 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 |  | 127.2142 | 132.2818 | 149.263 | 145.1216 | 114.7287 | 121.0617 | 127.0874 | 132.2231 | 137.5693 | 139.9211 | 143.1236 | 149.0518 | 147.13 | 154.8697 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386
97% | 52.5824 | 54.7158 | 62.2448 | 60.1832 | 46.8005 | 49.275 | 52.1278 | 54.2637 | 56.6168 | 57.8535 | 58.9243 | 61.568 | 59.9822 | 64.2905 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 |  | 55.9656 | 58.195 | 65.6656 | 63.8437 | 50.4729 | 53.2589 | 55.9099 | 58.1692 | 60.5212 | 61.5558 | 62.9647 | 65.5727 | 64.7273 | 68.1322 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982
95% | 129.4337 | 134.685 | 153.2181 | 148.1433 | 115.2012 | 121.2923 | 128.3145 | 133.5723 | 139.3645 | 142.4087 | 145.0443 | 151.5519 | 147.6485 | 158.2536 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 |  | 137.7615 | 143.2493 | 161.6385 | 157.1536 | 124.2409 | 131.099 | 137.6243 | 143.1858 | 148.9752 | 151.522 | 154.99 | 161.4097 | 159.3286 | 167.71 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494
90% | 1321.9761 | 1375.6113 | 1564.8992 | 1513.0675 | 1176.6126 | 1238.8238 | 1310.5453 | 1364.2462 | 1423.405 | 1454.4967 | 1481.4163 | 1547.882 | 1508.0136 | 1616.3296 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 |  | 1407.0332 | 1463.083 | 1650.9011 | 1605.0952 | 1268.9395 | 1338.9846 | 1405.6311 | 1462.4337 | 1521.5646 | 1547.5766 | 1582.9973 | 1648.5647 | 1627.3098 | 1712.9134 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406
85% | 3114.4974 | 3240.8588 | 3686.8101 | 3564.6975 | 2772.0297 | 2918.5955 | 3087.5672 | 3214.0833 | 3353.4581 | 3426.7082 | 3490.1292 | 3646.7184 | 3552.7909 | 3807.9769 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 |  | 3314.8869 | 3446.937 | 3889.4254 | 3781.5094 | 2989.5464 | 3154.5686 | 3311.5837 | 3445.4074 | 3584.7163 | 3645.999 | 3729.4479 | 3883.921 | 3833.8456 | 4035.5225 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703
80% | 5639.4649 | 5868.2694 | 6675.7596 | 6454.6487 | 5019.3538 | 5284.7425 | 5590.7021 | 5819.7865 | 6072.1545 | 6204.7896 | 6319.6269 | 6603.1651 | 6433.0892 | 6895.1581 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 |  | 6002.313 | 6241.4181 | 7042.6381 | 6847.2332 | 5413.2144 | 5712.0224 | 5996.3319 | 6238.6484 | 6490.897 | 6601.8625 | 6752.9646 | 7032.6712 | 6941.999 | 7307.1783 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319
75% | 6593.364 | 6860.8701 | 7804.945 | 7546.4338 | 5868.3629 | 6178.6414 | 6536.3531 | 6804.1864 | 7099.2417 | 7254.3117 | 7388.5734 | 7720.0713 | 7521.2276 | 8061.454 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 |  | 7017.5868 | 7297.1358 | 8233.8799 | 8005.4228 | 6328.8439 | 6678.1943 | 7010.594 | 7293.8976 | 7588.8133 | 7718.5483 | 7895.209 | 8222.2271 | 8116.2179 | 8543.1663 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852
70% | 7731.9758 | 8045.6776 | 9152.7853 | 8849.6317 | 6881.7738 | 7245.6344 | 7665.1196 | 7979.2052 | 8325.2138 | 8507.0628 | 8664.5103 | 9053.2547 | 8820.0726 | 9453.591 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 |  | 8229.4578 | 8557.2822 | 9655.7932 | 9387.8837 | 7421.7755 | 7831.4555 | 8221.2574 | 8553.4848 | 8899.3297 | 9051.4688 | 9258.637 | 9642.1281 | 9517.8121 | 10018.4904 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808
65% | 8472.8486 | 8816.6091 | 10029.7992 | 9697.5976 | 7541.1809 | 7939.9063 | 8399.5863 | 8743.7674 | 9122.9303 | 9322.204 | 9494.738 | 9920.7317 | 9665.2061 | 10359.428 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 |  | 9017.9991 | 9377.2354 | 10581.005 | 10287.4246 | 8132.9251 | 8581.8604 | 9009.0129 | 9373.0742 | 9752.0577 | 9918.7746 | 10145.7935 | 10566.0305 | 10429.8026 | 10978.4557 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465
60% | 9218.7775 | 9592.8018 | 10912.7982 | 10551.3504 | 8205.088 | 8638.9163 | 9139.0654 | 9513.5473 | 9926.0908 | 10142.908 | 10330.6315 | 10794.1286 | 10516.1073 | 11271.4467 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 |  | 9811.9216 | 10202.7843 | 11512.5308 | 11193.1043 | 8848.928 | 9337.3864 | 9802.1444 | 10198.2567 | 10610.605 | 10791.9992 | 11039.0044 | 11496.238 | 11348.017 | 11944.972 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523
55% | 9241.0239 | 9615.9508 | 10939.1325 | 10576.8125 | 8224.8882 | 8659.7634 | 9161.1194 | 9536.5051 | 9950.044 | 10167.3845 | 10355.561 | 10820.1766 | 10541.4843 | 11298.6465 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 |  | 9835.5994 | 10227.4053 | 11540.3124 | 11220.115 | 8870.2819 | 9359.919 | 9825.7986 | 10222.8668 | 10636.2101 | 10818.0421 | 11065.6433 | 11523.9803 | 11375.4016 | 11973.7972 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093
50% | 10886.5841 | 11328.2747 | 12887.077 | 12460.2382 | 9689.5039 | 10201.8178 | 10792.4509 | 11234.682 | 11721.8603 | 11977.9029 | 12199.5881 | 12746.9384 | 12418.6191 | 13310.61 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 |  | 11587.0364 | 12048.6116 | 13595.3097 | 13218.0944 | 10449.8236 | 11026.651 | 11575.4903 | 12043.2649 | 12530.2128 | 12744.4238 | 13036.1157 | 13576.0693 | 13401.033 | 14105.9856 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235
45% | 13615.4771 | 14167.8844 | 16117.4248 | 15583.5922 | 12118.33 | 12759.0634 | 13497.7479 | 14050.8311 | 14660.1284 | 14980.352 | 15257.6062 | 15942.1584 | 15531.5406 | 16647.1231 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 |  | 14491.5087 | 15068.7849 | 17003.1872 | 16531.4169 | 13069.2357 | 13790.654 | 14477.0684 | 15062.098 | 15671.1071 | 15939.0134 | 16303.8224 | 16979.1239 | 16760.212 | 17641.8721 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403
40% | 14417.022 | 15001.9495 | 17066.2597 | 16501.0003 | 12831.7376 | 13510.1911 | 14292.3621 | 14878.0054 | 15523.172 | 15862.2473 | 16155.8234 | 16880.6753 | 16445.8844 | 17627.1414 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 |  | 15344.6257 | 15955.8863 | 18004.167 | 17504.6236 | 13838.6233 | 14602.5116 | 15329.3353 | 15948.8057 | 16593.6672 | 16877.3452 | 17263.6306 | 17978.6871 | 17746.8878 | 18680.4513 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885
35% | 5895.2987 | 6134.4828 | 6978.6047 | 6747.4632 | 5247.0563 | 5524.4843 | 5844.3237 | 6083.8005 | 6347.6171 | 6486.2692 | 6606.3161 | 6902.717 | 6724.9256 | 7207.9562 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 |  | 6274.6073 | 6524.5593 | 7362.1266 | 7157.8572 | 5658.7843 | 5971.1476 | 6268.3549 | 6521.664 | 6785.3558 | 6901.3553 | 7059.3121 | 7351.7076 | 7256.922 | 7638.6677 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866
30% | 1818.4755 | 1892.2547 | 2152.6342 | 2081.3358 | 1618.5174 | 1704.0934 | 1802.7516 | 1876.6211 | 1957.9985 | 2000.7674 | 2037.7973 | 2129.2257 | 2074.3839 | 2223.3804 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 |  | 1935.4778 | 2012.5785 | 2270.9361 | 2207.9268 | 1745.5198 | 1841.872 | 1933.5491 | 2011.6854 | 2093.0243 | 2128.8057 | 2177.5294 | 2267.7223 | 2238.4845 | 2356.2385 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294
25% | 1338.4923 | 1392.7977 | 1584.4505 | 1531.9712 | 1191.3128 | 1254.3012 | 1326.9188 | 1381.2905 | 1441.1885 | 1472.6687 | 1499.9246 | 1567.2206 | 1526.8542 | 1636.5234 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 |  | 1424.6121 | 1481.3622 | 1671.5269 | 1625.1487 | 1284.7932 | 1355.7134 | 1423.1925 | 1480.7048 | 1540.5745 | 1566.9115 | 1602.7746 | 1669.1613 | 1647.6408 | 1734.3139 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587
20% | 1064.7941 | 1107.9949 | 1260.4581 | 1218.7099 | 947.7102 | 997.8185 | 1055.5871 | 1098.8408 | 1146.4907 | 1171.5337 | 1193.2163 | 1246.7515 | 1214.6392 | 1301.883 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 |  | 1133.3039 | 1178.4496 | 1329.7289 | 1292.8342 | 1022.0754 | 1078.4937 | 1132.1746 | 1177.9266 | 1225.554 | 1246.5055 | 1275.0353 | 1327.847 | 1310.7271 | 1379.677 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885
15% | 835.2516 | 869.1394 | 988.7354 | 955.9871 | 743.408 | 782.7142 | 828.0294 | 861.9587 | 899.3365 | 918.9808 | 935.9892 | 977.9836 | 952.7939 | 1021.2302 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 |  | 888.9924 | 924.4058 | 1043.0732 | 1014.1321 | 801.742 | 845.9979 | 888.1065 | 923.9956 | 961.3557 | 977.7906 | 1000.1701 | 1041.597 | 1028.1677 | 1082.2538 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829
10% | 586.4963 | 610.2916 | 694.2694 | 671.2742 | 522.0056 | 549.6056 | 581.425 | 605.2494 | 631.4954 | 645.2892 | 657.2321 | 686.7197 | 669.0321 | 717.0866 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 |  | 624.2319 | 649.0985 | 732.4243 | 712.1024 | 562.9665 | 594.0421 | 623.6099 | 648.8105 | 675.044 | 686.5842 | 702.2986 | 731.3877 | 721.9579 | 759.9361 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645
5% | 60.672 | 63.1336 | 71.821 | 69.4422 | 54.0006 | 56.8558 | 60.1474 | 62.612 | 65.3271 | 66.7541 | 67.9895 | 71.04 | 69.2102 | 74.1814 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 |  | 64.5757 | 67.1481 | 75.768 | 73.6658 | 58.2379 | 61.4526 | 64.5114 | 67.1183 | 69.8321 | 71.026 | 72.6516 | 75.6608 | 74.6853 | 78.6141 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102194.2775 | 106340.5049 | 120973.2554 | 116966.4448 | 90957.0754 | 95766.2561 | 101310.6328 | 105461.9332 | 110035.1621 | 112438.6786 | 114519.6771 | 119657.7503 | 116575.7591 | 124949.0348 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | E @ R (MWh) | 108769.5462 | 113102.4335 | 127621.5603 | 124080.5741 | 98094.3301 | 103509.1105 | 108661.1609 | 113052.2433 | 117623.3091 | 119634.1452 | 122372.308 | 127440.9473 | 125797.8508 | 132415.3652 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008
Option 3 Winter POE50 W E @ R (MWh) N 2 | 71535.9943 | 74438.3534 | 84681.2788 | 81876.5114 | 63669.9528 | 67036.3793 | 70917.4429 | 73823.3533 | 77024.6135 | 78707.075 | 80163.774 | 83760.4252 | 81603.0314 | 87464.3243 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 32630.8639 | 33930.7301 | 38286.4681 | 37224.1722 | 29428.299 | 31052.7331 | 32598.3483 | 33915.673 | 35286.9927 | 35890.2436 | 36711.6924 | 38232.2842 | 37739.3552 | 39724.6096 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43.3961 | 44.6487 | 49.4328 | 47.3811 | 38.5119 | 40.1473 | 41.4761 | 42.7544 | 43.8607 | 44.418 | 45.2368 | 46.173 | 47.1293 | 48.3305 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205
98% | 19.0952 | 19.5527 | 21.9141 | 20.9178 | 16.4141 | 17.2177 | 17.729 | 18.3123 | 18.7785 | 19.0832 | 19.8059 | 20.3062 | 20.5706 | 21.0589 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 |  | 21.48 | 22.1 | 24.468 | 23.4525 | 19.0624 | 19.8719 | 20.5296 | 21.1623 | 21.71 | 21.9858 | 22.3911 | 22.8545 | 23.3278 | 23.9224 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165
97% | 18.9014 | 19.3542 | 21.6917 | 20.7055 | 16.2474 | 17.0429 | 17.549 | 18.1264 | 18.5879 | 18.8895 | 19.6048 | 20.1001 | 20.3618 | 20.8451 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 |  | 42.5239 | 43.7512 | 48.4391 | 46.4287 | 37.7378 | 39.3403 | 40.6424 | 41.895 | 42.9791 | 43.5252 | 44.3275 | 45.2449 | 46.182 | 47.359 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453
95% | 55.8317 | 57.1693 | 64.0738 | 61.1608 | 47.9924 | 50.3421 | 51.8369 | 53.5427 | 54.9057 | 55.7965 | 57.9097 | 59.3726 | 60.1455 | 61.5732 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 |  | 83.7393 | 86.1562 | 95.3878 | 91.4289 | 74.3145 | 77.4702 | 80.0343 | 82.5009 | 84.6358 | 85.7112 | 87.2911 | 89.0977 | 90.943 | 93.2608 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276
90% | 125.5245 | 128.5317 | 144.0549 | 137.5056 | 107.8996 | 113.1822 | 116.5431 | 120.3781 | 123.4424 | 125.4453 | 130.1963 | 133.4852 | 135.2231 | 138.4329 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 |  | 302.5736 | 311.3066 | 344.663 | 330.3584 | 268.5192 | 279.9217 | 289.1865 | 298.0989 | 305.8128 | 309.6985 | 315.4071 | 321.935 | 328.6026 | 336.9776 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028
85% | 203.5532 | 208.4297 | 233.6025 | 222.9821 | 174.9724 | 183.5388 | 188.9888 | 195.2077 | 200.1769 | 203.4249 | 211.1291 | 216.4625 | 219.2806 | 224.4858 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 |  | 362.5431 | 373.007 | 412.9746 | 395.8348 | 321.7392 | 335.4016 | 346.5028 | 357.1816 | 366.4244 | 371.0802 | 377.9203 | 385.7419 | 393.7311 | 403.766 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538
80% | 783.6798 | 802.4544 | 899.3697 | 858.481 | 673.6436 | 706.6242 | 727.607 | 751.5495 | 770.6809 | 783.1858 | 812.847 | 833.3807 | 844.2304 | 864.2703 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 |  | 413.7898 | 425.7328 | 471.35 | 451.7874 | 367.2181 | 382.8118 | 395.4821 | 407.6704 | 418.2197 | 423.5336 | 431.3406 | 440.2678 | 449.3863 | 460.8397 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519
75% | 1186.9089 | 1215.3438 | 1362.1252 | 1300.1978 | 1020.2555 | 1070.2058 | 1101.9848 | 1138.2466 | 1167.2217 | 1186.1607 | 1231.0836 | 1262.1826 | 1278.6149 | 1308.966 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 |  | 354.9106 | 365.1542 | 404.2804 | 387.5015 | 314.9658 | 328.3406 | 339.208 | 349.662 | 358.7102 | 363.268 | 369.9641 | 377.621 | 385.442 | 395.2656 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82
70% | 1813.0773 | 1856.5133 | 2080.731 | 1986.1331 | 1558.5038 | 1634.8059 | 1683.3504 | 1738.7426 | 1783.0039 | 1811.9344 | 1880.5569 | 1928.0625 | 1953.1639 | 1999.5271 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 |  | 379.4436 | 390.3953 | 432.2261 | 414.2873 | 336.7376 | 351.0369 | 362.6555 | 373.8321 | 383.5058 | 388.3787 | 395.5376 | 403.7239 | 412.0855 | 422.5881 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25
65% | 3310.6471 | 3389.9605 | 3799.3781 | 3626.644 | 2845.8004 | 2985.1268 | 3073.7682 | 3174.9133 | 3255.7336 | 3308.5602 | 3433.8638 | 3520.6081 | 3566.4429 | 3651.1012 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 |  | 1000.946 | 1029.8359 | 1140.1826 | 1092.8613 | 888.2905 | 926.0112 | 956.6603 | 986.1434 | 1011.6619 | 1024.5162 | 1043.4009 | 1064.9957 | 1087.053 | 1114.7584 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423
60% | 6433.7346 | 6587.868 | 7383.5083 | 7047.826 | 5530.3762 | 5801.1357 | 5973.3967 | 6169.9568 | 6327.0186 | 6429.679 | 6673.1871 | 6841.7614 | 6930.8343 | 7095.3548 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 |  | 1117.614 | 1149.8713 | 1273.0797 | 1220.2427 | 991.8276 | 1033.9449 | 1068.1664 | 1101.086 | 1129.5789 | 1143.9315 | 1165.0174 | 1189.1292 | 1213.7575 | 1244.6921 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869
55% | 7457.3163 | 7635.9717 | 8558.1952 | 8169.1073 | 6410.2372 | 6724.0735 | 6923.7405 | 7151.5725 | 7333.6222 | 7452.6155 | 7734.8648 | 7930.2586 | 8033.5027 | 8224.1977 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 |  | 1818.1672 | 1870.6442 | 2071.0832 | 1985.1265 | 1613.5342 | 1682.0519 | 1737.7244 | 1791.279 | 1837.6321 | 1860.9812 | 1895.2844 | 1934.5102 | 1974.5762 | 2024.9015 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646
50% | 8773.1422 | 8983.321 | 10068.2687 | 9610.5271 | 7541.3085 | 7910.5204 | 8145.4182 | 8413.4507 | 8627.6226 | 8767.612 | 9099.6635 | 9329.5341 | 9450.9953 | 9675.3381 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 |  | 3171.2979 | 3262.8298 | 3612.4412 | 3462.513 | 2814.3714 | 2933.8818 | 3030.9874 | 3124.3988 | 3205.2491 | 3245.9753 | 3305.8078 | 3374.2267 | 3444.1109 | 3531.8897 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791
45% | 15608.1674 | 15982.0933 | 17912.3076 | 17097.9463 | 13416.6301 | 14073.4897 | 14491.3929 | 14968.2454 | 15349.2755 | 15598.3285 | 16189.0766 | 16598.0358 | 16814.1258 | 17213.2506 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 |  | 6318.6081 | 6500.9794 | 7197.5577 | 6898.8355 | 5607.4548 | 5845.5716 | 6039.0483 | 6225.1645 | 6386.2536 | 6467.3978 | 6586.6104 | 6722.9307 | 6862.1704 | 7037.0641 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378
40% | 17870.5156 | 18298.6407 | 20508.6327 | 19576.2327 | 15361.3229 | 16113.3919 | 16591.8686 | 17137.8392 | 17574.0983 | 17859.2507 | 18535.6255 | 19003.862 | 19251.2734 | 19708.25 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 |  | 10760.1697 | 11070.7361 | 12256.9625 | 11748.2585 | 9549.123 | 9954.6201 | 10284.098 | 10601.0416 | 10875.3656 | 11013.5488 | 11216.56 | 11448.7043 | 11685.8203 | 11983.6526 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792
35% | 10839.207 | 11098.8826 | 12439.3342 | 11873.795 | 9317.2778 | 9773.4388 | 10063.6547 | 10394.8085 | 10659.4177 | 10832.3744 | 11242.6237 | 11526.6285 | 11676.6938 | 11953.869 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 |  | 13027.0181 | 13403.0116 | 14839.1407 | 14223.2678 | 11560.8397 | 12051.763 | 12450.6522 | 12834.3664 | 13166.4823 | 13333.7766 | 13579.5562 | 13860.6064 | 14147.6757 | 14508.2525 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072
30% | 4492.2249 | 4599.8454 | 5155.3852 | 4921.0018 | 3861.4732 | 4050.5256 | 4170.8033 | 4308.0474 | 4417.7126 | 4489.3932 | 4659.4178 | 4777.1214 | 4839.3148 | 4954.1879 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 |  | 19901.1621 | 20475.5611 | 22669.5121 | 21728.6531 | 17661.3054 | 18411.2809 | 19020.6574 | 19606.8512 | 20114.2193 | 20369.7921 | 20745.2655 | 21174.6213 | 21613.1724 | 22164.0196 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812
25% | 2681.5709 | 2745.8134 | 3077.4351 | 2937.5233 | 2305.0525 | 2417.9046 | 2489.7027 | 2571.6287 | 2637.0918 | 2679.8805 | 2781.3743 | 2851.6358 | 2888.7613 | 2957.3332 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 |  | 16923.4022 | 17411.8554 | 19277.5311 | 18477.4504 | 15018.6896 | 15656.4481 | 16174.6452 | 16673.1283 | 17104.5802 | 17321.9123 | 17641.2046 | 18006.317 | 18379.2488 | 18847.6741 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794
20% | 2852.6525 | 2920.9937 | 3273.7725 | 3124.9344 | 2452.1126 | 2572.1646 | 2648.5433 | 2735.6961 | 2805.3357 | 2850.8543 | 2958.8233 | 3033.5674 | 3073.0615 | 3146.0082 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 |  | 4489.5373 | 4619.117 | 5114.0541 | 4901.8041 | 3984.2442 | 4153.4324 | 4290.9027 | 4423.1432 | 4537.6012 | 4595.2563 | 4679.96 | 4776.8192 | 4875.7526 | 5000.0192 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822
15% | 2954.9137 | 3025.7048 | 3391.1299 | 3236.9563 | 2540.0153 | 2664.371 | 2743.4877 | 2833.7647 | 2905.9007 | 2953.051 | 3064.8905 | 3142.3141 | 3183.2239 | 3258.7856 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 |  | 2782.0412 | 2862.3381 | 3169.0368 | 3037.5114 | 2468.9251 | 2573.7663 | 2658.9528 | 2740.8986 | 2811.825 | 2847.5523 | 2900.0408 | 2960.0617 | 3021.368 | 3098.3726 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571
10% | 1970.104 | 2017.3019 | 2260.9387 | 2158.1479 | 1693.4824 | 1776.393 | 1829.1418 | 1889.3314 | 1937.426 | 1968.8621 | 2043.4279 | 2095.0478 | 2122.3233 | 2172.7019 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 |  | 795.9593 | 818.9327 | 906.6811 | 869.0509 | 706.3748 | 736.3705 | 760.7429 | 784.1881 | 804.4806 | 814.7024 | 829.7197 | 846.892 | 864.4322 | 886.4636 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497
5% | 157.0267 | 160.7886 | 180.2077 | 172.0147 | 134.9787 | 141.587 | 145.7914 | 150.5888 | 154.4221 | 156.9278 | 162.871 | 166.9854 | 169.1593 | 173.1748 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 89607.7949 | 91754.5348 | 102836.0568 | 98160.7405 | 77025.9964 | 80797.082 | 83196.2991 | 85933.9495 | 88121.4752 | 89551.3094 | 92942.8434 | 95290.7127 | 96531.3032 | 98822.7123 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | E @ R (MWh) | 84110.3229 | 86537.9646 | 95810.4847 | 91834.0358 | 74643.787 | 77813.4851 | 80388.9556 | 82866.4468 | 85010.7885 | 86090.9419 | 87677.8437 | 89492.4743 | 91345.9677 | 93674.0698 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498
Option 3 Summer POE50 W E @ R (MWh) N 2 | 62725.4564 | 64228.1743 | 71985.2398 | 68712.5183 | 53918.1975 | 56557.9574 | 58237.4093 | 60153.7646 | 61685.0327 | 62685.9166 | 65059.9904 | 66703.4989 | 67571.9123 | 69175.8986 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 25233.0969 | 25961.3894 | 28743.1454 | 27550.2107 | 22393.1361 | 23344.0455 | 24116.6867 | 24859.934 | 25503.2366 | 25827.2826 | 26303.3531 | 26847.7423 | 27403.7903 | 28102.2209 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 40.2458 | 41.8786 | 47.6412 | 12.1949 | 14.8155 | 16.7094 | 18.8929 | 20.5278 | 22.3288 | 23.2753 | 24.0948 | 26.1183 | 24.9046 | 28.2021 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 | 32.5024 |  | 42.8352 | 44.5416 | 50.2595 | 14.9966 | 17.6263 | 19.7587 | 21.7877 | 23.5169 | 25.3171 | 26.109 | 27.1873 | 29.1835 | 28.5364 | 31.1425 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472 | 32.6472
98% | 119.5239 | 124.3732 | 141.4873 | 35.002 | 42.7847 | 48.4094 | 54.894 | 59.7493 | 65.098 | 67.9091 | 70.343 | 76.3523 | 72.7477 | 82.5409 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 | 95.3121 |  | 127.2142 | 132.2818 | 149.263 | 43.3225 | 51.1323 | 57.4653 | 63.491 | 68.6267 | 73.9729 | 76.3247 | 79.5272 | 85.4554 | 83.5336 | 91.2733 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422 | 95.7422
97% | 52.5824 | 54.7158 | 62.2448 | 14.853 | 18.2769 | 20.7514 | 23.6041 | 25.7401 | 28.0932 | 29.3299 | 30.4006 | 33.0443 | 31.4586 | 35.7669 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 | 41.3854 |  | 55.9656 | 58.195 | 65.6656 | 18.5135 | 21.9492 | 24.7353 | 27.3862 | 29.6456 | 31.9976 | 33.0322 | 34.4411 | 37.0491 | 36.2036 | 39.6086 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746 | 41.5746
95% | 129.4337 | 134.685 | 153.2181 | 34.4946 | 42.9226 | 49.0136 | 56.0358 | 61.2936 | 67.0858 | 70.13 | 72.7656 | 79.2732 | 75.3698 | 85.9749 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 | 99.805 |  | 137.7615 | 143.2493 | 161.6385 | 43.5049 | 51.9622 | 58.8203 | 65.3456 | 70.9071 | 76.6965 | 79.2434 | 82.7114 | 89.131 | 87.05 | 95.4313 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707 | 100.2707
90% | 1321.9761 | 1375.6113 | 1564.8992 | 300.3972 | 386.4769 | 448.688 | 520.4096 | 574.1104 | 633.2693 | 664.361 | 691.2806 | 757.7462 | 717.8779 | 826.1938 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 | 967.4479 |  | 1407.0332 | 1463.083 | 1650.9011 | 392.4249 | 478.8038 | 548.8489 | 615.4953 | 672.298 | 731.4289 | 757.4409 | 792.8615 | 858.429 | 837.174 | 922.7776 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049 | 972.2049
85% | 3114.4974 | 3240.8588 | 3686.8101 | 516.0201 | 718.8188 | 865.3845 | 1034.3563 | 1160.8723 | 1300.2471 | 1373.4973 | 1436.9183 | 1593.5074 | 1499.5799 | 1754.7659 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 | 2087.552 |  | 3314.8869 | 3446.937 | 3889.4254 | 732.832 | 936.3355 | 1101.3576 | 1258.3727 | 1392.1964 | 1531.5053 | 1592.788 | 1676.237 | 1830.71 | 1780.6346 | 1982.3116 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593 | 2098.7593
80% | 5639.4649 | 5868.2694 | 6675.7596 | 545.1809 | 912.3914 | 1177.7801 | 1483.7396 | 1712.824 | 1965.192 | 2097.8271 | 2212.6644 | 2496.2027 | 2326.1268 | 2788.1957 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 | 3390.7763 |  | 6002.313 | 6241.4181 | 7042.6381 | 937.7653 | 1306.252 | 1605.0599 | 1889.3695 | 2131.6859 | 2383.9345 | 2494.9 | 2646.0022 | 2925.7088 | 2835.0365 | 3200.2159 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695 | 3411.0695
75% | 6593.364 | 6860.8701 | 7804.945 | 144.9746 | 552.9949 | 863.2734 | 1220.9851 | 1488.8185 | 1783.8737 | 1938.9437 | 2073.2054 | 2404.7033 | 2205.8596 | 2746.0861 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 | 3450.5914 |  | 7017.5868 | 7297.1358 | 8233.8799 | 582.6608 | 1013.4759 | 1362.8264 | 1695.226 | 1978.5296 | 2273.4453 | 2403.1803 | 2579.841 | 2906.8591 | 2800.8499 | 3227.7983 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172 | 3474.3172
70% | 7731.9758 | 8045.6776 | 9152.7853 |  | 73.7002 | 328.5293 | 746.3023 | 1060.3879 | 1406.3965 | 1588.2455 | 1745.693 | 2134.4374 | 1901.2553 | 2534.7738 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 | 3360.9406 |  | 8229.4578 | 8557.2822 | 9655.7932 | 90.4584 | 502.9582 | 912.6382 | 1302.4401 | 1634.6676 | 1980.5125 | 2132.6515 | 2339.8197 | 2723.3108 | 2598.9948 | 3099.6732 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635 | 3388.7635
65% | 8472.8486 | 8816.6091 | 10029.7992 |  |  |  | 94.1178 | 315.5868 | 678.6412 | 877.9149 | 1050.4489 | 1476.4426 | 1220.9171 | 1915.1389 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 | 2820.4685 |  | 9017.9991 | 9377.2354 | 10581.005 |  | 10.8962 | 195.9637 | 564.7239 | 928.7851 | 1307.7686 | 1474.4855 | 1701.5045 | 2121.7414 | 1985.5136 | 2534.1666 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574 | 2850.9574
60% | 9218.7775 | 9592.8018 | 10912.7982 | [5 empty] | 21.7862 | 86.566 | 175.9185 | 521.2061 | 293.3239 | 995.1422 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 | 1980.1748 |  | 9811.9216 | 10202.7843 | 11512.5308 |  |  |  | 3.9426 | 109.7612 | 363.9255 | 519.2314 | 762.6999 | 1219.9335 | 1071.7125 | 1668.6676 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479 | 2013.3479
55% | 9241.0239 | 9615.9508 | 10939.1325 | [10 empty] | 58.6108 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 | 704.1265 |  | 9835.5994 | 10227.4053 | 11540.3124 | [7 empty] | 9.1787 | 145.5712 | 83.9931 | 427.9275 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999 | 737.1999
50% | FY25: 10886.5841; FY26: 11328.2747; FY27: 12887.077 |  | 11587.0364 | 12048.6116 | 13595.3097 | [11 empty] | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468 | 0.035468
45% | FY25: 13615.4771; FY26: 14167.8844; FY27: 16117.4248 |  | 14491.5087 | 15068.7849 | 17003.1872
40% | FY25: 14417.022; FY26: 15001.9495; FY27: 17066.2597 |  | 15344.6257 | 15955.8863 | 18004.167
35% | FY25: 5895.2987; FY26: 6134.4828; FY27: 6978.6047 |  | 6274.6073 | 6524.5593 | 7362.1266
30% | FY25: 1818.4755; FY26: 1892.2547; FY27: 2152.6342 |  | 1935.4778 | 2012.5785 | 2270.9361
25% | FY25: 1338.4923; FY26: 1392.7977; FY27: 1584.4505 |  | 1424.6121 | 1481.3622 | 1671.5269
20% | FY25: 1064.7941; FY26: 1107.9949; FY27: 1260.4581 |  | 1133.3039 | 1178.4496 | 1329.7289
15% | FY25: 835.2516; FY26: 869.1394; FY27: 988.7354 |  | 888.9924 | 924.4058 | 1043.0732
10% | FY25: 586.4963; FY26: 610.2916; FY27: 694.2694 |  | 624.2319 | 649.0985 | 732.4243
5% | FY25: 60.672; FY26: 63.1336; FY27: 71.821 |  | 64.5757 | 67.1481 | 75.768
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 102194.2775 | 106340.5049 | 120973.2554 | 1603.1172 | 2763.1818 | 3818.5391 | 5253.3375 | 6479.9107 | 7972.0119 | 8817.9997 | 9583.7332 | 11599.034 | 10369.4211 | 13851.3919 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | 19031.0828 | E @ R (MWh) | 108769.5462 | 113102.4335 | 127621.5603 | 2856.4789 | 4391.3915 | 5887.4742 | 7507.5806 | 9040.6201 | 10780.5049 | 11589.387 | 12732.0114 | 14973.0828 | 14229.2327 | 17320.9939 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898 | 19216.8898
Option 4 Winter POE50 W E @ R (MWh) N 2 | 71535.9943 | 74438.3534 | 84681.2788 | 1122.1821 | 1934.2273 | 2672.9774 | 3677.3362 | 4535.9375 | 5580.4083 | 6172.5998 | 6708.6132 | 8119.3238 | 7258.5947 | 9695.9743 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | 13321.758 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 32630.8639 | 33930.7301 | 38286.4681 | 856.9437 | 1317.4174 | 1766.2423 | 2252.2742 | 2712.186 | 3234.1515 | 3476.8161 | 3819.6034 | 4491.9248 | 4268.7698 | 5196.2982 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669 | 5765.0669
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43.3961 | 44.6487 | 49.4328 | 18.651 | 20.6938 | 22.3292 | 23.658 | 24.9362 | 26.0426 | 26.5999 | 27.4186 | 28.3549 | 29.3112 | 30.5123 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024 | 30.7024
98% | 19.0952 | 19.5527 | 21.9141 | 6.5254 | 7.4227 | 8.2264 | 8.7376 | 9.321 | 9.7872 | 10.0919 | 10.8146 | 11.3149 | 11.5793 | 12.0676 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 | 11.9274 |  | 21.48 | 22.1 | 24.468 | 9.06 | 10.0711 | 10.8806 | 11.5383 | 12.171 | 12.7186 | 12.9945 | 13.3997 | 13.8632 | 14.3365 | 14.931 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251 | 15.0251
97% | 18.9014 | 19.3542 | 21.6917 | 6.2856 | 7.1739 | 7.9693 | 8.4754 | 9.0528 | 9.5143 | 9.8159 | 10.5313 | 11.0265 | 11.2882 | 11.7715 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 | 11.6328 |  | 42.5239 | 43.7512 | 48.4391 | 17.589 | 19.5907 | 21.1932 | 22.4953 | 23.7478 | 24.8319 | 25.378 | 26.1803 | 27.0978 | 28.0348 | 29.2119 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981 | 29.3981
95% | 55.8317 | 57.1693 | 64.0738 | 17.7778 | 20.4016 | 22.7512 | 24.2461 | 25.9518 | 27.3148 | 28.2057 | 30.3188 | 31.7817 | 32.5547 | 33.9824 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 | 33.5725 |  | 83.7393 | 86.1562 | 95.3878 | 33.5849 | 37.5267 | 40.6824 | 43.2465 | 45.7131 | 47.8479 | 48.9233 | 50.5032 | 52.3099 | 54.1552 | 56.473 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398 | 56.8398
90% | 125.5245 | 128.5317 | 144.0549 | 35.6069 | 41.5058 | 46.7884 | 50.1493 | 53.9842 | 57.0486 | 59.0515 | 63.8024 | 67.0914 | 68.8292 | 72.0391 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 | 71.1175 |  | 302.5736 | 311.3066 | 344.663 | 112.004 | 126.2467 | 137.6492 | 146.914 | 155.8264 | 163.5403 | 167.426 | 173.1346 | 179.6625 | 186.3301 | 194.7051 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303 | 196.0303
85% | 203.5532 | 208.4297 | 233.6025 | 46.6535 | 56.2193 | 64.7857 | 70.2358 | 76.4546 | 81.4238 | 84.6718 | 92.376 | 97.7095 | 100.5276 | 105.7328 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 | 104.2383 |  | 362.5431 | 373.007 | 412.9746 | 116.6479 | 133.7136 | 147.376 | 158.4771 | 169.1559 | 178.3987 | 183.0546 | 189.8946 | 197.7163 | 205.7054 | 215.7403 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282 | 217.3282
80% | 783.6798 | 802.4544 | 899.3697 | 131.7556 | 168.5839 | 201.5645 | 222.5473 | 246.4899 | 265.6212 | 278.1261 | 307.7873 | 328.321 | 339.1708 | 359.2107 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 | 353.4571 |  | 413.7898 | 425.7328 | 471.35 | 110.6714 | 130.1493 | 145.743 | 158.4133 | 170.6016 | 181.1509 | 186.4648 | 194.2718 | 203.199 | 212.3175 | 223.7708 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831 | 225.5831
75% | 1186.9089 | 1215.3438 | 1362.1252 | 117.7088 | 173.4865 | 223.4368 | 255.2159 | 291.4777 | 320.4528 | 339.3918 | 384.3147 | 415.4137 | 431.846 | 462.1971 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 | 453.4832 |  | 354.9106 | 365.1542 | 404.2804 | 73.1689 | 89.8753 | 103.2501 | 114.1175 | 124.5715 | 133.6197 | 138.1775 | 144.8736 | 152.5306 | 160.3515 | 170.1752 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296 | 171.7296
70% | 1813.0773 | 1856.5133 | 2080.731 | 42.6654 | 122.7534 | 199.0556 | 247.6001 | 302.9923 | 347.2535 | 376.184 | 444.8066 | 492.3121 | 517.4136 | 563.7768 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 | 550.4657 |  | 379.4436 | 390.3953 | 432.2261 | 51.7601 | 69.6212 | 83.9206 | 95.5392 | 106.7158 | 116.3895 | 121.2623 | 128.4213 | 136.6075 | 144.9691 | 155.4718 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337 | 157.1337
65% | 3310.6471 | 3389.9605 | 3799.3781 |  | 11.0262 | 79.8024 | 154.0865 | 255.0147 | 335.835 | 388.6616 | 513.9651 | 600.7094 | 646.5443 | 731.2026 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 | 706.8969 |  | 1000.946 | 1029.8359 | 1140.1826 | 56.3791 | 103.4956 | 141.2163 | 171.8654 | 201.3485 | 226.867 | 239.7213 | 258.606 | 280.2009 | 302.2582 | 329.9635 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474 | 334.3474
60% | 6433.7346 | 6587.868 | 7383.5083 |  |  |  |  | 22.5626 | 80.9935 | 137.7814 | 328.1238 | 495.0609 | 584.1339 | 748.6544 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 | 701.42 |  | 1117.614 | 1149.8713 | 1273.0797 | 0.84409 | 20.6098 | 53.9337 | 88.0733 | 120.9929 | 149.4858 | 163.8383 | 184.9243 | 209.0361 | 233.6644 | 264.599 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938 | 269.4938
55% | 7457.3163 | 7635.9717 | 8558.1952 | [8 empty] | 10.3571 | 31.8625 | 101.3744 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 | 77.545 |  | 1818.1672 | 1870.6442 | 2071.0832 |  |  |  | 6.0197 | 26.2071 | 54.4783 | 72.3303 | 102.7689 | 141.787 | 181.853 | 232.1783 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414 | 240.1414
50% | FY25: 8773.1422; FY26: 8983.321; FY27: 10068.2687 |  | 3171.2979 | 3262.8298 | 3612.4412 | [8 empty] | 3.2543 | 18.0873 | 52.963 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789 | 60.0789
45% | FY25: 15608.1674; FY26: 15982.0933; FY27: 17912.3076 |  | 6318.6081 | 6500.9794 | 7197.5577
40% | FY25: 17870.5156; FY26: 18298.6407; FY27: 20508.6327 |  | 10760.1697 | 11070.7361 | 12256.9625
35% | FY25: 10839.207; FY26: 11098.8826; FY27: 12439.3342 |  | 13027.0181 | 13403.0116 | 14839.1407
30% | FY25: 4492.2249; FY26: 4599.8454; FY27: 5155.3852 |  | 19901.1621 | 20475.5611 | 22669.5121
25% | FY25: 2681.5709; FY26: 2745.8134; FY27: 3077.4351 |  | 16923.4022 | 17411.8554 | 19277.5311
20% | FY25: 2852.6525; FY26: 2920.9937; FY27: 3273.7725 |  | 4489.5373 | 4619.117 | 5114.0541
15% | FY25: 2954.9137; FY26: 3025.7048; FY27: 3391.1299 |  | 2782.0412 | 2862.3381 | 3169.0368
10% | FY25: 1970.104; FY26: 2017.3019; FY27: 2260.9387 |  | 795.9593 | 818.9327 | 906.6811
5% | FY25: 157.0267; FY26: 160.7886; FY27: 180.2077 |  | 0 | 0 | 0
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 89607.7949 | 91754.5348 | 102836.0568 | 404.9789 | 608.5733 | 854.3803 | 1041.2939 | 1293.3017 | 1535.2447 | 1711.9817 | 2186.8407 | 2561.0983 | 2775.75 | 3202.0092 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | 3075.7565 | E @ R (MWh) | 84110.3229 | 86537.9646 | 95810.4847 | 600.3605 | 761.5938 | 908.1742 | 1040.3576 | 1181.9879 | 1315.3714 | 1386.1709 | 1494.397 | 1625.6198 | 1771.3742 | 1970.6952 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317 | 2003.8317
Option 4 Summer POE50 W E @ R (MWh) N 2 | 62725.4564 | 64228.1743 | 71985.2398 | 283.4852 | 426.0013 | 598.0662 | 728.9057 | 905.3112 | 1074.6713 | 1198.3872 | 1530.7885 | 1792.7688 | 1943.025 | 2241.4064 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | 2153.0295 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 25233.0969 | 25961.3894 | 28743.1454 | 180.1082 | 228.4781 | 272.4523 | 312.1073 | 354.5964 | 394.6114 | 415.8513 | 448.3191 | 487.6859 | 531.4123 | 591.2086 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495 | 601.1495
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 40.2458 | 41.8786 | 47.6412 | 46.0633 | 35.8204 | 37.7143 | 39.8978 | 41.5326 | 43.3336 | 44.2802 | 45.0997 | 47.1232 | 45.9094 | 49.207 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 | 53.5073 |  | 42.8352 | 44.5416 | 50.2595 | 48.865 | 38.6312 | 40.7636 | 42.7925 | 44.5218 | 46.322 | 47.1139 | 48.1922 | 50.1883 | 49.5413 | 52.1473 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521 | 53.6521
98% | 119.5239 | 124.3732 | 141.4873 | 136.8011 | 106.3811 | 112.0058 | 118.4904 | 123.3457 | 128.6944 | 131.5055 | 133.9394 | 139.9487 | 136.3441 | 146.1373 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 | 158.9085 |  | 127.2142 | 132.2818 | 149.263 | 145.1216 | 114.7287 | 121.0617 | 127.0874 | 132.2231 | 137.5693 | 139.9211 | 143.1236 | 149.0518 | 147.13 | 154.8697 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386 | 159.3386
97% | 52.5824 | 54.7158 | 62.2448 | 60.1832 | 46.8005 | 49.275 | 52.1278 | 54.2637 | 56.6168 | 57.8535 | 58.9243 | 61.568 | 59.9822 | 64.2905 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 | 69.909 |  | 55.9656 | 58.195 | 65.6656 | 63.8437 | 50.4729 | 53.2589 | 55.9099 | 58.1692 | 60.5212 | 61.5558 | 62.9647 | 65.5727 | 64.7273 | 68.1322 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982 | 70.0982
95% | 129.4337 | 134.685 | 153.2181 | 148.1433 | 115.2012 | 121.2923 | 128.3145 | 133.5723 | 139.3645 | 142.4087 | 145.0443 | 151.5519 | 147.6485 | 158.2536 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 | 172.0837 |  | 137.7615 | 143.2493 | 161.6385 | 157.1536 | 124.2409 | 131.099 | 137.6243 | 143.1858 | 148.9752 | 151.522 | 154.99 | 161.4097 | 159.3286 | 167.71 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494 | 172.5494
90% | 1321.9761 | 1375.6113 | 1564.8992 | 1513.0675 | 1176.6126 | 1238.8238 | 1310.5453 | 1364.2462 | 1423.405 | 1454.4967 | 1481.4163 | 1547.882 | 1508.0136 | 1616.3296 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 | 1757.5836 |  | 1407.0332 | 1463.083 | 1650.9011 | 1605.0952 | 1268.9395 | 1338.9846 | 1405.6311 | 1462.4337 | 1521.5646 | 1547.5766 | 1582.9973 | 1648.5647 | 1627.3098 | 1712.9134 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406 | 1762.3406
85% | 3114.4974 | 3240.8588 | 3686.8101 | 3564.6975 | 2772.0297 | 2918.5955 | 3087.5672 | 3214.0833 | 3353.4581 | 3426.7082 | 3490.1292 | 3646.7184 | 3552.7909 | 3807.9769 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 | 4140.763 |  | 3314.8869 | 3446.937 | 3889.4254 | 3781.5094 | 2989.5464 | 3154.5686 | 3311.5837 | 3445.4074 | 3584.7163 | 3645.999 | 3729.4479 | 3883.921 | 3833.8456 | 4035.5225 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703 | 4151.9703
80% | 5639.4649 | 5868.2694 | 6675.7596 | 6454.6487 | 5019.3538 | 5284.7425 | 5590.7021 | 5819.7865 | 6072.1545 | 6204.7896 | 6319.6269 | 6603.1651 | 6433.0892 | 6895.1581 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 | 7497.7387 |  | 6002.313 | 6241.4181 | 7042.6381 | 6847.2332 | 5413.2144 | 5712.0224 | 5996.3319 | 6238.6484 | 6490.897 | 6601.8625 | 6752.9646 | 7032.6712 | 6941.999 | 7307.1783 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319 | 7518.0319
75% | 6593.364 | 6860.8701 | 7804.945 | 7546.4338 | 5868.3629 | 6178.6414 | 6536.3531 | 6804.1864 | 7099.2417 | 7254.3117 | 7388.5734 | 7720.0713 | 7521.2276 | 8061.454 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 | 8765.9594 |  | 7017.5868 | 7297.1358 | 8233.8799 | 8005.4228 | 6328.8439 | 6678.1943 | 7010.594 | 7293.8976 | 7588.8133 | 7718.5483 | 7895.209 | 8222.2271 | 8116.2179 | 8543.1663 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852 | 8789.6852
70% | 7731.9758 | 8045.6776 | 9152.7853 | 8849.6317 | 6881.7738 | 7245.6344 | 7665.1196 | 7979.2052 | 8325.2138 | 8507.0628 | 8664.5103 | 9053.2547 | 8820.0726 | 9453.591 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 | 10279.7579 |  | 8229.4578 | 8557.2822 | 9655.7932 | 9387.8837 | 7421.7755 | 7831.4555 | 8221.2574 | 8553.4848 | 8899.3297 | 9051.4688 | 9258.637 | 9642.1281 | 9517.8121 | 10018.4904 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808 | 10307.5808
65% | 8472.8486 | 8816.6091 | 10029.7992 | 9697.5976 | 7541.1809 | 7939.9063 | 8399.5863 | 8743.7674 | 9122.9303 | 9322.204 | 9494.738 | 9920.7317 | 9665.2061 | 10359.428 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 | 11264.7576 |  | 9017.9991 | 9377.2354 | 10581.005 | 10287.4246 | 8132.9251 | 8581.8604 | 9009.0129 | 9373.0742 | 9752.0577 | 9918.7746 | 10145.7935 | 10566.0305 | 10429.8026 | 10978.4557 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465 | 11295.2465
60% | 9218.7775 | 9592.8018 | 10912.7982 | 10551.3504 | 8205.088 | 8638.9163 | 9139.0654 | 9513.5473 | 9926.0908 | 10142.908 | 10330.6315 | 10794.1286 | 10516.1073 | 11271.4467 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 | 12256.4793 |  | 9811.9216 | 10202.7843 | 11512.5308 | 11193.1043 | 8848.928 | 9337.3864 | 9802.1444 | 10198.2567 | 10610.605 | 10791.9992 | 11039.0044 | 11496.238 | 11348.017 | 11944.972 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523 | 12289.6523
55% | 9241.0239 | 9615.9508 | 10939.1325 | 10576.8125 | 8224.8882 | 8659.7634 | 9161.1194 | 9536.5051 | 9950.044 | 10167.3845 | 10355.561 | 10820.1766 | 10541.4843 | 11298.6465 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 | 12286.0561 |  | 9835.5994 | 10227.4053 | 11540.3124 | 11220.115 | 8870.2819 | 9359.919 | 9825.7986 | 10222.8668 | 10636.2101 | 10818.0421 | 11065.6433 | 11523.9803 | 11375.4016 | 11973.7972 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093 | 12319.3093
50% | 10886.5841 | 11328.2747 | 12887.077 | 12460.2382 | 9689.5039 | 10201.8178 | 10792.4509 | 11234.682 | 11721.8603 | 11977.9029 | 12199.5881 | 12746.9384 | 12418.6191 | 13310.61 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 | 14473.8489 |  | 11587.0364 | 12048.6116 | 13595.3097 | 13218.0944 | 10449.8236 | 11026.651 | 11575.4903 | 12043.2649 | 12530.2128 | 12744.4238 | 13036.1157 | 13576.0693 | 13401.033 | 14105.9856 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235 | 14513.0235
45% | 13615.4771 | 14167.8844 | 16117.4248 | 15583.5922 | 12118.33 | 12759.0634 | 13497.7479 | 14050.8311 | 14660.1284 | 14980.352 | 15257.6062 | 15942.1584 | 15531.5406 | 16647.1231 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 | 18101.946 |  | 14491.5087 | 15068.7849 | 17003.1872 | 16531.4169 | 13069.2357 | 13790.654 | 14477.0684 | 15062.098 | 15671.1071 | 15939.0134 | 16303.8224 | 16979.1239 | 16760.212 | 17641.8721 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403 | 18150.9403
40% | 14417.022 | 15001.9495 | 17066.2597 | 16501.0003 | 12831.7376 | 13510.1911 | 14292.3621 | 14878.0054 | 15523.172 | 15862.2473 | 16155.8234 | 16880.6753 | 16445.8844 | 17627.1414 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 | 19167.6099 |  | 15344.6257 | 15955.8863 | 18004.167 | 17504.6236 | 13838.6233 | 14602.5116 | 15329.3353 | 15948.8057 | 16593.6672 | 16877.3452 | 17263.6306 | 17978.6871 | 17746.8878 | 18680.4513 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885 | 19219.4885
35% | 5895.2987 | 6134.4828 | 6978.6047 | 6747.4632 | 5247.0563 | 5524.4843 | 5844.3237 | 6083.8005 | 6347.6171 | 6486.2692 | 6606.3161 | 6902.717 | 6724.9256 | 7207.9562 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 | 7837.8728 |  | 6274.6073 | 6524.5593 | 7362.1266 | 7157.8572 | 5658.7843 | 5971.1476 | 6268.3549 | 6521.664 | 6785.3558 | 6901.3553 | 7059.3121 | 7351.7076 | 7256.922 | 7638.6677 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866 | 7859.0866
30% | 1818.4755 | 1892.2547 | 2152.6342 | 2081.3358 | 1618.5174 | 1704.0934 | 1802.7516 | 1876.6211 | 1957.9985 | 2000.7674 | 2037.7973 | 2129.2257 | 2074.3839 | 2223.3804 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 | 2417.6858 |  | 1935.4778 | 2012.5785 | 2270.9361 | 2207.9268 | 1745.5198 | 1841.872 | 1933.5491 | 2011.6854 | 2093.0243 | 2128.8057 | 2177.5294 | 2267.7223 | 2238.4845 | 2356.2385 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294 | 2424.2294
25% | 1338.4923 | 1392.7977 | 1584.4505 | 1531.9712 | 1191.3128 | 1254.3012 | 1326.9188 | 1381.2905 | 1441.1885 | 1472.6687 | 1499.9246 | 1567.2206 | 1526.8542 | 1636.5234 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 | 1779.5422 |  | 1424.6121 | 1481.3622 | 1671.5269 | 1625.1487 | 1284.7932 | 1355.7134 | 1423.1925 | 1480.7048 | 1540.5745 | 1566.9115 | 1602.7746 | 1669.1613 | 1647.6408 | 1734.3139 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587 | 1784.3587
20% | 1064.7941 | 1107.9949 | 1260.4581 | 1218.7099 | 947.7102 | 997.8185 | 1055.5871 | 1098.8408 | 1146.4907 | 1171.5337 | 1193.2163 | 1246.7515 | 1214.6392 | 1301.883 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 | 1415.657 |  | 1133.3039 | 1178.4496 | 1329.7289 | 1292.8342 | 1022.0754 | 1078.4937 | 1132.1746 | 1177.9266 | 1225.554 | 1246.5055 | 1275.0353 | 1327.847 | 1310.7271 | 1379.677 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885 | 1419.4885
15% | 835.2516 | 869.1394 | 988.7354 | 955.9871 | 743.408 | 782.7142 | 828.0294 | 861.9587 | 899.3365 | 918.9808 | 935.9892 | 977.9836 | 952.7939 | 1021.2302 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 | 1110.4774 |  | 888.9924 | 924.4058 | 1043.0732 | 1014.1321 | 801.742 | 845.9979 | 888.1065 | 923.9956 | 961.3557 | 977.7906 | 1000.1701 | 1041.597 | 1028.1677 | 1082.2538 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829 | 1113.4829
10% | 586.4963 | 610.2916 | 694.2694 | 671.2742 | 522.0056 | 549.6056 | 581.425 | 605.2494 | 631.4954 | 645.2892 | 657.2321 | 686.7197 | 669.0321 | 717.0866 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 | 779.7541 |  | 624.2319 | 649.0985 | 732.4243 | 712.1024 | 562.9665 | 594.0421 | 623.6099 | 648.8105 | 675.044 | 686.5842 | 702.2986 | 731.3877 | 721.9579 | 759.9361 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645 | 781.8645
5% | 60.672 | 63.1336 | 71.821 | 69.4422 | 54.0006 | 56.8558 | 60.1474 | 62.612 | 65.3271 | 66.7541 | 67.9895 | 71.04 | 69.2102 | 74.1814 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 | 80.6642 |  | 64.5757 | 67.1481 | 75.768 | 73.6658 | 58.2379 | 61.4526 | 64.5114 | 67.1183 | 69.8321 | 71.026 | 72.6516 | 75.6608 | 74.6853 | 78.6141 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825 | 80.8825
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102194.2775 | 106340.5049 | 120973.2554 | 116966.4448 | 90957.0754 | 95766.2561 | 101310.6328 | 105461.9332 | 110035.1621 | 112438.6786 | 114519.6771 | 119657.7503 | 116575.7591 | 124949.0348 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | 135868.5622 | E @ R (MWh) | 108769.5462 | 113102.4335 | 127621.5603 | 124080.5741 | 98094.3301 | 103509.1105 | 108661.1609 | 113052.2433 | 117623.3091 | 119634.1452 | 122372.308 | 127440.9473 | 125797.8508 | 132415.3652 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008 | 136236.3008
Option 5 Winter POE50 W E @ R (MWh) N 2 | 71535.9943 | 74438.3534 | 84681.2788 | 81876.5114 | 63669.9528 | 67036.3793 | 70917.4429 | 73823.3533 | 77024.6135 | 78707.075 | 80163.774 | 83760.4252 | 81603.0314 | 87464.3243 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | 95107.9936 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 32630.8639 | 33930.7301 | 38286.4681 | 37224.1722 | 29428.299 | 31052.7331 | 32598.3483 | 33915.673 | 35286.9927 | 35890.2436 | 36711.6924 | 38232.2842 | 37739.3552 | 39724.6096 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902 | 40870.8902
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43.3961 | 44.6487 | 49.4328 | 47.3811 | 38.5119 | 40.1473 | 41.4761 | 42.7544 | 43.8607 | 44.418 | 45.2368 | 46.173 | 47.1293 | 48.3305 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205 | 48.5205
98% | 19.0952 | 19.5527 | 21.9141 | 20.9178 | 16.4141 | 17.2177 | 17.729 | 18.3123 | 18.7785 | 19.0832 | 19.8059 | 20.3062 | 20.5706 | 21.0589 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 | 20.9187 |  | 21.48 | 22.1 | 24.468 | 23.4525 | 19.0624 | 19.8719 | 20.5296 | 21.1623 | 21.71 | 21.9858 | 22.3911 | 22.8545 | 23.3278 | 23.9224 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165 | 24.0165
97% | 18.9014 | 19.3542 | 21.6917 | 20.7055 | 16.2474 | 17.0429 | 17.549 | 18.1264 | 18.5879 | 18.8895 | 19.6048 | 20.1001 | 20.3618 | 20.8451 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 | 20.7063 |  | 42.5239 | 43.7512 | 48.4391 | 46.4287 | 37.7378 | 39.3403 | 40.6424 | 41.895 | 42.9791 | 43.5252 | 44.3275 | 45.2449 | 46.182 | 47.359 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453 | 47.5453
95% | 55.8317 | 57.1693 | 64.0738 | 61.1608 | 47.9924 | 50.3421 | 51.8369 | 53.5427 | 54.9057 | 55.7965 | 57.9097 | 59.3726 | 60.1455 | 61.5732 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 | 61.1634 |  | 83.7393 | 86.1562 | 95.3878 | 91.4289 | 74.3145 | 77.4702 | 80.0343 | 82.5009 | 84.6358 | 85.7112 | 87.2911 | 89.0977 | 90.943 | 93.2608 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276 | 93.6276
90% | 125.5245 | 128.5317 | 144.0549 | 137.5056 | 107.8996 | 113.1822 | 116.5431 | 120.3781 | 123.4424 | 125.4453 | 130.1963 | 133.4852 | 135.2231 | 138.4329 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 | 137.5114 |  | 302.5736 | 311.3066 | 344.663 | 330.3584 | 268.5192 | 279.9217 | 289.1865 | 298.0989 | 305.8128 | 309.6985 | 315.4071 | 321.935 | 328.6026 | 336.9776 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028 | 338.3028
85% | 203.5532 | 208.4297 | 233.6025 | 222.9821 | 174.9724 | 183.5388 | 188.9888 | 195.2077 | 200.1769 | 203.4249 | 211.1291 | 216.4625 | 219.2806 | 224.4858 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 | 222.9914 |  | 362.5431 | 373.007 | 412.9746 | 395.8348 | 321.7392 | 335.4016 | 346.5028 | 357.1816 | 366.4244 | 371.0802 | 377.9203 | 385.7419 | 393.7311 | 403.766 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538 | 405.3538
80% | 783.6798 | 802.4544 | 899.3697 | 858.481 | 673.6436 | 706.6242 | 727.607 | 751.5495 | 770.6809 | 783.1858 | 812.847 | 833.3807 | 844.2304 | 864.2703 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 | 858.5168 |  | 413.7898 | 425.7328 | 471.35 | 451.7874 | 367.2181 | 382.8118 | 395.4821 | 407.6704 | 418.2197 | 423.5336 | 431.3406 | 440.2678 | 449.3863 | 460.8397 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519 | 462.6519
75% | 1186.9089 | 1215.3438 | 1362.1252 | 1300.1978 | 1020.2555 | 1070.2058 | 1101.9848 | 1138.2466 | 1167.2217 | 1186.1607 | 1231.0836 | 1262.1826 | 1278.6149 | 1308.966 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 | 1300.2521 |  | 354.9106 | 365.1542 | 404.2804 | 387.5015 | 314.9658 | 328.3406 | 339.208 | 349.662 | 358.7102 | 363.268 | 369.9641 | 377.621 | 385.442 | 395.2656 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82 | 396.82
70% | 1813.0773 | 1856.5133 | 2080.731 | 1986.1331 | 1558.5038 | 1634.8059 | 1683.3504 | 1738.7426 | 1783.0039 | 1811.9344 | 1880.5569 | 1928.0625 | 1953.1639 | 1999.5271 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 | 1986.2161 |  | 379.4436 | 390.3953 | 432.2261 | 414.2873 | 336.7376 | 351.0369 | 362.6555 | 373.8321 | 383.5058 | 388.3787 | 395.5376 | 403.7239 | 412.0855 | 422.5881 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25 | 424.25
65% | 3310.6471 | 3389.9605 | 3799.3781 | 3626.644 | 2845.8004 | 2985.1268 | 3073.7682 | 3174.9133 | 3255.7336 | 3308.5602 | 3433.8638 | 3520.6081 | 3566.4429 | 3651.1012 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 | 3626.7955 |  | 1000.946 | 1029.8359 | 1140.1826 | 1092.8613 | 888.2905 | 926.0112 | 956.6603 | 986.1434 | 1011.6619 | 1024.5162 | 1043.4009 | 1064.9957 | 1087.053 | 1114.7584 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423 | 1119.1423
60% | 6433.7346 | 6587.868 | 7383.5083 | 7047.826 | 5530.3762 | 5801.1357 | 5973.3967 | 6169.9568 | 6327.0186 | 6429.679 | 6673.1871 | 6841.7614 | 6930.8343 | 7095.3548 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 | 7048.1204 |  | 1117.614 | 1149.8713 | 1273.0797 | 1220.2427 | 991.8276 | 1033.9449 | 1068.1664 | 1101.086 | 1129.5789 | 1143.9315 | 1165.0174 | 1189.1292 | 1213.7575 | 1244.6921 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869 | 1249.5869
55% | 7457.3163 | 7635.9717 | 8558.1952 | 8169.1073 | 6410.2372 | 6724.0735 | 6923.7405 | 7151.5725 | 7333.6222 | 7452.6155 | 7734.8648 | 7930.2586 | 8033.5027 | 8224.1977 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 | 8169.4485 |  | 1818.1672 | 1870.6442 | 2071.0832 | 1985.1265 | 1613.5342 | 1682.0519 | 1737.7244 | 1791.279 | 1837.6321 | 1860.9812 | 1895.2844 | 1934.5102 | 1974.5762 | 2024.9015 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646 | 2032.8646
50% | 8773.1422 | 8983.321 | 10068.2687 | 9610.5271 | 7541.3085 | 7910.5204 | 8145.4182 | 8413.4507 | 8627.6226 | 8767.612 | 9099.6635 | 9329.5341 | 9450.9953 | 9675.3381 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 | 9610.9285 |  | 3171.2979 | 3262.8298 | 3612.4412 | 3462.513 | 2814.3714 | 2933.8818 | 3030.9874 | 3124.3988 | 3205.2491 | 3245.9753 | 3305.8078 | 3374.2267 | 3444.1109 | 3531.8897 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791 | 3545.7791
45% | 15608.1674 | 15982.0933 | 17912.3076 | 17097.9463 | 13416.6301 | 14073.4897 | 14491.3929 | 14968.2454 | 15349.2755 | 15598.3285 | 16189.0766 | 16598.0358 | 16814.1258 | 17213.2506 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 | 17098.6606 |  | 6318.6081 | 6500.9794 | 7197.5577 | 6898.8355 | 5607.4548 | 5845.5716 | 6039.0483 | 6225.1645 | 6386.2536 | 6467.3978 | 6586.6104 | 6722.9307 | 6862.1704 | 7037.0641 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378 | 7064.7378
40% | 17870.5156 | 18298.6407 | 20508.6327 | 19576.2327 | 15361.3229 | 16113.3919 | 16591.8686 | 17137.8392 | 17574.0983 | 17859.2507 | 18535.6255 | 19003.862 | 19251.2734 | 19708.25 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 | 19577.0505 |  | 10760.1697 | 11070.7361 | 12256.9625 | 11748.2585 | 9549.123 | 9954.6201 | 10284.098 | 10601.0416 | 10875.3656 | 11013.5488 | 11216.56 | 11448.7043 | 11685.8203 | 11983.6526 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792 | 12030.7792
35% | 10839.207 | 11098.8826 | 12439.3342 | 11873.795 | 9317.2778 | 9773.4388 | 10063.6547 | 10394.8085 | 10659.4177 | 10832.3744 | 11242.6237 | 11526.6285 | 11676.6938 | 11953.869 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 | 11874.2911 |  | 13027.0181 | 13403.0116 | 14839.1407 | 14223.2678 | 11560.8397 | 12051.763 | 12450.6522 | 12834.3664 | 13166.4823 | 13333.7766 | 13579.5562 | 13860.6064 | 14147.6757 | 14508.2525 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072 | 14565.3072
30% | 4492.2249 | 4599.8454 | 5155.3852 | 4921.0018 | 3861.4732 | 4050.5256 | 4170.8033 | 4308.0474 | 4417.7126 | 4489.3932 | 4659.4178 | 4777.1214 | 4839.3148 | 4954.1879 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 | 4921.2074 |  | 19901.1621 | 20475.5611 | 22669.5121 | 21728.6531 | 17661.3054 | 18411.2809 | 19020.6574 | 19606.8512 | 20114.2193 | 20369.7921 | 20745.2655 | 21174.6213 | 21613.1724 | 22164.0196 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812 | 22251.1812
25% | 2681.5709 | 2745.8134 | 3077.4351 | 2937.5233 | 2305.0525 | 2417.9046 | 2489.7027 | 2571.6287 | 2637.0918 | 2679.8805 | 2781.3743 | 2851.6358 | 2888.7613 | 2957.3332 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 | 2937.646 |  | 16923.4022 | 17411.8554 | 19277.5311 | 18477.4504 | 15018.6896 | 15656.4481 | 16174.6452 | 16673.1283 | 17104.5802 | 17321.9123 | 17641.2046 | 18006.317 | 18379.2488 | 18847.6741 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794 | 18921.794
20% | 2852.6525 | 2920.9937 | 3273.7725 | 3124.9344 | 2452.1126 | 2572.1646 | 2648.5433 | 2735.6961 | 2805.3357 | 2850.8543 | 2958.8233 | 3033.5674 | 3073.0615 | 3146.0082 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 | 3125.0649 |  | 4489.5373 | 4619.117 | 5114.0541 | 4901.8041 | 3984.2442 | 4153.4324 | 4290.9027 | 4423.1432 | 4537.6012 | 4595.2563 | 4679.96 | 4776.8192 | 4875.7526 | 5000.0192 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822 | 5019.6822
15% | 2954.9137 | 3025.7048 | 3391.1299 | 3236.9563 | 2540.0153 | 2664.371 | 2743.4877 | 2833.7647 | 2905.9007 | 2953.051 | 3064.8905 | 3142.3141 | 3183.2239 | 3258.7856 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 | 3237.0916 |  | 2782.0412 | 2862.3381 | 3169.0368 | 3037.5114 | 2468.9251 | 2573.7663 | 2658.9528 | 2740.8986 | 2811.825 | 2847.5523 | 2900.0408 | 2960.0617 | 3021.368 | 3098.3726 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571 | 3110.5571
10% | 1970.104 | 2017.3019 | 2260.9387 | 2158.1479 | 1693.4824 | 1776.393 | 1829.1418 | 1889.3314 | 1937.426 | 1968.8621 | 2043.4279 | 2095.0478 | 2122.3233 | 2172.7019 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 | 2158.238 |  | 795.9593 | 818.9327 | 906.6811 | 869.0509 | 706.3748 | 736.3705 | 760.7429 | 784.1881 | 804.4806 | 814.7024 | 829.7197 | 846.892 | 864.4322 | 886.4636 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497 | 889.9497
5% | 157.0267 | 160.7886 | 180.2077 | 172.0147 | 134.9787 | 141.587 | 145.7914 | 150.5888 | 154.4221 | 156.9278 | 162.871 | 166.9854 | 169.1593 | 173.1748 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 | 172.0219 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 89607.7949 | 91754.5348 | 102836.0568 | 98160.7405 | 77025.9964 | 80797.082 | 83196.2991 | 85933.9495 | 88121.4752 | 89551.3094 | 92942.8434 | 95290.7127 | 96531.3032 | 98822.7123 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | 98164.8411 | E @ R (MWh) | 84110.3229 | 86537.9646 | 95810.4847 | 91834.0358 | 74643.787 | 77813.4851 | 80388.9556 | 82866.4468 | 85010.7885 | 86090.9419 | 87677.8437 | 89492.4743 | 91345.9677 | 93674.0698 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498 | 94042.4498
Option 5 Summer POE50 W E @ R (MWh) N 2 | 62725.4564 | 64228.1743 | 71985.2398 | 68712.5183 | 53918.1975 | 56557.9574 | 58237.4093 | 60153.7646 | 61685.0327 | 62685.9166 | 65059.9904 | 66703.4989 | 67571.9123 | 69175.8986 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | 68715.3888 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 25233.0969 | 25961.3894 | 28743.1454 | 27550.2107 | 22393.1361 | 23344.0455 | 24116.6867 | 24859.934 | 25503.2366 | 25827.2826 | 26303.3531 | 26847.7423 | 27403.7903 | 28102.2209 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349 | 28212.7349
Option 6 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 40.2458 | 41.8786 | 47.6412 | 52.495 | 55.1156 | 57.0096 | 59.193 | 60.8279 | 62.6289 | 63.5754 | 64.395 | 66.4184 | 65.2047 | 68.5022 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 |  | 42.8352 | 44.5416 | 50.2595 | 55.2967 | 57.9264 | 60.0588 | 62.0878 | 63.8171 | 65.6172 | 66.4091 | 67.4875 | 69.4836 | 68.8365 | 71.4426 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473
98% | 119.5239 | 124.3732 | 141.4873 | 155.9024 | 163.6851 | 169.3098 | 175.7944 | 180.6496 | 185.9984 | 188.8095 | 191.2433 | 197.2527 | 193.6481 | 203.4413 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 |  | 127.2142 | 132.2818 | 149.263 | 164.2229 | 172.0327 | 178.3657 | 184.3914 | 189.5271 | 194.8733 | 197.2251 | 200.4276 | 206.3557 | 204.434 | 212.1737 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426
97% | 52.5824 | 54.7158 | 62.2448 | 68.5865 | 72.0104 | 74.4849 | 77.3376 | 79.4736 | 81.8267 | 83.0634 | 84.1341 | 86.7778 | 85.1921 | 89.5004 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 |  | 55.9656 | 58.195 | 65.6656 | 72.247 | 75.6827 | 78.4688 | 81.1197 | 83.3791 | 85.7311 | 86.7657 | 88.1746 | 90.7826 | 89.9371 | 93.3421 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081
95% | 129.4337 | 134.685 | 153.2181 | 168.8283 | 177.2563 | 183.3473 | 190.3695 | 195.6273 | 201.4195 | 204.4637 | 207.0994 | 213.607 | 209.7035 | 220.3086 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 |  | 137.7615 | 143.2493 | 161.6385 | 177.8387 | 186.2959 | 193.154 | 199.6793 | 205.2408 | 211.0303 | 213.5771 | 217.0451 | 223.4648 | 221.3837 | 229.7651 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045
90% | 1321.9761 | 1375.6113 | 1564.8992 | 1724.3348 | 1810.4145 | 1872.6256 | 1944.3472 | 1998.0481 | 2057.2069 | 2088.2986 | 2115.2182 | 2181.6839 | 2141.8155 | 2250.1315 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 |  | 1407.0332 | 1463.083 | 1650.9011 | 1816.3625 | 1902.7414 | 1972.7865 | 2039.433 | 2096.2356 | 2155.3665 | 2181.3785 | 2216.7992 | 2282.3666 | 2261.1117 | 2346.7152 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425
85% | 3114.4974 | 3240.8588 | 3686.8101 | 4062.4308 | 4265.2295 | 4411.7952 | 4580.767 | 4707.283 | 4846.6578 | 4919.908 | 4983.329 | 5139.9182 | 5045.9907 | 5301.1766 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 |  | 3314.8869 | 3446.937 | 3889.4254 | 4279.2427 | 4482.7462 | 4647.7683 | 4804.7835 | 4938.6071 | 5077.916 | 5139.1988 | 5222.6477 | 5377.1207 | 5327.0453 | 5528.7223 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701
80% | 5639.4649 | 5868.2694 | 6675.7596 | 7355.9015 | 7723.112 | 7988.5007 | 8294.4602 | 8523.5446 | 8775.9126 | 8908.5477 | 9023.385 | 9306.9232 | 9136.8474 | 9598.9162 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 |  | 6002.313 | 6241.4181 | 7042.6381 | 7748.4859 | 8116.9725 | 8415.7805 | 8700.09 | 8942.4065 | 9194.6551 | 9305.6206 | 9456.7228 | 9736.4294 | 9645.7571 | 10010.9365 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901
75% | 6593.364 | 6860.8701 | 7804.945 | 8600.1308 | 9029.4539 | 9339.7323 | 9697.4441 | 9965.2774 | 10260.3327 | 10415.4026 | 10549.6644 | 10881.1622 | 10682.3185 | 11222.545 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 |  | 7017.5868 | 7297.1358 | 8233.8799 | 9059.1197 | 9489.9348 | 9839.2853 | 10171.685 | 10454.9886 | 10749.9043 | 10879.6393 | 11056.2999 | 11383.3181 | 11277.3089 | 11704.2572 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761
70% | 7731.9758 | 8045.6776 | 9152.7853 | 10085.2922 | 10588.7553 | 10952.6159 | 11372.1011 | 11686.1867 | 12032.1953 | 12214.0443 | 12371.4918 | 12760.2362 | 12527.0541 | 13160.5726 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 |  | 8229.4578 | 8557.2822 | 9655.7932 | 10623.5442 | 11128.757 | 11538.437 | 11928.2389 | 12260.4664 | 12606.3113 | 12758.4503 | 12965.6185 | 13349.1096 | 13224.7936 | 13725.472 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623
65% | 8472.8486 | 8816.6091 | 10029.7992 | 11051.6583 | 11603.3629 | 12002.0884 | 12461.7684 | 12805.9495 | 13185.1124 | 13384.3861 | 13556.92 | 13982.9137 | 13727.3882 | 14421.61 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 |  | 9017.9991 | 9377.2354 | 10581.005 | 11641.4852 | 12195.1072 | 12644.0425 | 13071.195 | 13435.2562 | 13814.2398 | 13980.9566 | 14207.9756 | 14628.2126 | 14491.9847 | 15040.6377 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285
60% | 9218.7775 | 9592.8018 | 10912.7982 | 12024.6193 | 12624.8946 | 13058.7229 | 13558.872 | 13933.354 | 14345.8974 | 14562.7147 | 14750.4381 | 15213.9352 | 14935.9139 | 15691.2533 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 |  | 9811.9216 | 10202.7843 | 11512.5308 | 12666.3731 | 13268.7346 | 13757.193 | 14221.951 | 14618.0633 | 15030.4117 | 15211.8059 | 15458.811 | 15916.0446 | 15767.8236 | 16364.7787 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459
55% | 9241.0239 | 9615.9508 | 10939.1325 | 12053.6366 | 12655.3606 | 13090.2357 | 13591.5918 | 13966.9774 | 14380.5164 | 14597.8569 | 14786.0333 | 15250.6489 | 14971.9567 | 15729.1189 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 |  | 9835.5994 | 10227.4053 | 11540.3124 | 12696.9392 | 13300.7542 | 13790.3914 | 14256.2709 | 14653.3391 | 15066.6825 | 15248.5144 | 15496.1157 | 15954.4526 | 15805.8739 | 16404.2696 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816
50% | 10886.5841 | 11328.2747 | 12887.077 | 14200.0421 | 14908.9158 | 15421.2297 | 16011.8628 | 16454.0938 | 16941.2722 | 17197.3148 | 17419 | 17966.3503 | 17638.031 | 18530.0219 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 |  | 11587.0364 | 12048.6116 | 13595.3097 | 14957.8983 | 15669.2355 | 16246.0629 | 16794.9022 | 17262.6768 | 17749.6247 | 17963.8357 | 18255.5276 | 18795.4812 | 18620.4449 | 19325.3975 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353
45% | 13615.4771 | 14167.8844 | 16117.4248 | 17759.5053 | 18646.0692 | 19286.8027 | 20025.4872 | 20578.5704 | 21187.8676 | 21508.0913 | 21785.3454 | 22469.8976 | 22059.2799 | 23174.8624 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 |  | 14491.5087 | 15068.7849 | 17003.1872 | 18707.33 | 19596.975 | 20318.3933 | 21004.8077 | 21589.8373 | 22198.8464 | 22466.7527 | 22831.5617 | 23506.8631 | 23287.9512 | 24169.6113 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796
40% | 14417.022 | 15001.9495 | 17066.2597 | 18805.0097 | 19743.7657 | 20422.2192 | 21204.3902 | 21790.0335 | 22435.2001 | 22774.2754 | 23067.8515 | 23792.7034 | 23357.9126 | 24539.1695 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 |  | 15344.6257 | 15955.8863 | 18004.167 | 19808.633 | 20750.6515 | 21514.5397 | 22241.3634 | 22860.8338 | 23505.6953 | 23789.3733 | 24175.6587 | 24890.7152 | 24658.9159 | 25592.4795 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166
35% | 5895.2987 | 6134.4828 | 6978.6047 | 7689.6011 | 8073.4701 | 8350.8981 | 8670.7375 | 8910.2143 | 9174.0309 | 9312.683 | 9432.7299 | 9729.1308 | 9551.3395 | 10034.37 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 |  | 6274.6073 | 6524.5593 | 7362.1266 | 8099.9951 | 8485.1981 | 8797.5615 | 9094.7687 | 9348.0778 | 9611.7696 | 9727.7691 | 9885.726 | 10178.1214 | 10083.3358 | 10465.0815 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005
30% | 1818.4755 | 1892.2547 | 2152.6342 | 2371.9496 | 2490.3586 | 2575.9346 | 2674.5928 | 2748.4623 | 2829.8397 | 2872.6086 | 2909.6385 | 3001.0669 | 2946.2251 | 3095.2216 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 |  | 1935.4778 | 2012.5785 | 2270.9361 | 2498.5405 | 2617.361 | 2713.7132 | 2805.3903 | 2883.5266 | 2964.8655 | 3000.6469 | 3049.3706 | 3139.5635 | 3110.3257 | 3228.0797 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706
25% | 1338.4923 | 1392.7977 | 1584.4505 | 1745.878 | 1833.0331 | 1896.0215 | 1968.6391 | 2023.0109 | 2082.9089 | 2114.389 | 2141.645 | 2208.941 | 2168.5746 | 2278.2438 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 |  | 1424.6121 | 1481.3622 | 1671.5269 | 1839.0555 | 1926.5135 | 1997.4338 | 2064.9129 | 2122.4252 | 2182.2949 | 2208.6319 | 2244.495 | 2310.8817 | 2289.3612 | 2376.0342 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079
20% | 1064.7941 | 1107.9949 | 1260.4581 | 1388.8765 | 1458.2099 | 1508.3183 | 1566.0869 | 1609.3406 | 1656.9905 | 1682.0335 | 1703.7161 | 1757.2512 | 1725.139 | 1812.3828 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 |  | 1133.3039 | 1178.4496 | 1329.7289 | 1463.0008 | 1532.5752 | 1588.9935 | 1642.6743 | 1688.4264 | 1736.0538 | 1757.0053 | 1785.5351 | 1838.3468 | 1821.2269 | 1890.1768 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883
15% | 835.2516 | 869.1394 | 988.7354 | 1089.4701 | 1143.857 | 1183.1633 | 1228.4784 | 1262.4077 | 1299.7855 | 1319.4299 | 1336.4382 | 1378.4326 | 1353.2429 | 1421.6792 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 |  | 888.9924 | 924.4058 | 1043.0732 | 1147.6151 | 1202.191 | 1246.447 | 1288.5556 | 1324.4446 | 1361.8048 | 1378.2397 | 1400.6191 | 1442.046 | 1428.6167 | 1482.7028 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932
10% | 586.4963 | 610.2916 | 694.2694 | 765.0032 | 803.1926 | 830.7926 | 862.612 | 886.4364 | 912.6823 | 926.4762 | 938.4191 | 967.9067 | 950.219 | 998.2735 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 |  | 624.2319 | 649.0985 | 732.4243 | 805.8314 | 844.1535 | 875.2291 | 904.7969 | 929.9974 | 956.2309 | 967.7712 | 983.4856 | 1012.5747 | 1003.1449 | 1041.123 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515
5% | 60.672 | 63.1336 | 71.821 | 79.1383 | 83.0889 | 85.9441 | 89.2357 | 91.7003 | 94.4154 | 95.8424 | 97.0778 | 100.1283 | 98.2985 | 103.2697 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 |  | 64.5757 | 67.1481 | 75.768 | 83.3619 | 87.3262 | 90.5409 | 93.5997 | 96.2066 | 98.9204 | 100.1143 | 101.7399 | 104.7491 | 103.7736 | 107.7024 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102194.2775 | 106340.5049 | 120973.2554 | 133298.2902 | 139952.6116 | 144761.7923 | 150306.169 | 154457.4695 | 159030.6983 | 161434.2148 | 163515.2133 | 168653.2865 | 165571.2953 | 173944.571 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | E @ R (MWh) | 108769.5462 | 113102.4335 | 127621.5603 | 140412.4195 | 147089.8663 | 152504.6467 | 157656.6971 | 162047.7795 | 166618.8453 | 168629.6814 | 171367.8442 | 176436.4835 | 174793.387 | 181410.9014 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837
Option 6 Winter POE50 W E @ R (MWh) N 2 | 71535.9943 | 74438.3534 | 84681.2788 | 93308.8031 | 97966.8281 | 101333.2546 | 105214.3183 | 108120.2286 | 111321.4888 | 113003.9503 | 114460.6493 | 118057.3006 | 115899.9067 | 121761.1997 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 32630.8639 | 33930.7301 | 38286.4681 | 42123.7258 | 44126.9599 | 45751.394 | 47297.0091 | 48614.3339 | 49985.6536 | 50588.9044 | 51410.3533 | 52930.9451 | 52438.0161 | 54423.2704 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43.3961 | 44.6487 | 49.4328 | 52.8371 | 54.8798 | 56.5152 | 57.844 | 59.1223 | 60.2286 | 60.7859 | 61.6047 | 62.5409 | 63.4972 | 64.6984 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884
98% | 19.0952 | 19.5527 | 21.9141 | 23.6184 | 24.5158 | 25.3194 | 25.8306 | 26.414 | 26.8802 | 27.1849 | 27.9076 | 28.4079 | 28.6723 | 29.1606 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 |  | 21.48 | 22.1 | 24.468 | 26.153 | 27.1641 | 27.9736 | 28.6313 | 29.264 | 29.8117 | 30.0875 | 30.4928 | 30.9562 | 31.4295 | 32.0241 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181
97% | 18.9014 | 19.3542 | 21.6917 | 23.3786 | 24.2669 | 25.0623 | 25.5684 | 26.1459 | 26.6073 | 26.9089 | 27.6243 | 28.1195 | 28.3812 | 28.8646 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 |  | 42.5239 | 43.7512 | 48.4391 | 51.775 | 53.7767 | 55.3792 | 56.6813 | 57.9339 | 59.018 | 59.5641 | 60.3664 | 61.2838 | 62.2209 | 63.3979 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842
95% | 55.8317 | 57.1693 | 64.0738 | 69.0569 | 71.6806 | 74.0303 | 75.5251 | 77.2309 | 78.5939 | 79.4847 | 81.5979 | 83.0608 | 83.8338 | 85.2615 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 |  | 83.7393 | 86.1562 | 95.3878 | 101.957 | 105.8988 | 109.0545 | 111.6186 | 114.0852 | 116.22 | 117.2954 | 118.8753 | 120.682 | 122.5273 | 124.8451 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119
90% | 125.5245 | 128.5317 | 144.0549 | 155.2581 | 161.157 | 166.4396 | 169.8005 | 173.6354 | 176.6997 | 178.7027 | 183.4536 | 186.7426 | 188.4804 | 191.6903 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 |  | 302.5736 | 311.3066 | 344.663 | 368.3993 | 382.6421 | 394.0446 | 403.3094 | 412.2218 | 419.9357 | 423.8214 | 429.53 | 436.0579 | 442.7255 | 451.1005 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257
85% | 203.5532 | 208.4297 | 233.6025 | 251.7698 | 261.3356 | 269.902 | 275.3521 | 281.5709 | 286.5401 | 289.7881 | 297.4924 | 302.8258 | 305.6439 | 310.8491 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 |  | 362.5431 | 373.007 | 412.9746 | 441.4154 | 458.4811 | 472.1435 | 483.2446 | 493.9234 | 503.1662 | 507.822 | 514.6621 | 522.4838 | 530.4729 | 540.5078 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957
80% | 783.6798 | 802.4544 | 899.3697 | 969.3138 | 1006.1421 | 1039.1228 | 1060.1055 | 1084.0481 | 1103.1795 | 1115.6843 | 1145.3456 | 1165.8792 | 1176.729 | 1196.7689 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 |  | 413.7898 | 425.7328 | 471.35 | 503.811 | 523.2889 | 538.8826 | 551.5529 | 563.7412 | 574.2905 | 579.6044 | 587.4113 | 596.3386 | 605.4571 | 616.9104 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227
75% | 1186.9089 | 1215.3438 | 1362.1252 | 1468.0578 | 1523.8356 | 1573.7859 | 1605.5649 | 1641.8267 | 1670.8018 | 1689.7408 | 1734.6637 | 1765.7627 | 1782.195 | 1812.5461 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 |  | 354.9106 | 365.1542 | 404.2804 | 432.1225 | 448.8288 | 462.2036 | 473.071 | 483.525 | 492.5733 | 497.1311 | 503.8271 | 511.4841 | 519.3051 | 529.1287 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831
70% | 1813.0773 | 1856.5133 | 2080.731 | 2242.5498 | 2327.7537 | 2404.0559 | 2452.6004 | 2507.9926 | 2552.2538 | 2581.1844 | 2649.8069 | 2697.3124 | 2722.4139 | 2768.7771 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 |  | 379.4436 | 390.3953 | 432.2261 | 461.9927 | 479.8539 | 494.1532 | 505.7718 | 516.9484 | 526.6221 | 531.495 | 538.6539 | 546.8402 | 555.2017 | 565.7044 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663
65% | 3310.6471 | 3389.9605 | 3799.3781 | 4094.8563 | 4250.4372 | 4389.7637 | 4478.4051 | 4579.5502 | 4660.3705 | 4713.1971 | 4838.5006 | 4925.2449 | 4971.0798 | 5055.7381 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 |  | 1000.946 | 1029.8359 | 1140.1826 | 1218.7049 | 1265.8214 | 1303.542 | 1334.1911 | 1363.6743 | 1389.1928 | 1402.047 | 1420.9318 | 1442.5266 | 1464.5839 | 1492.2892 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731
60% | 6433.7346 | 6587.868 | 7383.5083 | 7957.7247 | 8260.0724 | 8530.8319 | 8703.0928 | 8899.6529 | 9056.7147 | 9159.3751 | 9402.8833 | 9571.4576 | 9660.5305 | 9825.051 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 |  | 1117.614 | 1149.8713 | 1273.0797 | 1360.7544 | 1413.3626 | 1455.4799 | 1489.7014 | 1522.621 | 1551.1139 | 1565.4665 | 1586.5524 | 1610.6642 | 1635.2925 | 1666.2271 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219
55% | 7457.3163 | 7635.9717 | 8558.1952 | 9223.7673 | 9574.2172 | 9888.0535 | 10087.7205 | 10315.5525 | 10497.6022 | 10616.5955 | 10898.8448 | 11094.2386 | 11197.4827 | 11388.1777 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 |  | 1818.1672 | 1870.6442 | 2071.0832 | 2213.715 | 2299.2997 | 2367.8174 | 2423.4899 | 2477.0445 | 2523.3976 | 2546.7466 | 2581.0498 | 2620.2757 | 2660.3417 | 2710.667 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301
50% | 8773.1422 | 8983.321 | 10068.2687 | 10851.2793 | 11263.5653 | 11632.7773 | 11867.6751 | 12135.7075 | 12349.8795 | 12489.8688 | 12821.9204 | 13051.7909 | 13173.2522 | 13397.595 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 |  | 3171.2979 | 3262.8298 | 3612.4412 | 3861.2234 | 4010.5027 | 4130.0131 | 4227.1187 | 4320.5301 | 4401.3804 | 4442.1065 | 4501.9391 | 4570.358 | 4640.2422 | 4728.021 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104
45% | 15608.1674 | 15982.0933 | 17912.3076 | 19305.3503 | 20038.8422 | 20695.7017 | 21113.6049 | 21590.4575 | 21971.4876 | 22220.5406 | 22811.2886 | 23220.2479 | 23436.3378 | 23835.4627 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 |  | 6318.6081 | 6500.9794 | 7197.5577 | 7693.2404 | 7990.6698 | 8228.7865 | 8422.2633 | 8608.3795 | 8769.4686 | 8850.6128 | 8969.8254 | 9106.1456 | 9245.3853 | 9420.279 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528
40% | 17870.5156 | 18298.6407 | 20508.6327 | 22103.592 | 22943.401 | 23695.47 | 24173.9467 | 24719.9173 | 25156.1764 | 25441.3288 | 26117.7036 | 26585.9401 | 26833.3515 | 27290.3281 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 |  | 10760.1697 | 11070.7361 | 12256.9625 | 13101.0774 | 13607.5797 | 14013.0768 | 14342.5548 | 14659.4983 | 14933.8224 | 15072.0056 | 15275.0167 | 15507.161 | 15744.277 | 16042.1094 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359
35% | 10839.207 | 11098.8826 | 12439.3342 | 13406.743 | 13916.1219 | 14372.2829 | 14662.4988 | 14993.6526 | 15258.2617 | 15431.2184 | 15841.4678 | 16125.4726 | 16275.5378 | 16552.713 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 |  | 13027.0181 | 13403.0116 | 14839.1407 | 15861.0855 | 16474.2928 | 16965.2161 | 17364.1053 | 17747.8195 | 18079.9354 | 18247.2297 | 18493.0093 | 18774.0595 | 19061.1288 | 19421.7056 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603
30% | 4492.2249 | 4599.8454 | 5155.3852 | 5556.3202 | 5767.4283 | 5956.4807 | 6076.7584 | 6214.0025 | 6323.6677 | 6395.3483 | 6565.3729 | 6683.0765 | 6745.2698 | 6860.1429 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 |  | 19901.1621 | 20475.5611 | 22669.5121 | 24230.7204 | 25167.5072 | 25917.4827 | 26526.8592 | 27113.053 | 27620.4211 | 27875.9939 | 28251.4673 | 28680.8231 | 29119.3742 | 29670.2214 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383
25% | 2681.5709 | 2745.8134 | 3077.4351 | 3316.7677 | 3442.7857 | 3555.6379 | 3627.436 | 3709.3619 | 3774.825 | 3817.6138 | 3919.1076 | 3989.3691 | 4026.4946 | 4095.0665 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 |  | 16923.4022 | 17411.8554 | 19277.5311 | 20605.1398 | 21401.7576 | 22039.5161 | 22557.7132 | 23056.1964 | 23487.6483 | 23704.9803 | 24024.2726 | 24389.385 | 24762.3168 | 25230.7422 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862
20% | 2852.6525 | 2920.9937 | 3273.7725 | 3528.3742 | 3662.4321 | 3782.4841 | 3858.8629 | 3946.0156 | 4015.6552 | 4061.1738 | 4169.1428 | 4243.8869 | 4283.381 | 4356.3277 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 |  | 4489.5373 | 4619.117 | 5114.0541 | 5466.2498 | 5677.5811 | 5846.7694 | 5984.2397 | 6116.4802 | 6230.9382 | 6288.5933 | 6373.297 | 6470.1561 | 6569.0896 | 6693.3562 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191
15% | 2954.9137 | 3025.7048 | 3391.1299 | 3654.8586 | 3793.7221 | 3918.0777 | 3997.1945 | 4087.4715 | 4159.6075 | 4206.7578 | 4318.5973 | 4396.0208 | 4436.9307 | 4512.4923 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 |  | 2782.0412 | 2862.3381 | 3169.0368 | 3387.2827 | 3518.2388 | 3623.08 | 3708.2666 | 3790.2123 | 3861.1387 | 3896.866 | 3949.3545 | 4009.3754 | 4070.6817 | 4147.6863 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708
10% | 1970.104 | 2017.3019 | 2260.9387 | 2436.7722 | 2529.3555 | 2612.266 | 2665.0149 | 2725.2045 | 2773.2991 | 2804.7352 | 2879.301 | 2930.9209 | 2958.1963 | 3008.5749 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 |  | 795.9593 | 818.9327 | 906.6811 | 969.1226 | 1006.59 | 1036.5857 | 1060.9581 | 1084.4033 | 1104.6958 | 1114.9176 | 1129.9349 | 1147.1072 | 1164.6473 | 1186.6788 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649
5% | 157.0267 | 160.7886 | 180.2077 | 194.2224 | 201.6018 | 208.2101 | 212.4145 | 217.2119 | 221.0452 | 223.5509 | 229.4941 | 233.6085 | 235.7824 | 239.7979 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 89607.7949 | 91754.5348 | 102836.0568 | 110833.6316 | 115044.6699 | 118815.7555 | 121214.9726 | 123952.623 | 126140.1488 | 127569.9829 | 130961.5169 | 133309.3862 | 134549.9768 | 136841.3859 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | E @ R (MWh) | 84110.3229 | 86537.9646 | 95810.4847 | 102408.7793 | 106368.0177 | 109537.7157 | 112113.1862 | 114590.6774 | 116735.0192 | 117815.1726 | 119402.0743 | 121216.7049 | 123070.1983 | 125398.3005 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805
Option 6 Summer POE50 W E @ R (MWh) N 2 | 62725.4564 | 64228.1743 | 71985.2398 | 77583.5421 | 80531.2689 | 83171.0289 | 84850.4808 | 86766.8361 | 88298.1041 | 89298.9881 | 91673.0619 | 93316.5703 | 94184.9837 | 95788.9701 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 25233.0969 | 25961.3894 | 28743.1454 | 30722.6338 | 31910.4053 | 32861.3147 | 33633.9559 | 34377.2032 | 35020.5057 | 35344.5518 | 35820.6223 | 36365.0115 | 36921.0595 | 37619.4901 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 40.2458 | 41.8786 | 47.6412 | 52.495 | 55.1156 | 57.0096 | 59.193 | 60.8279 | 62.6289 | 63.5754 | 64.395 | 66.4184 | 65.2047 | 68.5022 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 |  | 42.8352 | 44.5416 | 50.2595 | 55.2967 | 57.9264 | 60.0588 | 62.0878 | 63.8171 | 65.6172 | 66.4091 | 67.4875 | 69.4836 | 68.8365 | 71.4426 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473
98% | 119.5239 | 124.3732 | 141.4873 | 155.9024 | 163.6851 | 169.3098 | 175.7944 | 180.6496 | 185.9984 | 188.8095 | 191.2433 | 197.2527 | 193.6481 | 203.4413 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 |  | 127.2142 | 132.2818 | 149.263 | 164.2229 | 172.0327 | 178.3657 | 184.3914 | 189.5271 | 194.8733 | 197.2251 | 200.4276 | 206.3557 | 204.434 | 212.1737 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426
97% | 52.5824 | 54.7158 | 62.2448 | 68.5865 | 72.0104 | 74.4849 | 77.3376 | 79.4736 | 81.8267 | 83.0634 | 84.1341 | 86.7778 | 85.1921 | 89.5004 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 |  | 55.9656 | 58.195 | 65.6656 | 72.247 | 75.6827 | 78.4688 | 81.1197 | 83.3791 | 85.7311 | 86.7657 | 88.1746 | 90.7826 | 89.9371 | 93.3421 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081
95% | 129.4337 | 134.685 | 153.2181 | 168.8283 | 177.2563 | 183.3473 | 190.3695 | 195.6273 | 201.4195 | 204.4637 | 207.0994 | 213.607 | 209.7035 | 220.3086 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 |  | 137.7615 | 143.2493 | 161.6385 | 177.8387 | 186.2959 | 193.154 | 199.6793 | 205.2408 | 211.0303 | 213.5771 | 217.0451 | 223.4648 | 221.3837 | 229.7651 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045
90% | 1321.9761 | 1375.6113 | 1564.8992 | 1724.3348 | 1810.4145 | 1872.6256 | 1944.3472 | 1998.0481 | 2057.2069 | 2088.2986 | 2115.2182 | 2181.6839 | 2141.8155 | 2250.1315 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 |  | 1407.0332 | 1463.083 | 1650.9011 | 1816.3625 | 1902.7414 | 1972.7865 | 2039.433 | 2096.2356 | 2155.3665 | 2181.3785 | 2216.7992 | 2282.3666 | 2261.1117 | 2346.7152 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425
85% | 3114.4974 | 3240.8588 | 3686.8101 | 4062.4308 | 4265.2295 | 4411.7952 | 4580.767 | 4707.283 | 4846.6578 | 4919.908 | 4983.329 | 5139.9182 | 5045.9907 | 5301.1766 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 |  | 3314.8869 | 3446.937 | 3889.4254 | 4279.2427 | 4482.7462 | 4647.7683 | 4804.7835 | 4938.6071 | 5077.916 | 5139.1988 | 5222.6477 | 5377.1207 | 5327.0453 | 5528.7223 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701
80% | 5639.4649 | 5868.2694 | 6675.7596 | 7355.9015 | 7723.112 | 7988.5007 | 8294.4602 | 8523.5446 | 8775.9126 | 8908.5477 | 9023.385 | 9306.9232 | 9136.8474 | 9598.9162 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 |  | 6002.313 | 6241.4181 | 7042.6381 | 7748.4859 | 8116.9725 | 8415.7805 | 8700.09 | 8942.4065 | 9194.6551 | 9305.6206 | 9456.7228 | 9736.4294 | 9645.7571 | 10010.9365 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901
75% | 6593.364 | 6860.8701 | 7804.945 | 8600.1308 | 9029.4539 | 9339.7323 | 9697.4441 | 9965.2774 | 10260.3327 | 10415.4026 | 10549.6644 | 10881.1622 | 10682.3185 | 11222.545 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 |  | 7017.5868 | 7297.1358 | 8233.8799 | 9059.1197 | 9489.9348 | 9839.2853 | 10171.685 | 10454.9886 | 10749.9043 | 10879.6393 | 11056.2999 | 11383.3181 | 11277.3089 | 11704.2572 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761
70% | 7731.9758 | 8045.6776 | 9152.7853 | 10085.2922 | 10588.7553 | 10952.6159 | 11372.1011 | 11686.1867 | 12032.1953 | 12214.0443 | 12371.4918 | 12760.2362 | 12527.0541 | 13160.5726 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 |  | 8229.4578 | 8557.2822 | 9655.7932 | 10623.5442 | 11128.757 | 11538.437 | 11928.2389 | 12260.4664 | 12606.3113 | 12758.4503 | 12965.6185 | 13349.1096 | 13224.7936 | 13725.472 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623
65% | 8472.8486 | 8816.6091 | 10029.7992 | 11051.6583 | 11603.3629 | 12002.0884 | 12461.7684 | 12805.9495 | 13185.1124 | 13384.3861 | 13556.92 | 13982.9137 | 13727.3882 | 14421.61 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 |  | 9017.9991 | 9377.2354 | 10581.005 | 11641.4852 | 12195.1072 | 12644.0425 | 13071.195 | 13435.2562 | 13814.2398 | 13980.9566 | 14207.9756 | 14628.2126 | 14491.9847 | 15040.6377 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285
60% | 9218.7775 | 9592.8018 | 10912.7982 | 12024.6193 | 12624.8946 | 13058.7229 | 13558.872 | 13933.354 | 14345.8974 | 14562.7147 | 14750.4381 | 15213.9352 | 14935.9139 | 15691.2533 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 |  | 9811.9216 | 10202.7843 | 11512.5308 | 12666.3731 | 13268.7346 | 13757.193 | 14221.951 | 14618.0633 | 15030.4117 | 15211.8059 | 15458.811 | 15916.0446 | 15767.8236 | 16364.7787 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459
55% | 9241.0239 | 9615.9508 | 10939.1325 | 12053.6366 | 12655.3606 | 13090.2357 | 13591.5918 | 13966.9774 | 14380.5164 | 14597.8569 | 14786.0333 | 15250.6489 | 14971.9567 | 15729.1189 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 |  | 9835.5994 | 10227.4053 | 11540.3124 | 12696.9392 | 13300.7542 | 13790.3914 | 14256.2709 | 14653.3391 | 15066.6825 | 15248.5144 | 15496.1157 | 15954.4526 | 15805.8739 | 16404.2696 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816
50% | 10886.5841 | 11328.2747 | 12887.077 | 14200.0421 | 14908.9158 | 15421.2297 | 16011.8628 | 16454.0938 | 16941.2722 | 17197.3148 | 17419 | 17966.3503 | 17638.031 | 18530.0219 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 |  | 11587.0364 | 12048.6116 | 13595.3097 | 14957.8983 | 15669.2355 | 16246.0629 | 16794.9022 | 17262.6768 | 17749.6247 | 17963.8357 | 18255.5276 | 18795.4812 | 18620.4449 | 19325.3975 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353
45% | 13615.4771 | 14167.8844 | 16117.4248 | 17759.5053 | 18646.0692 | 19286.8027 | 20025.4872 | 20578.5704 | 21187.8676 | 21508.0913 | 21785.3454 | 22469.8976 | 22059.2799 | 23174.8624 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 |  | 14491.5087 | 15068.7849 | 17003.1872 | 18707.33 | 19596.975 | 20318.3933 | 21004.8077 | 21589.8373 | 22198.8464 | 22466.7527 | 22831.5617 | 23506.8631 | 23287.9512 | 24169.6113 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796
40% | 14417.022 | 15001.9495 | 17066.2597 | 18805.0097 | 19743.7657 | 20422.2192 | 21204.3902 | 21790.0335 | 22435.2001 | 22774.2754 | 23067.8515 | 23792.7034 | 23357.9126 | 24539.1695 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 |  | 15344.6257 | 15955.8863 | 18004.167 | 19808.633 | 20750.6515 | 21514.5397 | 22241.3634 | 22860.8338 | 23505.6953 | 23789.3733 | 24175.6587 | 24890.7152 | 24658.9159 | 25592.4795 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166
35% | 5895.2987 | 6134.4828 | 6978.6047 | 7689.6011 | 8073.4701 | 8350.8981 | 8670.7375 | 8910.2143 | 9174.0309 | 9312.683 | 9432.7299 | 9729.1308 | 9551.3395 | 10034.37 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 |  | 6274.6073 | 6524.5593 | 7362.1266 | 8099.9951 | 8485.1981 | 8797.5615 | 9094.7687 | 9348.0778 | 9611.7696 | 9727.7691 | 9885.726 | 10178.1214 | 10083.3358 | 10465.0815 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005
30% | 1818.4755 | 1892.2547 | 2152.6342 | 2371.9496 | 2490.3586 | 2575.9346 | 2674.5928 | 2748.4623 | 2829.8397 | 2872.6086 | 2909.6385 | 3001.0669 | 2946.2251 | 3095.2216 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 |  | 1935.4778 | 2012.5785 | 2270.9361 | 2498.5405 | 2617.361 | 2713.7132 | 2805.3903 | 2883.5266 | 2964.8655 | 3000.6469 | 3049.3706 | 3139.5635 | 3110.3257 | 3228.0797 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706
25% | 1338.4923 | 1392.7977 | 1584.4505 | 1745.878 | 1833.0331 | 1896.0215 | 1968.6391 | 2023.0109 | 2082.9089 | 2114.389 | 2141.645 | 2208.941 | 2168.5746 | 2278.2438 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 |  | 1424.6121 | 1481.3622 | 1671.5269 | 1839.0555 | 1926.5135 | 1997.4338 | 2064.9129 | 2122.4252 | 2182.2949 | 2208.6319 | 2244.495 | 2310.8817 | 2289.3612 | 2376.0342 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079
20% | 1064.7941 | 1107.9949 | 1260.4581 | 1388.8765 | 1458.2099 | 1508.3183 | 1566.0869 | 1609.3406 | 1656.9905 | 1682.0335 | 1703.7161 | 1757.2512 | 1725.139 | 1812.3828 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 |  | 1133.3039 | 1178.4496 | 1329.7289 | 1463.0008 | 1532.5752 | 1588.9935 | 1642.6743 | 1688.4264 | 1736.0538 | 1757.0053 | 1785.5351 | 1838.3468 | 1821.2269 | 1890.1768 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883
15% | 835.2516 | 869.1394 | 988.7354 | 1089.4701 | 1143.857 | 1183.1633 | 1228.4784 | 1262.4077 | 1299.7855 | 1319.4299 | 1336.4382 | 1378.4326 | 1353.2429 | 1421.6792 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 |  | 888.9924 | 924.4058 | 1043.0732 | 1147.6151 | 1202.191 | 1246.447 | 1288.5556 | 1324.4446 | 1361.8048 | 1378.2397 | 1400.6191 | 1442.046 | 1428.6167 | 1482.7028 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932
10% | 586.4963 | 610.2916 | 694.2694 | 765.0032 | 803.1926 | 830.7926 | 862.612 | 886.4364 | 912.6823 | 926.4762 | 938.4191 | 967.9067 | 950.219 | 998.2735 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 |  | 624.2319 | 649.0985 | 732.4243 | 805.8314 | 844.1535 | 875.2291 | 904.7969 | 929.9974 | 956.2309 | 967.7712 | 983.4856 | 1012.5747 | 1003.1449 | 1041.123 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515
5% | 60.672 | 63.1336 | 71.821 | 79.1383 | 83.0889 | 85.9441 | 89.2357 | 91.7003 | 94.4154 | 95.8424 | 97.0778 | 100.1283 | 98.2985 | 103.2697 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 |  | 64.5757 | 67.1481 | 75.768 | 83.3619 | 87.3262 | 90.5409 | 93.5997 | 96.2066 | 98.9204 | 100.1143 | 101.7399 | 104.7491 | 103.7736 | 107.7024 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102194.2775 | 106340.5049 | 120973.2554 | 133298.2902 | 139952.6116 | 144761.7923 | 150306.169 | 154457.4695 | 159030.6983 | 161434.2148 | 163515.2133 | 168653.2865 | 165571.2953 | 173944.571 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | E @ R (MWh) | 108769.5462 | 113102.4335 | 127621.5603 | 140412.4195 | 147089.8663 | 152504.6467 | 157656.6971 | 162047.7795 | 166618.8453 | 168629.6814 | 171367.8442 | 176436.4835 | 174793.387 | 181410.9014 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837
Option 7 Winter POE50 W E @ R (MWh) N 2 | 71535.9943 | 74438.3534 | 84681.2788 | 93308.8031 | 97966.8281 | 101333.2546 | 105214.3183 | 108120.2286 | 111321.4888 | 113003.9503 | 114460.6493 | 118057.3006 | 115899.9067 | 121761.1997 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 32630.8639 | 33930.7301 | 38286.4681 | 42123.7258 | 44126.9599 | 45751.394 | 47297.0091 | 48614.3339 | 49985.6536 | 50588.9044 | 51410.3533 | 52930.9451 | 52438.0161 | 54423.2704 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43.3961 | 44.6487 | 49.4328 | 52.8371 | 54.8798 | 56.5152 | 57.844 | 59.1223 | 60.2286 | 60.7859 | 61.6047 | 62.5409 | 63.4972 | 64.6984 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884
98% | 19.0952 | 19.5527 | 21.9141 | 23.6184 | 24.5158 | 25.3194 | 25.8306 | 26.414 | 26.8802 | 27.1849 | 27.9076 | 28.4079 | 28.6723 | 29.1606 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 |  | 21.48 | 22.1 | 24.468 | 26.153 | 27.1641 | 27.9736 | 28.6313 | 29.264 | 29.8117 | 30.0875 | 30.4928 | 30.9562 | 31.4295 | 32.0241 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181
97% | 18.9014 | 19.3542 | 21.6917 | 23.3786 | 24.2669 | 25.0623 | 25.5684 | 26.1459 | 26.6073 | 26.9089 | 27.6243 | 28.1195 | 28.3812 | 28.8646 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 |  | 42.5239 | 43.7512 | 48.4391 | 51.775 | 53.7767 | 55.3792 | 56.6813 | 57.9339 | 59.018 | 59.5641 | 60.3664 | 61.2838 | 62.2209 | 63.3979 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842
95% | 55.8317 | 57.1693 | 64.0738 | 69.0569 | 71.6806 | 74.0303 | 75.5251 | 77.2309 | 78.5939 | 79.4847 | 81.5979 | 83.0608 | 83.8338 | 85.2615 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 |  | 83.7393 | 86.1562 | 95.3878 | 101.957 | 105.8988 | 109.0545 | 111.6186 | 114.0852 | 116.22 | 117.2954 | 118.8753 | 120.682 | 122.5273 | 124.8451 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119
90% | 125.5245 | 128.5317 | 144.0549 | 155.2581 | 161.157 | 166.4396 | 169.8005 | 173.6354 | 176.6997 | 178.7027 | 183.4536 | 186.7426 | 188.4804 | 191.6903 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 |  | 302.5736 | 311.3066 | 344.663 | 368.3993 | 382.6421 | 394.0446 | 403.3094 | 412.2218 | 419.9357 | 423.8214 | 429.53 | 436.0579 | 442.7255 | 451.1005 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257
85% | 203.5532 | 208.4297 | 233.6025 | 251.7698 | 261.3356 | 269.902 | 275.3521 | 281.5709 | 286.5401 | 289.7881 | 297.4924 | 302.8258 | 305.6439 | 310.8491 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 |  | 362.5431 | 373.007 | 412.9746 | 441.4154 | 458.4811 | 472.1435 | 483.2446 | 493.9234 | 503.1662 | 507.822 | 514.6621 | 522.4838 | 530.4729 | 540.5078 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957
80% | 783.6798 | 802.4544 | 899.3697 | 969.3138 | 1006.1421 | 1039.1228 | 1060.1055 | 1084.0481 | 1103.1795 | 1115.6843 | 1145.3456 | 1165.8792 | 1176.729 | 1196.7689 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 |  | 413.7898 | 425.7328 | 471.35 | 503.811 | 523.2889 | 538.8826 | 551.5529 | 563.7412 | 574.2905 | 579.6044 | 587.4113 | 596.3386 | 605.4571 | 616.9104 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227
75% | 1186.9089 | 1215.3438 | 1362.1252 | 1468.0578 | 1523.8356 | 1573.7859 | 1605.5649 | 1641.8267 | 1670.8018 | 1689.7408 | 1734.6637 | 1765.7627 | 1782.195 | 1812.5461 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 |  | 354.9106 | 365.1542 | 404.2804 | 432.1225 | 448.8288 | 462.2036 | 473.071 | 483.525 | 492.5733 | 497.1311 | 503.8271 | 511.4841 | 519.3051 | 529.1287 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831
70% | 1813.0773 | 1856.5133 | 2080.731 | 2242.5498 | 2327.7537 | 2404.0559 | 2452.6004 | 2507.9926 | 2552.2538 | 2581.1844 | 2649.8069 | 2697.3124 | 2722.4139 | 2768.7771 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 |  | 379.4436 | 390.3953 | 432.2261 | 461.9927 | 479.8539 | 494.1532 | 505.7718 | 516.9484 | 526.6221 | 531.495 | 538.6539 | 546.8402 | 555.2017 | 565.7044 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663
65% | 3310.6471 | 3389.9605 | 3799.3781 | 4094.8563 | 4250.4372 | 4389.7637 | 4478.4051 | 4579.5502 | 4660.3705 | 4713.1971 | 4838.5006 | 4925.2449 | 4971.0798 | 5055.7381 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 |  | 1000.946 | 1029.8359 | 1140.1826 | 1218.7049 | 1265.8214 | 1303.542 | 1334.1911 | 1363.6743 | 1389.1928 | 1402.047 | 1420.9318 | 1442.5266 | 1464.5839 | 1492.2892 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731
60% | 6433.7346 | 6587.868 | 7383.5083 | 7957.7247 | 8260.0724 | 8530.8319 | 8703.0928 | 8899.6529 | 9056.7147 | 9159.3751 | 9402.8833 | 9571.4576 | 9660.5305 | 9825.051 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 |  | 1117.614 | 1149.8713 | 1273.0797 | 1360.7544 | 1413.3626 | 1455.4799 | 1489.7014 | 1522.621 | 1551.1139 | 1565.4665 | 1586.5524 | 1610.6642 | 1635.2925 | 1666.2271 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219
55% | 7457.3163 | 7635.9717 | 8558.1952 | 9223.7673 | 9574.2172 | 9888.0535 | 10087.7205 | 10315.5525 | 10497.6022 | 10616.5955 | 10898.8448 | 11094.2386 | 11197.4827 | 11388.1777 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 |  | 1818.1672 | 1870.6442 | 2071.0832 | 2213.715 | 2299.2997 | 2367.8174 | 2423.4899 | 2477.0445 | 2523.3976 | 2546.7466 | 2581.0498 | 2620.2757 | 2660.3417 | 2710.667 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301
50% | 8773.1422 | 8983.321 | 10068.2687 | 10851.2793 | 11263.5653 | 11632.7773 | 11867.6751 | 12135.7075 | 12349.8795 | 12489.8688 | 12821.9204 | 13051.7909 | 13173.2522 | 13397.595 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 |  | 3171.2979 | 3262.8298 | 3612.4412 | 3861.2234 | 4010.5027 | 4130.0131 | 4227.1187 | 4320.5301 | 4401.3804 | 4442.1065 | 4501.9391 | 4570.358 | 4640.2422 | 4728.021 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104
45% | 15608.1674 | 15982.0933 | 17912.3076 | 19305.3503 | 20038.8422 | 20695.7017 | 21113.6049 | 21590.4575 | 21971.4876 | 22220.5406 | 22811.2886 | 23220.2479 | 23436.3378 | 23835.4627 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 |  | 6318.6081 | 6500.9794 | 7197.5577 | 7693.2404 | 7990.6698 | 8228.7865 | 8422.2633 | 8608.3795 | 8769.4686 | 8850.6128 | 8969.8254 | 9106.1456 | 9245.3853 | 9420.279 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528
40% | 17870.5156 | 18298.6407 | 20508.6327 | 22103.592 | 22943.401 | 23695.47 | 24173.9467 | 24719.9173 | 25156.1764 | 25441.3288 | 26117.7036 | 26585.9401 | 26833.3515 | 27290.3281 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 |  | 10760.1697 | 11070.7361 | 12256.9625 | 13101.0774 | 13607.5797 | 14013.0768 | 14342.5548 | 14659.4983 | 14933.8224 | 15072.0056 | 15275.0167 | 15507.161 | 15744.277 | 16042.1094 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359
35% | 10839.207 | 11098.8826 | 12439.3342 | 13406.743 | 13916.1219 | 14372.2829 | 14662.4988 | 14993.6526 | 15258.2617 | 15431.2184 | 15841.4678 | 16125.4726 | 16275.5378 | 16552.713 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 |  | 13027.0181 | 13403.0116 | 14839.1407 | 15861.0855 | 16474.2928 | 16965.2161 | 17364.1053 | 17747.8195 | 18079.9354 | 18247.2297 | 18493.0093 | 18774.0595 | 19061.1288 | 19421.7056 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603
30% | 4492.2249 | 4599.8454 | 5155.3852 | 5556.3202 | 5767.4283 | 5956.4807 | 6076.7584 | 6214.0025 | 6323.6677 | 6395.3483 | 6565.3729 | 6683.0765 | 6745.2698 | 6860.1429 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 |  | 19901.1621 | 20475.5611 | 22669.5121 | 24230.7204 | 25167.5072 | 25917.4827 | 26526.8592 | 27113.053 | 27620.4211 | 27875.9939 | 28251.4673 | 28680.8231 | 29119.3742 | 29670.2214 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383
25% | 2681.5709 | 2745.8134 | 3077.4351 | 3316.7677 | 3442.7857 | 3555.6379 | 3627.436 | 3709.3619 | 3774.825 | 3817.6138 | 3919.1076 | 3989.3691 | 4026.4946 | 4095.0665 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 |  | 16923.4022 | 17411.8554 | 19277.5311 | 20605.1398 | 21401.7576 | 22039.5161 | 22557.7132 | 23056.1964 | 23487.6483 | 23704.9803 | 24024.2726 | 24389.385 | 24762.3168 | 25230.7422 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862
20% | 2852.6525 | 2920.9937 | 3273.7725 | 3528.3742 | 3662.4321 | 3782.4841 | 3858.8629 | 3946.0156 | 4015.6552 | 4061.1738 | 4169.1428 | 4243.8869 | 4283.381 | 4356.3277 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 |  | 4489.5373 | 4619.117 | 5114.0541 | 5466.2498 | 5677.5811 | 5846.7694 | 5984.2397 | 6116.4802 | 6230.9382 | 6288.5933 | 6373.297 | 6470.1561 | 6569.0896 | 6693.3562 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191
15% | 2954.9137 | 3025.7048 | 3391.1299 | 3654.8586 | 3793.7221 | 3918.0777 | 3997.1945 | 4087.4715 | 4159.6075 | 4206.7578 | 4318.5973 | 4396.0208 | 4436.9307 | 4512.4923 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 |  | 2782.0412 | 2862.3381 | 3169.0368 | 3387.2827 | 3518.2388 | 3623.08 | 3708.2666 | 3790.2123 | 3861.1387 | 3896.866 | 3949.3545 | 4009.3754 | 4070.6817 | 4147.6863 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708
10% | 1970.104 | 2017.3019 | 2260.9387 | 2436.7722 | 2529.3555 | 2612.266 | 2665.0149 | 2725.2045 | 2773.2991 | 2804.7352 | 2879.301 | 2930.9209 | 2958.1963 | 3008.5749 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 |  | 795.9593 | 818.9327 | 906.6811 | 969.1226 | 1006.59 | 1036.5857 | 1060.9581 | 1084.4033 | 1104.6958 | 1114.9176 | 1129.9349 | 1147.1072 | 1164.6473 | 1186.6788 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649
5% | 157.0267 | 160.7886 | 180.2077 | 194.2224 | 201.6018 | 208.2101 | 212.4145 | 217.2119 | 221.0452 | 223.5509 | 229.4941 | 233.6085 | 235.7824 | 239.7979 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 89607.7949 | 91754.5348 | 102836.0568 | 110833.6316 | 115044.6699 | 118815.7555 | 121214.9726 | 123952.623 | 126140.1488 | 127569.9829 | 130961.5169 | 133309.3862 | 134549.9768 | 136841.3859 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | E @ R (MWh) | 84110.3229 | 86537.9646 | 95810.4847 | 102408.7793 | 106368.0177 | 109537.7157 | 112113.1862 | 114590.6774 | 116735.0192 | 117815.1726 | 119402.0743 | 121216.7049 | 123070.1983 | 125398.3005 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805
Option 7 Summer POE50 W E @ R (MWh) N 2 | 62725.4564 | 64228.1743 | 71985.2398 | 77583.5421 | 80531.2689 | 83171.0289 | 84850.4808 | 86766.8361 | 88298.1041 | 89298.9881 | 91673.0619 | 93316.5703 | 94184.9837 | 95788.9701 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 25233.0969 | 25961.3894 | 28743.1454 | 30722.6338 | 31910.4053 | 32861.3147 | 33633.9559 | 34377.2032 | 35020.5057 | 35344.5518 | 35820.6223 | 36365.0115 | 36921.0595 | 37619.4901 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 40.2458 | 41.8786 | 47.6412 | 52.495 | 55.1156 | 57.0096 | 59.193 | 60.8279 | 62.6289 | 63.5754 | 64.395 | 66.4184 | 65.2047 | 68.5022 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 | 72.8025 |  | 42.8352 | 44.5416 | 50.2595 | 55.2967 | 57.9264 | 60.0588 | 62.0878 | 63.8171 | 65.6172 | 66.4091 | 67.4875 | 69.4836 | 68.8365 | 71.4426 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473 | 72.9473
98% | 119.5239 | 124.3732 | 141.4873 | 155.9024 | 163.6851 | 169.3098 | 175.7944 | 180.6496 | 185.9984 | 188.8095 | 191.2433 | 197.2527 | 193.6481 | 203.4413 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 | 216.2125 |  | 127.2142 | 132.2818 | 149.263 | 164.2229 | 172.0327 | 178.3657 | 184.3914 | 189.5271 | 194.8733 | 197.2251 | 200.4276 | 206.3557 | 204.434 | 212.1737 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426 | 216.6426
97% | 52.5824 | 54.7158 | 62.2448 | 68.5865 | 72.0104 | 74.4849 | 77.3376 | 79.4736 | 81.8267 | 83.0634 | 84.1341 | 86.7778 | 85.1921 | 89.5004 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 | 95.1189 |  | 55.9656 | 58.195 | 65.6656 | 72.247 | 75.6827 | 78.4688 | 81.1197 | 83.3791 | 85.7311 | 86.7657 | 88.1746 | 90.7826 | 89.9371 | 93.3421 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081 | 95.3081
95% | 129.4337 | 134.685 | 153.2181 | 168.8283 | 177.2563 | 183.3473 | 190.3695 | 195.6273 | 201.4195 | 204.4637 | 207.0994 | 213.607 | 209.7035 | 220.3086 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 | 234.1387 |  | 137.7615 | 143.2493 | 161.6385 | 177.8387 | 186.2959 | 193.154 | 199.6793 | 205.2408 | 211.0303 | 213.5771 | 217.0451 | 223.4648 | 221.3837 | 229.7651 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045 | 234.6045
90% | 1321.9761 | 1375.6113 | 1564.8992 | 1724.3348 | 1810.4145 | 1872.6256 | 1944.3472 | 1998.0481 | 2057.2069 | 2088.2986 | 2115.2182 | 2181.6839 | 2141.8155 | 2250.1315 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 | 2391.3855 |  | 1407.0332 | 1463.083 | 1650.9011 | 1816.3625 | 1902.7414 | 1972.7865 | 2039.433 | 2096.2356 | 2155.3665 | 2181.3785 | 2216.7992 | 2282.3666 | 2261.1117 | 2346.7152 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425 | 2396.1425
85% | 3114.4974 | 3240.8588 | 3686.8101 | 4062.4308 | 4265.2295 | 4411.7952 | 4580.767 | 4707.283 | 4846.6578 | 4919.908 | 4983.329 | 5139.9182 | 5045.9907 | 5301.1766 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 | 5633.9628 |  | 3314.8869 | 3446.937 | 3889.4254 | 4279.2427 | 4482.7462 | 4647.7683 | 4804.7835 | 4938.6071 | 5077.916 | 5139.1988 | 5222.6477 | 5377.1207 | 5327.0453 | 5528.7223 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701 | 5645.1701
80% | 5639.4649 | 5868.2694 | 6675.7596 | 7355.9015 | 7723.112 | 7988.5007 | 8294.4602 | 8523.5446 | 8775.9126 | 8908.5477 | 9023.385 | 9306.9232 | 9136.8474 | 9598.9162 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 | 10201.4969 |  | 6002.313 | 6241.4181 | 7042.6381 | 7748.4859 | 8116.9725 | 8415.7805 | 8700.09 | 8942.4065 | 9194.6551 | 9305.6206 | 9456.7228 | 9736.4294 | 9645.7571 | 10010.9365 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901 | 10221.7901
75% | 6593.364 | 6860.8701 | 7804.945 | 8600.1308 | 9029.4539 | 9339.7323 | 9697.4441 | 9965.2774 | 10260.3327 | 10415.4026 | 10549.6644 | 10881.1622 | 10682.3185 | 11222.545 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 | 11927.0504 |  | 7017.5868 | 7297.1358 | 8233.8799 | 9059.1197 | 9489.9348 | 9839.2853 | 10171.685 | 10454.9886 | 10749.9043 | 10879.6393 | 11056.2999 | 11383.3181 | 11277.3089 | 11704.2572 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761 | 11950.7761
70% | 7731.9758 | 8045.6776 | 9152.7853 | 10085.2922 | 10588.7553 | 10952.6159 | 11372.1011 | 11686.1867 | 12032.1953 | 12214.0443 | 12371.4918 | 12760.2362 | 12527.0541 | 13160.5726 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 | 13986.7394 |  | 8229.4578 | 8557.2822 | 9655.7932 | 10623.5442 | 11128.757 | 11538.437 | 11928.2389 | 12260.4664 | 12606.3113 | 12758.4503 | 12965.6185 | 13349.1096 | 13224.7936 | 13725.472 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623 | 14014.5623
65% | 8472.8486 | 8816.6091 | 10029.7992 | 11051.6583 | 11603.3629 | 12002.0884 | 12461.7684 | 12805.9495 | 13185.1124 | 13384.3861 | 13556.92 | 13982.9137 | 13727.3882 | 14421.61 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 | 15326.9396 |  | 9017.9991 | 9377.2354 | 10581.005 | 11641.4852 | 12195.1072 | 12644.0425 | 13071.195 | 13435.2562 | 13814.2398 | 13980.9566 | 14207.9756 | 14628.2126 | 14491.9847 | 15040.6377 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285 | 15357.4285
60% | 9218.7775 | 9592.8018 | 10912.7982 | 12024.6193 | 12624.8946 | 13058.7229 | 13558.872 | 13933.354 | 14345.8974 | 14562.7147 | 14750.4381 | 15213.9352 | 14935.9139 | 15691.2533 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 | 16676.2859 |  | 9811.9216 | 10202.7843 | 11512.5308 | 12666.3731 | 13268.7346 | 13757.193 | 14221.951 | 14618.0633 | 15030.4117 | 15211.8059 | 15458.811 | 15916.0446 | 15767.8236 | 16364.7787 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459 | 16709.459
55% | 9241.0239 | 9615.9508 | 10939.1325 | 12053.6366 | 12655.3606 | 13090.2357 | 13591.5918 | 13966.9774 | 14380.5164 | 14597.8569 | 14786.0333 | 15250.6489 | 14971.9567 | 15729.1189 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 | 16716.5285 |  | 9835.5994 | 10227.4053 | 11540.3124 | 12696.9392 | 13300.7542 | 13790.3914 | 14256.2709 | 14653.3391 | 15066.6825 | 15248.5144 | 15496.1157 | 15954.4526 | 15805.8739 | 16404.2696 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816 | 16749.7816
50% | 10886.5841 | 11328.2747 | 12887.077 | 14200.0421 | 14908.9158 | 15421.2297 | 16011.8628 | 16454.0938 | 16941.2722 | 17197.3148 | 17419 | 17966.3503 | 17638.031 | 18530.0219 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 | 19693.2608 |  | 11587.0364 | 12048.6116 | 13595.3097 | 14957.8983 | 15669.2355 | 16246.0629 | 16794.9022 | 17262.6768 | 17749.6247 | 17963.8357 | 18255.5276 | 18795.4812 | 18620.4449 | 19325.3975 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353 | 19732.4353
45% | 13615.4771 | 14167.8844 | 16117.4248 | 17759.5053 | 18646.0692 | 19286.8027 | 20025.4872 | 20578.5704 | 21187.8676 | 21508.0913 | 21785.3454 | 22469.8976 | 22059.2799 | 23174.8624 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 | 24629.6853 |  | 14491.5087 | 15068.7849 | 17003.1872 | 18707.33 | 19596.975 | 20318.3933 | 21004.8077 | 21589.8373 | 22198.8464 | 22466.7527 | 22831.5617 | 23506.8631 | 23287.9512 | 24169.6113 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796 | 24678.6796
40% | 14417.022 | 15001.9495 | 17066.2597 | 18805.0097 | 19743.7657 | 20422.2192 | 21204.3902 | 21790.0335 | 22435.2001 | 22774.2754 | 23067.8515 | 23792.7034 | 23357.9126 | 24539.1695 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 | 26079.638 |  | 15344.6257 | 15955.8863 | 18004.167 | 19808.633 | 20750.6515 | 21514.5397 | 22241.3634 | 22860.8338 | 23505.6953 | 23789.3733 | 24175.6587 | 24890.7152 | 24658.9159 | 25592.4795 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166 | 26131.5166
35% | 5895.2987 | 6134.4828 | 6978.6047 | 7689.6011 | 8073.4701 | 8350.8981 | 8670.7375 | 8910.2143 | 9174.0309 | 9312.683 | 9432.7299 | 9729.1308 | 9551.3395 | 10034.37 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 | 10664.2867 |  | 6274.6073 | 6524.5593 | 7362.1266 | 8099.9951 | 8485.1981 | 8797.5615 | 9094.7687 | 9348.0778 | 9611.7696 | 9727.7691 | 9885.726 | 10178.1214 | 10083.3358 | 10465.0815 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005 | 10685.5005
30% | 1818.4755 | 1892.2547 | 2152.6342 | 2371.9496 | 2490.3586 | 2575.9346 | 2674.5928 | 2748.4623 | 2829.8397 | 2872.6086 | 2909.6385 | 3001.0669 | 2946.2251 | 3095.2216 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 | 3289.527 |  | 1935.4778 | 2012.5785 | 2270.9361 | 2498.5405 | 2617.361 | 2713.7132 | 2805.3903 | 2883.5266 | 2964.8655 | 3000.6469 | 3049.3706 | 3139.5635 | 3110.3257 | 3228.0797 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706 | 3296.0706
25% | 1338.4923 | 1392.7977 | 1584.4505 | 1745.878 | 1833.0331 | 1896.0215 | 1968.6391 | 2023.0109 | 2082.9089 | 2114.389 | 2141.645 | 2208.941 | 2168.5746 | 2278.2438 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 | 2421.2626 |  | 1424.6121 | 1481.3622 | 1671.5269 | 1839.0555 | 1926.5135 | 1997.4338 | 2064.9129 | 2122.4252 | 2182.2949 | 2208.6319 | 2244.495 | 2310.8817 | 2289.3612 | 2376.0342 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079 | 2426.079
20% | 1064.7941 | 1107.9949 | 1260.4581 | 1388.8765 | 1458.2099 | 1508.3183 | 1566.0869 | 1609.3406 | 1656.9905 | 1682.0335 | 1703.7161 | 1757.2512 | 1725.139 | 1812.3828 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 | 1926.1568 |  | 1133.3039 | 1178.4496 | 1329.7289 | 1463.0008 | 1532.5752 | 1588.9935 | 1642.6743 | 1688.4264 | 1736.0538 | 1757.0053 | 1785.5351 | 1838.3468 | 1821.2269 | 1890.1768 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883 | 1929.9883
15% | 835.2516 | 869.1394 | 988.7354 | 1089.4701 | 1143.857 | 1183.1633 | 1228.4784 | 1262.4077 | 1299.7855 | 1319.4299 | 1336.4382 | 1378.4326 | 1353.2429 | 1421.6792 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 | 1510.9264 |  | 888.9924 | 924.4058 | 1043.0732 | 1147.6151 | 1202.191 | 1246.447 | 1288.5556 | 1324.4446 | 1361.8048 | 1378.2397 | 1400.6191 | 1442.046 | 1428.6167 | 1482.7028 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932 | 1513.932
10% | 586.4963 | 610.2916 | 694.2694 | 765.0032 | 803.1926 | 830.7926 | 862.612 | 886.4364 | 912.6823 | 926.4762 | 938.4191 | 967.9067 | 950.219 | 998.2735 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 | 1060.941 |  | 624.2319 | 649.0985 | 732.4243 | 805.8314 | 844.1535 | 875.2291 | 904.7969 | 929.9974 | 956.2309 | 967.7712 | 983.4856 | 1012.5747 | 1003.1449 | 1041.123 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515 | 1063.0515
5% | 60.672 | 63.1336 | 71.821 | 79.1383 | 83.0889 | 85.9441 | 89.2357 | 91.7003 | 94.4154 | 95.8424 | 97.0778 | 100.1283 | 98.2985 | 103.2697 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 | 109.7525 |  | 64.5757 | 67.1481 | 75.768 | 83.3619 | 87.3262 | 90.5409 | 93.5997 | 96.2066 | 98.9204 | 100.1143 | 101.7399 | 104.7491 | 103.7736 | 107.7024 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708 | 109.9708
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 102194.2775 | 106340.5049 | 120973.2554 | 133298.2902 | 139952.6116 | 144761.7923 | 150306.169 | 154457.4695 | 159030.6983 | 161434.2148 | 163515.2133 | 168653.2865 | 165571.2953 | 173944.571 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | 184864.0984 | E @ R (MWh) | 108769.5462 | 113102.4335 | 127621.5603 | 140412.4195 | 147089.8663 | 152504.6467 | 157656.6971 | 162047.7795 | 166618.8453 | 168629.6814 | 171367.8442 | 176436.4835 | 174793.387 | 181410.9014 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837 | 185231.837
Option 8 Winter POE50 W E @ R (MWh) N 2 | 71535.9943 | 74438.3534 | 84681.2788 | 93308.8031 | 97966.8281 | 101333.2546 | 105214.3183 | 108120.2286 | 111321.4888 | 113003.9503 | 114460.6493 | 118057.3006 | 115899.9067 | 121761.1997 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | 129404.8689 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 32630.8639 | 33930.7301 | 38286.4681 | 42123.7258 | 44126.9599 | 45751.394 | 47297.0091 | 48614.3339 | 49985.6536 | 50588.9044 | 51410.3533 | 52930.9451 | 52438.0161 | 54423.2704 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511 | 55569.5511
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 43.3961 | 44.6487 | 49.4328 | 52.8371 | 54.8798 | 56.5152 | 57.844 | 59.1223 | 60.2286 | 60.7859 | 61.6047 | 62.5409 | 63.4972 | 64.6984 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884 | 64.8884
98% | 19.0952 | 19.5527 | 21.9141 | 23.6184 | 24.5158 | 25.3194 | 25.8306 | 26.414 | 26.8802 | 27.1849 | 27.9076 | 28.4079 | 28.6723 | 29.1606 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 | 29.0204 |  | 21.48 | 22.1 | 24.468 | 26.153 | 27.1641 | 27.9736 | 28.6313 | 29.264 | 29.8117 | 30.0875 | 30.4928 | 30.9562 | 31.4295 | 32.0241 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181 | 32.1181
97% | 18.9014 | 19.3542 | 21.6917 | 23.3786 | 24.2669 | 25.0623 | 25.5684 | 26.1459 | 26.6073 | 26.9089 | 27.6243 | 28.1195 | 28.3812 | 28.8646 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 | 28.7258 |  | 42.5239 | 43.7512 | 48.4391 | 51.775 | 53.7767 | 55.3792 | 56.6813 | 57.9339 | 59.018 | 59.5641 | 60.3664 | 61.2838 | 62.2209 | 63.3979 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842 | 63.5842
95% | 55.8317 | 57.1693 | 64.0738 | 69.0569 | 71.6806 | 74.0303 | 75.5251 | 77.2309 | 78.5939 | 79.4847 | 81.5979 | 83.0608 | 83.8338 | 85.2615 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 | 84.8516 |  | 83.7393 | 86.1562 | 95.3878 | 101.957 | 105.8988 | 109.0545 | 111.6186 | 114.0852 | 116.22 | 117.2954 | 118.8753 | 120.682 | 122.5273 | 124.8451 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119 | 125.2119
90% | 125.5245 | 128.5317 | 144.0549 | 155.2581 | 161.157 | 166.4396 | 169.8005 | 173.6354 | 176.6997 | 178.7027 | 183.4536 | 186.7426 | 188.4804 | 191.6903 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 | 190.7687 |  | 302.5736 | 311.3066 | 344.663 | 368.3993 | 382.6421 | 394.0446 | 403.3094 | 412.2218 | 419.9357 | 423.8214 | 429.53 | 436.0579 | 442.7255 | 451.1005 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257 | 452.4257
85% | 203.5532 | 208.4297 | 233.6025 | 251.7698 | 261.3356 | 269.902 | 275.3521 | 281.5709 | 286.5401 | 289.7881 | 297.4924 | 302.8258 | 305.6439 | 310.8491 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 | 309.3546 |  | 362.5431 | 373.007 | 412.9746 | 441.4154 | 458.4811 | 472.1435 | 483.2446 | 493.9234 | 503.1662 | 507.822 | 514.6621 | 522.4838 | 530.4729 | 540.5078 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957 | 542.0957
80% | 783.6798 | 802.4544 | 899.3697 | 969.3138 | 1006.1421 | 1039.1228 | 1060.1055 | 1084.0481 | 1103.1795 | 1115.6843 | 1145.3456 | 1165.8792 | 1176.729 | 1196.7689 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 | 1191.0154 |  | 413.7898 | 425.7328 | 471.35 | 503.811 | 523.2889 | 538.8826 | 551.5529 | 563.7412 | 574.2905 | 579.6044 | 587.4113 | 596.3386 | 605.4571 | 616.9104 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227 | 618.7227
75% | 1186.9089 | 1215.3438 | 1362.1252 | 1468.0578 | 1523.8356 | 1573.7859 | 1605.5649 | 1641.8267 | 1670.8018 | 1689.7408 | 1734.6637 | 1765.7627 | 1782.195 | 1812.5461 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 | 1803.8322 |  | 354.9106 | 365.1542 | 404.2804 | 432.1225 | 448.8288 | 462.2036 | 473.071 | 483.525 | 492.5733 | 497.1311 | 503.8271 | 511.4841 | 519.3051 | 529.1287 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831 | 530.6831
70% | 1813.0773 | 1856.5133 | 2080.731 | 2242.5498 | 2327.7537 | 2404.0559 | 2452.6004 | 2507.9926 | 2552.2538 | 2581.1844 | 2649.8069 | 2697.3124 | 2722.4139 | 2768.7771 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 | 2755.4661 |  | 379.4436 | 390.3953 | 432.2261 | 461.9927 | 479.8539 | 494.1532 | 505.7718 | 516.9484 | 526.6221 | 531.495 | 538.6539 | 546.8402 | 555.2017 | 565.7044 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663 | 567.3663
65% | 3310.6471 | 3389.9605 | 3799.3781 | 4094.8563 | 4250.4372 | 4389.7637 | 4478.4051 | 4579.5502 | 4660.3705 | 4713.1971 | 4838.5006 | 4925.2449 | 4971.0798 | 5055.7381 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 | 5031.4324 |  | 1000.946 | 1029.8359 | 1140.1826 | 1218.7049 | 1265.8214 | 1303.542 | 1334.1911 | 1363.6743 | 1389.1928 | 1402.047 | 1420.9318 | 1442.5266 | 1464.5839 | 1492.2892 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731 | 1496.6731
60% | 6433.7346 | 6587.868 | 7383.5083 | 7957.7247 | 8260.0724 | 8530.8319 | 8703.0928 | 8899.6529 | 9056.7147 | 9159.3751 | 9402.8833 | 9571.4576 | 9660.5305 | 9825.051 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 | 9777.8166 |  | 1117.614 | 1149.8713 | 1273.0797 | 1360.7544 | 1413.3626 | 1455.4799 | 1489.7014 | 1522.621 | 1551.1139 | 1565.4665 | 1586.5524 | 1610.6642 | 1635.2925 | 1666.2271 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219 | 1671.1219
55% | 7457.3163 | 7635.9717 | 8558.1952 | 9223.7673 | 9574.2172 | 9888.0535 | 10087.7205 | 10315.5525 | 10497.6022 | 10616.5955 | 10898.8448 | 11094.2386 | 11197.4827 | 11388.1777 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 | 11333.4286 |  | 1818.1672 | 1870.6442 | 2071.0832 | 2213.715 | 2299.2997 | 2367.8174 | 2423.4899 | 2477.0445 | 2523.3976 | 2546.7466 | 2581.0498 | 2620.2757 | 2660.3417 | 2710.667 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301 | 2718.6301
50% | 8773.1422 | 8983.321 | 10068.2687 | 10851.2793 | 11263.5653 | 11632.7773 | 11867.6751 | 12135.7075 | 12349.8795 | 12489.8688 | 12821.9204 | 13051.7909 | 13173.2522 | 13397.595 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 | 13333.1854 |  | 3171.2979 | 3262.8298 | 3612.4412 | 3861.2234 | 4010.5027 | 4130.0131 | 4227.1187 | 4320.5301 | 4401.3804 | 4442.1065 | 4501.9391 | 4570.358 | 4640.2422 | 4728.021 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104 | 4741.9104
45% | 15608.1674 | 15982.0933 | 17912.3076 | 19305.3503 | 20038.8422 | 20695.7017 | 21113.6049 | 21590.4575 | 21971.4876 | 22220.5406 | 22811.2886 | 23220.2479 | 23436.3378 | 23835.4627 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 | 23720.8726 |  | 6318.6081 | 6500.9794 | 7197.5577 | 7693.2404 | 7990.6698 | 8228.7865 | 8422.2633 | 8608.3795 | 8769.4686 | 8850.6128 | 8969.8254 | 9106.1456 | 9245.3853 | 9420.279 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528 | 9447.9528
40% | 17870.5156 | 18298.6407 | 20508.6327 | 22103.592 | 22943.401 | 23695.47 | 24173.9467 | 24719.9173 | 25156.1764 | 25441.3288 | 26117.7036 | 26585.9401 | 26833.3515 | 27290.3281 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 | 27159.1286 |  | 10760.1697 | 11070.7361 | 12256.9625 | 13101.0774 | 13607.5797 | 14013.0768 | 14342.5548 | 14659.4983 | 14933.8224 | 15072.0056 | 15275.0167 | 15507.161 | 15744.277 | 16042.1094 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359 | 16089.2359
35% | 10839.207 | 11098.8826 | 12439.3342 | 13406.743 | 13916.1219 | 14372.2829 | 14662.4988 | 14993.6526 | 15258.2617 | 15431.2184 | 15841.4678 | 16125.4726 | 16275.5378 | 16552.713 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 | 16473.1351 |  | 13027.0181 | 13403.0116 | 14839.1407 | 15861.0855 | 16474.2928 | 16965.2161 | 17364.1053 | 17747.8195 | 18079.9354 | 18247.2297 | 18493.0093 | 18774.0595 | 19061.1288 | 19421.7056 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603 | 19478.7603
30% | 4492.2249 | 4599.8454 | 5155.3852 | 5556.3202 | 5767.4283 | 5956.4807 | 6076.7584 | 6214.0025 | 6323.6677 | 6395.3483 | 6565.3729 | 6683.0765 | 6745.2698 | 6860.1429 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 | 6827.1625 |  | 19901.1621 | 20475.5611 | 22669.5121 | 24230.7204 | 25167.5072 | 25917.4827 | 26526.8592 | 27113.053 | 27620.4211 | 27875.9939 | 28251.4673 | 28680.8231 | 29119.3742 | 29670.2214 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383 | 29757.383
25% | 2681.5709 | 2745.8134 | 3077.4351 | 3316.7677 | 3442.7857 | 3555.6379 | 3627.436 | 3709.3619 | 3774.825 | 3817.6138 | 3919.1076 | 3989.3691 | 4026.4946 | 4095.0665 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 | 4075.3792 |  | 16923.4022 | 17411.8554 | 19277.5311 | 20605.1398 | 21401.7576 | 22039.5161 | 22557.7132 | 23056.1964 | 23487.6483 | 23704.9803 | 24024.2726 | 24389.385 | 24762.3168 | 25230.7422 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862 | 25304.862
20% | 2852.6525 | 2920.9937 | 3273.7725 | 3528.3742 | 3662.4321 | 3782.4841 | 3858.8629 | 3946.0156 | 4015.6552 | 4061.1738 | 4169.1428 | 4243.8869 | 4283.381 | 4356.3277 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 | 4335.3844 |  | 4489.5373 | 4619.117 | 5114.0541 | 5466.2498 | 5677.5811 | 5846.7694 | 5984.2397 | 6116.4802 | 6230.9382 | 6288.5933 | 6373.297 | 6470.1561 | 6569.0896 | 6693.3562 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191 | 6713.0191
15% | 2954.9137 | 3025.7048 | 3391.1299 | 3654.8586 | 3793.7221 | 3918.0777 | 3997.1945 | 4087.4715 | 4159.6075 | 4206.7578 | 4318.5973 | 4396.0208 | 4436.9307 | 4512.4923 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 | 4490.7983 |  | 2782.0412 | 2862.3381 | 3169.0368 | 3387.2827 | 3518.2388 | 3623.08 | 3708.2666 | 3790.2123 | 3861.1387 | 3896.866 | 3949.3545 | 4009.3754 | 4070.6817 | 4147.6863 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708 | 4159.8708
10% | 1970.104 | 2017.3019 | 2260.9387 | 2436.7722 | 2529.3555 | 2612.266 | 2665.0149 | 2725.2045 | 2773.2991 | 2804.7352 | 2879.301 | 2930.9209 | 2958.1963 | 3008.5749 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 | 2994.1111 |  | 795.9593 | 818.9327 | 906.6811 | 969.1226 | 1006.59 | 1036.5857 | 1060.9581 | 1084.4033 | 1104.6958 | 1114.9176 | 1129.9349 | 1147.1072 | 1164.6473 | 1186.6788 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649 | 1190.1649
5% | 157.0267 | 160.7886 | 180.2077 | 194.2224 | 201.6018 | 208.2101 | 212.4145 | 217.2119 | 221.0452 | 223.5509 | 229.4941 | 233.6085 | 235.7824 | 239.7979 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 | 238.645 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 89607.7949 | 91754.5348 | 102836.0568 | 110833.6316 | 115044.6699 | 118815.7555 | 121214.9726 | 123952.623 | 126140.1488 | 127569.9829 | 130961.5169 | 133309.3862 | 134549.9768 | 136841.3859 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | 136183.5147 | E @ R (MWh) | 84110.3229 | 86537.9646 | 95810.4847 | 102408.7793 | 106368.0177 | 109537.7157 | 112113.1862 | 114590.6774 | 116735.0192 | 117815.1726 | 119402.0743 | 121216.7049 | 123070.1983 | 125398.3005 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805 | 125766.6805
Option 8 Summer POE50 W E @ R (MWh) N 2 | 62725.4564 | 64228.1743 | 71985.2398 | 77583.5421 | 80531.2689 | 83171.0289 | 84850.4808 | 86766.8361 | 88298.1041 | 89298.9881 | 91673.0619 | 93316.5703 | 94184.9837 | 95788.9701 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | 95328.4603 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 25233.0969 | 25961.3894 | 28743.1454 | 30722.6338 | 31910.4053 | 32861.3147 | 33633.9559 | 34377.2032 | 35020.5057 | 35344.5518 | 35820.6223 | 36365.0115 | 36921.0595 | 37619.4901 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041 | 37730.0041

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-OFR-TRNFMR-9000014181 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 2 Pof | DS-OFR-TRNFMR-9000016122 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522% | 0.5522%
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.3818% | 0.3818% | 0.4219% | 0.4644% | 0.5094% | 0.5569% | 0.607% | 0.6597% | 0.715% | 0.7729% | 0.8336% | 0.8971% | 0.9634% | 1.032% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104% | 1.104%
N-1 Risk |  | 0.1473% | 0.1473% | 0.1628% | 0.1792% | 0.1965% | 0.2149% | 0.2342% | 0.2545% | 0.2758% | 0.2982% | 0.3216% | 0.3461% | 0.3717% | 0.3983% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261% | 0.4261%
N-2 Risk |  | 8.542e-05% | 8.542e-05% | 0.0001043% | 0.0001264% | 0.0001521% | 0.0001818% | 0.0002159% | 0.000255% | 0.0002995% | 0.0003501% | 0.0004073% | 0.0004716% | 0.0005439% | 0.0006247% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148% | 0.0007148%
N Risk |  | 99.85% | 99.85% | 99.84% | 99.82% | 99.8% | 99.78% | 99.77% | 99.75% | 99.72% | 99.7% | 99.68% | 99.65% | 99.63% | 99.6% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57% | 99.57%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.10473 | 0.1444 | 0.77561 | 3.0555 | 5.7555 | 8.998 | 13.3279 | 18.1976 | 24.413 | 29.2607 | 35.7549 | 46.6588 | 47.2657 | 65.3577 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.20047 | 0.20706 | 0.28468 | 0.37551 | 0.47161 | 0.58261 | 0.71234 | 0.86249 | 1.0373 | 1.2276 | 1.4539 | 1.7247 | 1.9829 | 2.352 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759
Total EUE (MWh) - Option 1 | 0.3052 | 0.35146 | 1.0603 | 3.431 | 6.2272 | 9.5806 | 14.0402 | 19.0601 | 25.4503 | 30.4883 | 37.2088 | 48.3835 | 49.2485 | 67.7097 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341
Cost of EUE ($) - Option 1 | 13196.3859 | 15196.3984 | 45844.9213 | 148350.7431 | 269249.4833 | 414243.9635 | 607070.7247 | 824119.3833 | 1100419.6711 | 1318251.2557 | 1608830.9194 | 2092003.4094 | 2129406.4711 | 2927630.9309 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178
Hours at Risk pA. (Hrs) (N) | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916 | 0.8916
Option 2 - 1B New PHS ZSS + Three new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.10473 | 0.1444 | 0.77561 | 3.0555 | 0.16308 | 0.30912 | 0.59634 | 1.0985 | 2.01 | 2.7731 | 3.9982 | 6.7646 | 6.3034 | 11.907 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132 | 20.7132
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.20047 | 0.20706 | 0.28468 | 0.37551 | 0.36676 | 0.45729 | 0.56348 | 0.68668 | 0.83078 | 0.9862 | 1.1731 | 1.3995 | 1.6079 | 1.9213 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662 | 2.2662
Total EUE (MWh) - Option 2 | 0.3052 | 0.35146 | 1.0603 | 3.431 | 0.52985 | 0.76641 | 1.1598 | 1.7852 | 2.8408 | 3.7593 | 5.1713 | 8.1641 | 7.9113 | 13.8283 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794 | 22.9794
Cost of EUE ($) - Option 2 | 13196.3859 | 15196.3984 | 45844.9213 | 148350.7431 | 22909.438 | 33138.1215 | 50148.1033 | 77188.9986 | 122828.9999 | 162544.6491 | 223598.4879 | 352997.3507 | 342068.9058 | 597906.8533 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78 | 993583.78
Option 3 - 2B PHM 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.10473 | 0.1444 | 0.77561 | 0.4818 | 0.0227 | 0.049285 | 0.08554 | 0.14504 | 0.23896 | 0.33104 | 0.51421 | 1.0188 | 0.98882 | 2.3462 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.20047 | 0.20706 | 0.28468 | 0.33194 | 0.31434 | 0.39463 | 0.48905 | 0.59877 | 0.72752 | 0.86551 | 1.0327 | 1.2369 | 1.4204 | 1.706 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198
Total EUE (MWh) - Option 3 | 0.3052 | 0.35146 | 1.0603 | 0.81374 | 0.33704 | 0.44392 | 0.57459 | 0.74382 | 0.96648 | 1.1965 | 1.5469 | 2.2558 | 2.4092 | 4.0522 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304
Cost of EUE ($) - Option 3 | 13196.3859 | 15196.3984 | 45844.9213 | 35184.4137 | 14572.768 | 19194.0255 | 24844.0046 | 32161.0752 | 41788.4821 | 51736.2577 | 66885.8549 | 97534.3462 | 104170.0637 | 175207.2761 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483
Option 4 - 3B OFR 3rd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.10473 | 0.1444 | 0.77561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.20047 | 0.20706 | 0.28468 | 0.0036061 | 0.0069116 | 0.011222 | 0.017456 | 0.025158 | 0.03569 | 0.045691 | 0.05917 | 0.081513 | 0.08874 | 0.12865 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035
Total EUE (MWh) - Option 4 | 0.3052 | 0.35146 | 1.0603 | 0.0036061 | 0.0069116 | 0.011222 | 0.017456 | 0.025158 | 0.03569 | 0.045691 | 0.05917 | 0.081513 | 0.08874 | 0.12865 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035 | 0.18035
Cost of EUE ($) - Option 4 | 13196.3859 | 15196.3984 | 45844.9213 | 155.9224 | 298.8454 | 485.2322 | 754.7819 | 1087.8001 | 1543.1527 | 1975.5832 | 2558.3798 | 3524.4367 | 3836.9522 | 5562.7507 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645 | 7797.9645
Option 5 - 4B LLG 2nd Tx + Switchroom + Two new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.10473 | 0.1444 | 0.77561 | 0.4818 | 0.0227 | 0.049285 | 0.08554 | 0.14504 | 0.23896 | 0.33104 | 0.51421 | 1.0188 | 0.98882 | 2.3462 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106 | 5.6106
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.20047 | 0.20706 | 0.28468 | 0.33194 | 0.31434 | 0.39463 | 0.48905 | 0.59877 | 0.72752 | 0.86551 | 1.0327 | 1.2369 | 1.4204 | 1.706 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198 | 2.0198
Total EUE (MWh) - Option 5 | 0.3052 | 0.35146 | 1.0603 | 0.81374 | 0.33704 | 0.44392 | 0.57459 | 0.74382 | 0.96648 | 1.1965 | 1.5469 | 2.2558 | 2.4092 | 4.0522 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304 | 7.6304
Cost of EUE ($) - Option 5 | 13196.3859 | 15196.3984 | 45844.9213 | 35184.4137 | 14572.768 | 19194.0255 | 24844.0046 | 32161.0752 | 41788.4821 | 51736.2577 | 66885.8549 | 97534.3462 | 104170.0637 | 175207.2761 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483 | 329921.8483
Option 6 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.10473 | 0.1444 | 0.77561 | 3.0555 | 5.7555 | 8.998 | 13.3279 | 18.1976 | 24.413 | 29.2607 | 35.7549 | 46.6588 | 47.2657 | 65.3577 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.20047 | 0.20706 | 0.28468 | 0.37551 | 0.47161 | 0.58261 | 0.71234 | 0.86249 | 1.0373 | 1.2276 | 1.4539 | 1.7247 | 1.9829 | 2.352 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759
Total EUE (MWh) - Option 6 | 0.3052 | 0.35146 | 1.0603 | 3.431 | 6.2272 | 9.5806 | 14.0402 | 19.0601 | 25.4503 | 30.4883 | 37.2088 | 48.3835 | 49.2485 | 67.7097 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341
Cost of EUE ($) - Option 6 | 13196.3859 | 15196.3984 | 45844.9213 | 148350.7431 | 269249.4833 | 414243.9635 | 607070.7247 | 824119.3833 | 1100419.6711 | 1318251.2557 | 1608830.9194 | 2092003.4094 | 2129406.4711 | 2927630.9309 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.10473 | 0.1444 | 0.77561 | 3.0555 | 5.7555 | 8.998 | 13.3279 | 18.1976 | 24.413 | 29.2607 | 35.7549 | 46.6588 | 47.2657 | 65.3577 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.20047 | 0.20706 | 0.28468 | 0.37551 | 0.47161 | 0.58261 | 0.71234 | 0.86249 | 1.0373 | 1.2276 | 1.4539 | 1.7247 | 1.9829 | 2.352 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759
Total EUE (MWh) - Option 7 | 0.3052 | 0.35146 | 1.0603 | 3.431 | 6.2272 | 9.5806 | 14.0402 | 19.0601 | 25.4503 | 30.4883 | 37.2088 | 48.3835 | 49.2485 | 67.7097 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341
Cost of EUE ($) - Option 7 | 13196.3859 | 15196.3984 | 45844.9213 | 148350.7431 | 269249.4833 | 414243.9635 | 607070.7247 | 824119.3833 | 1100419.6711 | 1318251.2557 | 1608830.9194 | 2092003.4094 | 2129406.4711 | 2927630.9309 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.10473 | 0.1444 | 0.77561 | 3.0555 | 5.7555 | 8.998 | 13.3279 | 18.1976 | 24.413 | 29.2607 | 35.7549 | 46.6588 | 47.2657 | 65.3577 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751 | 86.9751
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.20047 | 0.20706 | 0.28468 | 0.37551 | 0.47161 | 0.58261 | 0.71234 | 0.86249 | 1.0373 | 1.2276 | 1.4539 | 1.7247 | 1.9829 | 2.352 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759 | 2.759
Total EUE (MWh) - Option 8 | 0.3052 | 0.35146 | 1.0603 | 3.431 | 6.2272 | 9.5806 | 14.0402 | 19.0601 | 25.4503 | 30.4883 | 37.2088 | 48.3835 | 49.2485 | 67.7097 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341 | 89.7341
Cost of EUE ($) - Option 8 | 13196.3859 | 15196.3984 | 45844.9213 | 148350.7431 | 269249.4833 | 414243.9635 | 607070.7247 | 824119.3833 | 1100419.6711 | 1318251.2557 | 1608830.9194 | 2092003.4094 | 2129406.4711 | 2927630.9309 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178 | 3879919.0178