## Info
Document description
This model Energy at Risk model has been developed to calculated Energy at Risk (EaR) in terms of Expected Unsureved Energy (EUE) and the cost of EUE. The modelling inputs, calculation steps and outputs are described in the 'Modelling Steps' tab. Further detail on EaR/EUE calculations can be found in AusNet's Network Planning Policy and Guidelines.
Tab # | Tab Name | Description | Source/ Inputs
0.1 | Modelling Steps | E@R model process flowchart and underlying equations | N/A
0.2 | Modelling Example & QA | Example E@R model calculations and data flow; also used to validate base case | N/A
0.3 | QA | Quality assurance and data validation | Entire workbook
1.1 | Output for AusNet's NPV Model | Aggregates Supply Risk ($M) and EUE (MWh) for input into AusNet’s NPV model | Summary tab
2.1 | Key Model Assumptions & Inputs | E@R model inputs and asset selection | Augmentation plans from RPs/EPCs, Embedded Generation DB, Demand Management DB
2.2 | Tx PoF | Transformer Probabilities of Failure | Provided by Asset Management Team
2.3 | Customer No. and Volume per Feeder | Customer consumption data | Provided by Finance Team
2.4 | AER VCR Rates (2024) | AER 2024 VCR rates | AER VCR Factsheet
2.5 | Forecast - Summer | Summer Forecast Data | Extract from Forecasting Toolbox
2.6 | Forecast- Winter | Winter Forecast Data | Extract from Forecasting Toolbox
2.7 | Ratings | Station Rating Data | AMS 20-101 / Provided by Asset mangement Team
2.8 | FT (Forecast & Transfers) | Forecast, transfer & PF inputs | Forecast Summer , Forecast Winter , NP Transfer Sheet, PF = avg. max demand PF across stations
2.9 | Load Duration Curves | Load duration curve data | LDC Tool; data sourced from PI SCADA Historian and AEMO
3.1 | Capacity N | Option N capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.2 | Capacity N-1 | Option N-1 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.3 | Capacity N-1 | Option N-2 capacity calculated | FT Sheet, Ratings & Key Model Assumptions
3.4 | Demand | Calculates maximum demand | FT Sheet & Key Model Assumptions
3.5 | MD Weighted LDC | Maps maximum demand forecast to load duration curve | Demand Sheet & Load Duration Curve Sheet
3.6 | Locational VCR | Calculates tailored VCR by location using feeder energy mix and AER rates | AER VCR Rates (2024) & Customer No./Volume per Feeder
3.7 | E@R N | Calculates N EUE using capacity and demand inputs | MD Weighted LDC & Capacity N
3.8 | E@R N-1 | Calculates N-1 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-1
3.9 | E@R N-2 | Calculates N-2 EUE using capacity and demand inputs | MD Weighted LDC & Capacity N-2
4 | POF N,N-1 & N-2 Risk | Calculates Station N , N-1 & N-2 PoF's from Tx PoF Data & MTTR | TX PoF & Key Model Assumptions
4.1 | Summary | Collates weighted EUE and calculates supply risk | E@R & Locational VCR
Revision table
Date | Editted by | Change
2025-10-14 | HT | Draft Version 2.1
2025-10-20 | HT | Version 2.2
2025-11-10 | HT | Version 2.3 Example Page Update and General Refinements

## Modelling Steps
Eq1. Locational VCR |  | Data Inputs |  |  | Calculations |  |  |  |  | Outputs
|  |  | Customer No. and Vol per Feeder |  | Eq1.
Locational VCR
Eq2. Maximum Demand
AER Latetst VCR Rates
Eq3. Options & Do nothing Capacity
Eq6. & Eq7.
Load Forecast
[9 empty] | Summary Sheet | Output for AusNet's NPV Model
Eq4. Help Sheet | Re Name Forecasted LDC add Forecast MD to eq
Transfer Capacity
Eq2.
Eq5. Energy at Risk ( Option/ Do Nothing Capacity) |  |  |  |  | Options & Do Nothing Max Demand
Embeded Generation
Eq6. Weighted Expected Unserved Energy
[6 empty] | Eq.4 | Eq.5
Demand Mangement Capacity
[6 empty] | Forecasted LDC |  | Energy @ Risk Sheet
Eq7. Supply Risk
Load Duration Curves
|  |  | Asset Ratings |  | Eq3.
Options & Do Nothing Capacity
Planned & Proposed Works

## Modelling Steps Example & QA
End of Sheet
Data Inputs |  |  | Calculations | [12 empty] | Outputs
AER VCR Rates(2024 |  |  | Locational (Tailored VCR)
Category | Rate |  | Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 |  | Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 |  | Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 |  | Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 |  | Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
[5 empty] | 199480479.3698 |  | 38.6062
Customer No. and Vol per Feeder | [6 empty] | 38606.1513 | [8 empty] | Summary |  | Outputs for NPV model
COMMERCIAL | 101368150.4504 | [14 empty] | Year | 2031 | Year | 2031
[16 empty] | E@R MWh | 10.0369 | E@R MWh | 10.0369
RESIDENTL | 67934749.1441 | [14 empty] | cost of EUE ($) | 387486.1996 | cost of EUE ($M) | 0.38749
FARM | 12451243.5083
INDUSTRIAL | 17726336.2671
Forecast (FCT)
Forecast | 2031
Summer POE50 | 82.5169
Summer POE10 | 89.3084
Winter POE50 | 80.6241
Winter POE10 | 83.8742
Transfer Capacity |  |  | Option Max Demand |  |  |  | MD Weighted LDC |  |  | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
Year | 2031 |  | Forecast | 2031 |  |  | % of MD | Summer - AD - Hours | FY31 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
Capacity | 1.58 |  | Summer POE50 | 80.9369 |  |  | 100% | 0 | 80.9369 | 100% |  | 100% |  | 100%
|  |  | Summer POE10 | 87.7284 |  |  | 99% | 0 | 80.1275 | 99% |  | 99% | 0 | 99% | 0
Embedded Generation |  |  | Winter POE50 | 79.0441 |  |  | 98% | 0 | 79.3181 | 98% |  | 98% | 0 | 98% | 0
|  |  | Winter POE10 | 82.2942 |  |  | 97% | 0.37816 | 78.5088 | 97% |  | 97% | 12.8249 | 97% | 29.8423
Year | 2031 | [5 empty] | 95% | 2.269 | 76.89 | 95% |  | 95% | 61.8287 | 95% | 146.9157
Capacity | 0 | [5 empty] | 90% | 5.6725 | 72.8432 | 90% |  | 90% | 101.6504 | 90% | 254.8069
[7 empty] | 85% | 15.8829 | 68.7963 | 85% |  | 85% | 263.6311 | 85% | 723.1007
Demand Mangement | [6 empty] | 80% | 31.0095 | 64.7495 | 80% |  | 80% | 329.3497 | 80% | 1010.0454
[7 empty] | 75% | 72.9857 | 60.7027 | 75% |  | 75% | 744.0742 | 75% | 2633.0048
Year | 2031 | [5 empty] | 70% | 150.5094 | 56.6558 | 70% |  | 70% | 1060.4649 | 70% | 4549.0304
Capacity | 0 | [5 empty] | 65% | 359.6342 | 52.609 | 65% |  | 65% | 2014.373 | 65% | 11424.9912
[7 empty] | 60% | 689.7717 | 48.5621 | 60% |  | 60% | 1843.9992 | 60% | 16700.1831
LDC | [6 empty] | 55% | 1095.5419 | 44.5153 | 55% |  | 55% | 636.1403 | 55% | 18884.0238
[7 empty] | 50% | 1666.1918 | 40.4684 | 50% |  | 50% |  | 50% | 24247.9772
% of MD | Summer - AD - Duration % | Summer - AD - Hours |  |  |  |  | 45% | 2506.0947 | 36.4216 | 45% |  | 45% |  | 45% | 32290.0814
100% | 0% | 0 |  |  |  |  | 40% | 3164.4787 | 32.3748 | 40% |  | 40% |  | 40% | 22647.2082
99% | 0% | 0 |  |  |  |  | 35% | 3551.3408 | 28.3279 | 35% |  | 35% |  | 35% | 11741.7782
98% | 0% | 0 |  |  |  |  | 30% | 3758.953 | 24.2811 | 30% |  | 30% |  | 30% | 5461.132
97% | 0.00861% | 0.37816 |  |  |  |  | 25% | 3926.4798 | 20.2342 | 25% |  | 25% |  | 25% | 3728.7511
95% | 0.05166% | 2.269 |  |  |  |  | 20% | 4050.5177 | 16.1874 | 20% |  | 20% |  | 20% | 2258.8289
90% | 0.1292% | 5.6725 |  |  |  |  | 15% | 4152.622 | 12.1405 | 15% |  | 15% |  | 15% | 1446.2014
85% | 0.3616% | 15.8829 |  |  |  |  | 10% | 4248.2976 | 8.0937 | 10% |  | 10% |  | 10% | 967.9602
80% | 0.706% | 31.0095 |  |  |  |  | 5% | 4361.7469 | 4.0468 | 5% |  | 5% |  | 5% | 688.6673
75% | 1.662% | 72.9857 |  |  |  |  | 9.992e-14% | 4391.6218 | 8.0872e-14 | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 60.4497
70% | 3.427% | 150.5094 | [7 empty] | Total E@R | 0 | Total E@R | 7068.3364 | Total E@R | 161894.98
65% | 8.188% | 359.6342 | [7 empty] | Total WE@R | 0 | Total WE@R | 2.1876 | Total WE@R | 0.0065575
60% | 15.71% | 689.7717 |  |  |  |  | MD Weighted LDC
55% | 24.94% | 1095.5419
50% | 37.94% | 1666.1918 |  |  |  |  | % of MD | Summer - MD - Hours | FY31
45% | 57.06% | 2506.0947 |  |  |  |  | 100% | 0 | 87.7284 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
40% | 72.05% | 3164.4787 |  |  |  |  | 99% | 1.5127 | 86.8512
35% | 80.86% | 3551.3408 |  |  |  |  | 98% | 2.269 | 85.9739 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
30% | 85.59% | 3758.953 |  |  |  |  | 97% | 3.7816 | 85.0966 | 100% |  | 100% |  | 100%
25% | 89.4% | 3926.4798 |  |  |  |  | 95% | 6.0506 | 83.342 | 99% |  | 99% | 63.97 | 99% | 132.0395
20% | 92.22% | 4050.5177 |  |  |  |  | 90% | 16.2611 | 78.9556 | 98% |  | 98% | 31.3215 | 98% | 65.3562
15% | 94.55% | 4152.622 |  |  |  |  | 85% | 26.4715 | 74.5692 | 97% |  | 97% | 61.3159 | 97% | 129.3855
10% | 96.73% | 4248.2976 |  |  |  |  | 80% | 34.0348 | 70.1827 | 95% |  | 95% | 88.988 | 95% | 191.0924
5% | 99.31% | 4361.7469 |  |  |  |  | 75% | 48.405 | 65.7963 | 90% |  | 90% | 369.095 | 90% | 828.5646
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 70% | 76.3892 | 61.4099 | 85% |  | 85% | 324.3078 | 85% | 783.7774
[7 empty] | 65% | 114.2056 | 57.0235 | 80% |  | 80% | 207.0522 | 80% | 547.4001
[7 empty] | 60% | 178.1154 | 52.6371 | 75% |  | 75% | 330.3652 | 75% | 977.0262
[7 empty] | 55% | 311.6074 | 48.2506 | 70% |  | 70% | 520.5925 | 70% | 1779.8796
LDC | [6 empty] | 50% | 636.0723 | 43.8642 | 65% |  | 65% | 537.6246 | 65% | 2239.3639
[7 empty] | 45% | 1179.4944 | 39.4778 | 60% |  | 60% | 628.2504 | 60% | 3504.1898
% of MD | Summer - MD - Duration % | Summer - MD - Hours |  |  |  |  | 40% | 1808.3816 | 35.0914 | 55% |  | 55% | 726.7105 | 55% | 6733.8501
100% | 0% | 0 |  |  |  |  | 35% | 2779.1293 | 30.705 | 50% |  | 50% | 390.8095 | 50% | 14944.0217
99% | 0.03444% | 1.5127 |  |  |  |  | 30% | 3814.165 | 26.3185 | 45% |  | 45% |  | 45% | 22644.9453
98% | 0.05166% | 2.269 |  |  |  |  | 25% | 4166.9923 | 21.9321 | 40% |  | 40% |  | 40% | 23447.7987
97% | 0.0861% | 3.7816 |  |  |  |  | 20% | 4282.7105 | 17.5457 | 35% |  | 35% |  | 35% | 31935.8172
95% | 0.1378% | 6.0506 |  |  |  |  | 15% | 4364.7722 | 13.1593 | 30% |  | 30% |  | 30% | 29510.6691
90% | 0.3702% | 16.2611 |  |  |  |  | 10% | 4391.6218 | 8.7728 | 25% |  | 25% |  | 25% | 8512.071
85% | 0.6027% | 26.4715 |  |  |  |  | 5% | 4391.6218 | 4.3864 | 20% |  | 20% |  | 20% | 2284.1512
80% | 0.7749% | 34.0348 |  |  |  |  | 9.992e-14% | 4391.6218 | 8.7658e-14 | 15% |  | 15% |  | 15% | 1259.8495
75% | 1.102% | 48.405 | [7 empty] | 10% |  | 10% |  | 10% | 294.4349
70% | 1.739% | 76.3892 | [7 empty] | 5% |  | 5% |  | 5% | 0
65% | 2.6% | 114.2056 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
60% | 4.055% | 178.1154 | [7 empty] | Total E@R | 0 | Total E@R | 4280.4031 | Total E@R | 152745.6837
55% | 7.095% | 311.6074 |  |  |  |  | MD Weighted LDC |  |  | Total WE@R | 0 | Total WE@R | 0.56774 | Total WE@R | 0.0026515
50% | 14.48% | 636.0723
45% | 26.86% | 1179.4944 |  |  |  |  | % of MD | Winter - AD - Hours | FY31
40% | 41.17% | 1808.3816 |  |  |  |  | 100% | 0 | 79.0441
35% | 63.28% | 2779.1293 |  |  |  |  | 99% | 1.486 | 78.2537 | E@R (N) |  | E@R (N-1) |  | E@R (N-2)
30% | 86.84% | 3814.165 |  |  |  |  | 98% | 3.2692 | 77.4632
25% | 94.88% | 4166.9923 |  |  |  |  | 97% | 6.8356 | 76.6728 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 97.51% | 4282.7105 |  |  |  |  | 95% | 17.5347 | 75.0919 | 100% |  | 100% |  | 100%
15% | 99.38% | 4364.7722 |  |  |  |  | 90% | 78.7576 | 71.1397 | 99% |  | 99% | 43.9094 | 99% | 116.8717
10% | 99.99% | 4391.6218 |  |  |  |  | 85% | 236.8672 | 67.1875 | 98% |  | 98% | 51.2818 | 98% | 138.8365
5% | 99.99% | 4391.6218 |  |  |  |  | 80% | 497.5104 | 63.2353 | 97% |  | 97% | 99.7446 | 97% | 274.854
9.992e-14% | 99.99% | 4391.6218 |  |  |  |  | 75% | 803.6248 | 59.2831 | 95% |  | 95% | 286.5483 | 95% | 811.8764
[7 empty] | 70% | 1155.2107 | 55.3309 | 90% |  | 90% | 1470.3172 | 90% | 4476.3615
[7 empty] | 65% | 1553.1596 | 51.3787 | 85% |  | 85% | 3172.248 | 85% | 10935.4305
[7 empty] | 60% | 2026.2996 | 47.4265 | 80% |  | 80% | 4199.3237 | 80% | 16996.9008
LDC | [6 empty] | 55% | 2598.4068 | 43.4743 | 75% |  | 75% | 3722.1035 | 75% | 18752.3252
[7 empty] | 50% | 3233.5201 | 39.5221 | 70% |  | 70% | 2885.4588 | 70% | 20148.3251
% of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours |  |  |  |  | 45% | 3775.313 | 35.5699 | 65% |  | 65% | 1693.1832 | 65% | 21232.4714
100% | 0% | 0 |  |  |  |  | 40% | 4072.8088 | 31.6176 | 60% |  | 60% | 310.8024 | 60% | 23374.3358
99% | 0.03383% | 1.486 |  |  |  |  | 35% | 4198.821 | 27.6654 | 55% |  | 55% |  | 55% | 26002.4804
98% | 0.07443% | 3.2692 |  |  |  |  | 30% | 4271.3374 | 23.7132 | 50% |  | 50% |  | 50% | 26356.0319
97% | 0.1556% | 6.8356 |  |  |  |  | 25% | 4321.8611 | 19.761 | 45% |  | 45% |  | 45% | 20342.1324
95% | 0.3992% | 17.5347 |  |  |  |  | 20% | 4353.067 | 15.8088 | 40% |  | 40% |  | 40% | 9993.9968
90% | 1.793% | 78.7576 |  |  |  |  | 15% | 4369.4129 | 11.8566 | 35% |  | 35% |  | 35% | 3735.1954
85% | 5.393% | 236.8672 |  |  |  |  | 10% | 4378.6261 | 7.9044 | 30% |  | 30% |  | 30% | 1862.8993
80% | 11.33% | 497.5104 |  |  |  |  | 5% | 4391.7028 | 3.9522 | 25% |  | 25% |  | 25% | 1098.2414
75% | 18.3% | 803.6248 |  |  |  |  | 9.992e-14% | 4391.7028 | 7.8981e-14 | 20% |  | 20% |  | 20% | 554.9937
70% | 26.3% | 1155.2107 | [7 empty] | 15% |  | 15% |  | 15% | 226.1085
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 91.0307
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 77.5229
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% |  | 9.992e-14% | 0
50% | 73.62% | 3233.5201 |  |  |  |  | MD Weighted LDC |  |  | Total E@R | 0 | Total E@R | 17934.9211 | Total E@R | 207599.2223
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 4.7159 | Total WE@R | 0.0071443
40% | 92.73% | 4072.8088 |  |  |  |  | % of MD | Winter - MD - Hours | FY31
35% | 95.6% | 4198.821 |  |  |  |  | 100% | 0 | 82.2942 | E@R (N) |  | E@R (N) |  | E@R (N)
30% | 97.25% | 4271.3374 |  |  |  |  | 99% | 1.486 | 81.4712
25% | 98.4% | 4321.8611 |  |  |  |  | 98% | 3.2692 | 80.6483 | % of MD | FY31 | % of MD | FY31 | % of MD | FY31
20% | 99.11% | 4353.067 |  |  |  |  | 97% | 6.8356 | 79.8254 | 100% |  | 100% |  | 100%
15% | 99.49% | 4369.4129 |  |  |  |  | 95% | 17.5347 | 78.1795 | 99% |  | 99% | 48.7149 | 99% | 121.6771
10% | 99.7% | 4378.6261 |  |  |  |  | 90% | 78.7576 | 74.0648 | 98% |  | 98% | 56.9904 | 98% | 144.5451
5% | 99.99% | 4391.7028 |  |  |  |  | 85% | 236.8672 | 69.9501 | 97% |  | 97% | 111.0458 | 97% | 286.1552
9.992e-14% | 99.99% | 4391.7028 |  |  |  |  | 80% | 497.5104 | 65.8353 | 95% |  | 95% | 319.9304 | 95% | 845.2585
[7 empty] | 75% | 803.6248 | 61.7206 | 90% |  | 90% | 1654.3725 | 90% | 4660.4169
[7 empty] | 70% | 1155.2107 | 57.6059 | 85% |  | 85% | 3621.8821 | 85% | 11385.0646
[7 empty] | 65% | 1553.1596 | 53.4912 | 80% |  | 80% | 4898.1884 | 80% | 17695.7655
LDC | [6 empty] | 60% | 2026.2996 | 49.3765 | 75% |  | 75% | 4493.1463 | 75% | 19523.368
[7 empty] | 55% | 2598.4068 | 45.2618 | 70% |  | 70% | 3713.9012 | 70% | 20976.7675
% of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours |  |  |  |  | 50% | 3233.5201 | 41.1471 | 65% |  | 65% | 2566.2027 | 65% | 22105.4909
100% | 0% | 0 |  |  |  |  | 45% | 3775.313 | 37.0324 | 60% |  | 60% | 1104.2451 | 60% | 24335.4227
99% | 0.03383% | 1.486 |  |  |  |  | 40% | 4072.8088 | 32.9177 | 55% |  | 55% | 5.3153 | 55% | 27071.6291
98% | 0.07443% | 3.2692 |  |  |  |  | 35% | 4198.821 | 28.803 | 50% |  | 50% |  | 50% | 27439.7177
97% | 0.1556% | 6.8356 |  |  |  |  | 30% | 4271.3374 | 24.6883 | 45% |  | 45% |  | 45% | 21178.5436
95% | 0.3992% | 17.5347 |  |  |  |  | 25% | 4321.8611 | 20.5735 | 40% |  | 40% |  | 40% | 10404.9218
90% | 1.793% | 78.7576 |  |  |  |  | 20% | 4353.067 | 16.4588 | 35% |  | 35% |  | 35% | 3888.7761
85% | 5.393% | 236.8672 |  |  |  |  | 15% | 4369.4129 | 12.3441 | 30% |  | 30% |  | 30% | 1939.4965
80% | 11.33% | 497.5104 |  |  |  |  | 10% | 4378.6261 | 8.2294 | 25% |  | 25% |  | 25% | 1143.398
75% | 18.3% | 803.6248 |  |  |  |  | 5% | 4391.7028 | 4.1147 | 20% |  | 20% |  | 20% | 577.8134
70% | 26.3% | 1155.2107 |  |  |  |  | 9.992e-14% | 4391.7028 | 8.2228e-14 | 15% |  | 15% |  | 15% | 235.4055
65% | 35.36% | 1553.1596 | [7 empty] | 10% |  | 10% |  | 10% | 94.7736
60% | 46.14% | 2026.2996 | [7 empty] | 5% |  | 5% |  | 5% | 80.7104
55% | 59.16% | 2598.4068 | [7 empty] | 9.992e-14% |  | 9.992e-14% | 0 | 9.992e-14% | 0
50% | 73.62% | 3233.5201 | [7 empty] | Total E@R | 0 | Total E@R | 22593.9352 | Total E@R | 216135.1177
45% | 85.96% | 3775.313 | [7 empty] | Total WE@R | 0 | Total WE@R | 2.5461 | Total WE@R | 0.0031877
40% | 92.73% | 4072.8088
35% | 95.6% | 4198.821
30% | 97.25% | 4271.3374
25% | 98.4% | 4321.8611
20% | 99.11% | 4353.067
15% | 99.49% | 4369.4129
10% | 99.7% | 4378.6261
5% | 99.99% | 4391.7028
9.992e-14% | 99.99% | 4391.7028
Ratings (MVA) |  |  |  | Option Capacity
SCR (N) | 91.9 |  |  | Year | 2031
SCR (N-1) | 45 |  |  | SCR (N) | 91.9
SCR (N-2) | 0 |  |  | SCR (N-1) | 45
WCR (N) | 95.7 |  |  | SCR (N-2) | 0
WCR (N-1) | 49.1 |  |  | WCR (N) | 95.7
WCR (N-2) | 0 |  |  | WCR (N-1) | 49.1
|  |  |  | WCR (N-2) | 0
Planned Works
Year | 2031
Capacity (N) | 0
Capacity (N-1) | 0
Capacity (N-2) | 0
Power Factor
Value | 1
End of Sheet

## QA
Overall Status
Good
Number | Check Name | Status | Info
1 | Forecast | Good | Confirms POE10 forecast is higher than POE50
2 | Option Maximum Demand | Good | Confirms whether transfers, embedded generation, and demand management contribute to demand reduction when present
3 | EUE Base Case | Good | Confirms Do Nothing/Base Case EUE for FY31 is the same as the example / checks model in Modelling Steps Example Sheet
4 | Feeder Consumption | Good | Confirms if aggregated feeder energy consumption by customer category matches with total feeder energy consumption (excluding uncategorised consumption)

## Output for AusNet's NPV model
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Base Case
Cost
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.15651 | 0.20359 | 0.27196 | 0.38749 | 0.51872 | 0.70091 | 0.97181 | 1.0624 | 1.1495 | 1.4581 | 1.9768 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Residual Values
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.00079776 | 0.0010467 | 0.0014866 | 0.002524 | 0.0042842 | 0.0094572 | 0.039838 | 0.021712 | 0.018765 | 0.033762 | 0.085667 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 0.020664 | 0.027112 | 0.038506 | 0.065379 | 0.11097 | 0.24497 | 1.0319 | 0.5624 | 0.48606 | 0.87452 | 2.219 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 1.4963e-05 | 2.4358e-05 | 3.9698e-05 | 6.7481e-05 | 0.00010654 | 0.00016781 | 0.00027133 | 0.00035474 | 0.00046329 | 0.00065563 | 0.0010211 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164 | 0.0011164
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 0.00038758 | 0.00063093 | 0.0010283 | 0.0017479 | 0.0027597 | 0.0043468 | 0.0070283 | 0.0091888 | 0.012 | 0.016983 | 0.026449 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.021895 | 0.030054 | 0.04472 | 0.078826 | 0.11879 | 0.18509 | 0.30953 | 0.30957 | 0.31075 | 0.43445 | 0.67076 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667 | 0.61667
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 0.56715 | 0.77847 | 1.1584 | 2.0418 | 3.077 | 4.7942 | 8.0175 | 8.0187 | 8.0493 | 11.2533 | 17.3744 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.00079776 | 0.0010467 | 0.0014866 | 0.002524 | 0.0042842 | 0.0094572 | 0.039838 | 0.021712 | 0.018765 | 0.033762 | 0.085667 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752 | 0.056752
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 0.020664 | 0.027112 | 0.038506 | 0.065379 | 0.11097 | 0.24497 | 1.0319 | 0.5624 | 0.48606 | 0.87452 | 2.219 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.00030971 | 0.010386 | 0.031925 | 0.044942 | 0.060361 | 0.085155 | 0.1346 | 0.19149 | 0.27952 | 0.43075 | 0.44146 | 0.45001 | 0.60828 | 0.88648 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828 | 0.84828
Total EUE (MWh) | 0.0080222 | 0.26904 | 0.82695 | 1.1641 | 1.5635 | 2.2057 | 3.4864 | 4.9602 | 7.2403 | 11.1575 | 11.4349 | 11.6563 | 15.7561 | 22.9621 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.15651 | 0.20359 | 0.27196 | 0.38749 | 0.51872 | 0.70091 | 0.97181 | 1.0624 | 1.1495 | 1.4581 | 1.9768 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Cost of Avoided EUE ($M) | 0.0013201 | 0.05225 | 0.11664 | 0.15651 | 0.20359 | 0.27196 | 0.38749 | 0.51872 | 0.70091 | 0.97181 | 1.0624 | 1.1495 | 1.4581 | 1.9768 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779 | 1.9779
Total EUE (MWh) | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234

## Key Model Assumption & Inputs
Select ZSS & Region | PHM | Central | MTTR
Probability Weighting for 10% POE MDs | 30% |  |  | Central | North | East | For Analysis
Probability Weighting for 50% POE MDs | 70% |  | N-1 MTTR (years) | 0.3858 | 0.1418 | 0.3858 | 0.3858
First year of analysis | FY25 |  | N-2 MTTR (years) | 0.2344 | 0.049 | 0.2344 | 0.2344
Select Sensitivity Variant | Forecast Sensitivity
High | 110% |  | PV Factor's |  |  | PoF Sensitvity
Options | Name |  | Summer | 1.33 |  | Varaint
Option 1 - Do Nothing / Base Case | Do Nothing / Base Case |  | Winter | 1.13 |  | Base | 100%
Option 2 - 1A New PHS ZSS + Four new feeders | 1A New PHS ZSS + Four new feeders
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Demand Response
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder |  | Average Rate % | 20%
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Option 6 - Non Network | Non Network
Option 7 -
Option 8 -
Added Capacity (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Added Capacity (MVA) Option 1 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 1 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 2 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 3 N |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-1 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 3 N-2 |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Added Capacity (MVA) Option 4 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 4 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 5 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 6 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 7 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Capacity (MVA) Option 8 N-2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Embedded Generation (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Embedded Generation (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Embedded Generation (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Demand Management (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Avaliable Demand Management (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 2 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 4 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 5 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 6 | 7.7456 | 9.9603 | 10.5358 | 10.4984 | 10.4969 | 10.5537 | 10.7079 | 10.8089 | 10.9091 | 11.0267 | 11.1341 | 11.2396 | 11.2492 | 11.3728 | 11.2743
Added Demand Management (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Demand Management (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Transfers (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Planned Transfers (MVA) Option 1 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 2 |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Transfers (MVA) Option 3 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 4 |  |  |  | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Transfers (MVA) Option 5 |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Transfers (MVA) Option 6 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 7 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Added Transfers (MVA) Option 8 | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Block Loads Not in Forecast (MVA) | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Block Loads (MVA) | FY32: 0; FY33: 0; FY34: 0; FY35: 0; FY36: 0; FY37: 0; FY38: 0; FY39: 0
Base | FY25: 100%
High | FY25: 110%
Low | FY25: 90%

## Tx PoF
Transformer Failure Rates for individual Transformers
[5 empty] | 10 | 8 | 10 | 6 | 8 | 6 | 6 | 10 | 6
Zone | arm_asset_id | floc | user_status | Age | Major Winding insulation | Accelerated cellulose Aging | Winding insulating liquid | Hot metal fault covered by paper | Chemical contamination, degradation | Physical & chemical contamination, degradation | Physical contamination | Short Circuit Concern | OLTC | WMA Health Score | WMA CS | WMA effective age | WMA Beta | WMA Eta | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WGI | 30192717 | DS-WGI-TRNFMR-9000004493 |  | 59 | 5 | 3 | 1 | 5 | 2 | 1 | 5 | 5 | 5 | 351.4286 | 4 | 60 | 3.5 | 82 | 1.976% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089% | 3.195% | 3.303% | 3.413% | 3.525% | 3.639% | 3.755% | 3.873% | 3.994% | 4.116% | 4.241% | 4.368% | 4.497% | 4.628% | 4.761% | 4.897% | 5.034%
WGI | 30111322 | DS-WGI-TRNFMR-9000003147 |  | 59 | 5 | 5 | 1 | 3 | 2 | 1 | 4 | 5 | 5 | 348.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30026486 | DS-EPG-TRNFMR-9000010175 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
EPG | 30058367 | DS-EPG-TRNFMR-9000010174 |  | 45 | 5 | 3 | 2 | 1 | 2 | 1 | 4 | 5 | 5 | 322.8571 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
WGI | 30475971 | DS-WGI-TRNFMR-9000007146 |  | 49 | 5 | 5 | 1 | 1 | 1 | 1 | 2 | 5 | 1 | 268.5714 | 3 | 44 | 3.5 | 82 | 0.9218% | 0.9218% | 0.9742% | 1.028% | 1.084% | 1.142% | 1.201% | 1.262% | 1.325% | 1.39% | 1.457% | 1.525% | 1.596% | 1.668% | 1.742% | 1.818% | 1.896% | 1.976% | 2.058% | 2.142% | 2.227% | 2.315% | 2.405% | 2.496% | 2.59% | 2.686% | 2.783% | 2.883% | 2.985% | 3.089%
EPG | 30209984 | DS-EPG-TRNFMR-9000007095 |  | 24 | 3 | 3 | 1 | 3 | 2 | 1 | 4 | 3 | 3 | 251.4286 | 3 | 44 | 3.5 | 84.05 | 0.8458% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276% | 1.337% | 1.4% | 1.465% | 1.531% | 1.599% | 1.669% | 1.741% | 1.814% | 1.889% | 1.966% | 2.045% | 2.125% | 2.208% | 2.292% | 2.378% | 2.466% | 2.556% | 2.648% | 2.741% | 2.837%
CLN | 30338702 | DS-CLN-TRNFMR-9000006730 |  | 21 | 3 | 2 | 2 | 3 | 1 | 1 | 3 | 3 | 2 | 225.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30165029 | DS-CRE-TRNFMR-9000525811 |  | 13 | 3 | 2 | 1 | 3 | 2 | 1 | 4 | 2 | 2 | 217.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
LLG | 30359074 | DS-LLG-TRNFMR-9000007796 |  | 20 | 1 | 2 | 1 | 2 | 1 | 1 | 5 | 3 | 2 | 191.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CRE | 30380287 | DS-CRE-TRNFMR-9000525810 |  | 13 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 2 | 177.1429 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
CLN | 30000439 | DS-CLN-TRNFMR-9000001306 |  | 19 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30035965 | DS-OFR-TRNFMR-9000014181 |  | 16 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 165.7143 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30002764 | DS-KLO-TRNFMR-9000412348 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 160 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
OFR | 30221642 | DS-OFR-TRNFMR-9000016122 |  | 16 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
KLO | 30208816 | DS-KLO-TRNFMR-9000412347 |  | 15 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 151.4286 | 2 | 24 | 3.5 | 84.05 | 0.1909% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162% | 0.5522% | 0.5897% | 0.6286% | 0.669% | 0.7109% | 0.7543% | 0.7993% | 0.8458% | 0.8939% | 0.9436% | 0.9949% | 1.048% | 1.102% | 1.159% | 1.216% | 1.276%
PHM | 32944656 | DS-PHM-TRNFMR-9000004393 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%
PHM | 32944654 | DS-PHM-TRNFMR-9000007050 |  | 8 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 142.8571 | 1 | 8 | 3.5 | 84.05 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1543% | 0.172% | 0.1909% | 0.211% | 0.2322% | 0.2547% | 0.2785% | 0.3035% | 0.3298% | 0.3575% | 0.3865% | 0.4168% | 0.4486% | 0.4817% | 0.5162%

## AER VCR Rates(2024)
Category | Rate | Notes
Dec 24 AER VCR ($/kWh) - Res | 49.23 | Vic Av Res
Dec 24 AER VCR ($/kWh) - Com | 34.39 | Vic Av Com
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | Vic Av Ind
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | Vic Av Agr

## Customer No. and Vol per Feeder
CUSTOMER_CLASS | Feeder | VOL | CUST_NO | ZSS | Customer mix received from AusNet Financial Planning & Strategy on 25/7/2025
COMMERCIAL | bra11 | 9860526.7854 | 168 | bra
COMMERCIAL | bge13 | 654988.62 | 45 | bge
COMMERCIAL | phi11 | 1878610.03 | 37 | phi
NCONUML | moe11 | 47447.48 | 18 | moe
NCONUML | drn13 | 27414.73 | 17 | drn
COMMERCIAL | smg34 | 5224461.8 | 1 | smg
FARM | wgl13 | 901266.5312 | 97 | wgl
FARM | msd2 | 2808295.5668 | 471 | msd
NCONUML | elm34 | 86758.8 | 34 | elm
| rwt36 | 703.54 | 2 | rwt
COMMERCIAL | lga41 | 1099100.22 | 2 | lga
| bdl33 | 4298.82 | 8 | bdl
NCONUML | smr14 | 27225.34 | 18 | smr
COMMERCIAL | cln24 | 4484028.8333 | 290 | cln
RESIDENTL | ofr14 | 13024383.6958 | 3554 | ofr
NCONUML | bdl43 | 100361.9983 | 38 | bdl
| ofr22 | 16469.09 | 22 | ofr
NCONUML | rwn33 | 8721.79 | 7 | rwn
LIGHTING | hpk12 | 342838 | 1 | hpk
COMMERCIAL | bra23 | 6262297.01 | 84 | bra
FARM | tt1 | 1865.76 | 1 | tt
LIGHTING | mfa14 | 787800.53 | 1 | mfa
RESIDENTL | brt22 | 9968534.1043 | 1376 | brt
RESIDENTL | mwl25 | 4092575.372 | 493 | mwl
NCONUML | wgi22 | 83961.44 | 23 | wgi
INDUSTRIAL | ldl22 | 4379901.5885 | 45 | ldl
RESIDENTL | phm22 | 3628742.5283 | 796 | phm
FARM | mfa23 | 2691321.6324 | 201 | mfa
NCONUML | rwn32 | 60415.37 | 23 | rwn
FARM | cre22 | 55644.16 | 17 | cre
RESIDENTL | elm24 | 17367685.5307 | 2999 | elm
COMMERCIAL | tt9 | 7181168.3052 | 213 | tt
COMMERCIAL | kms12 | 15257134.8455 | 395 | kms
NCONUML | cyn31 | 24759.23 | 14 | cyn
| llg12 | 26420.7189 | 15 | llg
LIGHTING | ruba22 | 247422.69 | 1 | ruba
RESIDENTL | wt12 | 10803758.701 | 2579 | wt
COMMERCIAL | bwn14 | 6975240.1 | 156 | bwn
NCONUML | bge12 | 37366.03 | 11 | bge
NCONUML | rwn24 | 30489.76 | 21 | rwn
FARM | sfs1 | 113380.09 | 9 | sfs
| bwr13 | 80076.52 | 46 | bwr
FARM | wt13 | 37228.86 | 3 | wt
FARM | cre23 | 226478.55 | 9 | cre
COMMERCIAL | rwn22 | 1886562.0146 | 72 | rwn
| tgn23 | 13898.1302 | 15 | tgn
FARM | ldl22 | 7887.95 | 1 | ldl
RESIDENTL | fgy21 | 7153989.4877 | 1047 | fgy
FARM | mjg11 | 735019.886 | 74 | mjg
| ldl14 | 17432.2687 | 11 | ldl
INDUSTRIAL | ldl24 | 64751.4 | 12 | ldl
| sle13 | 253.3245 | 2 | sle
FARM | moe21 | 6301170.9744 | 504 | moe
FARM | bge23 | 671977.1074 | 66 | bge
RESIDENTL | elm32 | 19949095.4752 | 2463 | elm
COMMERCIAL | ftr12 | 1975462.7263 | 113 | ftr
RESIDENTL | lyd12 | 6657897.88 | 1592 | lyd
RESIDENTL | epg31 | 11862355.3417 | 3027 | epg
NCONUML | ofr11 | 57102.89 | 18 | ofr
FARM | moe11 | 65350.2807 | 7 | moe
FARM | nla32 | 1181128.1259 | 84 | nla
FARM | smr24 | 4141783.4574 | 392 | smr
RESIDENTL | fgy13 | 7970231.1446 | 1518 | fgy
FARM | bdl41 | 1305847.5951 | 258 | bdl
NCONUML | elm23 | 62172.37 | 40 | elm
| elm22 | 20617.5429 | 26 | elm
NCONUML | cre21 | 58240.1 | 18 | cre
FARM | phm32 | 50851.13 | 8 | phm
INDUSTRIAL | lga21 | 208132.02 | 16 | lga
INDUSTRIAL | nrn13 | 39703.59 | 6 | nrn
RESIDENTL | hpk22 | 18949862.0449 | 4569 | hpk
NCONUML | cyn13 | 17637.49 | 6 | cyn
COMMERCIAL | cre31 | 14851829.6913 | 363 | cre
COMMERCIAL | epg32 | 5001490.9226 | 156 | epg
| phm32 | 41386.12 | 47 | phm
NCONUML | wo33 | 6875.31 | 2 | wo
FARM | wgl21 | 5056187.7677 | 366 | wgl
INDUSTRIAL | cre22 | 240829.25 | 4 | cre
RESIDENTL | wgi34 | 3671110.7601 | 570 | wgi
INDUSTRIAL | ldl12 | 10352583.7 | 7 | ldl
INDUSTRIAL | wyk12 | 149433.7 | 6 | wyk
INDUSTRIAL | cyn14 | 23200.151 | 3 | cyn
| wo11 | 4136.2425 | 3 | wo
| msd4 | 20521.76 | 37 | msd
FARM | mby12 | 52034.88 | 19 | mby
COMMERCIAL | rwt22 | 7145877.6761 | 143 | rwt
COMMERCIAL | wo12 | 23719023.8 | 1 | wo
RESIDENTL | wn2 | 17414453.5902 | 3500 | wn
COMMERCIAL | wots25 | 3483725.2811 | 72 | wots
RESIDENTL | bwr33 | 46024.67 | 2 | bwr
RESIDENTL | wn3 | 12349888.6736 | 2099 | wn
RESIDENTL | bn24 | 2992797.8263 | 559 | bn
| bra21 | 41455.7142 | 65 | bra
INDUSTRIAL | hpk14 | 16381.88 | 4 | hpk
RESIDENTL | epg32 | 14811809.1158 | 3829 | epg
COMMERCIAL | cln14 | 10141314.5039 | 129 | cln
FARM | smg31 | 14995.46 | 5 | smg
INDUSTRIAL | drn22 | 2117102.6666 | 12 | drn
NCONUML | drn12 | 43785.8374 | 16 | drn
INDUSTRIAL | fgy34 | 128392.6893 | 5 | fgy
NCONUML | fgy31 | 6707.46 | 4 | fgy
| wt8 | 7059.0655 | 13 | wt
| bwn12 | 6521.57 | 6 | bwn
COMMERCIAL | myt12 | 10774273.2986 | 307 | myt
COMMERCIAL | ldl21 | 5339830.9491 | 117 | ldl
| cln21 | 32425.72 | 66 | cln
INDUSTRIAL | fgy14 | 162921.94 | 7 | fgy
| tgn12 | 22490.11 | 3 | tgn
COMMERCIAL | epg12 | 8214339.5389 | 163 | epg
NCONUML | moe23 | 69334.91 | 17 | moe
FARM | cyn14 | 7715.15 | 1 | cyn
RESIDENTL | lyd14 | 10580841.4317 | 1203 | lyd
COMMERCIAL | smg23 | 21963007.1063 | 434 | smg
INDUSTRIAL | bra33 | 2076536.62 | 34 | bra
INDUSTRIAL | rwt14 | 2271244.55 | 44 | rwt
COMMERCIAL | lga14 | 2174194.9787 | 115 | lga
INDUSTRIAL | myt22 | 3176.32 | 3 | myt
FARM | cyn21 | 10230.57 | 2 | cyn
| klo24 | 65411.35 | 119 | klo
COMMERCIAL | brt21 | 6571769.7252 | 216 | brt
FARM | kms11 | 665243.0597 | 75 | kms
| elm34 | 25999.6869 | 33 | elm
INDUSTRIAL | mwl11 | 366139.79 | 15 | mwl
INDUSTRIAL | lyd14 | 80895.88 | 12 | lyd
LIGHTING | cpk11 | 1086.88 | 1 | cpk
NCONUML | fgy23 | 34402.31 | 12 | fgy
| bra32 | 15753.982 | 22 | bra
RESIDENTL | epg12 | 26391788.5687 | 6905 | epg
COMMERCIAL | cyn24 | 15647575.1097 | 304 | cyn
INDUSTRIAL | phm21 | 511727.73 | 19 | phm
NCONUML | ftr12 | 5424.58 | 5 | ftr
| bwa23 | 5447.575 | 8 | bwa
NCONUML | llg12 | 4182.92 | 3 | llg
COMMERCIAL | drn13 | 5299129.684 | 96 | drn
INDUSTRIAL | hpk21 | 31624.71 | 8 | hpk
INDUSTRIAL | wyk23 | 1500537.4334 | 28 | wyk
RESIDENTL | lga12 | 4152631.2896 | 644 | lga
RESIDENTL | cyn11 | 6009338.551 | 1440 | cyn
NCONUML | fgy24 | 70027.41 | 43 | fgy
| moe23 | 74726.3012 | 22 | moe
COMMERCIAL | elm24 | 3531802.26 | 46 | elm
LIGHTING | elm33 | 1000.47 | 1 | elm
RESIDENTL | smg23 | 6500499.5996 | 1411 | smg
FARM | msd4 | 1851245.0012 | 252 | msd
COMMERCIAL | lga24 | 21693950.3379 | 92 | lga
COMMERCIAL | ldl11 | 7360578.73 | 74 | ldl
NCONUML | rve13 | 29515.6981 | 24 | rve
COMMERCIAL | trc01 | 365242.5067 | 42 | trc
COMMERCIAL | wt15 | 1164715.6471 | 30 | wt
COMMERCIAL | bra14 | 811059.401 | 59 | bra
| ftr21 | 17034.7542 | 20 | ftr
RESIDENTL | bra23 | 7643359.408 | 1736 | bra
INDUSTRIAL | cpk11 | 59065.36 | 14 | cpk
INDUSTRIAL | hpk12 | 531460.54 | 46 | hpk
FARM | fgy23 | 137430.23 | 3 | fgy
INDUSTRIAL | tt4 | 77015.1997 | 16 | tt
FARM | cpk22 | 45399.86 | 6 | cpk
INDUSTRIAL | yn31 | 1004932.7745 | 6 | yn
FARM | myt22 | 1873055.6433 | 191 | myt
| cpk12 | 20188.43 | 32 | cpk
RESIDENTL | bwa22 | 6606654.3694 | 1106 | bwa
| mfa34 | 1434.55 | 6 | mfa
| nla31 | 4780.58 | 5 | nla
FARM | mdg1 | 36782.2 | 6 | mdg
RESIDENTL | mwl21 | 3605605.4081 | 859 | mwl
COMMERCIAL | phm33 | 14452041.4603 | 180 | phm
INDUSTRIAL | ofr23 | 154535.41 | 17 | ofr
INDUSTRIAL | elm21 | 177435.466 | 7 | elm
INDUSTRIAL | wt5 | 89.11 | 1 | wt
FARM | llg13 | 1917532.2118 | 152 | llg
INDUSTRIAL | klk21 | 41156.68 | 10 | klk
NCONUML | wt9 | 48247.64 | 17 | wt
FARM | mdi1 | 153288.2952 | 21 | mdi
INDUSTRIAL | nrn14 | 19245.31 | 5 | nrn
INDUSTRIAL | wgl12 | 500659.11 | 16 | wgl
FARM | fgy13 | 80534.51 | 6 | fgy
INDUSTRIAL | bwr14 | 1597974.48 | 1 | bwr
LIGHTING | bn11 | 103048.5 | 1 | bn
RESIDENTL | klo14 | 40411755.0117 | 10946 | klo
RESIDENTL | fgy33 | 9101921.8028 | 1763 | fgy
LIGHTING | cre31 | 2308168.51 | 1 | cre
RESIDENTL | wn5 | 8555201.9981 | 1156 | wn
COMMERCIAL | mfa22 | 5299491.9938 | 179 | mfa
COMMERCIAL | lyd11 | 3798691.89 | 62 | lyd
LIGHTING | bn24 | 2014.81 | 1 | bn
COMMERCIAL | cf1 | 9360587.4941 | 189 | cf
FARM | lga11 | 4665290.6529 | 555 | lga
RESIDENTL | lyd13 | 10895753.2364 | 2051 | lyd
NCONUML | cre33 | 35388.67 | 19 | cre
| smg32 | 685.05 | 3 | smg
INDUSTRIAL | cyn11 | 1966971.1028 | 55 | cyn
COMMERCIAL | wn2 | 10157994.9798 | 156 | wn
| phm21 | 32464.7212 | 22 | phm
| sfs1 | 13890.635 | 10 | sfs
NCONUML | tt12 | 15011.94 | 8 | tt
FARM | lga21 | 1065599.6961 | 147 | lga
| ldl12 | 52350.63 | 6 | ldl
INDUSTRIAL | smg31 | 231921 | 9 | smg
LIGHTING | myt12 | 813470.88 | 6 | myt
| smr24 | 66801.9 | 34 | smr
NCONUML | cre32 | 49453.4427 | 23 | cre
INDUSTRIAL | bdl44 | 2337630.2078 | 41 | bdl
| rve11 | 302066.1 | 12 | rve
FARM | wo31 | 3245.01 | 1 | wo
LIGHTING | ofr13 | 171706.2 | 2 | ofr
RESIDENTL | tt9 | 13181645.445 | 3553 | tt
COMMERCIAL | wgl11 | 13522117.9742 | 216 | wgl
COMMERCIAL | hpk24 | 15242696.9791 | 271 | hpk
COMMERCIAL | bwr34 | 12222544.1423 | 437 | bwr
NCONUML | nla34 | 19980.17 | 11 | nla
FARM | bwr24 | 9303.26 | 1 | bwr
| wgi23 | 15962.8799 | 36 | wgi
RESIDENTL | cln13 | 18593732.5659 | 6830 | cln
RESIDENTL | lga13 | 1879247.7046 | 295 | lga
RESIDENTL | cnr3 | 108696.4186 | 22 | cnr
| wgl12 | 112644.3661 | 43 | wgl
COMMERCIAL | cln12 | 8203266.5202 | 86 | cln
NCONUML | ofr21 | 100427.35 | 34 | ofr
RESIDENTL | drn24 | 10021102.8231 | 2473 | drn
COMMERCIAL | cyn31 | 1940881.6507 | 53 | cyn
NCONUML | ldl24 | 34534.3 | 19 | ldl
COMMERCIAL | ofr13 | 9302944.2987 | 197 | ofr
| wots13 | 58538.6484 | 32 | wots
| cpk23 | 23360.0808 | 24 | cpk
NCONUML | cln11 | 4587.8606 | 9 | cln
| wt15 | 51811.4 | 11 | wt
COMMERCIAL | epg24 | 26841528 | 1 | epg
FARM | drn22 | 329138.5031 | 52 | drn
| mfa31 | 16838.31 | 22 | mfa
COMMERCIAL | bra32 | 4055727.3404 | 158 | bra
COMMERCIAL | cpk21 | 14974774.5549 | 258 | cpk
INDUSTRIAL | myt21 | 335981.9667 | 19 | myt
FARM | nrn14 | 139044.47 | 14 | nrn
| wt5 | 22324.85 | 13 | wt
INDUSTRIAL | mfa23 | 139940.33 | 14 | mfa
FARM | wyk12 | 2634438.6357 | 233 | wyk
RESIDENTL | epg23 | 3653084.6682 | 932 | epg
COMMERCIAL | tgn11 | 2525258.71 | 85 | tgn
| wt13 | 22551.0062 | 37 | wt
| cyn13 | 10533.28 | 7 | cyn
INDUSTRIAL | fgy13 | 259435.94 | 2 | fgy
RESIDENTL | cln12 | 23908773.0216 | 6775 | cln
COMMERCIAL | brt22 | 9042592.2197 | 210 | brt
COMMERCIAL | rwt25 | 7526054.6961 | 146 | rwt
FARM | mfa31 | 218040.8355 | 21 | mfa
COMMERCIAL | cln22 | 3248277.4443 | 37 | cln
NCONUML | bdl33 | 22970.8 | 8 | bdl
COMMERCIAL | fgy12 | 74427.591 | 4 | fgy
RESIDENTL | mwl16 | 8188909.2298 | 1700 | mwl
INDUSTRIAL | moe25 | 612177.9824 | 16 | moe
COMMERCIAL | tt7 | 24970154.3491 | 341 | tt
INDUSTRIAL | bwr24 | 4118148.7987 | 125 | bwr
RESIDENTL | moe13 | 2791200.4315 | 357 | moe
FARM | wyk24 | 694188.3378 | 94 | wyk
NCONUML | wo14 | 36996.26 | 12 | wo
RESIDENTL | bra13 | 6470560.8911 | 1572 | bra
RESIDENTL | tt7 | 39398.92 | 9 | tt
FARM | epg34 | 15821.91 | 5 | epg
INDUSTRIAL | yn35 | 6582.38 | 2 | yn
NCONUML | bwa23 | 749.23 | 1 | bwa
FARM | sle13 | 1461316.56 | 213 | sle
COMMERCIAL | cpk13 | 4127340.5971 | 198 | cpk
INDUSTRIAL | ldl14 | 1064067.7426 | 16 | ldl
| rwt14 | 62105.3312 | 18 | rwt
LIGHTING | hpk13 | 14513.85 | 1 | hpk
RESIDENTL | klk22 | 940238.19 | 128 | klk
COMMERCIAL | mwl25 | 259300.06 | 16 | mwl
| mjg11 | 96977.3135 | 7 | mjg
RESIDENTL | hpk24 | 4867180.3451 | 1284 | hpk
FARM | ftr21 | 6703423.0704 | 705 | ftr
FARM | smr12 | 441800.25 | 44 | smr
FARM | bwr13 | 73574.54 | 13 | bwr
| ldl22 | 9241.11 | 9 | ldl
FARM | wo22 | 35676.335 | 7 | wo
NCONUML | moe12 | 9318.9 | 3 | moe
INDUSTRIAL | bdl31 | 1561951.6978 | 44 | bdl
COMMERCIAL | ofr14 | 8393968.2568 | 77 | ofr
NCONUML | tgn23 | 48562.71 | 16 | tgn
NCONUML | cyn21 | 25127.29 | 5 | cyn
FARM | phm34 | 22945.58 | 3 | phm
INDUSTRIAL | cyn33 | 36519.92 | 4 | cyn
LIGHTING | bm8b32 | 1070.04 | 1 | bmb
FARM | llg12 | 5311057.9488 | 488 | llg
NCONUML | rwt32 | 94072.85 | 46 | rwt
COMMERCIAL | myt11 | 912988.53 | 42 | myt
INDUSTRIAL | cpk22 | 129954.91 | 11 | cpk
| cre22 | 20388.051 | 33 | cre
RESIDENTL | ldl21 | 5451727.7741 | 1502 | ldl
FARM | bdl44 | 8189534.7866 | 736 | bdl
INDUSTRIAL | bn11 | 1899511.3657 | 45 | bn
INDUSTRIAL | wgi31 | 152399.6 | 19 | wgi
INDUSTRIAL | mdi1 | 16.0426 | 1 | mdi
| ofr11 | 90492.4817 | 79 | ofr
LIGHTING | kms11 | 547479.19 | 1 | kms
RESIDENTL | phi12 | 18738852.0082 | 4967 | phi
COMMERCIAL | bwr12 | 7897915.6022 | 287 | bwr
FARM | msd1 | 2520603.4144 | 354 | msd
COMMERCIAL | tgn44 | 4662112.18 | 89 | tgn
NCONUML | uwy1 | 29815.85 | 15 | uwy
NCONUML | lga22 | 54192.29 | 17 | lga
NCONUML | lga23 | 17186.13 | 6 | lga
INDUSTRIAL | hpk13 | 1952010.47 | 3 | hpk
FARM | drn23 | 391232.6382 | 58 | drn
FARM | ldl23 | 5910515.5529 | 453 | ldl
FARM | bdl31 | 55336.85 | 12 | bdl
RESIDENTL | bwr34 | 11176240.016 | 2984 | bwr
RESIDENTL | ofr13 | 5689359.8131 | 1445 | ofr
NCONUML | bra21 | 145563.002 | 72 | bra
COMMERCIAL | cf2 | 1114027.3697 | 138 | cf
RESIDENTL | bdl32 | 16368580.902 | 3124 | bdl
COMMERCIAL | smr22 | 10240657.5236 | 95 | smr
NCONUML | rve12 | 34563.18 | 21 | rve
COMMERCIAL | cnr3 | 208527.63 | 11 | cnr
| elm25 | 9741.0155 | 15 | elm
INDUSTRIAL | lyd13 | 30651.21 | 5 | lyd
INDUSTRIAL | mby12 | 279353.09 | 7 | mby
INDUSTRIAL | epg21 | 31298.6803 | 2 | epg
FARM | wgl12 | 7817936.5802 | 624 | wgl
COMMERCIAL | moe13 | 1401894.0174 | 82 | moe
RESIDENTL | lga14 | 7239522.4699 | 1158 | lga
RESIDENTL | epg35 | 308209.78 | 22 | epg
FARM | hpk14 | 29274.39 | 5 | hpk
LIGHTING | bn22 | 341591.58 | 1 | bn
NCONUML | bge11 | 85890.46 | 45 | bge
NCONUML | wt7 | 26985.19 | 18 | wt
| wo31 | 27869.149 | 41 | wo
INDUSTRIAL | elm32 | 759094.4258 | 68 | elm
NCONUML | cre23 | 95638.5 | 25 | cre
RESIDENTL | cln23 | 19292170.1488 | 4992 | cln
| lga21 | 17263.28 | 18 | lga
NCONUML | bwn12 | 35975.24 | 12 | bwn
| fgy31 | 1671.76 | 6 | fgy
NCONUML | ftr23 | 39743.6852 | 30 | ftr
NCONUML | smg21 | 9405.11 | 5 | smg
RESIDENTL | epg13 | 24819451.0174 | 7299 | epg
RESIDENTL | ruba22 | 5955886.59 | 1080 | ruba
INDUSTRIAL | bwr23 | 1917390.4058 | 110 | bwr
COMMERCIAL | bn23 | 4585306.9 | 117 | bn
| fgy24 | 60212.15 | 95 | fgy
LIGHTING | brt21 | 27441.26 | 1 | brt
COMMERCIAL | mby14 | 13812.56 | 3 | mby
RESIDENTL | drn21 | 15235611.8074 | 3585 | drn
RESIDENTL | nrn11 | 3368324.1063 | 703 | nrn
NCONUML | cln21 | 97183.1897 | 28 | cln
NCONUML | tgn12 | 26909.78 | 9 | tgn
FARM | moe22 | 48531.59 | 7 | moe
RESIDENTL | bra14 | 17287022.2386 | 4193 | bra
RESIDENTL | brt21 | 8587133.8204 | 1368 | brt
INDUSTRIAL | ldl23 | 2181365.61 | 45 | ldl
NCONUML | klo24 | 121410.57 | 41 | klo
INDUSTRIAL | wt8 | 22231.36 | 5 | wt
| bdl41 | 27628.4721 | 32 | bdl
COMMERCIAL | sle14 | 13227565.7623 | 343 | sle
| smr14 | 17300.3116 | 19 | smr
INDUSTRIAL | llg11 | 439641.21 | 9 | llg
| wgi22 | 13903.1 | 35 | wgi
NCONUML | moe22 | 34069.45 | 10 | moe
| ftr12 | 15921.46 | 17 | ftr
COMMERCIAL | epg11 | 902129.45 | 16 | epg
RESIDENTL | cpk13 | 21255549.7429 | 4974 | cpk
| fgy23 | 9273.25 | 10 | fgy
FARM | cyn12 | 9105.46 | 2 | cyn
INDUSTRIAL | rwn31 | 527467.66 | 22 | rwn
RESIDENTL | bm8b32 | 357081.227 | 62 | bmb
FARM | ruba22 | 1060033.1321 | 158 | ruba
INDUSTRIAL | cnr1 | 88077.93 | 3 | cnr
FARM | cpk12 | 972803.9358 | 91 | cpk
COMMERCIAL | wo14 | 14658340.7796 | 304 | wo
COMMERCIAL | tt5 | 6134357.4395 | 224 | tt
INDUSTRIAL | wo11 | 18559582.74 | 7 | wo
| wgl23 | 17798.7289 | 12 | wgl
NCONUML | cyn12 | 64730.9 | 21 | cyn
COMMERCIAL | bwr33 | 3515549.759 | 83 | bwr
COMMERCIAL | cyn22 | 10287381.4837 | 183 | cyn
COMMERCIAL | rwt32 | 5482054.6843 | 198 | rwt
INDUSTRIAL | nrn12 | 7260.73 | 2 | nrn
RESIDENTL | cln22 | 8137131.1146 | 3340 | cln
| kms12 | 36774.1343 | 44 | kms
| cyn24 | 12784.0842 | 11 | cyn
| smg33 | 11524.64 | 21 | smg
COMMERCIAL | rve11 | 18192998.0721 | 274 | rve
FARM | wt5 | 8146.48 | 2 | wt
INDUSTRIAL | bge23 | 983662.8538 | 7 | bge
| msd2 | 9983.6 | 13 | msd
| bra12 | 98134.87 | 2 | bra
RESIDENTL | hpk23 | 13762355.5073 | 3377 | hpk
COMMERCIAL | smr13 | 15057236.7589 | 394 | smr
INDUSTRIAL | rwt21 | 372221.49 | 45 | rwt
FARM | rve12 | 22362.86 | 5 | rve
NCONUML | fgy32 | 32042.28 | 18 | fgy
INDUSTRIAL | smr12 | 37387308.69 | 3 | smr
NCONUML | mfa34 | 19451.19 | 8 | mfa
FARM | wots13 | 4844280.0942 | 510 | wots
COMMERCIAL | drn21 | 3220798.94 | 52 | drn
INDUSTRIAL | wo31 | 765.77 | 1 | wo
| fgy32 | 8528.5063 | 10 | fgy
INDUSTRIAL | bwr32 | 3058614 | 72 | bwr
| elm23 | 20831.6 | 30 | elm
INDUSTRIAL | mwl12 | 574569.29 | 12 | mwl
RESIDENTL | cpk21 | 7771248.352 | 1679 | cpk
COMMERCIAL | wots11 | 6621581.9604 | 243 | wots
INDUSTRIAL | ftr21 | 313604.8 | 24 | ftr
NCONUML | lyd11 | 43059.75 | 9 | lyd
FARM | phm21 | 25361.56 | 3 | phm
INDUSTRIAL | wyk13 | 453974.55 | 15 | wyk
INDUSTRIAL | mdg1 | 21781.42 | 1 | mdg
INDUSTRIAL | tt1 | 7434378.9861 | 77 | tt
INDUSTRIAL | wgi34 | 1206209.57 | 8 | wgi
LIGHTING | wgi33 | 1050486.0487 | 2 | wgi
COMMERCIAL | wgl15 | 27996457.3831 | 596 | wgl
RESIDENTL | bge23 | 16900476.9279 | 2094 | bge
INDUSTRIAL | bwr13 | 2417661.2776 | 147 | bwr
NCONUML | epg23 | 28250.73 | 7 | epg
INDUSTRIAL | drn14 | 25996.95 | 2 | drn
RESIDENTL | drn14 | 23831050.9741 | 4399 | drn
RESIDENTL | rwt31 | 5842296.4371 | 1436 | rwt
COMMERCIAL | drn24 | 1717660.9 | 35 | drn
FARM | epg14 | 3614.72 | 1 | epg
RESIDENTL | smr13 | 11225814.5464 | 2447 | smr
COMMERCIAL | wots12 | 14359758.4732 | 371 | wots
COMMERCIAL | klk11 | 3080934.4269 | 114 | klk
NCONUML | mwl14 | 31252.61 | 13 | mwl
INDUSTRIAL | sle11 | 266690.1 | 32 | sle
NCONUML | epg31 | 41319.36 | 24 | epg
RESIDENTL | cf1 | 4176161.3871 | 493 | cf
INDUSTRIAL | phm34 | 816155.12 | 6 | phm
FARM | rwn34 | 20402.21 | 4 | rwn
| mby12 | 1524.95 | 3 | mby
RESIDENTL | wgi31 | 14866992.8529 | 3617 | wgi
RESIDENTL | wots25 | 16858284.9544 | 3532 | wots
RESIDENTL | cre33 | 21876811.5892 | 4235 | cre
RESIDENTL | fgy34 | 4606270.9018 | 975 | fgy
RESIDENTL | cyn32 | 15011504.2579 | 3573 | cyn
RESIDENTL | klk11 | 9194980.7775 | 1227 | klk
INDUSTRIAL | fgy33 | 1452360.19 | 13 | fgy
INDUSTRIAL | wgl13 | 6688610.4344 | 14 | wgl
| tgn41 | 12751.16 | 13 | tgn
COMMERCIAL | klk22 | 85830.78 | 8 | klk
| mby11 | 4292.69 | 12 | mby
FARM | drn12 | 9939.61 | 1 | drn
RESIDENTL | rwn24 | 15617115.6722 | 2794 | rwn
RESIDENTL | cre32 | 8053371.5554 | 2218 | cre
COMMERCIAL | bwn11 | 5920812.2037 | 76 | bwn
NCONUML | smg33 | 19709.42 | 12 | smg
INDUSTRIAL | mby11 | 90387.22 | 16 | mby
COMMERCIAL | tgn41 | 8173213.7745 | 338 | tgn
INDUSTRIAL | wn7 | 3582803.57 | 9 | wn
FARM | bwr23 | 29264.76 | 8 | bwr
RESIDENTL | bwn13 | 8026926.4045 | 1629 | bwn
FARM | wgi24 | 1757204.2906 | 142 | wgi
| rve13 | 21148.03 | 29 | rve
RESIDENTL | wgl21 | 23764201.6622 | 4642 | wgl
COMMERCIAL | wn1 | 22168293.2818 | 620 | wn
INDUSTRIAL | cyn32 | 738566.1077 | 85 | cyn
| hpk21 | 27858.58 | 57 | hpk
COMMERCIAL | klo11 | 2030116.61 | 11 | klo
INDUSTRIAL | bn22 | 260832.7234 | 23 | bn
| ofr24 | 25053.77 | 43 | ofr
| drn12 | 30292.1138 | 29 | drn
COMMERCIAL | smg22 | 18806077.0677 | 136 | smg
COMMERCIAL | bwa22 | 4509592.2057 | 144 | bwa
COMMERCIAL | drn12 | 15118769.4919 | 112 | drn
| ldl23 | 80304.9161 | 48 | ldl
| rwn32 | 14306.27 | 22 | rwn
| drn23 | 12868.4314 | 15 | drn
RESIDENTL | mwl22 | 12904194.2639 | 2809 | mwl
COMMERCIAL | tt6 | 3682930.1298 | 115 | tt
COMMERCIAL | bra24 | 3429037.1414 | 127 | bra
NCONUML | hpk11 | 112614.82 | 31 | hpk
RESIDENTL | mfa21 | 12551518.2306 | 1921 | mfa
RESIDENTL | bge22 | 19945240.9452 | 3164 | bge
| tt4 | 9710.0483 | 41 | tt
NCONUML | phm22 | 22255.8232 | 9 | phm
COMMERCIAL | fgy21 | 1241019.6707 | 34 | fgy
INDUSTRIAL | nla31 | 516137.35 | 16 | nla
FARM | wyk13 | 707273.0378 | 84 | wyk
NCONUML | elm25 | 44655.33 | 20 | elm
| ofr23 | 28214.1089 | 26 | ofr
INDUSTRIAL | ruba22 | 167892.49 | 8 | ruba
FARM | hpk21 | 3124.97 | 1 | hpk
FARM | wn4 | 999664.927 | 129 | wn
COMMERCIAL | wn6 | 8795190.5545 | 246 | wn
| cre23 | 50195.43 | 25 | cre
COMMERCIAL | bwr22 | 15914202.1636 | 269 | bwr
INDUSTRIAL | elm22 | 545216.4127 | 27 | elm
NCONUML | bwr32 | 46210.27 | 31 | bwr
COMMERCIAL | moe12 | 4799517.76 | 51 | moe
| drn22 | 43438.5 | 28 | drn
FARM | bn22 | 13032.09 | 3 | bn
FARM | ldl24 | 222231.4641 | 11 | ldl
| bdl31 | 24144.6762 | 16 | bdl
FARM | cpk11 | 227979.0877 | 18 | cpk
FARM | elm33 | 50441.5205 | 4 | elm
INDUSTRIAL | rve13 | 147824.4003 | 10 | rve
COMMERCIAL | uwy1 | 603856.89 | 33 | uwy
FARM | mfa21 | 13347321.3386 | 701 | mfa
RESIDENTL | wo14 | 1446838.665 | 266 | wo
NCONUML | rwt14 | 102266.96 | 37 | rwt
| kms11 | 9612.23 | 20 | kms
RESIDENTL | phi11 | 5828644.3864 | 1391 | phi
COMMERCIAL | tgn12 | 10174331.2835 | 242 | tgn
LIGHTING | drn21 | 522455.53 | 1 | drn
INDUSTRIAL | smr22 | 2060432.23 | 13 | smr
| moe21 | 19173.8011 | 29 | moe
NCONUML | fgy12 | 1668.8419 | 4 | fgy
COMMERCIAL | elm25 | 2590499.6378 | 73 | elm
| epg34 | 11737.1961 | 27 | epg
COMMERCIAL | cpk23 | 2022573.8223 | 44 | cpk
COMMERCIAL | sle31 | 4198591.4215 | 178 | sle
FARM | nrn13 | 23844.37 | 5 | nrn
FARM | elm26 | 83060.0495 | 12 | elm
INDUSTRIAL | rve12 | 67014.5 | 12 | rve
INDUSTRIAL | moe21 | 304282.5341 | 37 | moe
COMMERCIAL | ofr21 | 9424773.56 | 126 | ofr
FARM | wn3 | 4385381.9629 | 585 | wn
FARM | klk21 | 574949.1868 | 82 | klk
NCONUML | wyk13 | 97422.66 | 49 | wyk
FARM | bwn12 | 14573.05 | 3 | bwn
NCONUML | msd2 | 8161.26 | 6 | msd
COMMERCIAL | elm31 | 474386.1613 | 1 | elm
RESIDENTL | rwt35 | 12065.95 | 2 | rwt
RESIDENTL | wt6 | 15702930.1084 | 3397 | wt
RESIDENTL | cln24 | 3991370.9732 | 1090 | cln
COMMERCIAL | smg21 | 2744632.8687 | 43 | smg
| myt21 | 64545.94 | 22 | myt
RESIDENTL | lga22 | 9862202.3617 | 1608 | lga
INDUSTRIAL | cyn13 | 4447831.06 | 67 | cyn
COMMERCIAL | ruba12 | 6703349.3664 | 290 | ruba
| smr23 | 7378.7014 | 9 | smr
FARM | phi13 | 230339.12 | 15 | phi
RESIDENTL | wt11 | 8665012.8839 | 2213 | wt
RESIDENTL | bge13 | 9255563.8982 | 1458 | bge
COMMERCIAL | bge11 | 11367890.3817 | 330 | bge
COMMERCIAL | wgi23 | 2290528.82 | 95 | wgi
COMMERCIAL | epg35 | 29855241.8371 | 304 | epg
NCONUML | mwl23 | 55631.52 | 20 | mwl
RESIDENTL | tgn11 | 18615536.7391 | 4196 | tgn
RESIDENTL | klo24 | 35150523.3753 | 8219 | klo
| wgi32 | 32777.55 | 36 | wgi
| uwy1 | 1895.86 | 6 | uwy
COMMERCIAL | wots24 | 5008654.6646 | 265 | wots
INDUSTRIAL | phi13 | 601326.64 | 38 | phi
LIGHTING | cf1 | 76883.018 | 3 | cf
RESIDENTL | cre21 | 18876617.5647 | 4715 | cre
INDUSTRIAL | wo32 | 73086.25 | 1 | wo
COMMERCIAL | lga13 | 621321.4861 | 47 | lga
FARM | cnr2 | 245915.51 | 48 | cnr
COMMERCIAL | bge22 | 4521687.9575 | 100 | bge
INDUSTRIAL | cyn12 | 101425.5 | 5 | cyn
FARM | drn11 | 51881.33 | 8 | drn
INDUSTRIAL | wo23 | 212041.78 | 1 | wo
RESIDENTL | lga23 | 5064870.5947 | 821 | lga
RESIDENTL | bn12 | 3438265.7182 | 625 | bn
RESIDENTL | bra21 | 23268334.8963 | 5707 | bra
| bdl42 | 11198.42 | 14 | bdl
FARM | cnr1 | 2440.03 | 2 | cnr
| phm34 | 68320.3174 | 32 | phm
FARM | rwt31 | 12148.87 | 1 | rwt
| smg31 | 8879.89 | 17 | smg
LIGHTING | tgn11 | 1064655.8 | 1 | tgn
FARM | llg14 | 4195351.6172 | 347 | llg
FARM | mwl11 | 2401732.236 | 295 | mwl
INDUSTRIAL | brt22 | 103539.39 | 15 | brt
COMMERCIAL | mwl14 | 15268408.4249 | 139 | mwl
RESIDENTL | wn1 | 4757807.4084 | 1039 | wn
COMMERCIAL | wo33 | 4706642.85 | 27 | wo
| nrn14 | 10562.91 | 10 | nrn
RESIDENTL | wgl15 | 10836827.2608 | 2158 | wgl
RESIDENTL | mfa22 | 4069843.249 | 701 | mfa
NCONUML | wyk24 | 96009.71 | 32 | wyk
NCONUML | rwn34 | 17137.95 | 21 | rwn
NCONUML | rve11 | 32578.28 | 16 | rve
INDUSTRIAL | klk11 | 54511.69 | 7 | klk
RESIDENTL | tt2 | 73044.37 | 7 | tt
COMMERCIAL | rwn32 | 3002784.6794 | 97 | rwn
NCONUML | tt1 | 9612.49 | 4 | tt
NCONUML | bwr23 | 79898.93 | 30 | bwr
NCONUML | epg14 | 19866.64 | 14 | epg
| elm26 | 27328.755 | 32 | elm
INDUSTRIAL | bdl32 | 418697.92 | 34 | bdl
FARM | wt11 | 3746.97 | 1 | wt
NCONUML | ofr23 | 50364.93 | 30 | ofr
INDUSTRIAL | smg23 | 412547.84 | 9 | smg
LIGHTING | klo14 | 3058096.87 | 1 | klo
| nrn13 | 13473.67 | 22 | nrn
FARM | bra12 | 12444.91 | 1 | bra
COMMERCIAL | cre21 | 15222170.3645 | 489 | cre
INDUSTRIAL | wgi32 | 984365.53 | 33 | wgi
NCONUML | rwt25 | 118451.05 | 54 | rwt
INDUSTRIAL | mwe236 | 280541.09 | 16 | mwe
RESIDENTL | epg33 | 183201.2006 | 6 | epg
INDUSTRIAL | elm33 | 243571.284 | 12 | elm
RESIDENTL | ldl11 | 13512975.3636 | 2241 | ldl
| mwl12 | 15850.97 | 9 | mwl
INDUSTRIAL | fgy21 | 6595081.67 | 18 | fgy
LIGHTING | smr24 | 109914.08 | 1 | smr
RESIDENTL | rwt25 | 10768082.8154 | 2324 | rwt
INDUSTRIAL | rwt15 | 3409961.2906 | 83 | rwt
INDUSTRIAL | phi12 | 3418741.3516 | 25 | phi
INDUSTRIAL | bwa22 | 1592049.74 | 9 | bwa
NCONUML | wo22 | 90587.46 | 26 | wo
INDUSTRIAL | ldl21 | 599666.7 | 44 | ldl
INDUSTRIAL | wt6 | 1814.16 | 1 | wt
NCONUML | ofr22 | 9198.59 | 2 | ofr
INDUSTRIAL | bra13 | 1860337.5903 | 47 | bra
COMMERCIAL | fgy24 | 2616699.5517 | 109 | fgy
RESIDENTL | epg11 | 6094828.0666 | 1503 | epg
NCONUML | rwt36 | 1279.88 | 1 | rwt
RESIDENTL | bwn14 | 23184606.5946 | 3016 | bwn
COMMERCIAL | bra31 | 7996775.7312 | 141 | bra
| nla32 | 13550.62 | 15 | nla
FARM | brt11 | 223967.42 | 33 | brt
| hpk12 | 10433.13 | 13 | hpk
INDUSTRIAL | llg13 | 899195.7591 | 21 | llg
INDUSTRIAL | wgl21 | 1687828.17 | 29 | wgl
INDUSTRIAL | cnr2 | 615523.18 | 19 | cnr
INDUSTRIAL | mfa14 | 499885.98 | 5 | mfa
RESIDENTL | drn13 | 15714620.5428 | 2698 | drn
FARM | kms12 | 1180373.8068 | 156 | kms
COMMERCIAL | rwn24 | 15303994.2605 | 63 | rwn
NCONUML | wn4 | 65357.11 | 21 | wn
COMMERCIAL | rwn33 | 562037.42 | 22 | rwn
| moe22 | 3614.75 | 12 | moe
| wgl13 | 39374.2 | 44 | wgl
| moe11 | 8193.3901 | 21 | moe
COMMERCIAL | wt7 | 4475658.5866 | 198 | wt
NCONUML | bwr13 | 106489.72 | 46 | bwr
NCONUML | kms12 | 115620.45 | 45 | kms
NCONUML | cyn24 | 41312.6858 | 21 | cyn
COMMERCIAL | mwl13 | 8520395.3383 | 232 | mwl
COMMERCIAL | cyn32 | 10902527.7138 | 351 | cyn
INDUSTRIAL | tgn31 | 3050316.88 | 29 | tgn
| wo13 | 12961.22 | 9 | wo
NCONUML | bra12 | 30121.15 | 6 | bra
| mwl24 | 4141.68 | 3 | mwl
RESIDENTL | ftr22 | 5196242.6186 | 1010 | ftr
| cyn12 | 33132.831 | 28 | cyn
| mwl11 | 4217.9 | 11 | mwl
NCONUML | sle13 | 9744.3474 | 7 | sle
RESIDENTL | sle14 | 16027394.2978 | 4223 | sle
RESIDENTL | wgl23 | 5362246.1099 | 739 | wgl
COMMERCIAL | cre23 | 25513720.5265 | 132 | cre
RESIDENTL | bdl43 | 5886157.096 | 1122 | bdl
RESIDENTL | bge21 | 100743.92 | 11 | bge
RESIDENTL | smg22 | 10427736.14 | 2476 | smg
FARM | rwn31 | 347566.14 | 21 | rwn
INDUSTRIAL | bn12 | 8173831.79 | 6 | bn
| wgi24 | 27543.5394 | 32 | wgi
| mfa23 | 2828.28 | 3 | mfa
NCONUML | elm22 | 93887.89 | 42 | elm
INDUSTRIAL | wots13 | 2426481.9937 | 28 | wots
RESIDENTL | mwl13 | 9372820.2657 | 1896 | mwl
COMMERCIAL | epg31 | 8736205.1691 | 170 | epg
| bdl44 | 43009.9658 | 33 | bdl
COMMERCIAL | wgl24 | 14484234.4559 | 200 | wgl
INDUSTRIAL | wn3 | 1104797.78 | 30 | wn
| wgi33 | 38017.7186 | 28 | wgi
NCONUML | wo31 | 91536.41 | 24 | wo
FARM | ldl14 | 3990495.203 | 142 | ldl
NCONUML | wyk12 | 43139.17 | 24 | wyk
INDUSTRIAL | mwl15 | 15961047.4 | 1 | mwl
LIGHTING | bdl32 | 23514.52 | 1 | bdl
| rve12 | 15159.19 | 33 | rve
NCONUML | phm34 | 55440.25 | 17 | phm
COMMERCIAL | phm22 | 18761180.3018 | 732 | phm
RESIDENTL | cyn22 | 8715945.6121 | 2142 | cyn
FARM | fgy31 | 3345.68 | 2 | fgy
RESIDENTL | smr22 | 8159798.5324 | 1327 | smr
RESIDENTL | cyn23 | 7298806.6664 | 1621 | cyn
FARM | bdl42 | 2407309.4815 | 483 | bdl
| wyk23 | 31976.68 | 33 | wyk
INDUSTRIAL | rwn26 | 257525.5397 | 10 | rwn
NCONUML | bwn11 | 91006.47 | 23 | bwn
COMMERCIAL | cyn23 | 7883296.3431 | 299 | cyn
| moe15 | 19145.0797 | 16 | moe
| drn11 | 44271.4909 | 65 | drn
INDUSTRIAL | moe22 | 88009.47 | 4 | moe
NCONUML | mdg1 | 4146.1 | 9 | mdg
FARM | bra33 | 5568.67 | 1 | bra
LIGHTING | bwa22 | 75542.46 | 1 | bwa
NCONUML | hpk14 | 64164.68 | 20 | hpk
NCONUML |  | 262.3928 | 5 | #REF!
INDUSTRIAL | cln13 | 2016187.9013 | 2 | cln
FARM | ofr11 | 1184021.9516 | 51 | ofr
FARM | phm31 | 2011038.4476 | 90 | phm
NCONUML | elm21 | 62554.36 | 23 | elm
NCONUML | wt8 | 36862.33 | 14 | wt
NCONUML | cnr1 | 1922.85 | 2 | cnr
INDUSTRIAL | cre31 | 212230.18 | 2 | cre
COMMERCIAL | mfa34 | 8313764.4144 | 170 | mfa
INDUSTRIAL | tt5 | 637183.9506 | 23 | tt
INDUSTRIAL | llg14 | 1201432.9268 | 29 | llg
RESIDENTL | wo23 | 1549813.7708 | 361 | wo
| bwr23 | 25383.1703 | 47 | bwr
| sle11 | 3997.21 | 10 | sle
NCONUML | epg22 | 8538.04 | 7 | epg
NCONUML | bwr24 | 20744.02 | 14 | bwr
INDUSTRIAL | myt12 | 952524.23 | 20 | myt
| ftr23 | 53453.1274 | 33 | ftr
RESIDENTL | bra11 | 9331476.9371 | 2277 | bra
FARM | ldl13 | 3504918.0126 | 302 | ldl
| brt11 | 8693.81 | 14 | brt
INDUSTRIAL | phm31 | 91642.7039 | 2 | phm
COMMERCIAL | bdl43 | 22280533.2345 | 523 | bdl
FARM | moe23 | 4928404.5033 | 365 | moe
| klk21 | 7164.56 | 8 | klk
| wt7 | 8483.27 | 17 | wt
FARM | llg11 | 4501914.1562 | 365 | llg
LIGHTING | cf2 | 13221.322 | 1 | cf
| tgn31 | 23134.1673 | 13 | tgn
RESIDENTL | nla31 | 3471883.5329 | 742 | nla
COMMERCIAL | bdl31 | 6479518.62 | 206 | bdl
COMMERCIAL | smr23 | 799486.21 | 26 | smr
INDUSTRIAL | rve11 | 154936.16 | 21 | rve
RESIDENTL | bm8b33 | 130717.0048 | 17 | bmb
FARM | phi12 | 364625.9 | 40 | phi
INDUSTRIAL | klk22 | 5518.6 | 1 | klk
RESIDENTL | llg12 | 7619865.2998 | 1210 | llg
RESIDENTL | cln21 | 24090170.4832 | 5877 | cln
NCONUML | cpk11 | 17830.25 | 17 | cpk
COMMERCIAL | ruba22 | 3463594.5603 | 120 | ruba
NCONUML | brt22 | 9306.55 | 7 | brt
INDUSTRIAL | epg32 | 7635590.16 | 5 | epg
INDUSTRIAL | cln12 | 360384.55 | 1 | cln
COMMERCIAL | bwr13 | 10101102.0366 | 288 | bwr
COMMERCIAL | wo22 | 9017310.64 | 153 | wo
INDUSTRIAL | hpk24 | 9439809.63 | 31 | hpk
COMMERCIAL | cpk12 | 5057421.24 | 115 | cpk
| lyd14 | 55928.8081 | 17 | lyd
INDUSTRIAL | klo11 | 67703.26 | 1 | klo
RESIDENTL | ldl14 | 11349760.1474 | 1905 | ldl
LIGHTING | myt21 | 2294.9 | 1 | myt
RESIDENTL | rwn22 | 13452598.5118 | 2640 | rwn
COMMERCIAL | bm8b32 | 168652.4116 | 16 | bmb
INDUSTRIAL | bdl34 | 328519.77 | 31 | bdl
| tt12 | 16952.1045 | 5 | tt
RESIDENTL | wots24 | 6979604.5034 | 1172 | wots
INDUSTRIAL | wyk24 | 160679.33 | 16 | wyk
COMMERCIAL | klo12 | 12237846.22 | 9 | klo
RESIDENTL | wo33 | 232024.16 | 58 | wo
COMMERCIAL | bn24 | 3468313.5774 | 163 | bn
COMMERCIAL | lga12 | 9341312.33 | 61 | lga
| msd1 | 16071.3636 | 20 | msd
INDUSTRIAL | ofr24 | 300622.14 | 4 | ofr
INDUSTRIAL | bwn13 | 24333.45 | 4 | bwn
| tt1 | 26786.62 | 3 | tt
INDUSTRIAL | rwt31 | 22449174.23 | 3 | rwt
FARM | mfa14 | 28798.91 | 1 | mfa
| bwr32 | 10607.4826 | 52 | bwr
INDUSTRIAL | wn4 | 1120535.2101 | 54 | wn
RESIDENTL | bwr12 | 975012.274 | 199 | bwr
INDUSTRIAL | wgi24 | 1432383.73 | 33 | wgi
| llg13 | 135285.4952 | 24 | llg
| rwn34 | 10950.9 | 10 | rwn
FARM | elm34 | 16399.68 | 6 | elm
RESIDENTL | ruba12 | 12797333.4035 | 1890 | ruba
COMMERCIAL | hpk22 | 5875279.82 | 181 | hpk
| cln11 | 262675.9461 | 229 | cln
RESIDENTL | cf2 | 494427.3912 | 409 | cf
FARM | elm22 | 15544.2323 | 4 | elm
INDUSTRIAL | smg32 | 67645.78 | 1 | smg
FARM | bwa23 | 3495492.525 | 169 | bwa
NCONUML | phm24 | 66511.6 | 15 | phm
NCONUML | wgi23 | 35701.3 | 15 | wgi
NCONUML | epg35 | 18576.68 | 9 | epg
NCONUML | llg13 | 26801.83 | 12 | llg
LIGHTING | phi13 | 74566.47 | 1 | phi
| ldl24 | 28689.7774 | 48 | ldl
| bge11 | 41147.6131 | 30 | bge
RESIDENTL | ofr21 | 18456788.2346 | 4412 | ofr
INDUSTRIAL | ofr11 | 52339.71 | 6 | ofr
COMMERCIAL | nrn11 | 8254682.48 | 13 | nrn
FARM | moe15 | 1053275.4428 | 126 | moe
INDUSTRIAL | lyd12 | 15947.41 | 3 | lyd
INDUSTRIAL | wt10 | 5540.7 | 1 | wt
RESIDENTL | rwt21 | 965731.93 | 282 | rwt
FARM | wo13 | 51683.13 | 6 | wo
INDUSTRIAL | epg34 | 25722.81 | 2 | epg
COMMERCIAL | lys36 | 31611.41 | 1 | lys
RESIDENTL | wn6 | 17451542.0984 | 3750 | wn
NCONUML | hpk12 | 23613.79 | 7 | hpk
INDUSTRIAL | ruba24 | 189283.4035 | 13 | ruba
| nrn12 | 36108.6 | 9 | nrn
NCONUML | nla32 | 30069.03 | 18 | nla
COMMERCIAL | bm8b31 | 174913.9253 | 14 | bmb
| wo22 | 26321.2427 | 38 | wo
INDUSTRIAL | fgy31 | 4952.61 | 1 | fgy
RESIDENTL | cln14 | 25051991.2109 | 8311 | cln
RESIDENTL | lga24 | 3807672.9803 | 653 | lga
RESIDENTL | bra31 | 2624204.8049 | 649 | bra
COMMERCIAL | cln21 | 7282112.3749 | 104 | cln
COMMERCIAL | ftr23 | 8984637.4811 | 336 | ftr
RESIDENTL | klo13 | 97850.5847 | 89 | klo
INDUSTRIAL | ofr14 | 250.62 | 1 | ofr
FARM | mwl24 | 966080.4815 | 75 | mwl
NCONUML | bdl41 | 86032.0652 | 28 | bdl
INDUSTRIAL | epg13 | 201122.3196 | 20 | epg
COMMERCIAL | tgn23 | 6173474.1124 | 95 | tgn
| moe12 | 11374.0239 | 16 | moe
INDUSTRIAL | drn11 | 8297.91 | 2 | drn
| wn4 | 46461.2191 | 29 | wn
NCONUML | wgl13 | 85005.64 | 23 | wgl
INDUSTRIAL | ftr22 | 264831.3749 | 23 | ftr
NCONUML | mjg11 | 5653.43 | 3 | mjg
RESIDENTL | klo12 | 526.2 | 1 | klo
COMMERCIAL | cln11 | 18408618.7138 | 182 | cln
NCONUML | wo13 | 11132.69 | 4 | wo
COMMERCIAL | yn38 | 28127.08 | 5 | yn
NCONUML | mwl24 | 19701.6 | 5 | mwl
RESIDENTL | wots12 | 7880580.6899 | 1786 | wots
COMMERCIAL | tgn43 | 5598797.62 | 126 | tgn
NCONUML | mfa23 | 6277.17 | 3 | mfa
NCONUML | bra32 | 63005.82 | 38 | bra
FARM | bdl34 | 247623.03 | 51 | bdl
INDUSTRIAL | wn5 | 6299826.69 | 33 | wn
| mby13 | 155.9226 | 1 | mby
FARM | ofr23 | 2419763.5413 | 305 | ofr
NCONUML | cre22 | 86458.6773 | 42 | cre
NCONUML | hpk23 | 84001.53 | 23 | hpk
RESIDENTL | bra24 | 8260262.5707 | 1824 | bra
| cyn14 | 12637.7523 | 26 | cyn
LIGHTING | wgl11 | 2443513.25 | 2 | wgl
NCONUML | wgi24 | 69610.83 | 24 | wgi
COMMERCIAL | klo14 | 11961206.944 | 269 | klo
FARM | drn14 | 379625.3327 | 36 | drn
RESIDENTL | bwr22 | 1941843.629 | 510 | bwr
| llg14 | 42684.6726 | 22 | llg
INDUSTRIAL | drn21 | 709809.96 | 3 | drn
INDUSTRIAL | tgn42 | 199383.97 | 5 | tgn
RESIDENTL | sle32 | 6677118.757 | 1350 | sle
RESIDENTL | myt12 | 14552002.0991 | 2380 | myt
FARM | myt21 | 821475.54 | 124 | myt
| bn11 | 39921.12 | 40 | bn
NCONUML | mby12 | 15769.2 | 4 | mby
NCONUML | bdl44 | 1602.59 | 5 | bdl
COMMERCIAL | tt12 | 10810239.5174 | 467 | tt
NCONUML | wn7 | 7884.6 | 2 | wn
| bdl34 | 14430.17 | 36 | bdl
RESIDENTL | lyd11 | 11014119.7855 | 2574 | lyd
FARM | wyk23 | 2329152.6841 | 202 | wyk
| epg23 | 66262.7623 | 20 | epg
RESIDENTL | rwt32 | 15157646.1346 | 3808 | rwt
RESIDENTL | cre31 | 23125994.5084 | 5990 | cre
FARM | bn11 | 9012293.1298 | 1372 | bn
COMMERCIAL |  | 2470964.7554 | 79 | #REF!
INDUSTRIAL | kms11 | 3849512.37 | 9 | kms
RESIDENTL | sle31 | 15232222.0022 | 4728 | sle
RESIDENTL | myt11 | 3230941.4261 | 365 | myt
| wyk12 | 33744.4845 | 17 | wyk
| lga11 | 13750.1489 | 25 | lga
COMMERCIAL | cre33 | 14716025.8299 | 132 | cre
RESIDENTL | trc01 | 404888.8876 | 85 | trc
| moe25 | 10579.3743 | 23 | moe
NCONUML | msd1 | 8725.66 | 9 | msd
RESIDENTL | mwl14 | 1637810.9082 | 178 | mwl
FARM | wn5 | 10157746.9699 | 1090 | wn
INDUSTRIAL | bwr33 | 13101695.07 | 41 | bwr
NCONUML | ofr24 | 72292.73 | 18 | ofr
| mdg1 | 5594.13 | 4 | mdg
FARM | wgi33 | 86057.74 | 7 | wgi
RESIDENTL | rwt22 | 12512450.4989 | 3066 | rwt
RESIDENTL | cnr2 | 3844076.3719 | 1054 | cnr
| hpk14 | 17565.23 | 35 | hpk
NCONUML | drn23 | 37389.78 | 20 | drn
RESIDENTL | tgn44 | 11943542.7304 | 2804 | tgn
| tgn42 | 0 | 1 | tgn
NCONUML | rwt22 | 27503.296 | 22 | rwt
FARM | mwl16 | 172184.54 | 14 | mwl
COMMERCIAL | nla34 | 1413700.5844 | 93 | nla
| epg22 | 2049.9261 | 2 | epg
FARM | tgn41 | 3728231.4432 | 423 | tgn
COMMERCIAL | lga23 | 3382991.9134 | 119 | lga
NCONUML | sle31 | 61055.23 | 20 | sle
NCONUML | tgn44 | 66469.79 | 20 | tgn
| phm24 | 18272.6834 | 34 | phm
RESIDENTL | hpk11 | 16523367.4098 | 4141 | hpk
| hpk13 | 40054.7485 | 22 | hpk
| bwr24 | 10180.34 | 28 | bwr
COMMERCIAL | bdl33 | 34051046.7333 | 257 | bdl
COMMERCIAL | wt9 | 7035668.1433 | 128 | wt
NCONUML | wt15 | 16005.53 | 14 | wt
FARM | ruba24 | 730484.142 | 55 | ruba
NCONUML | cpk23 | 20021.69 | 18 | cpk
INDUSTRIAL | mwl21 | 320021.87 | 5 | mwl
COMMERCIAL | hpk23 | 12064171.7331 | 206 | hpk
INDUSTRIAL | wt11 | 2563605.84 | 2 | wt
RESIDENTL | wt15 | 8580853.2399 | 1947 | wt
| elm21 | 24345.52 | 16 | elm
INDUSTRIAL | mwl16 | 183545.9668 | 9 | mwl
FARM | rve13 | 9637.99 | 1 | rve
NCONUML | drn22 | 69938.3 | 27 | drn
NCONUML | bdl31 | 70697.58 | 29 | bdl
NCONUML | bwa24 | 1320.25 | 1 | bwa
COMMERCIAL | mwl23 | 10773058.8537 | 154 | mwl
COMMERCIAL | elm23 | 5093994.3825 | 95 | elm
FARM | smr23 | 1078615.6398 | 156 | smr
| cpk11 | 37835.6667 | 47 | cpk
INDUSTRIAL | bra14 | 14750.52 | 4 | bra
RESIDENTL | rwn33 | 5693275.4596 | 1153 | rwn
| bn22 | 41634.09 | 21 | bn
INDUSTRIAL | tt2 | 11531135.8238 | 100 | tt
INDUSTRIAL | wt12 | 3871876.0911 | 67 | wt
INDUSTRIAL | mwl22 | 292678.42 | 8 | mwl
RESIDENTL | bn23 | 8695284.412 | 1665 | bn
COMMERCIAL | cyn11 | 9621618.8569 | 233 | cyn
| cyn21 | 22400.14 | 28 | cyn
INDUSTRIAL | mjg11 | 1321804.29 | 13 | mjg
INDUSTRIAL | cf2 | 1970.494 | 2 | cf
RESIDENTL | tt5 | 6560032.4165 | 1633 | tt
COMMERCIAL | smr14 | 6818307.6657 | 239 | smr
COMMERCIAL | smg33 | 1348313.99 | 14 | smg
RESIDENTL | rwt15 | 11066767.0768 | 2454 | rwt
COMMERCIAL | cre32 | 14440881.1645 | 427 | cre
INDUSTRIAL | smr24 | 4639865.5557 | 45 | smr
COMMERCIAL | fgy23 | 10185283.97 | 98 | fgy
COMMERCIAL | hpk11 | 3476478.711 | 53 | hpk
| cre32 | 19011.64 | 13 | cre
NCONUML | wgl23 | 12760.41 | 6 | wgl
COMMERCIAL | nrn15 | 84419.81 | 3 | nrn
NCONUML | moe15 | 22748.39 | 11 | moe
RESIDENTL | tt12 | 86039.86 | 6 | tt
RESIDENTL | cyn31 | 8632445.7043 | 2077 | cyn
RESIDENTL | wgl24 | 16633542.8094 | 2715 | wgl
COMMERCIAL | wgi22 | 6881286.006 | 159 | wgi
INDUSTRIAL | smr13 | 992080.85 | 26 | smr
NCONUML | cpk12 | 17033.61 | 10 | cpk
NCONUML | ftr21 | 16597.26 | 11 | ftr
FARM | mwl12 | 18529.37 | 2 | mwl
INDUSTRIAL | epg33 | 1129768.4897 | 4 | epg
| wyk13 | 9658.4809 | 15 | wyk
LIGHTING | trc01 | 669938.2281 | 2 | trc
FARM | hpk13 | 2305.94 | 1 | hpk
RESIDENTL | tt6 | 19150788.3328 | 4695 | tt
FARM | tgn31 | 5369095.0164 | 562 | tgn
NCONUML | wgl24 | 11028.97 | 10 | wgl
INDUSTRIAL | brt11 | 82545.9018 | 12 | brt
LIGHTING | mby11 | 10728.24 | 1 | mby
NCONUML | myt21 | 24178.1 | 12 | myt
| wt10 | 6115.9374 | 5 | wt
RESIDENTL | bge12 | 9796026.1467 | 1789 | bge
FARM | myt11 | 2640136.7565 | 257 | myt
NCONUML | cyn11 | 21168.08 | 13 | cyn
INDUSTRIAL |  | 942329979.1078 | 12 | #REF!
INDUSTRIAL | elm34 | 168803.0667 | 15 | elm
| brt22 | 30486.3216 | 18 | brt
INDUSTRIAL | epg11 | 6777.42 | 2 | epg
RESIDENTL | elm34 | 19825611.7814 | 4189 | elm
COMMERCIAL | sle13 | 974523.8832 | 109 | sle
INDUSTRIAL | lga13 | 207007.5439 | 9 | lga
RESIDENTL | mwl23 | 3618535.6291 | 812 | mwl
| fgy14 | 28887.99 | 26 | fgy
COMMERCIAL | mby13 | 2521770.2974 | 71 | mby
| lga12 | 14720.56 | 12 | lga
RESIDENTL | cpk12 | 17343162.547 | 2927 | cpk
COMMERCIAL | wt5 | 19785711.5258 | 118 | wt
INDUSTRIAL | drn24 | 4643890.64 | 3 | drn
FARM | drn21 | 13254.24 | 1 | drn
NCONUML | mwl11 | 360.93 | 3 | mwl
RESIDENTL | epg34 | 15669683.4078 | 3862 | epg
NCONUML | wt10 | 27658.61 | 16 | wt
LIGHTING | rwt14 | 962126.36 | 3 | rwt
COMMERCIAL | drn23 | 5472888.3558 | 161 | drn
LIGHTING | bwn11 | 6340546.01 | 1 | bwn
INDUSTRIAL | sfs1 | 80102.39 | 5 | sfs
COMMERCIAL | phm34 | 4610839.9937 | 66 | phm
COMMERCIAL | mfa31 | 3803351.87 | 100 | mfa
INDUSTRIAL | rwt25 | 2203508.65 | 42 | rwt
| bwa22 | 41045.3074 | 24 | bwa
FARM | smr13 | 139441.5096 | 27 | smr
NCONUML | phi12 | 84007.84 | 24 | phi
| fgy21 | 10377.87 | 9 | fgy
NCONUML | rwt15 | 44056.974 | 28 | rwt
LIGHTING | nla34 | 5187.52 | 1 | nla
RESIDENTL | sfs1 | 6449039.4989 | 958 | sfs
RESIDENTL | msd4 | 16354350.3097 | 2395 | msd
INDUSTRIAL | phm33 | 724516.58 | 21 | phm
COMMERCIAL | wgl14 | 59932538.6 | 1 | wgl
COMMERCIAL | rwt31 | 3904134.109 | 54 | rwt
RESIDENTL | wt5 | 5466545.168 | 1335 | wt
FARM | ftr22 | 3872176.8459 | 271 | ftr
| wn5 | 51237.831 | 23 | wn
INDUSTRIAL | kms12 | 880994.04 | 26 | kms
NCONUML | rwt31 | 27889.28 | 18 | rwt
RESIDENTL | elm22 | 20622579.4478 | 3120 | elm
| bn24 | 7126.586 | 9 | bn
FARM | wots11 | 7572710.4051 | 689 | wots
INDUSTRIAL | myt11 | 122662.09 | 11 | myt
NCONUML | bdl32 | 81716.25 | 38 | bdl
NCONUML | cyn33 | 39860.39 | 20 | cyn
| lga13 | 7900.07 | 12 | lga
COMMERCIAL | wn7 | 705796.26 | 31 | wn
RESIDENTL | tgn23 | 12995258.1614 | 2157 | tgn
RESIDENTL | wgl12 | 18309192.1093 | 3011 | wgl
NCONUML | drn14 | 58816.42 | 20 | drn
INDUSTRIAL | tt9 | 1853761.73 | 4 | tt
RESIDENTL | kms12 | 23913269.0041 | 4277 | kms
COMMERCIAL | wgi33 | 13737748.8552 | 364 | wgi
COMMERCIAL | phm21 | 28428865.0993 | 838 | phm
FARM | sle32 | 5441049.7096 | 310 | sle
NCONUML | cyn32 | 58907.16 | 38 | cyn
INDUSTRIAL | msd2 | 165834.72 | 18 | msd
COMMERCIAL | bwr23 | 26845428.111 | 233 | bwr
RESIDENTL | msd2 | 5810770.2828 | 1153 | msd
FARM | klk11 | 2014936.8264 | 177 | klk
| wots12 | 13459.1171 | 22 | wots
INDUSTRIAL | rwn24 | 4339629.96 | 13 | rwn
INDUSTRIAL | tgn41 | 1853911.3546 | 62 | tgn
COMMERCIAL | smg32 | 6595824.87 | 22 | smg
| wgi34 | 86239.94 | 15 | wgi
RESIDENTL | bn22 | 13286130.4589 | 3118 | bn
RESIDENTL | mfa31 | 9237847.4317 | 2206 | mfa
COMMERCIAL | wgi34 | 9571334.08 | 60 | wgi
RESIDENTL | mdi1 | 176577.17 | 31 | mdi
NCONUML | rwn31 | 16738.19 | 15 | rwn
INDUSTRIAL | drn13 | 239296.9 | 11 | drn
INDUSTRIAL | bdl43 | 306419.52 | 21 | bdl
NCONUML | wo23 | 56204.51 | 16 | wo
COMMERCIAL | ftr21 | 2804675.8206 | 100 | ftr
COMMERCIAL | bwa23 | 206762.2501 | 23 | bwa
NCONUML | mfa21 | 28416.84 | 12 | mfa
| cln23 | 52144.7804 | 85 | cln
RESIDENTL | rve11 | 2276471.0008 | 508 | rve
COMMERCIAL | ofr24 | 6649904.8426 | 113 | ofr
NCONUML | phi13 | 105028.33 | 33 | phi
FARM | smg22 | 25054.15 | 4 | smg
FARM | bwn11 | 18419.1 | 1 | bwn
INDUSTRIAL | epg31 | 360181.3871 | 31 | epg
COMMERCIAL | fgy14 | 7872993.2117 | 231 | fgy
| ldl11 | 24480.7 | 22 | ldl
INDUSTRIAL | wgl24 | 939120.3004 | 39 | wgl
| phm22 | 31542.7748 | 10 | phm
COMMERCIAL | moe15 | 2469270.3666 | 172 | moe
| cnr3 | 100.0469 | 1 | cnr
RESIDENTL | bwn12 | 4456239.3509 | 1013 | bwn
COMMERCIAL | mwl24 | 5791496.4979 | 78 | mwl
COMMERCIAL | wo13 | 2493976.37 | 46 | wo
RESIDENTL | elm25 | 10534980.5572 | 2009 | elm
RESIDENTL | phm32 | 14466986.7977 | 3288 | phm
COMMERCIAL | ofr11 | 14130002.2904 | 224 | ofr
INDUSTRIAL | bge13 | 1057475.88 | 11 | bge
RESIDENTL | ofr22 | 7907197.5875 | 2174 | ofr
INDUSTRIAL | lga22 | 745287.81 | 44 | lga
FARM | hpk22 | 33600.65 | 5 | hpk
COMMERCIAL | epg23 | 63543126.9632 | 711 | epg
NCONUML | epg34 | 29379.47 | 21 | epg
| mwl23 | 14018.9088 | 10 | mwl
FARM | lyd14 | 350081.37 | 31 | lyd
| elm33 | 18371.0537 | 30 | elm
RESIDENTL | bwn11 | 14758921.2622 | 2984 | bwn
| cyn33 | 33636.86 | 37 | cyn
INDUSTRIAL | ldl13 | 1566146.5513 | 31 | ldl
NCONUML | smg32 | 19512.15 | 10 | smg
NCONUML | lga21 | 24931.49 | 9 | lga
RESIDENTL | mfa34 | 6438005.323 | 995 | mfa
COMMERCIAL | lga22 | 10229963.6597 | 340 | lga
COMMERCIAL | wgi31 | 4363035.5887 | 128 | wgi
| wt9 | 17175.83 | 21 | wt
INDUSTRIAL | mfa21 | 1292894.4886 | 57 | mfa
FARM | wgi32 | 343056.5273 | 19 | wgi
COMMERCIAL | bge21 | 44944.8 | 1 | bge
INDUSTRIAL | elm26 | 46289.86 | 5 | elm
NCONUML | msd4 | 12187.83 | 6 | msd
COMMERCIAL | bra21 | 14789918.5926 | 289 | bra
| cpk22 | 7305.07 | 12 | cpk
NCONUML | phm32 | 76324.09 | 20 | phm
NCONUML | sfs1 | 44865.78 | 10 | sfs
COMMERCIAL | lyd13 | 6072257.17 | 42 | lyd
FARM | cyn33 | 36456.98 | 4 | cyn
NCONUML | phm21 | 71428.0533 | 24 | phm
COMMERCIAL | sle32 | 5434267.6149 | 190 | sle
NCONUML | smg31 | 21751.86 | 17 | smg
NCONUML | wots11 | 25057.91 | 11 | wots
RESIDENTL | tgn43 | 15724147.9465 | 3608 | tgn
INDUSTRIAL | cyn21 | 9259443.95 | 23 | cyn
INDUSTRIAL | bn23 | 1923467.13 | 19 | bn
NCONUML | nrn14 | 79150.17 | 17 | nrn
NCONUML | cyn22 | 32483.16 | 10 | cyn
NCONUML | wgl12 | 47271.49 | 20 | wgl
COMMERCIAL | phm24 | 600129.57 | 25 | phm
NCONUML | lga11 | 25837.14 | 8 | lga
NCONUML | tgn41 | 7415.11 | 5 | tgn
RESIDENTL | wgl11 | 17118670.1537 | 3818 | wgl
RESIDENTL | wots11 | 15871220.8415 | 2910 | wots
| rwn31 | 40233.5106 | 27 | rwn
COMMERCIAL | elm32 | 8171019.0636 | 263 | elm
FARM | mby11 | 1335559.7721 | 187 | mby
INDUSTRIAL | mwl25 | 33119.15 | 8 | mwl
FARM | rwn26 | 5055.63 | 2 | rwn
| nla34 | 8234.98 | 10 | nla
RESIDENTL |  | 349105.8277 | 492 | #REF!
FARM | epg13 | 82815.8863 | 12 | epg
| wyk24 | 32167.14 | 30 | wyk
FARM | sle11 | 16862.17 | 6 | sle
COMMERCIAL | bm8b33 | 3349.12 | 2 | bmb
RESIDENTL | smg21 | 17914575.4009 | 3718 | smg
INDUSTRIAL | bdl42 | 622534.62 | 24 | bdl
| yn38 | 7519.7419 | 1 | yn
| phi13 | 28221.5917 | 27 | phi
| epg14 | 9258.9052 | 38 | epg
FARM | nla31 | 1791184.5035 | 140 | nla
INDUSTRIAL | wgi33 | 1188063.8119 | 37 | wgi
LIGHTING | phm33 | 4303153.65 | 2 | phm
RESIDENTL | phm33 | 12878778.4238 | 2134 | phm
COMMERCIAL | wgl23 | 3870974.8784 | 252 | wgl
NCONUML | wt5 | 58508.56 | 14 | wt
NCONUML | bwn14 | 81385.02 | 37 | bwn
NCONUML | mfa31 | 49958.93 | 14 | mfa
COMMERCIAL | bra12 | 23355928.37 | 122 | bra
NCONUML | wt13 | 98966.19 | 41 | wt
COMMERCIAL | klo24 | 13267963.2484 | 244 | klo
COMMERCIAL | bge12 | 6262328.83 | 64 | bge
COMMERCIAL | wn4 | 10511680.2174 | 332 | wn
INDUSTRIAL | tt6 | 2940006.87 | 14 | tt
FARM | cln13 | 4519.0334 | 1 | cln
RESIDENTL | bwa23 | 1839261.5711 | 259 | bwa
RESIDENTL | smr12 | 601661.7559 | 102 | smr
NCONUML | bra31 | 17155.48 | 11 | bra
FARM | cln22 | 84599.56 | 6 | cln
RESIDENTL | moe23 | 10757204.18 | 1872 | moe
FARM | bn23 | 4995698.9571 | 709 | bn
INDUSTRIAL | bwr12 | 7576207.2428 | 317 | bwr
COMMERCIAL | elm33 | 8652520.7547 | 229 | elm
RESIDENTL | tgn12 | 769554.192 | 239 | tgn
NCONUML | bn23 | 5729.17 | 9 | bn
| cyn11 | 35169.6447 | 13 | cyn
INDUSTRIAL | wots12 | 5742170.47 | 22 | wots
INDUSTRIAL | llg12 | 8080777.31 | 18 | llg
NCONUML | ofr14 | 11958.45 | 3 | ofr
RESIDENTL | rwn34 | 11161403.5989 | 1490 | rwn
RESIDENTL | fgy12 | 975691.3435 | 398 | fgy
COMMERCIAL | wyk24 | 11852940.7836 | 290 | wyk
COMMERCIAL | smr12 | 1199230.8 | 20 | smr
INDUSTRIAL | wgl11 | 590499.13 | 17 | wgl
INDUSTRIAL | moe13 | 8896507.14 | 13 | moe
INDUSTRIAL | wots11 | 14616083.73 | 22 | wots
NCONUML | epg13 | 4325.18 | 2 | epg
NCONUML | bn22 | 72789.04 | 38 | bn
RESIDENTL | bwr23 | 15381612.1105 | 3589 | bwr
NCONUML | cln13 | 19538.3161 | 10 | cln
COMMERCIAL | bwa24 | 4350900.07 | 4 | bwa
COMMERCIAL | bwr32 | 11258727.4704 | 251 | bwr
RESIDENTL | bra32 | 8710928.5985 | 2041 | bra
FARM | klo14 | 681766.459 | 92 | klo
INDUSTRIAL | tt7 | 9353368.9205 | 125 | tt
RESIDENTL | wo11 | 815896.564 | 156 | wo
LIGHTING | mwl24 | 803944.3 | 2 | mwl
COMMERCIAL | bwr24 | 7860784.794 | 262 | bwr
COMMERCIAL | drn14 | 5284276.4061 | 147 | drn
NCONUML | hpk24 | 27055.52 | 10 | hpk
| cyn32 | 34865.18 | 48 | cyn
| bra23 | 7974.72 | 25 | bra
RESIDENTL | rve13 | 16767421.4281 | 3587 | rve
COMMERCIAL | bwn13 | 11531398.8601 | 263 | bwn
FARM | cln23 | 76487.94 | 5 | cln
NCONUML | ruba24 | 1482.28 | 4 | ruba
COMMERCIAL | msd1 | 4448954.738 | 126 | msd
| phm31 | 2299.25 | 4 | phm
LIGHTING | wn1 | 677520.74 | 1 | wn
COMMERCIAL | wt8 | 2125517.5597 | 71 | wt
RESIDENTL | bdl33 | 5101200.3632 | 906 | bdl
COMMERCIAL | rwt21 | 33203170.5825 | 281 | rwt
FARM |  | 15223.9488 | 53 | #REF!
| fgy13 | 16173.63 | 19 | fgy
| wt11 | 14907.843 | 20 | wt
RESIDENTL | mwl24 | 4259131.5949 | 729 | mwl
INDUSTRIAL | bwn12 | 375603.57 | 33 | bwn
| lyd12 | 10355.6 | 16 | lyd
| lyd13 | 31235.27 | 24 | lyd
| elm32 | 28931.8643 | 22 | elm
RESIDENTL | ldl13 | 20183081.1078 | 3515 | ldl
COMMERCIAL | epg14 | 4722560.1631 | 66 | epg
FARM | epg32 | 616929.8369 | 16 | epg
| smg23 | 6841.4304 | 12 | smg
NCONUML | mwl16 | 31954.29 | 10 | mwl
COMMERCIAL | ofr22 | 3955299.41 | 63 | ofr
FARM | wgl24 | 9990463.449 | 886 | wgl
COMMERCIAL | llg14 | 8402501.0583 | 280 | llg
COMMERCIAL | wgi24 | 3234685.3433 | 136 | wgi
FARM | cnr3 | 47812.597 | 17 | cnr
| epg33 | 55263.0616 | 6 | epg
INDUSTRIAL | bra24 | 1115020.317 | 14 | bra
NCONUML | wgi33 | 84992.31 | 23 | wgi
FARM | rwt15 | 1849.17 | 1 | rwt
RESIDENTL | ldl12 | 620798.3677 | 119 | ldl
INDUSTRIAL | bwr22 | 8606432.4227 | 334 | bwr
FARM | cf2 | 2033.193 | 1 | cf
NCONUML | klo14 | 36515.49 | 28 | klo
INDUSTRIAL | trc01 | 31629.57 | 2 | trc
RESIDENTL | lga21 | 9412760.8279 | 1623 | lga
RESIDENTL | wt13 | 15834142.0313 | 3223 | wt
RESIDENTL | cyn13 | 3260017.5153 | 858 | cyn
INDUSTRIAL | ofr21 | 138382.59 | 9 | ofr
NCONUML | sle32 | 22407.43 | 13 | sle
COMMERCIAL | lyd12 | 210380 | 9 | lyd
NCONUML | wyk23 | 87622.06 | 45 | wyk
| fgy33 | 11652.67 | 18 | fgy
INDUSTRIAL | hpk22 | 98414.21 | 14 | hpk
NCONUML | sle11 | 59204.61 | 19 | sle
RESIDENTL | bwr13 | 20902397.8318 | 4170 | bwr
COMMERCIAL | rwn34 | 3999387.7688 | 144 | rwn
| hpk22 | 19671.58 | 41 | hpk
FARM | klk22 | 332413.14 | 10 | klk
INDUSTRIAL | wn1 | 2988984.92 | 20 | wn
NCONUML | rwn26 | 27156.61 | 25 | rwn
| bwr33 | 13120.641 | 3 | bwr
NCONUML | mby11 | 20114.34 | 7 | mby
RESIDENTL | smg33 | 11198068.0634 | 2626 | smg
FARM | bn12 | 813334.585 | 146 | bn
FARM | bdl32 | 1026406.0127 | 170 | bdl
FARM | drn24 | 15422429 | 2 | drn
LIGHTING | cre21 | 378603.77 | 3 | cre
RESIDENTL | smg32 | 834640.09 | 219 | smg
| wt12 | 39199.7023 | 19 | wt
FARM | bwn14 | 804408.7 | 76 | bwn
NCONUML | bwr33 | 16865.43 | 3 | bwr
INDUSTRIAL | rwn22 | 12871.85 | 4 | rwn
NCONUML | drn11 | 63307.01 | 20 | drn
INDUSTRIAL | mwl13 | 228128.43 | 11 | mwl
COMMERCIAL | elm22 | 6567142.5918 | 154 | elm
FARM | trc01 | 521142.3328 | 100 | trc
COMMERCIAL | rwt14 | 11855990.576 | 301 | rwt
INDUSTRIAL | sle14 | 1780526.4437 | 64 | sle
RESIDENTL | smr24 | 17064871.7804 | 2952 | smr
FARM | bwa22 | 1586063.9755 | 254 | bwa
NCONUML | tt4 | 37478.54 | 17 | tt
| tt9 | 28146.8116 | 74 | tt
COMMERCIAL | epg34 | 4040655.8363 | 65 | epg
FARM | nrn11 | 7816.07 | 2 | nrn
LIGHTING | cpk23 | 1632459.3 | 1 | cpk
RESIDENTL | fgy31 | 4476808.4262 | 913 | fgy
COMMERCIAL | fgy33 | 6399813.6929 | 132 | fgy
| cnr2 | 20535.9245 | 15 | cnr
INDUSTRIAL | sle32 | 10933678.58 | 25 | sle
| bra13 | 120577.89 | 18 | bra
RESIDENTL | wgi23 | 12118480.0079 | 2685 | wgi
INDUSTRIAL | wn6 | 922850.6842 | 19 | wn
LIGHTING | tgn44 | 752.53 | 1 | tgn
RESIDENTL | wt8 | 8250779.9392 | 1851 | wt
COMMERCIAL | moe25 | 5695010.3572 | 176 | moe
FARM | wgi34 | 4315044.5216 | 374 | wgi
INDUSTRIAL | fgy32 | 667572.7217 | 61 | fgy
NCONUML | wo32 | 55386.46 | 14 | wo
INDUSTRIAL | lys36 | 1267258.48 | 1 | lys
| bn12 | 10728.35 | 13 | bn
NCONUML | brt11 | 10828.27 | 7 | brt
| drn21 | 27694.76 | 39 | drn
| drn24 | 16030.7 | 26 | drn
RESIDENTL | cpk23 | 11646034.7633 | 2466 | cpk
RESIDENTL | wots13 | 7948103.7952 | 1344 | wots
FARM | wgl23 | 3908847.1376 | 390 | wgl
COMMERCIAL | wyk13 | 4417313.7071 | 191 | wyk
NCONUML | klk21 | 10664.54 | 6 | klk
INDUSTRIAL | smg22 | 31514.93 | 2 | smg
RESIDENTL | wgi22 | 12719214.8315 | 3088 | wgi
| cpk13 | 49314.0333 | 41 | cpk
COMMERCIAL | bdl41 | 11311068.2286 | 367 | bdl
NCONUML | nrn12 | 43208.48 | 18 | nrn
RESIDENTL | fgy23 | 5177398.3937 | 1023 | fgy
NCONUML | brt21 | 3240.29 | 5 | brt
NCONUML | tgn31 | 2100.01 | 7 | tgn
RESIDENTL | mjg11 | 6256821.3625 | 1064 | mjg
INDUSTRIAL | lga24 | 175905.212 | 21 | lga
COMMERCIAL | moe21 | 6644337.36 | 291 | moe
INDUSTRIAL | bwn14 | 326743.47 | 17 | bwn
INDUSTRIAL | phm22 | 15545673.5732 | 29 | phm
LIGHTING | klo24 | 2201282.63 | 3 | klo
FARM | epg12 | 13782.33 | 2 | epg
INDUSTRIAL | cln14 | 247.5387 | 1 | cln
FARM | bge13 | 383352.554 | 75 | bge
NCONUML | bra14 | 25509.54 | 26 | bra
RESIDENTL | fgy24 | 17189073.2659 | 3574 | fgy
NCONUML | lyd14 | 37348.84 | 18 | lyd
FARM | fgy21 | 91303 | 9 | fgy
INDUSTRIAL | elm24 | 6476.78 | 2 | elm
FARM | bra24 | 985.88 | 1 | bra
COMMERCIAL | ldl24 | 1420329.0926 | 55 | ldl
INDUSTRIAL | wots24 | 329358.8434 | 32 | wots
| moe13 | 6325.43 | 5 | moe
COMMERCIAL | cyn14 | 5422735.5047 | 221 | cyn
LIGHTING | smg21 | 4640189.26 | 4 | smg
COMMERCIAL | tgn42 | 24454733.755 | 420 | tgn
INDUSTRIAL | lga14 | 502652.15 | 16 | lga
INDUSTRIAL | cre33 | 377497.19 | 17 | cre
FARM | ldl11 | 223383.36 | 16 | ldl
INDUSTRIAL | bn24 | 28582582.13 | 34 | bn
COMMERCIAL | tt1 | 14308038.8686 | 155 | tt
| wn3 | 30735.58 | 33 | wn
NCONUML | ldl21 | 10778.31 | 7 | ldl
NCONUML | wt6 | 188781.23 | 35 | wt
RESIDENTL | elm23 | 20356024.4153 | 3325 | elm
COMMERCIAL | drn11 | 4003224.2127 | 79 | drn
COMMERCIAL | bra34 | 7850026.49 | 9 | bra
FARM | cyn32 | 3133.97 | 2 | cyn
FARM | cpk23 | 18946.87 | 2 | cpk
FARM | wt15 | 5251.96 | 1 | wt
NCONUML | wgi32 | 95036.63 | 31 | wgi
COMMERCIAL | phm32 | 13343791.1884 | 221 | phm
COMMERCIAL | epg22 | 38007492.3668 | 89 | epg
INDUSTRIAL | wgl15 | 1553419.6108 | 26 | wgl
FARM | phm33 | 7138587.5126 | 545 | phm
LIGHTING | bra32 | 1301740.84 | 1 | bra
COMMERCIAL | bra22 | 30448240 | 1 | bra
COMMERCIAL | msd4 | 11090376.2999 | 395 | msd
COMMERCIAL | lyd14 | 7038791.6959 | 51 | lyd
| phi12 | 701365.4285 | 34 | phi
| nrn11 | 5120.38 | 9 | nrn
INDUSTRIAL | smg21 | 777155.28 | 5 | smg
NCONUML | nla31 | 5002.08 | 5 | nla
RESIDENTL | wyk13 | 19583843.7522 | 3346 | wyk
RESIDENTL | tgn41 | 6800482.2089 | 1104 | tgn
COMMERCIAL | fgy34 | 7285642.6158 | 201 | fgy
FARM | wgl11 | 5210774.8775 | 355 | wgl
FARM | tgn11 | 616949.6887 | 82 | tgn
NCONUML | wn5 | 5268.61 | 9 | wn
NCONUML | bdl42 | 6088.6 | 9 | bdl
INDUSTRIAL | hpk23 | 515987.93 | 6 | hpk
FARM | tgn44 | 47621.17 | 6 | tgn
| smr13 | 35140.976 | 19 | smr
| wgi31 | 18377.08 | 37 | wgi
NCONUML | bwr34 | 85519.21 | 30 | bwr
| bdl32 | 24365.9844 | 40 | bdl
COMMERCIAL | fgy13 | 5672167.28 | 57 | fgy
INDUSTRIAL | sle31 | 621920.2305 | 85 | sle
NCONUML | cyn23 | 72679.67 | 24 | cyn
NCONUML | hpk22 | 92149.17 | 38 | hpk
RESIDENTL | cre23 | 13902510.3441 | 3180 | cre
COMMERCIAL | lga21 | 4415159.211 | 179 | lga
| cre33 | 51988.0123 | 70 | cre
INDUSTRIAL | bra32 | 800790.5812 | 33 | bra
| rwn26 | 43959.1499 | 36 | rwn
NCONUML | ftr22 | 27457.1971 | 11 | ftr
FARM | cyn23 | 28738.28 | 3 | cyn
FARM | wn2 | 2722540.844 | 262 | wn
FARM | wots25 | 1192605.1156 | 155 | wots
COMMERCIAL | lga11 | 2601951.4442 | 115 | lga
COMMERCIAL | cnr1 | 836269.15 | 40 | cnr
RESIDENTL | cre22 | 15737441.9951 | 3931 | cre
RESIDENTL | cyn24 | 3227627.7482 | 729 | cyn
| drn14 | 42739.5968 | 43 | drn
NCONUML | wgi34 | 240.62 | 2 | wgi
COMMERCIAL | mdi1 | 200221.43 | 4 | mdi
LIGHTING | lga22 | 290997.27 | 1 | lga
RESIDENTL | sle13 | 2426821.6594 | 1643 | sle
RESIDENTL | mby12 | 3267894.3821 | 609 | mby
FARM | wgi31 | 368672.79 | 43 | wgi
INDUSTRIAL | cyn24 | 15644182.2427 | 207 | cyn
| fgy34 | 3433.61 | 11 | fgy
RESIDENTL | bge11 | 15368827.4604 | 2654 | bge
RESIDENTL | ftr12 | 3825364.7454 | 636 | ftr
| mfa21 | 17049.39 | 26 | mfa
COMMERCIAL | wgi21 | 45541.7604 | 2 | wgi
INDUSTRIAL | wo14 | 2975508 | 24 | wo
COMMERCIAL | wgl12 | 5759083.9004 | 210 | wgl
INDUSTRIAL | moe23 | 765740.5661 | 26 | moe
COMMERCIAL | hpk14 | 5487941.7 | 85 | hpk
NCONUML | tt2 | 10017.24 | 3 | tt
INDUSTRIAL | cpk13 | 1507420.269 | 6 | cpk
INDUSTRIAL | lga41 | 52440142.6 | 1 | lga
NCONUML | elm26 | 60173.53 | 25 | elm
FARM | cf1 | 12492.747 | 1 | cf
RESIDENTL | bwr32 | 11435795.4629 | 2903 | bwr
NCONUML | cln23 | 19017.15 | 5 | cln
RESIDENTL | bdl41 | 18711766.0554 | 3582 | bdl
RESIDENTL | tt4 | 9918702.5206 | 2673 | tt
NCONUML | nrn13 | 44749.68 | 14 | nrn
NCONUML | mwl12 | 43601.75 | 11 | mwl
FARM | cln12 | 30466.72 | 1 | cln
INDUSTRIAL | cpk21 | 122110.94 | 5 | cpk
NCONUML | epg11 | 2275 | 2 | epg
FARM | brt22 | 1064314.9433 | 146 | brt
NCONUML | moe21 | 60919.67 | 15 | moe
RESIDENTL | ldl22 | 4948357.507 | 1104 | ldl
INDUSTRIAL | epg22 | 206880.17 | 13 | epg
NCONUML | cln12 | 55224.6632 | 17 | cln
| wo14 | 16653.0726 | 14 | wo
INDUSTRIAL | wo13 | 14774006.15 | 3 | wo
INDUSTRIAL | wgi22 | 729700.7 | 28 | wgi
COMMERCIAL | msd2 | 2629949.014 | 87 | msd
NCONUML | ldl22 | 11421.24 | 5 | ldl
RESIDENTL | wo22 | 17812297.6729 | 4125 | wo
FARM | mwl25 | 2028215.2676 | 224 | mwl
| cln14 | 46492.03 | 68 | cln
INDUSTRIAL | smr14 | 413387.45 | 34 | smr
FARM | rwn33 | 39914.72 | 5 | rwn
NCONUML | tt7 | 28203.83 | 11 | tt
INDUSTRIAL | lga11 | 317451.8284 | 16 | lga
INDUSTRIAL | tt12 | 6074893.6495 | 86 | tt
INDUSTRIAL | rwn32 | 87972.96 | 1 | rwn
RESIDENTL | myt21 | 10899844.0445 | 1487 | myt
RESIDENTL | cyn14 | 9596207.6734 | 2758 | cyn
RESIDENTL | kms11 | 9874885.3712 | 1972 | kms
COMMERCIAL | wo32 | 9961950.2687 | 147 | wo
NCONUML | hpk21 | 96497.83 | 40 | hpk
FARM | mwl13 | 248036.6173 | 7 | mwl
RESIDENTL | smr23 | 3447913.5369 | 523 | smr
INDUSTRIAL | nla32 | 1443086.18 | 25 | nla
| rwt32 | 35174.87 | 36 | rwt
INDUSTRIAL | moe11 | 65970.59 | 6 | moe
INDUSTRIAL | wo33 | 33298223.9508 | 7 | wo
INDUSTRIAL | bra31 | 2919.84 | 1 | bra
RESIDENTL | moe15 | 9740983.6859 | 1552 | moe
RESIDENTL | moe12 | 4538532.291 | 887 | moe
INDUSTRIAL | bdl41 | 1328921.5447 | 34 | bdl
NCONUML | tt6 | 36560.52 | 20 | tt
RESIDENTL | uwy1 | 6496143.3356 | 1032 | uwy
RESIDENTL | wgi32 | 16438958.2366 | 3917 | wgi
COMMERCIAL | rwn31 | 2125446.8547 | 72 | rwn
| ldl13 | 45979.2126 | 34 | ldl
LIGHTING | hpk23 | 2010173.36 | 1 | hpk
RESIDENTL | fgy14 | 9703108.5669 | 2483 | fgy
FARM | rwn24 | 30208.83 | 4 | rwn
COMMERCIAL | wo23 | 11409957.4027 | 304 | wo
| myt12 | 115131.3847 | 34 | myt
| bge13 | 13458.3255 | 19 | bge
| sle32 | 15918.6359 | 20 | sle
FARM | epg11 | 14625.27 | 2 | epg
NCONUML | mwl21 | 34561.25 | 17 | mwl
COMMERCIAL | nrn12 | 21654160.6835 | 271 | nrn
COMMERCIAL | llg13 | 15983000.2277 | 99 | llg
| lga22 | 14116.8478 | 12 | lga
FARM | hpk11 | 14620.89 | 5 | hpk
RESIDENTL | ofr11 | 25072251.243 | 5672 | ofr
FARM | ftr12 | 9732520.1395 | 879 | ftr
RESIDENTL | epg21 | 580054.4394 | 151 | epg
FARM | bge22 | 343097.1961 | 60 | bge
COMMERCIAL | sfs1 | 1879673.1771 | 124 | sfs
| cln24 | 61460.6675 | 37 | cln
NCONUML | smg22 | 48204.28 | 25 | smg
RESIDENTL | phm34 | 11301839.7716 | 2904 | phm
RESIDENTL | phm31 | 2762476.4376 | 550 | phm
NCONUML | smr13 | 69764.68 | 26 | smr
RESIDENTL | wyk12 | 12357178.5976 | 1789 | wyk
INDUSTRIAL | sle13 | 125251.914 | 47 | sle
FARM | phm24 | 689286.43 | 52 | phm
| cre31 | 63798.4484 | 85 | cre
INDUSTRIAL | bge12 | 121322.77 | 7 | bge
FARM | wots12 | 5076.62 | 1 | wots
NCONUML | cf1 | 1922.85 | 2 | cf
RESIDENTL | wo31 | 20016820.444 | 4554 | wo
FARM | smr22 | 1275801.32 | 154 | smr
FARM | lga22 | 1443457.6222 | 105 | lga
COMMERCIAL | mwl22 | 10003347.9587 | 192 | mwl
FARM | bn24 | 2239563.0749 | 370 | bn
NCONUML | wots25 | 45798.68 | 13 | wots
NCONUML | wgi31 | 79233.36 | 21 | wgi
FARM | epg23 | 30049.96 | 2 | epg
NCONUML | klk11 | 24723.1 | 13 | klk
| mwl14 | 3593.32 | 2 | mwl
RESIDENTL | mdg1 | 4384126.608 | 684 | mdg
RESIDENTL | nrn14 | 9562152.1887 | 1877 | nrn
LIGHTING | msd4 | 139319.89 | 1 | msd
LIGHTING | sfs1 | 1558457.9 | 1 | sfs
| klo14 | 120043.1087 | 185 | klo
RESIDENTL | hpk14 | 17025183.7337 | 3944 | hpk
FARM | lga12 | 4046898.7707 | 351 | lga
COMMERCIAL | ldl14 | 12475957.7156 | 266 | ldl
RESIDENTL | bn11 | 14382992.5485 | 2912 | bn
COMMERCIAL | bdl34 | 6213094.4744 | 204 | bdl
FARM | lyd11 | 23799.7 | 3 | lyd
| mwl22 | 10189.434 | 23 | mwl
NCONUML | cf2 | 120.31 | 1 | cf
| epg32 | 18473.04 | 31 | epg
RESIDENTL | bdl34 | 21922135.2151 | 5106 | bdl
COMMERCIAL | rwn26 | 3719056.4225 | 81 | rwn
INDUSTRIAL | mby13 | 219583.33 | 2 | mby
NCONUML | fgy33 | 40029.49 | 14 | fgy
| ftr22 | 13372.1897 | 14 | ftr
NCONUML | mwl13 | 53127.87 | 17 | mwl
INDUSTRIAL | rwt32 | 132361.99 | 4 | rwt
COMMERCIAL | phm23 | 17053480.4 | 2 | phm
COMMERCIAL | bra13 | 19208526.3529 | 181 | bra
FARM | wn1 | 37241.96 | 7 | wn
FARM | bm8b33 | 1540.9 | 2 | bmb
COMMERCIAL | wt10 | 13883699.3972 | 155 | wt
INDUSTRIAL | uwy1 | 90405.23 | 3 | uwy
RESIDENTL | ldl23 | 26005181.5029 | 4084 | ldl
FARM | klo24 | 194259.84 | 22 | klo
| hpk11 | 33718.6052 | 42 | hpk
NCONUML | phm33 | 47915.862 | 19 | phm
FARM | wn6 | 4543418.3442 | 605 | wn
COMMERCIAL | cyn21 | 3633643.5973 | 195 | cyn
INDUSTRIAL | wo22 | 393144.5 | 11 | wo
RESIDENTL | tgn42 | 795534.2193 | 223 | tgn
INDUSTRIAL | mwl23 | 715134.0252 | 54 | mwl
| rwt22 | 26934.55 | 52 | rwt
COMMERCIAL | phm31 | 4117822.4369 | 32 | phm
RESIDENTL | epg22 | 39578.43 | 14 | epg
RESIDENTL | nla32 | 6559402.1513 | 1220 | nla
RESIDENTL | myt22 | 1017937.6841 | 120 | myt
| wgl15 | 30619.4 | 19 | wgl
LIGHTING | mjg11 | 68938.73 | 1 | mjg
COMMERCIAL | phi12 | 2400712.314 | 73 | phi
COMMERCIAL | rwt36 | 2264519.95 | 43 | rwt
INDUSTRIAL | wgi23 | 157973.74 | 15 | wgi
NCONUML | elm24 | 74942.52 | 25 | elm
RESIDENTL | wt10 | 3332972.5881 | 860 | wt
NCONUML | ruba22 | 360.93 | 3 | ruba
FARM | phi11 | 82538.05 | 19 | phi
| bra11 | 11169.2884 | 32 | bra
INDUSTRIAL | moe15 | 1465208.8927 | 46 | moe
| tt5 | 13084.5535 | 33 | tt
LIGHTING | elm34 | 2971413.79 | 6 | elm
FARM | rwt25 | 33966.32 | 4 | rwt
RESIDENTL | moe11 | 9711471.9521 | 1967 | moe
INDUSTRIAL | rwt22 | 12240.297 | 2 | rwt
FARM | tgn23 | 1979366.6929 | 215 | tgn
COMMERCIAL | elm34 | 4840398.0166 | 153 | elm
NCONUML | phi11 | 19831.48 | 5 | phi
NCONUML | bra13 | 31922.03 | 14 | bra
RESIDENTL | mwl11 | 7113484.1589 | 1047 | mwl
| sle14 | 9929.5555 | 28 | sle
COMMERCIAL | cpk11 | 7316179.79 | 51 | cpk
| cyn31 | 5192.9 | 11 | cyn
NCONUML | epg12 | 1563.57 | 9 | epg
| epg11 | 4794.77 | 9 | epg
INDUSTRIAL | bwa23 | 17470876.21 | 8 | bwa
FARM | cln21 | 792.83 | 1 | cln
COMMERCIAL | wn3 | 8489705.5245 | 275 | wn
COMMERCIAL | bwn12 | 29123057.9665 | 274 | bwn
NCONUML | bra23 | 28962.5293 | 21 | bra
| bge12 | 5967.8256 | 14 | bge
INDUSTRIAL | tgn12 | 464065.58 | 15 | tgn
LIGHTING | fgy31 | 1047083.29 | 1 | fgy
NCONUML | moe25 | 63582.44 | 18 | moe
NCONUML | fgy21 | 30728.13 | 12 | fgy
INDUSTRIAL | lyd11 | 151654.68 | 9 | lyd
FARM | bwn13 | 5960.02 | 1 | bwn
RESIDENTL | lga11 | 6965787.8425 | 1044 | lga
NCONUML | bwr22 | 31744.79 | 14 | bwr
COMMERCIAL | llg12 | 3977405.3306 | 115 | llg
COMMERCIAL | mfa21 | 3716072.0048 | 197 | mfa
INDUSTRIAL | phm32 | 1008.48 | 1 | phm
COMMERCIAL | nrn13 | 3605622.38 | 41 | nrn
FARM | cyn22 | 1131.4275 | 1 | cyn
INDUSTRIAL | ftr23 | 1828762.8842 | 76 | ftr
INDUSTRIAL | mfa31 | 463955.39 | 14 | mfa
INDUSTRIAL | bge11 | 395339.98 | 10 | bge
RESIDENTL | wo13 | 2691801.805 | 586 | wo
RESIDENTL | llg11 | 4969161.4408 | 709 | llg
| cpk21 | 8908.612 | 12 | cpk
INDUSTRIAL | cre23 | 238715.04 | 8 | cre
COMMERCIAL | epg33 | 43303826.6612 | 357 | epg
FARM | ofr21 | 60907.55 | 6 | ofr
COMMERCIAL | cpk22 | 8802072.7366 | 32 | cpk
NCONUML | bra24 | 34184.91 | 27 | bra
NCONUML | wn6 | 84222.69 | 35 | wn
FARM | mfa22 | 15017348.1505 | 702 | mfa
FARM | lga24 | 2675198.7919 | 323 | lga
COMMERCIAL | phi13 | 13565764.588 | 480 | phi
FARM | lga13 | 6142984.8245 | 572 | lga
NCONUML | wn2 | 74469.51 | 25 | wn
COMMERCIAL | wyk23 | 9043742.9219 | 306 | wyk
INDUSTRIAL | cyn31 | 110897.03 | 2 | cyn
RESIDENTL | wt7 | 9398293.9689 | 2293 | wt
COMMERCIAL | rwt15 | 2407529.701 | 118 | rwt
| wots11 | 29868.01 | 43 | wots
COMMERCIAL | wt12 | 9788397.4198 | 246 | wt
FARM | wots24 | 5049980.8194 | 706 | wots
COMMERCIAL | ftr22 | 3919173.7529 | 139 | ftr
INDUSTRIAL | ruba12 | 859698.6565 | 35 | ruba
| wots25 | 37134.4365 | 43 | wots
RESIDENTL | ofr24 | 14317680.0438 | 3420 | ofr
COMMERCIAL | bdl32 | 9327480.3168 | 349 | bdl
NCONUML | trc01 | 2600.11 | 1 | trc
RESIDENTL | wgi33 | 15074294.4922 | 2906 | wgi
RESIDENTL | wyk24 | 16651462.561 | 3130 | wyk
NCONUML | wn1 | 109135.95 | 32 | wn
NCONUML | fgy34 | 69468.4 | 26 | fgy
| tgn43 | 23585.3 | 37 | tgn
| bwn11 | 22540.96 | 33 | bwn
COMMERCIAL | bn11 | 11469939.8143 | 448 | bn
RESIDENTL | wn7 | 334597.06 | 81 | wn
FARM | lga23 | 6580772.0568 | 604 | lga
RESIDENTL | mby13 | 1114988.13 | 129 | mby
INDUSTRIAL | moe12 | 309363.05 | 10 | moe
NCONUML | wgl21 | 72341.71 | 26 | wgl
| rwn22 | 13422.17 | 20 | rwn
FARM | ofr13 | 1726.88 | 2 | ofr
INDUSTRIAL | smg33 | 3791.86 | 1 | smg
COMMERCIAL | cnr2 | 2241662.7301 | 123 | cnr
NCONUML | bwn13 | 114734.08 | 27 | bwn
INDUSTRIAL | tgn43 | 8336.37 | 2 | tgn
NCONUML | bra33 | 54640.5039 | 38 | bra
LIGHTING | drn23 | 137376.82 | 1 | drn
COMMERCIAL | wt11 | 6045415.4763 | 137 | wt
| wo23 | 3425.76 | 13 | wo
RESIDENTL | drn11 | 23689909.4015 | 5897 | drn
RESIDENTL | bra33 | 17227071.6094 | 3920 | bra
FARM | cre21 | 1165190.53 | 9 | cre
| wo32 | 20472.5797 | 26 | wo
NCONUML | mfa22 | 12133.93 | 8 | mfa
COMMERCIAL | fgy32 | 10874129.2215 | 316 | fgy
INDUSTRIAL | bdl33 | 6444229.03 | 34 | bdl
NCONUML | cnr3 | 880.96 | 3 | cnr
COMMERCIAL | bwr14 | 64319.73 | 1 | bwr
NCONUML | ldl11 | 15379.88 | 9 | ldl
FARM | bdl33 | 333127.23 | 48 | bdl
INDUSTRIAL | elm23 | 351538.3612 | 12 | elm
NCONUML | lga14 | 16509.29 | 6 | lga
NCONUML | rwt21 | 45520.76 | 13 | rwt
INDUSTRIAL | mwl24 | 3823292.43 | 15 | mwl
RESIDENTL | epg14 | 8906284.5994 | 2218 | epg
NCONUML | drn21 | 11559.57 | 6 | drn
FARM | ldl21 | 4274.77 | 1 | ldl
| lga14 | 13272.15 | 11 | lga
LIGHTING | wo22 | 1145144.2306 | 3 | wo
LIGHTING | bdl33 | 755365.47 | 1 | bdl
INDUSTRIAL | lga12 | 340570.559 | 7 | lga
RESIDENTL | ofr23 | 20573594.8025 | 3065 | ofr
LIGHTING | tgn12 | 393.8997 | 1 | tgn
RESIDENTL | fgy32 | 4718000.0914 | 1180 | fgy
COMMERCIAL | moe11 | 6876107.6583 | 169 | moe
COMMERCIAL | wgl13 | 16726185.3211 | 289 | wgl
COMMERCIAL | cre22 | 19152716.1468 | 212 | cre
RESIDENTL | drn12 | 16081122.8597 | 3986 | drn
COMMERCIAL | mfa23 | 8005013.26 | 78 | mfa
| cln13 | 39224.5517 | 61 | cln
INDUSTRIAL | mfa22 | 1793714.26 | 36 | mfa
LIGHTING | smr23 | 37560.88 | 1 | smr
RESIDENTL | rwn32 | 6727398.7344 | 1603 | rwn
FARM | lga14 | 4550189.1065 | 436 | lga
| cln12 | 24735.6225 | 51 | cln
COMMERCIAL | kms11 | 4936701.5866 | 120 | kms
RESIDENTL | smr14 | 10997106.9114 | 1697 | smr
| epg13 | 194183.3358 | 102 | epg
| brt21 | 9723.1397 | 7 | brt
INDUSTRIAL | drn12 | 10032.09 | 2 | drn
| tt7 | 34871.95 | 3 | tt
INDUSTRIAL | wots25 | 7153785.931 | 7 | wots
FARM | tgn43 | 14451.81 | 2 | tgn
NCONUML | ldl14 | 38917.21 | 26 | ldl
INDUSTRIAL | brt21 | 238786.6 | 10 | brt
| llg11 | 8477.8 | 10 | llg
RESIDENTL | wgi24 | 12721878.952 | 3596 | wgi
RESIDENTL | cyn21 | 10508542.767 | 2257 | cyn
INDUSTRIAL | bra11 | 3982632.29 | 3 | bra
INDUSTRIAL | phi11 | 184139.3994 | 13 | phi
| hpk24 | 8609.4373 | 14 | hpk
NCONUML | ldl13 | 24965.12 | 22 | ldl
RESIDENTL | hpk21 | 20637351.8958 | 5254 | hpk
RESIDENTL | wgl13 | 19626090.0794 | 4751 | wgl
COMMERCIAL | elm21 | 12124007.57 | 258 | elm
COMMERCIAL | wt13 | 23168272.4303 | 498 | wt
| hpk23 | 55023.71 | 41 | hpk
COMMERCIAL | mdg1 | 1157212.0402 | 52 | mdg
NCONUML | wt11 | 64055.27 | 25 | wt
NCONUML | phm31 | 9383.328 | 4 | phm
COMMERCIAL | bge23 | 4904566.2339 | 176 | bge
NCONUML | smg23 | 17942.69 | 11 | smg
| mwl16 | 4764.4783 | 12 | mwl
COMMERCIAL | hpk12 | 20352329.5415 | 361 | hpk
RESIDENTL | ruba24 | 4395729.6843 | 894 | ruba
COMMERCIAL | nla32 | 3390681.6399 | 175 | nla
NCONUML | lyd12 | 44439.84 | 9 | lyd
| cln22 | 289385.5413 | 85 | cln
NCONUML | cpk21 | 53769.1 | 26 | cpk
| ruba22 | 8482.6526 | 15 | ruba
COMMERCIAL | myt22 | 191990.12 | 18 | myt
RESIDENTL | mby11 | 5261006.6685 | 922 | mby
RESIDENTL | rwn26 | 21195116.3973 | 2454 | rwn
| rwt31 | 14608.62 | 19 | rwt
INDUSTRIAL | epg35 | 1615230.05 | 4 | epg
| bge23 | 30837.693 | 28 | bge
NCONUML | bdl34 | 70291.97 | 25 | bdl
NCONUML | ofr13 | 30258.73 | 11 | ofr
| klk11 | 25230.2094 | 21 | klk
NCONUML | bn12 | 1241.66 | 2 | bn
COMMERCIAL | wgi32 | 5461052.6827 | 195 | wgi
NCONUML | ldl12 | 45990.38 | 14 | ldl
INDUSTRIAL | bra23 | 3394433.4433 | 42 | bra
| wo33 | 4138.8 | 1 | wo
NCONUML | myt12 | 33269.22 | 16 | myt
INDUSTRIAL | ldl11 | 1468879.69 | 10 | ldl
RESIDENTL | msd1 | 8481569.4252 | 1750 | msd
NCONUML | bn11 | 57126.91 | 28 | bn
INDUSTRIAL | ftr12 | 2824402.5 | 31 | ftr
INDUSTRIAL | hpk11 | 29483.41 | 8 | hpk
NCONUML | epg33 | 5589.26 | 2 | epg
COMMERCIAL | wo31 | 10532525.1457 | 139 | wo
| wgl21 | 38182.04 | 53 | wgl
| bge22 | 25062.3495 | 31 | bge
RESIDENTL | tt1 | 171030.69 | 8 | tt
INDUSTRIAL | bwr34 | 134229.36 | 26 | bwr
COMMERCIAL | bra33 | 14409139.6368 | 303 | bra
COMMERCIAL | bdl44 | 4495186.894 | 197 | bdl
| bwn13 | 12482.8878 | 14 | bwn
NCONUML | wn3 | 40552.61 | 16 | wn
NCONUML | smr24 | 41055.27 | 16 | smr
INDUSTRIAL | mwl14 | 4499194.0326 | 50 | mwl
| wots24 | 36833.8626 | 36 | wots
NCONUML | wt12 | 74491.29 | 36 | wt
COMMERCIAL | smg31 | 17181337.4 | 81 | smg
FARM | lyd13 | 146611.14 | 18 | lyd
NCONUML | wots12 | 53576.05 | 15 | wots
INDUSTRIAL | fgy12 | 30820.7097 | 2 | fgy
FARM | myt12 | 4025860.4278 | 600 | myt
INDUSTRIAL | cyn22 | 204983.76 | 12 | cyn
COMMERCIAL | cyn33 | 3196035.4476 | 122 | cyn
COMMERCIAL | mby12 | 1853426.4391 | 89 | mby
NCONUML | tgn43 | 111938.06 | 34 | tgn
NCONUML | wo11 | 17571.55 | 5 | wo
INDUSTRIAL | epg12 | 1405424.52 | 3 | epg
| cf2 | 30699.57 | 2 | cf
COMMERCIAL | llg11 | 3213282.749 | 85 | llg
LIGHTING | rwn24 | 1936572.72 | 3 | rwn
INDUSTRIAL | cln24 | 15633.29 | 3 | cln
FARM | sle31 | 4999785.6618 | 315 | sle
INDUSTRIAL | cf1 | 129164.746 | 4 | cf
| ruba12 | 126134.0367 | 24 | ruba
| bwr12 | 18318.3952 | 15 | bwr
FARM | elm32 | 382389.8968 | 32 | elm
| ofr21 | 113717.1 | 52 | ofr
INDUSTRIAL | wn2 | 282430.54 | 13 | wn
NCONUML | bge22 | 82280.88 | 49 | bge
NCONUML | cnr2 | 33661.17 | 17 | cnr
NCONUML | wots13 | 10386.18 | 6 | wots
FARM | elm24 | 39172.3194 | 4 | elm
COMMERCIAL | nrn14 | 6896476.1265 | 116 | nrn
NCONUML | ruba12 | 27603.68 | 16 | ruba
NCONUML | hpk13 | 50290.3 | 16 | hpk
NCONUML | bra11 | 44798.92 | 35 | bra
| rwt21 | 23376.2409 | 6 | rwt
RESIDENTL | drn23 | 20613814.4846 | 2434 | drn
RESIDENTL | rwt36 | 2676215.9999 | 821 | rwt
RESIDENTL | llg13 | 6857833.0372 | 1230 | llg
COMMERCIAL | wyk12 | 4295149.2844 | 131 | wyk
INDUSTRIAL | ofr13 | 1622296.11 | 21 | ofr
| bra14 | 30334.7783 | 42 | bra
INDUSTRIAL | tgn11 | 3321263.75 | 18 | tgn
LIGHTING | mby13 | 9944.78 | 1 | mby
RESIDENTL | cln11 | 39284605.9906 | 12154 | cln
COMMERCIAL | drn22 | 10741065.2473 | 246 | drn
RESIDENTL | wo32 | 11244170.0715 | 2343 | wo
| bra33 | 27895.4569 | 47 | bra
COMMERCIAL | epg21 | 21867278.1603 | 75 | epg
INDUSTRIAL | cre21 | 293542.6 | 2 | cre
RESIDENTL | bwr24 | 1834966.95 | 415 | bwr
RESIDENTL | hpk13 | 8888406.848 | 2283 | hpk
NCONUML | moe13 | 240.62 | 2 | moe
RESIDENTL | mwl12 | 3605926.3697 | 887 | mwl
| elm24 | 29520.3106 | 27 | elm
COMMERCIAL | tgn31 | 5251765.7474 | 163 | tgn
| rwt25 | 17882.0217 | 23 | rwt
RESIDENTL | moe21 | 9438147.1697 | 1978 | moe
COMMERCIAL | mjg11 | 16973320.0649 | 258 | mjg
COMMERCIAL | moe22 | 1619971.835 | 34 | moe
NCONUML | cpk13 | 44472.2623 | 32 | cpk
| phi11 | 13149.9006 | 9 | phi
FARM | cyn11 | 2814.65 | 1 | cyn
FARM | cyn24 | 25049.8 | 2 | cyn
FARM | drn13 | 379220.8035 | 25 | drn
COMMERCIAL | mwe236 | 663523.2 | 21 | mwe
INDUSTRIAL | phm24 | 35612.08 | 4 | phm
INDUSTRIAL | bge22 | 36211.2493 | 9 | bge
RESIDENTL | cnr1 | 478523.9112 | 104 | cnr
| lga24 | 10918.35 | 11 | lga
NCONUML | sle14 | 98131.7526 | 34 | sle
NCONUML | tt5 | 14462.54 | 12 | tt
| epg12 | 53720.6497 | 70 | epg
NCONUML | kms11 | 42647.24 | 13 | kms
FARM | elm23 | 38507.8 | 8 | elm
COMMERCIAL | cyn12 | 12045879.7132 | 241 | cyn
INDUSTRIAL | fgy23 | 1420677.79 | 11 | fgy
COMMERCIAL | mfa14 | 259168.13 | 17 | mfa
| bra31 | 49797.7422 | 13 | bra
COMMERCIAL | mwl12 | 1780079.4127 | 78 | mwl
| bwr22 | 2405.71 | 25 | bwr
INDUSTRIAL | fgy24 | 415478.9 | 15 | fgy
COMMERCIAL | hpk13 | 9763023.5697 | 134 | hpk
| cyn22 | 22272.33 | 22 | cyn
| ldl21 | 13369.5383 | 42 | ldl
| wt6 | 17591.4373 | 23 | wt
RESIDENTL | wn4 | 11276854.4814 | 2349 | wn
FARM | mwl14 | 451834.7532 | 54 | mwl
RESIDENTL | bm8b31 | 357131.6719 | 111 | bmb
NCONUML | cyn14 | 48577.9677 | 22 | cyn
FARM | cre32 | 5136.47 | 1 | cre
FARM | bwr34 | 4550.33 | 1 | bwr
RESIDENTL | llg14 | 14855712.1657 | 2170 | llg
FARM | smg33 | 29400.19 | 7 | smg
RESIDENTL | drn22 | 21996972.8148 | 3999 | drn
NCONUML | elm32 | 42948.38 | 25 | elm
INDUSTRIAL | klo14 | 587332.99 | 17 | klo
| tgn11 | 22256.53 | 32 | tgn
INDUSTRIAL | tgn44 | 4536032.57 | 9 | tgn
COMMERCIAL | ldl23 | 15994398.5627 | 272 | ldl
| wn6 | 146062.0009 | 59 | wn
COMMERCIAL | tt2 | 18806104.6367 | 399 | tt
COMMERCIAL | brt11 | 4047117.81 | 129 | brt
NCONUML | llg14 | 65195.01 | 40 | llg
FARM | fgy24 | 95940.3 | 9 | fgy
NCONUML | fgy14 | 61562.37 | 33 | fgy
COMMERCIAL | rve12 | 3272242.91 | 54 | rve
INDUSTRIAL | cpk23 | 208291.634 | 5 | cpk
| lga23 | 41697.3391 | 21 | lga
INDUSTRIAL | yn38 | 642769.3081 | 6 | yn
COMMERCIAL | bwa21 | 7920817.52 | 6 | bwa
INDUSTRIAL | elm25 | 2097.04 | 1 | elm
COMMERCIAL | wots13 | 3416108.1488 | 213 | wots
FARM | wgi22 | 191494.2501 | 24 | wgi
NCONUML | fgy13 | 27847.71 | 7 | fgy
| bra24 | 9840.15 | 27 | bra
FARM | ofr14 | 100163.6258 | 21 | ofr
NCONUML | nrn11 | 16820.36 | 5 | nrn
RESIDENTL | smg31 | 12434679.8443 | 2879 | smg
COMMERCIAL | smr24 | 15083854.4686 | 348 | smr
| lyd11 | 12152.66 | 25 | lyd
INDUSTRIAL | bra12 | 1282907.1727 | 55 | bra
FARM | wgl15 | 3297105.6723 | 233 | wgl
INDUSTRIAL | msd1 | 544058.7154 | 15 | msd
| epg31 | 13971.3347 | 31 | epg
INDUSTRIAL | wgl23 | 572354.5027 | 44 | wgl
INDUSTRIAL | cpk12 | 343353.79 | 14 | cpk
INDUSTRIAL | mfa34 | 4790944.63 | 37 | mfa
| wn2 | 65478.1843 | 60 | wn
INDUSTRIAL | drn23 | 222019.33 | 21 | drn
| klo11 | 24997.4 | 1 | klo
COMMERCIAL | cyn13 | 11562540.4133 | 213 | cyn
| tgn44 | 15598.29 | 27 | tgn
| wn1 | 5093 | 9 | wn
NCONUML | wots24 | 22958.48 | 11 | wots
RESIDENTL | ftr21 | 5974099.1685 | 1654 | ftr
NCONUML | wgl11 | 116770.29 | 32 | wgl
FARM | phm22 | 2513172.8482 | 159 | phm
| mfa22 | 25912.0235 | 15 | mfa
| tt2 | 5693.01 | 1 | tt
RESIDENTL | cyn12 | 11384819.6049 | 2642 | cyn
COMMERCIAL | mby11 | 1920906.95 | 83 | mby
RESIDENTL | bdl42 | 7579399.6648 | 1528 | bdl
COMMERCIAL | sle11 | 16789466.3124 | 430 | sle
COMMERCIAL | bdl42 | 3935066.2305 | 228 | bdl
NCONUML | rwn22 | 25304.89 | 19 | rwn
INDUSTRIAL | cre32 | 1414910.91 | 33 | cre
INDUSTRIAL | bwn11 | 121807.37 | 8 | bwn
NCONUML | smr22 | 29006.3 | 13 | smr
RESIDENTL | phm24 | 12991887.5254 | 2975 | phm
RESIDENTL | phm21 | 5600884.0097 | 1319 | phm
NCONUML | ldl23 | 93357.12 | 44 | ldl
RESIDENTL | ldl24 | 19255310.9766 | 3964 | ldl
INDUSTRIAL | bra21 | 9682528.358 | 10 | bra
| sle31 | 21276.5675 | 34 | sle
| myt11 | 11671.01 | 10 | myt
RESIDENTL | elm21 | 10927220.6891 | 2208 | elm
COMMERCIAL | epg13 | 13081700.0195 | 121 | epg
COMMERCIAL | hpk21 | 6771211.022 | 80 | hpk
NCONUML | bwr12 | 55323.1848 | 22 | bwr
| trc01 | 7370.1419 | 1 | trc
| epg35 | 12733.43 | 3 | epg
INDUSTRIAL | bge21 | 30163.23 | 3 | bge
RESIDENTL | tgn31 | 10330935.5842 | 1504 | tgn
COMMERCIAL | moe23 | 8180066.6029 | 204 | moe
FARM | bra21 | 5211.11 | 2 | bra
LIGHTING | llg12 | 9573.66 | 1 | llg
RESIDENTL | bdl31 | 18828777.9984 | 3534 | bdl
COMMERCIAL | nla31 | 1365542.8767 | 73 | nla
INDUSTRIAL | klo24 | 421040.3606 | 14 | klo
FARM | bdl43 | 35833.9 | 4 | bdl
FARM | cyn31 | 3324.08 | 1 | cyn
FARM | sle14 | 508528.62 | 59 | sle
FARM | fgy34 | 3609.3 | 1 | fgy
RESIDENTL | elm26 | 19204314.084 | 3128 | elm
COMMERCIAL | ldl13 | 4974121.0157 | 271 | ldl
NCONUML | tgn42 | 32526.3 | 9 | tgn
RESIDENTL | nrn13 | 11128338.9236 | 2708 | nrn
| drn13 | 33230.29 | 35 | drn
RESIDENTL | mfa14 | 15628.16 | 8 | mfa
RESIDENTL | rwt14 | 5266292.5405 | 1232 | rwt
FARM | ftr23 | 7584335.745 | 587 | ftr
FARM | moe12 | 2890738.1544 | 266 | moe
RESIDENTL | klk21 | 6022162.144 | 692 | klk
COMMERCIAL | bn22 | 11917129.8815 | 407 | bn
COMMERCIAL | cln13 | 10498926.3291 | 102 | cln
INDUSTRIAL | cln11 | 955300.36 | 11 | cln
FARM | bge11 | 1450445.3683 | 132 | bge
| mwl25 | 368.2898 | 2 | mwl
| rwn33 | 13688.96 | 19 | rwn
| bdl43 | 33766.9817 | 15 | bdl
NCONUML | cln14 | 95979.5703 | 31 | cln
NCONUML | lga24 | 7306.35 | 4 | lga
| bn23 | 36133.4118 | 23 | bn
| ofr14 | 18460.3638 | 32 | ofr
FARM | wo14 | 29381.84 | 3 | wo
FARM | cln24 | 15169.45 | 1 | cln
FARM | smg21 | 2813.13 | 1 | smg
FARM | uwy1 | 50419.26 | 6 | uwy
RESIDENTL | cpk11 | 18255270.9798 | 3705 | cpk
INDUSTRIAL | rwn34 | 151721.8975 | 12 | rwn
FARM | mfa34 | 8352796.4311 | 398 | mfa
INDUSTRIAL | cyn23 | 283668.3977 | 39 | cyn
COMMERCIAL | cln23 | 7919442.4187 | 94 | cln
| rwn24 | 145239.1574 | 36 | rwn
INDUSTRIAL | cln21 | 91173.7471 | 8 | cln
INDUSTRIAL | wots23 | 9771996.01 | 2 | wots
COMMERCIAL | ofr23 | 7962081.4442 | 137 | ofr
FARM | cln11 | 5358747.3528 | 175 | cln
INDUSTRIAL | epg23 | 1603069.098 | 49 | epg
NCONUML | elm33 | 106570.09 | 33 | elm
| tt6 | 16214.4725 | 50 | tt
NCONUML | lga12 | 120.31 | 1 | lga
RESIDENTL | moe25 | 15202048.016 | 3044 | moe
RESIDENTL | moe22 | 6183768.6959 | 1343 | moe
RESIDENTL | mfa23 | 1535883.9368 | 206 | mfa
FARM | rwn22 | 76017.25 | 13 | rwn
COMMERCIAL | fgy31 | 26687.08 | 5 | fgy
RESIDENTL | elm33 | 17751529.9107 | 3238 | elm
COMMERCIAL | ldl22 | 7642772.3181 | 272 | ldl
NCONUML | llg11 | 13058.17 | 7 | llg
| ruba24 | 72607.09 | 10 | ruba
FARM | rwt32 | 21924.18 | 3 | rwt
FARM | ruba12 | 5735958.293 | 534 | ruba
FARM | brt21 | 526055.8565 | 65 | brt
| rwt15 | 24735.76 | 50 | rwt
NCONUML | bge13 | 40077 | 45 | bge
COMMERCIAL | klk21 | 1344972.0506 | 75 | klk
INDUSTRIAL | msd4 | 532825.24 | 27 | msd
| mwl21 | 2371.576 | 7 | mwl
RESIDENTL | wt9 | 13126762.7947 | 2901 | wt
FARM | wgi23 | 957555.9102 | 143 | wgi
| wgl24 | 12928.4076 | 27 | wgl
NCONUML | tgn11 | 50804.93 | 14 | tgn
LIGHTING | hpk22 | 402155.12 | 2 | hpk
INDUSTRIAL | wt13 | 198794.34 | 24 | wt
LIGHTING | wots24 | 69082.45 | 1 | wots
| ofr13 | 25120.5182 | 29 | ofr
| cre21 | 98632.2224 | 69 | cre
| smg22 | 13378.71 | 23 | smg
COMMERCIAL | tt4 | 4770691.1401 | 169 | tt
COMMERCIAL | elm26 | 2765254.86 | 47 | elm
NCONUML | bwa22 | 120.31 | 1 | bwa
| cyn23 | 386495.78 | 52 | cyn
INDUSTRIAL | nla34 | 227255.6563 | 13 | nla
FARM | mwl22 | 63.01 | 1 | mwl
| cf1 | 5771.13 | 3 | cf
NCONUML | cpk22 | 15413.02 | 10 | cpk
NCONUML | lyd13 | 28195.47 | 10 | lyd
NCONUML | cre31 | 35482.06 | 18 | cre
COMMERCIAL | wo11 | 6006584.4175 | 54 | wo
INDUSTRIAL | wt7 | 2382042.5333 | 25 | wt
| bwr34 | 19530.96 | 64 | bwr
NCONUML | bge23 | 57838.96 | 34 | bge
INDUSTRIAL | tgn23 | 187420.5 | 24 | tgn
RESIDENTL | cyn33 | 17836008.3498 | 3662 | cyn
RESIDENTL | nla34 | 7124747.0562 | 1408 | nla
| wgl11 | 21820.8596 | 38 | wgl
COMMERCIAL | bn12 | 3658135.6563 | 31 | bn
| mwl13 | 7054.2121 | 17 | mwl
COMMERCIAL | rwt26 | 65754589.65 | 1 | rwt
FARM | wt9 | 2789.4 | 1 | wt
RESIDENTL | bdl44 | 10906570.4152 | 1766 | bdl
FARM | cre33 | 2156267.3416 | 81 | cre
COMMERCIAL | wgl21 | 7364849.9167 | 150 | wgl
COMMERCIAL | wn5 | 3727109.367 | 208 | wn
NCONUML | mwl22 | 81020 | 27 | mwl
NCONUML | bn24 | 14677.57 | 9 | bn
| smr22 | 9887.67 | 15 | smr
|  | 8782.36 | 2 | #REF!
RESIDENTL | sle11 | 5311421.2716 | 1344 | sle
RESIDENTL | nw13 | 126364.0108 | 18 | nw
RESIDENTL | ftr23 | 12909653.9148 | 2620 | ftr
COMMERCIAL | mwl11 | 1278518.3133 | 72 | mwl
LIGHTING | llg13 | 66328.6913 | 1 | llg
NCONUML | klk22 | 2600.11 | 1 | klk
RESIDENTL | wyk23 | 22445865.182 | 3391 | wyk
COMMERCIAL | wt6 | 6354339.6482 | 191 | wt
RESIDENTL | brt11 | 6592458.6386 | 1001 | brt
NCONUML | tt9 | 66916.75 | 41 | tt
FARM | smr14 | 4406259.38 | 487 | smr
NCONUML | epg32 | 55568.91 | 13 | epg
RESIDENTL | rwn31 | 17135173.2235 | 2210 | rwn
| phm33 | 20993.1171 | 27 | phm
NCONUML | myt11 | 6079.5 | 6 | myt
RESIDENTL | nrn12 | 2807836.1314 | 591 | nrn
COMMERCIAL | mwl16 | 411566.3345 | 42 | mwl
INDUSTRIAL | lga23 | 1068068.6578 | 23 | lga
COMMERCIAL | ldl12 | 15390056.6509 | 380 | ldl
FARM | nla34 | 624678.3932 | 78 | nla
COMMERCIAL | rve13 | 1685040.429 | 44 | rve
NCONUML | drn24 | 11009.3526 | 4 | drn
COMMERCIAL | myt21 | 6919383.7104 | 251 | myt
FARM | moe13 | 3478506.4958 | 306 | moe
COMMERCIAL | mwl21 | 9182796.6603 | 240 | mwl
NCONUML | wgl15 | 97647.0301 | 36 | wgl
| bwn14 | 31300.22 | 31 | bwn
RESIDENTL | cpk22 | 8203984.593 | 1482 | cpk
RESIDENTL | rve12 | 17634581.2748 | 3656 | rve
RESIDENTL | phi13 | 17016004.0328 | 4317 | phi
RESIDENTL | hpk12 | 5058413.1519 | 1238 | hpk
COMMERCIAL | ruba24 | 4555190.3466 | 105 | ruba
FARM | cln14 | 51639.06 | 13 | cln
INDUSTRIAL | wt9 | 148098.11 | 5 | wt
| smg21 | 44014.37 | 27 | smg
INDUSTRIAL | smr23 | 883845.12 | 6 | smr

## Forecast - Summer
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Summer | 50 | 38619 | 72.2578 | 77.9086 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Summer | 10 | 38619 | 72.2578 | 91.3183 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 10 | 41429 | 81.3604 | 97.5884 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Summer | 50 | 41429 | 81.3604 | 83.3369 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 10 | 44846 | 94.6588 | 104.9463 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Summer | 50 | 44846 | 94.6588 | 89.7351 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 119.6766 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 104.3341 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 124.2514 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 108.3435 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 128.0364 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 111.4611 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 131.3686 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 115.2173 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 136.7682 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 119.0984 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 141.634 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 123.2461 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.4809 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 128.0275 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 155.6302 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 133.6994 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 161.4365 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 139.0092 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 166.8996 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 144.6013 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 175.1342 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 154.2938 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 181.0486 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 157.43 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 187.0195 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 163.5566 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 193.3671 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 168.1999 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 192.0421 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 167.0472 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 10 | 24937 | 39.5122 | 71.3044 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Summer | 50 | 24937 | 39.5122 | 64.1683 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 10 | 25835 | 43.8704 | 73.6781 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Summer | 50 | 25835 | 43.8704 | 65.8328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 10 | 26314 | 48.9572 | 74.7994 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Summer | 50 | 26314 | 48.9572 | 66.0879 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 89.8342 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 80.6612 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 90.653 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 81.4056 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 89.7773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 80.6131 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 94.9573 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 85.9509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 94.8385 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 85.6114 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 96.1186 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 85.7941 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 97.2062 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 86.4866 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 98.0786 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 87.2925 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 98.8781 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 88.2343 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 99.6475 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 88.9575 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 99.2707 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 89.8044 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 99.9981 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 89.5675 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 101.1509 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.5821 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 101.3208 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 90.3196 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 99.6095 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.5146 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 10 | 29371 | 40.0067 | 87.2498 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Summer | 50 | 29371 | 40.0067 | 72.9666 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 10 | 30422 | 45.1511 | 90.3071 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Summer | 50 | 30422 | 45.1511 | 75.7012 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 10 | 32118 | 51.557 | 95.8895 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Summer | 50 | 32118 | 51.557 | 79.9844 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 109.0669 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 92.5622 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 118.5447 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 101.6723 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 121.4869 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 104.4042 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 119.8786 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 102.6031 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 121.9204 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 105.5757 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 124.6444 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 106.371 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 127.5507 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 110.1341 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 131.8742 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 112.2581 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 136.3355 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 113.9316 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 140.9437 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 117.5793 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 144.5914 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 120.4726 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 128.0797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 149.6115 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 152.9797 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 129.922 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 155.1715 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 132.5568 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 152.1644 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 125.7761 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 10 | 14879 | 23.0226 | 53.5677 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Summer | 50 | 14879 | 23.0226 | 41.9423 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 10 | 17175 | 27.7177 | 61.121 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Summer | 50 | 17175 | 27.7177 | 48.3019 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 10 | 19951 | 34.2052 | 70.1897 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Summer | 50 | 19951 | 34.2052 | 55.7613 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 83.6879 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 68.2523 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 94.1984 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 77.9353 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 102.4436 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 84.7194 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 118.3247 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 99.6669 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 126.3487 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 106.8624 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 135.5692 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 115.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 148.561 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 127.0156 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 164.8827 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 137.8179 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 180.5841 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 151.2391 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 196.9964 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 164.8814 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 212.9758 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 181.5355 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 230.0573 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 195.8954 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 248.4456 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 212.2991 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 266.5409 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 225.6959 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 272.6357 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 228.9049 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 10 | 23246 | 35.5119 | 59.9776 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Summer | 50 | 23246 | 35.5119 | 53.856 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 10 | 24109 | 39.5748 | 62.0639 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Summer | 50 | 24109 | 39.5748 | 55.451 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 10 | 24997 | 44.4669 | 64.073 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Summer | 50 | 24997 | 44.4669 | 56.9594 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 69.589 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 61.9907 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 76.597 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 68.9791 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 81.5678 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 74.0072 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 84.5283 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 76.6284 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 86.8984 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 78.9811 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 88.8048 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 80.4506 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 90.6365 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 82.1352 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 92.2256 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 83.4813 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 92.9929 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 84.3346 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 94.1573 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 86.446 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 95.4952 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 87.894 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 96.8516 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 88.627 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 98.5806 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 90.0391 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 98.8168 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 89.5765 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 97.8239 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 88.3981 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 50 | 16270 | 23.521 | 51.4174 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Summer | 10 | 16270 | 23.521 | 56.9097 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 10 | 16562 | 25.5412 | 57.758 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Summer | 50 | 16562 | 25.5412 | 52.1386 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 10 | 16854 | 27.7496 | 58.7282 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Summer | 50 | 16854 | 27.7496 | 52.8621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 75.5207 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 69.621 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 79.8845 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 74.1527 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 79.6008 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 73.9998 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 79.5894 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 73.965 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 80.0199 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 74.4648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 81.1895 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 75.0153 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 81.9552 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 76.1566 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 82.7146 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 76.9783 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 83.6062 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 77.4148 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 84.4206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 77.8841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 85.2206 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 78.3211 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 85.2937 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 79.127 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 86.2309 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 80.1321 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 85.4841 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 80.0404 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 79.3417 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 73.3195 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 10 | 7174 | 11.5134 | 25.3928 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Summer | 50 | 7174 | 11.5134 | 23.4346 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 10 | 7235 | 12.7349 | 25.4543 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Summer | 50 | 7235 | 12.7349 | 23.4406 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 10 | 7295 | 13.7538 | 25.544 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Summer | 50 | 7295 | 13.7538 | 23.5081 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 28.7312 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 26.0976 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 33.0834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 30.4575 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 33.0249 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 30.4247 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 33.0633 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 30.3952 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 33.1822 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 30.8677 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 33.5865 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 31.5616 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 33.8573 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 32.037 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 34.0794 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 31.4591 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 34.1121 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 31.5166 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 34.3124 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 31.792 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 34.3834 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 32.8827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 34.3832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 31.8492 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 34.3374 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 31.7885 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 34.3276 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 31.7234 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 32.6827 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 30.3101 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Summer | 10 | 21696 | 27.3902 | 50.299 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Summer | 50 | 21696 | 27.3902 | 41.2414 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 10 | 22045 | 30.4273 | 50.6919 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Summer | 50 | 22045 | 30.4273 | 41.4384 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 10 | 22388 | 33.5461 | 51.0465 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Summer | 50 | 22388 | 33.5461 | 41.5121 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 10 |  |  | 54.5057 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Summer | 50 |  |  | 44.6075 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 10 |  |  | 54.6012 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Summer | 50 |  |  | 44.9185 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 10 |  |  | 54.4983 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Summer | 50 |  |  | 44.7661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 10 |  |  | 54.5247 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Summer | 50 |  |  | 44.911 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 10 |  |  | 54.7136 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Summer | 50 |  |  | 44.9706 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 10 |  |  | 55.0965 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Summer | 50 |  |  | 45.1615 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 10 |  |  | 55.7707 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Summer | 50 |  |  | 45.5541 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 50 |  |  | 45.8843 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Summer | 10 |  |  | 56.122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 10 |  |  | 56.3761 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Summer | 50 |  |  | 46.0363 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 10 |  |  | 56.7608 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Summer | 50 |  |  | 45.9008 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 10 |  |  | 57.2519 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Summer | 50 |  |  | 46.4689 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 10 |  |  | 57.8457 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Summer | 50 |  |  | 46.559 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 10 |  |  | 58.1569 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Summer | 50 |  |  | 46.4523 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 10 |  |  | 58.056 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Summer | 50 |  |  | 46.6661 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 10 |  |  | 56.811 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Summer | 50 |  |  | 45.5652 | 202503 | MVA | east

## Forecast- Winter
Forecasting Application - 13/10/2025
asset_type | asset | extremum | scenario | demand_year | season | poe | customer_count | pv_capacity | value | forecast_round | unit | region
zone_sub | cln | maximum |  | 2022 | Winter | 10 | 38619 | 72.2578 | 63.0362 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2022 | Winter | 50 | 38619 | 72.2578 | 58.8161 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 10 | 41429 | 81.3604 | 67.9918 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2023 | Winter | 50 | 41429 | 81.3604 | 63.4647 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 10 | 44846 | 94.6588 | 74.018 | 202503 | MVA | central
zone_sub | cln | maximum |  | 2024 | Winter | 50 | 44846 | 94.6588 | 69.1182 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 89.4372 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 84.5179 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 93.2911 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 88.1502 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 98.0701 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.8679 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 102.5171 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 97.437 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 107.2692 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 101.4753 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 112.2902 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 107.1286 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 119.5588 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 113.3315 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 125.8642 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 119.6901 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 131.807 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 125.9989 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 137.993 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 131.579 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 145.465 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 137.6925 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 147.8036 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 139.8743 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 155.8793 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 147.8441 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 163.4009 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 156.1056 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 133.5693 | 202503 | MVA | central
zone_sub | cln | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 127.2077 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 10 | 24937 | 39.5122 | 50.635 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2022 | Winter | 50 | 24937 | 39.5122 | 48.3881 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 10 | 25835 | 43.8704 | 52.4586 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2023 | Winter | 50 | 25835 | 43.8704 | 50.1308 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 10 | 26314 | 48.9572 | 53.4328 | 202503 | MVA | central
zone_sub | cre | maximum |  | 2024 | Winter | 50 | 26314 | 48.9572 | 51.0617 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 68.4471 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 65.7336 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 69.4459 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 66.605 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 69.249 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 66.728 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 74.3386 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.0847 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 74.5773 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 72.2361 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.3193 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 74.0669 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.7248 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 75.6012 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.2116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.7507 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 79.7367 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8762 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 80.3545 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.6625 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 81.081 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 79.0014 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 80.0375 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.1499 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 83.4116 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 80.9567 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 84.3767 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 81.4995 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 72.4681 | 202503 | MVA | central
zone_sub | cre | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 69.0004 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 10 | 29371 | 40.0067 | 65.9271 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2022 | Winter | 50 | 29371 | 40.0067 | 59.4269 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 10 | 30422 | 45.1511 | 68.3101 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2023 | Winter | 50 | 30422 | 45.1511 | 61.7598 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 50 | 32118 | 51.557 | 65.5719 | 202503 | MVA | central
zone_sub | epg | maximum |  | 2024 | Winter | 10 | 32118 | 51.557 | 72.1952 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 85.9871 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 79.3939 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 95.0802 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 89.3565 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 100.5082 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 92.7492 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 99.8778 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 93.3308 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 103.1049 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 96.5577 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 109.1359 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 102.3455 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 112.51 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 104.2867 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 121.7799 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 114.0182 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 127.6696 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 119.7255 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 133.3287 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 125.5482 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 135.1129 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 126.6853 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 142.2751 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 134.3407 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 149.629 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 142.1357 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 150.109 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 141.9626 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 116.0207 | 202503 | MVA | central
zone_sub | epg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 101.3122 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 10 | 14879 | 23.0226 | 48.7862 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2022 | Winter | 50 | 14879 | 23.0226 | 43.3886 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 10 | 17175 | 27.7177 | 56.3067 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2023 | Winter | 50 | 17175 | 27.7177 | 50.077 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 10 | 19951 | 34.2052 | 65.4015 | 202503 | MVA | central
zone_sub | klo | maximum |  | 2024 | Winter | 50 | 19951 | 34.2052 | 58.1655 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 79.8942 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 72.3119 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 92.3723 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 83.7626 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 102.9502 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 93.3778 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 120.3965 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 109.8362 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 129.7211 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 118.6301 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 142.5707 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 129.8167 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 159.4027 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 143.8497 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 178.8568 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 161.743 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 196.8658 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 178.8635 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 214.3536 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 194.8729 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 235.0946 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 213.0243 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 246.5584 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 225.0657 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 273.2503 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 249.8153 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 298.8878 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 271.7276 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 252.4111 | 202503 | MVA | central
zone_sub | klo | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 227.0702 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 10 | 7174 | 11.5134 | 22.426 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2022 | Winter | 50 | 7174 | 11.5134 | 20.2322 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 10 | 7235 | 12.7349 | 22.5982 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2023 | Winter | 50 | 7235 | 12.7349 | 20.4035 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 10 | 7295 | 13.7538 | 22.7705 | 202503 | MVA | central
zone_sub | llg | maximum |  | 2024 | Winter | 50 | 7295 | 13.7538 | 20.5738 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 26.1225 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 23.9159 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 30.6829 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 28.4398 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 31.049 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 28.8402 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 31.3064 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 29.108 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 31.5714 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 29.4846 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 32.5932 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 30.3426 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 33.1905 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 31.0163 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 33.8014 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 31.6154 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 34.0793 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 31.8255 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 34.2253 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 32.0656 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 33.7185 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 31.7299 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 33.9832 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 31.9069 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 34.9987 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 32.7389 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 34.5209 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 32.3709 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 28.3277 | 202503 | MVA | central
zone_sub | llg | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 26.2847 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 10 | 23246 | 35.5119 | 49.8939 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2022 | Winter | 50 | 23246 | 35.5119 | 46.8764 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 10 | 24109 | 39.5748 | 51.7437 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2023 | Winter | 50 | 24109 | 39.5748 | 48.6149 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 10 | 24997 | 44.4669 | 53.6497 | 202503 | MVA | central
zone_sub | ofr | maximum |  | 2024 | Winter | 50 | 24997 | 44.4669 | 50.4065 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 59.4536 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 56.1183 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 66.5595 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 63.2802 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.8129 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3039 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 76.0509 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 72.5305 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 78.6773 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 74.8582 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 81.1629 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 77.5373 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 83.2732 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 79.5294 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 85.4834 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 81.7407 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 86.4197 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 82.8706 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 87.7259 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 83.8526 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 90.1815 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 86.3425 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 89.3155 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 84.7668 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 92.5351 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 88.8524 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 94.3753 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 94.1939 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 80.6717 | 202503 | MVA | central
zone_sub | ofr | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 77.1549 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 10 | 16270 | 23.521 | 48.1658 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2022 | Winter | 50 | 16270 | 23.521 | 45.1092 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 10 | 16562 | 25.5412 | 49.0318 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2023 | Winter | 50 | 16562 | 25.5412 | 45.9202 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 10 | 16854 | 27.7496 | 49.8978 | 202503 | MVA | central
zone_sub | phm | maximum |  | 2024 | Winter | 50 | 16854 | 27.7496 | 46.7311 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 67.0847 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 64.1376 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 71.7531 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 68.6294 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 72.4584 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 69.3785 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 72.887 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 69.9467 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 73.8781 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 70.9603 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 76.2493 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 73.2946 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 77.5227 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 74.8388 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 79.9897 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 76.8149 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 87.5343 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 77.8299 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 81.2629 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 78.7091 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 80.0205 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 77.0055 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 81.6454 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 78.9538 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 85.2253 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 82.0295 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 82.7648 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 79.6564 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 67.0558 | 202503 | MVA | central
zone_sub | phm | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 63.9852 | 202503 | MVA | central
zone_sub | wgi | maximum |  | 2022 | Winter | 10 | 21696 | 27.3902 | 41.941 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2022 | Winter | 50 | 21696 | 27.3902 | 38.234 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 10 | 22045 | 30.4273 | 42.6315 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2023 | Winter | 50 | 22045 | 30.4273 | 38.883 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 10 | 22388 | 33.5461 | 43.3126 | 202503 | MVA | east
zone_sub | wgi | maximum |  | 2024 | Winter | 50 | 22388 | 33.5461 | 39.5207 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 10 |  |  | 47.2482 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2025 | Winter | 50 |  |  | 43.6466 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 10 |  |  | 47.6557 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2026 | Winter | 50 |  |  | 44.0841 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 10 |  |  | 49.0622 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2027 | Winter | 50 |  |  | 44.625 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 10 |  |  | 49.028 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2028 | Winter | 50 |  |  | 45.3431 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 10 |  |  | 49.3373 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2029 | Winter | 50 |  |  | 46.0239 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 10 |  |  | 50.5469 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2030 | Winter | 50 |  |  | 47.2137 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 10 |  |  | 54.0224 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2031 | Winter | 50 |  |  | 50.206 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 10 |  |  | 55.4565 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2032 | Winter | 50 |  |  | 51.8155 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 10 |  |  | 54.099 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2033 | Winter | 50 |  |  | 50.6413 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 10 |  |  | 57.8491 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2034 | Winter | 50 |  |  | 54.2764 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 10 |  |  | 56.2746 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2035 | Winter | 50 |  |  | 54.9313 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 10 |  |  | 57.6913 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2036 | Winter | 50 |  |  | 55.4021 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 10 |  |  | 58.7122 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2037 | Winter | 50 |  |  | 57.6212 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 10 |  |  | 58.2928 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2038 | Winter | 50 |  |  | 57.9824 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 10 |  |  | 49.2493 | 202503 | MVA | east
zone_sub | wgi | maximum | Step Change - Added Block Loads | 2039 | Winter | 50 |  |  | 45.4578 | 202503 | MVA | east

## Ratings
STATION OUTPUT RATING (TRANSFORMER SUMMATION) SUMMARY
|  |  | Station N Rating |  | Station N-1 Rating |  | Station N-2 Rating
|  |  | SCR | WCR | SCR | WCR | SCR | WCR | Remarks | Remarks | Bus Target | Station Cap Bank
S/S Name | No. TX | Name Plate MVA | MVA | MVA | MVA | MVA | MVA | MVA | For N-1 Ratings | N-2 | Voltage kV | MVAr
CLN | 3 | 99 | 130.95 | 142.95 | 89.2 | 97.8 | 44.6 | 48.9
LLG | 1 | 33 | 47.4 | 48.3 | 0 | 0 | 0 | 0 | N rating only |  | 22 | 4
OFR | 2 | 66 | 93.2 | 93.2 | 45.2 | 48 | 0 | 0 | Loss of T1 or T2 |  | 22 | 6
PHM | 2 | 66 | 91.9 | 95.7 | 45 | 49.1 | 0 | 0 | Loss of T1 or T2 |  | 22 | 12

## Power Factor
asset_type | asset | PF
zone_sub | cln | 1
zone_sub | llg | 0.99
zone_sub | ofr | 1
zone_sub | phm | 1

## FT
Forecast tool (MVA) |  | Forecast Capacity & Transfers
ZSS |  | PHM
Summer
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DY (Apr 1 to Mar 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Summer POE50 | 50 |  |  | 52.8621 | 69.621 | 74.1527 | 73.9998 | 73.965 | 74.4648 | 75.0153 | 76.1566 | 76.9783 | 77.4148 | 77.8841 | 78.3211 | 79.127 | 80.1321 | 80.0404
Summer POE10 | 10 |  |  | 58.7282 | 75.5207 | 79.8845 | 79.6008 | 79.5894 | 80.0199 | 81.1895 | 81.9552 | 82.7146 | 83.6062 | 84.4206 | 85.2206 | 85.2937 | 86.2309 | 85.4841
Winter
[5 empty] | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads | Step Change - Added Block Loads
DM (Apr 1 to Mar 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
DY (Apr 1 to Mar 30) |  |  |  | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
FY (Jul 1 to Jun 30) |  |  |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39
FY (Jul 1 to Jun 30) |  |  |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
Winter POE50 | 50 |  |  | 46.7311 | 64.1376 | 68.6294 | 69.3785 | 69.9467 | 70.9603 | 73.2946 | 74.8388 | 76.8149 | 77.8299 | 78.7091 | 77.0055 | 78.9538 | 82.0295 | 79.6564
Winter POE10 | 10 |  |  | 49.8978 | 67.0847 | 71.7531 | 72.4584 | 72.887 | 73.8781 | 76.2493 | 77.5227 | 79.9897 | 87.5343 | 81.2629 | 80.0205 | 81.6454 | 85.2253 | 82.7648
Transfers (MVA)
|  | Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39
|  | PHM | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4
|  | PowerFactor | 1

## Load Duration Curves
Station
PHM
POE10
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - MD (P10) - Duration % | Winter - MD - Hours | Summer - MD - Duration % | Summer - MD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0.03444% | 1.5127 | 99% | 0.01722% | 0.02707% | 0% | 0.04737% | 0% | 0% | 0.00861% | 0.01353% | 0.03444% | 0.03383% | 0.01722% | 0.0203% | 0.02583% | 0.006767% | 0% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0.05166% | 2.269 | 98% | 0.01722% | 0.07443% | 0.00861% | 0.08797% | 0.02583% | 0.01353% | 0.02583% | 0.0203% | 0.05166% | 0.07443% | 0.02583% | 0.0812% | 0.04305% | 0.0203% | 0% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.0861% | 3.7816 | 97% | 0.02583% | 0.09474% | 0.02583% | 0.1421% | 0.04305% | 0.02707% | 0.05166% | 0.03383% | 0.0861% | 0.1556% | 0.04305% | 0.1083% | 0.05166% | 0.04737% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.1378% | 6.0506 | 95% | 0.05166% | 0.1895% | 0.09471% | 0.3519% | 0.0861% | 0.08797% | 0.1033% | 0.05413% | 0.1378% | 0.3992% | 0.07749% | 0.1759% | 0.09471% | 0.09474% | 0.00861% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.3702% | 16.2611 | 90% | 0.0861% | 0.9135% | 0.1894% | 1.786% | 0.1894% | 0.7579% | 0.1808% | 0.07443% | 0.3702% | 1.793% | 0.2066% | 0.8932% | 0.353% | 0.2639% | 0.01722% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.6027% | 26.4715 | 85% | 0.1205% | 2.355% | 0.353% | 4.588% | 0.2669% | 2.761% | 0.3272% | 0.318% | 0.6027% | 5.393% | 0.3702% | 2.68% | 0.7147% | 0.7443% | 0.02583% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.7749% | 34.0348 | 80% | 0.31% | 5.616% | 0.6458% | 8.885% | 0.4219% | 6.787% | 0.4477% | 0.9406% | 0.7749% | 11.33% | 0.5683% | 6.11% | 1.317% | 1.915% | 0.06027% | 2.118%
| 75% | 18.3% | 803.6248 | 1.102% | 48.405 | 75% | 0.4822% | 9.995% | 0.9988% | 14.05% | 0.5338% | 11.76% | 0.5855% | 2.876% | 1.102% | 18.3% | 0.7491% | 10.38% | 2.764% | 4.601% | 0.07749% | 4.486%
| 70% | 26.3% | 1155.2107 | 1.739% | 76.3892 | 70% | 0.7491% | 14.12% | 1.498% | 19.88% | 0.8438% | 17.56% | 0.7921% | 7.376% | 1.739% | 26.3% | 0.9557% | 15.73% | 6.225% | 8.837% | 0.1292% | 8.607%
| 65% | 35.36% | 1553.1596 | 2.6% | 114.2056 | 65% | 1.154% | 18.84% | 2.265% | 27.11% | 1.102% | 25.21% | 1.05% | 12.51% | 2.6% | 35.36% | 1.541% | 22.03% | 12.05% | 15.25% | 0.1464% | 14.03%
| 60% | 46.14% | 2026.2996 | 4.055% | 178.1154 | 60% | 1.602% | 25.14% | 3.203% | 35.21% | 1.627% | 33.62% | 1.748% | 18.2% | 4.055% | 46.14% | 2.247% | 29.44% | 20.92% | 25.15% | 0.2583% | 21.29%
| 55% | 59.16% | 2598.4068 | 7.095% | 311.6074 | 55% | 2.411% | 33.56% | 4.357% | 45.33% | 2.48% | 42.68% | 2.419% | 25.42% | 7.095% | 59.16% | 3.496% | 37.5% | 33.11% | 37.15% | 0.8094% | 29.85%
| 50% | 73.62% | 3233.5201 | 14.48% | 636.0723 | 50% | 4.598% | 44.25% | 6.303% | 58.26% | 3.84% | 54.87% | 4.064% | 34.04% | 14.48% | 73.62% | 5.881% | 47.91% | 47.93% | 51.32% | 2.17% | 39.4%
| 45% | 85.96% | 3775.313 | 26.86% | 1179.4944 | 45% | 9.592% | 58.98% | 10.8% | 69.36% | 6.535% | 71.48% | 8.378% | 45.63% | 26.86% | 85.96% | 11.13% | 62.3% | 62.8% | 65.85% | 4.753% | 49.36%
| 40% | 92.73% | 4072.8088 | 41.17% | 1808.3816 | 40% | 19.83% | 71.65% | 21.2% | 75.98% | 14.01% | 84.31% | 16.88% | 65.51% | 41.17% | 92.73% | 21.13% | 79.32% | 76.24% | 79.08% | 8.662% | 59.42%
| 35% | 95.6% | 4198.821 | 63.28% | 2779.1293 | 35% | 37.74% | 78.94% | 37.58% | 85.16% | 27.53% | 88.52% | 26.59% | 78.66% | 63.28% | 95.6% | 34.85% | 87.21% | 86.9% | 88.41% | 15.86% | 68.26%
| 30% | 97.25% | 4271.3374 | 86.84% | 3814.165 | 30% | 66.82% | 83.24% | 57.09% | 93.38% | 49.73% | 90.98% | 45.59% | 83.41% | 86.84% | 97.25% | 59.02% | 90.02% | 92.6% | 93.97% | 28.71% | 75.35%
| 25% | 98.4% | 4321.8611 | 94.88% | 4166.9923 | 25% | 77.33% | 87.43% | 77.75% | 96.1% | 81.07% | 93.44% | 72.26% | 87.95% | 94.88% | 98.4% | 83.32% | 92.46% | 96.47% | 96.66% | 44.75% | 80.55%
| 20% | 99.11% | 4353.067 | 97.51% | 4282.7105 | 20% | 85.59% | 92.06% | 96.84% | 97.65% | 89.22% | 95.65% | 79.18% | 93.87% | 97.51% | 99.11% | 91.2% | 94.84% | 98.65% | 98.41% | 56.7% | 84.95%
| 15% | 99.49% | 4369.4129 | 99.38% | 4364.7722 | 15% | 96.14% | 98.9% | 99.64% | 98.65% | 96.11% | 97.43% | 86.26% | 99.55% | 99.38% | 99.49% | 97.48% | 97.23% | 99.31% | 99.14% | 68.25% | 89.03%
| 10% | 99.7% | 4378.6261 | 99.99% | 4391.6218 | 10% | 99.99% | 99.99% | 99.99% | 99.16% | 99.9% | 98.78% | 98.3% | 99.6% | 99.99% | 99.7% | 99.99% | 99.59% | 99.63% | 99.41% | 79.5% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 5% | 99.99% | 99.99% | 99.99% | 99.49% | 99.99% | 99.76% | 99.99% | 99.61% | 99.99% | 99.99% | 99.99% | 99.99% | 99.68% | 99.6% | 90.07% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.71% | 99.63% | 99.99% | 99.99%
POE 50
[6 empty] | Stations | KLO |  | EPG |  | CRE |  | CLN |  | PHM |  | OFR |  | LLG |  | WGI
| % of MD | Winter - AD (P50) - Duration % | Winter - AD - Hours | Summer - AD - Duration % | Summer - AD - Hours | %MD | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration % | Summer Duration % | Winter Duration %
| 100% | 0% | 0 | 0% | 0 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| 99% | 0.03383% | 1.486 | 0% | 0 | 99% | 0.03444% | 0.02707% | 0.04305% | 0.04737% | 0% | 0% | 0% | 0.01353% | 0% | 0.03383% | 0% | 0.0203% | 0.00861% | 0.006767% | 0.00861% | 0.006767%
| 98% | 0.07443% | 3.2692 | 0% | 0 | 98% | 0.05166% | 0.07443% | 0.07749% | 0.08797% | 0% | 0.01353% | 0.00861% | 0.0203% | 0% | 0.07443% | 0.00861% | 0.0812% | 0.00861% | 0.0203% | 0.00861% | 0.006767%
| 97% | 0.1556% | 6.8356 | 0.00861% | 0.37816 | 97% | 0.06888% | 0.09474% | 0.07749% | 0.1421% | 0.02583% | 0.02707% | 0.01722% | 0.03383% | 0.00861% | 0.1556% | 0.01722% | 0.1083% | 0.01722% | 0.0406% | 0.00861% | 0.006767%
| 95% | 0.3992% | 17.5347 | 0.05166% | 2.269 | 95% | 0.0861% | 0.1895% | 0.1378% | 0.3519% | 0.04305% | 0.08797% | 0.02583% | 0.05413% | 0.05166% | 0.3992% | 0.04305% | 0.1759% | 0.01722% | 0.1015% | 0.01722% | 0.03383%
| 90% | 1.793% | 78.7576 | 0.1292% | 5.6725 | 90% | 0.1292% | 0.9135% | 0.2583% | 1.786% | 0.1119% | 0.7579% | 0.1033% | 0.07443% | 0.1292% | 1.793% | 0.1033% | 0.8932% | 0.0861% | 0.3451% | 0.2066% | 0.1962%
| 85% | 5.393% | 236.8672 | 0.3616% | 15.8829 | 85% | 0.2497% | 2.355% | 0.465% | 4.588% | 0.2755% | 2.761% | 0.1808% | 0.318% | 0.3616% | 5.393% | 0.2066% | 2.68% | 0.31% | 0.9% | 0.9213% | 0.9135%
| 80% | 11.33% | 497.5104 | 0.706% | 31.0095 | 80% | 0.4133% | 5.616% | 0.7835% | 8.885% | 0.6113% | 6.787% | 0.2669% | 0.9406% | 0.706% | 11.33% | 0.6286% | 6.11% | 0.8008% | 2.517% | 2.153% | 2.118%
| 75% | 18.3% | 803.6248 | 1.662% | 72.9857 | 75% | 0.8352% | 9.995% | 1.257% | 14.05% | 0.9902% | 11.76% | 0.4047% | 2.876% | 1.662% | 18.3% | 1.309% | 10.38% | 1.834% | 5.562% | 4.486% | 4.486%
| 70% | 26.3% | 1155.2107 | 3.427% | 150.5094 | 70% | 1.619% | 14.12% | 2.101% | 19.88% | 1.911% | 17.56% | 0.8008% | 7.376% | 3.427% | 26.3% | 2.419% | 15.73% | 4.374% | 10.11% | 7.672% | 8.607%
| 65% | 35.36% | 1553.1596 | 8.188% | 359.6342 | 65% | 3.057% | 18.84% | 4.288% | 27.11% | 3.504% | 25.21% | 1.352% | 12.51% | 8.188% | 35.36% | 4.598% | 22.03% | 9.179% | 17.54% | 11.87% | 14.03%
| 60% | 46.14% | 2026.2996 | 15.71% | 689.7717 | 60% | 5.528% | 25.14% | 9.342% | 35.21% | 7.758% | 33.62% | 3.573% | 18.2% | 15.71% | 46.14% | 9.17% | 29.44% | 16.83% | 27.53% | 18.5% | 21.29%
| 55% | 59.16% | 2598.4068 | 24.94% | 1095.5419 | 55% | 11.8% | 33.56% | 17.61% | 45.33% | 16.05% | 42.68% | 8.283% | 25.42% | 24.94% | 59.16% | 14.93% | 37.5% | 27.43% | 40.02% | 27.37% | 29.85%
| 50% | 73.62% | 3233.5201 | 37.94% | 1666.1918 | 50% | 21.47% | 44.25% | 28.46% | 58.26% | 24.85% | 54.87% | 17.57% | 34.04% | 37.94% | 73.62% | 22.35% | 47.91% | 40.6% | 54.15% | 38.39% | 39.4%
| 45% | 85.96% | 3775.313 | 57.06% | 2506.0947 | 45% | 35.07% | 58.98% | 42.44% | 69.36% | 37.15% | 71.48% | 28.59% | 45.63% | 57.06% | 85.96% | 36.95% | 62.3% | 53.97% | 68.39% | 48.48% | 49.36%
| 40% | 92.73% | 4072.8088 | 72.05% | 3164.4787 | 40% | 60.78% | 71.65% | 63.35% | 75.98% | 61.17% | 84.31% | 46.88% | 65.51% | 72.05% | 92.73% | 55.62% | 79.32% | 65.21% | 80.79% | 56.57% | 59.42%
| 35% | 95.6% | 4198.821 | 80.86% | 3551.3408 | 35% | 70.59% | 78.94% | 76.04% | 85.16% | 71.05% | 88.52% | 69.68% | 78.66% | 80.86% | 95.6% | 68.46% | 87.21% | 75.09% | 89.43% | 63.94% | 68.26%
| 30% | 97.25% | 4271.3374 | 85.59% | 3758.953 | 30% | 76.73% | 83.24% | 80.97% | 93.38% | 75.06% | 90.98% | 76.64% | 83.41% | 85.59% | 97.25% | 74.6% | 90.02% | 81.51% | 94.17% | 70.48% | 75.35%
| 25% | 98.4% | 4321.8611 | 89.4% | 3926.4798 | 25% | 83.08% | 87.43% | 85.41% | 96.1% | 78.56% | 93.44% | 83.93% | 87.95% | 89.4% | 98.4% | 78.93% | 92.46% | 86.44% | 96.81% | 76.48% | 80.55%
| 20% | 99.11% | 4353.067 | 92.22% | 4050.5177 | 20% | 91.12% | 92.06% | 89.28% | 97.65% | 81.79% | 95.65% | 91.73% | 93.87% | 92.22% | 99.11% | 84.56% | 94.84% | 90.52% | 98.48% | 81.71% | 84.95%
| 15% | 99.49% | 4369.4129 | 94.55% | 4152.622 | 15% | 99.18% | 98.9% | 92.61% | 98.65% | 86.18% | 97.43% | 98.93% | 99.55% | 94.55% | 99.49% | 92.06% | 97.23% | 93.75% | 99.28% | 86.58% | 89.03%
| 10% | 99.7% | 4378.6261 | 96.73% | 4248.2976 | 10% | 99.99% | 99.99% | 95.16% | 99.16% | 91.73% | 98.78% | 99.75% | 99.6% | 96.73% | 99.7% | 99.06% | 99.59% | 96.19% | 99.59% | 91.64% | 92.79%
| 5% | 99.99% | 4391.7028 | 99.31% | 4361.7469 | 5% | 99.99% | 99.99% | 97.15% | 99.49% | 97.84% | 99.76% | 99.99% | 99.61% | 99.31% | 99.99% | 99.99% | 99.99% | 98.14% | 99.77% | 96.54% | 96.81%
| 9.992e-14% | 99.99% | 4391.7028 | 99.99% | 4391.6218 | 0% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.99% | 99.63% | 99.99% | 99.99% | 99.99% | 99.99% | 99.78% | 99.99% | 99.99% | 99.99%
POE10
|  | Summer | Winter
| Year | 2019/2020 | 2023
| Start | 2024-10-01 | 2024-04-01
| End | 2025-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392
POE50
|  | Summer | Winter
| Year | 2023/2024 | 2023
| Start | 2023-10-01 | 2024-04-01
| End | 2024-04-01 | 2024-10-01
| Days | 183 | 183
| Hours | 4392 | 4392

## Capacity N
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 1 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 1 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 2 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 2 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 3 | 95.7 | 95.7 | 95.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7
SCR N Rating (MVA) - Option 3 | 91.9 | 91.9 | 91.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9 | 136.9
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 4 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 4 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 5 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 5 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 6 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 6 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 7 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N Rating (MVA) - Option 8 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7
SCR N Rating (MVA) - Option 8 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9 | 91.9
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-1
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 1 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 2 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 2 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 3 | 49.1 | 49.1 | 49.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1
SCR N-1 Rating (MVA) - Option 3 | 45 | 45 | 45 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 4 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 4 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 5 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 5 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 6 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 6 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 7 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 7 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-1 Rating (MVA) - Option 8 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
SCR N-1 Rating (MVA) - Option 8 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Capacity N-2
Option 1 - Do Nothing / Base Case - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Planned Additional Capacity (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 - 1A New PHS ZSS + Four new feeders - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
SCR N-2 Rating (MVA) - Option 3 | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Capacity Added (MVA) | 0 | 0 | 0 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 - - Capacity
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
WCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCR N-2 Rating (MVA) - Option 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Added (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Demand
Option 1 - Do Nothing / Base Case
Winter Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 51.4042 | 70.5514 | 75.4923 | 76.3163 | 76.9414 | 78.0563 | 80.6241 | 82.3226 | 84.4964 | 85.6129 | 86.5801 | 84.7061 | 86.8492 | 90.2325 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221 | 87.6221
Maximum Demand (MVA) - P10 | 54.8876 | 73.7932 | 78.9284 | 79.7042 | 80.1757 | 81.2659 | 83.8742 | 85.2749 | 87.9887 | 96.2877 | 89.3892 | 88.0226 | 89.8099 | 93.7478 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413 | 91.0413
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221
Total Maximum Demand (MVA) - Option 1 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
Summer Season | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Maximum Demand (MVA) - P50 | 58.1483 | 76.5831 | 81.568 | 81.3998 | 81.3614 | 81.9113 | 82.5169 | 83.7723 | 84.6761 | 85.1563 | 85.6725 | 86.1532 | 87.0397 | 88.1453 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445 | 88.0445
Maximum Demand (MVA) - P10 | 64.601 | 83.0728 | 87.873 | 87.5609 | 87.5484 | 88.0219 | 89.3084 | 90.1508 | 90.9861 | 91.9669 | 92.8626 | 93.7427 | 93.823 | 94.854 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325 | 94.0325
Block loads (MVA) not in the forecast | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Available Transfers (MVA) | 1.7 | 1.7 | 1.67 | 1.65 | 1.62 | 1.6 | 1.58 | 1.55 | 1.53 | 1.51 | 1.48 | 1.46 | 1.44 | 1.42 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 1 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445
Total Maximum Demand (MVA) - Option 1 Summer POE10 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
Option 2 - 1A New PHS ZSS + Four new feeders
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 2 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 45.6663 | 46.3214 | 47.4563 | 50.0441 | 51.7726 | 53.9664 | 55.1029 | 56.1001 | 54.2461 | 56.4092 | 59.8125 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221
Total Maximum Demand (MVA) - Option 2 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 49.0542 | 49.5557 | 50.6659 | 53.2942 | 54.7249 | 57.4587 | 65.7777 | 58.9092 | 57.5626 | 59.3699 | 63.3278 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413
Total Maximum Demand (MVA) - Option 2 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 50.7498 | 50.7414 | 51.3113 | 51.9369 | 53.2223 | 54.1461 | 54.6463 | 55.1925 | 55.6932 | 56.5997 | 57.7253 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445
Total Maximum Demand (MVA) - Option 2 Summer POE10 | 62.901 | 81.3728 | 86.203 | 56.9109 | 56.9284 | 57.4219 | 58.7284 | 59.6008 | 60.4561 | 61.4569 | 62.3826 | 63.2827 | 63.383 | 64.434 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 3 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221
Total Maximum Demand (MVA) - Option 3 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
Total Maximum Demand (MVA) - Option 3 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445
Total Maximum Demand (MVA) - Option 3 Summer POE10 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 4 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 60.1663 | 60.8214 | 61.9563 | 64.5441 | 66.2726 | 68.4664 | 69.6029 | 70.6001 | 68.7461 | 70.9092 | 74.3125 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221
Total Maximum Demand (MVA) - Option 4 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 63.5542 | 64.0557 | 65.1659 | 67.7942 | 69.2249 | 71.9587 | 80.2777 | 73.4092 | 72.0626 | 73.8699 | 77.8278 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413
Total Maximum Demand (MVA) - Option 4 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 65.2498 | 65.2414 | 65.8113 | 66.4369 | 67.7223 | 68.6461 | 69.1463 | 69.6925 | 70.1932 | 71.0997 | 72.2253 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445
Total Maximum Demand (MVA) - Option 4 Summer POE10 | 62.901 | 81.3728 | 86.203 | 71.4109 | 71.4284 | 71.9219 | 73.2284 | 74.1008 | 74.9561 | 75.9569 | 76.8826 | 77.7827 | 77.883 | 78.934 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 5 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 45.6663 | 46.3214 | 47.4563 | 50.0441 | 51.7726 | 53.9664 | 55.1029 | 56.1001 | 54.2461 | 56.4092 | 59.8125 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221
Total Maximum Demand (MVA) - Option 5 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 49.0542 | 49.5557 | 50.6659 | 53.2942 | 54.7249 | 57.4587 | 65.7777 | 58.9092 | 57.5626 | 59.3699 | 63.3278 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413
Total Maximum Demand (MVA) - Option 5 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 50.7498 | 50.7414 | 51.3113 | 51.9369 | 53.2223 | 54.1461 | 54.6463 | 55.1925 | 55.6932 | 56.5997 | 57.7253 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445
Total Maximum Demand (MVA) - Option 5 Summer POE10 | 62.901 | 81.3728 | 86.203 | 56.9109 | 56.9284 | 57.4219 | 58.7284 | 59.6008 | 60.4561 | 61.4569 | 62.3826 | 63.2827 | 63.383 | 64.434 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325
Option 6 - Non Network
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 7.7456 | 9.9603 | 10.5358 | 10.4984 | 10.4969 | 10.5537 | 10.7079 | 10.8089 | 10.9091 | 11.0267 | 11.1341 | 11.2396 | 11.2492 | 11.3728 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743 | 11.2743
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 6 Winter POE50 | 41.9587 | 58.8911 | 63.2865 | 64.1679 | 64.8245 | 65.9027 | 68.3362 | 69.9637 | 72.0573 | 73.0762 | 73.966 | 72.0065 | 74.16 | 77.4396 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477
Total Maximum Demand (MVA) - Option 6 Winter POE10 | 45.442 | 62.1329 | 66.7226 | 67.5558 | 68.0587 | 69.1122 | 71.5862 | 72.916 | 75.5496 | 83.7511 | 76.7751 | 75.323 | 77.1207 | 80.9549 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367
Total Maximum Demand (MVA) - Option 6 Summer POE50 | 48.7027 | 64.9228 | 69.3621 | 69.2514 | 69.2445 | 69.7576 | 70.2289 | 71.4133 | 72.237 | 72.6196 | 73.0584 | 73.4536 | 74.3505 | 75.3524 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701
Total Maximum Demand (MVA) - Option 6 Summer POE10 | 55.1554 | 71.4125 | 75.6672 | 75.4125 | 75.4315 | 75.8682 | 77.0205 | 77.7918 | 78.547 | 79.4302 | 80.2485 | 81.0431 | 81.1338 | 82.0611 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581
Option 7 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 7 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221
Total Maximum Demand (MVA) - Option 7 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
Total Maximum Demand (MVA) - Option 7 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445
Total Maximum Demand (MVA) - Option 7 Summer POE10 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
Option 8 -
Year | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Added Transfers (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Demand management (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Added Embedded generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Maximum Demand (MVA) - Option 8 Winter POE50 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221
Total Maximum Demand (MVA) - Option 8 Winter POE10 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
Total Maximum Demand (MVA) - Option 8 Summer POE50 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445
Total Maximum Demand (MVA) - Option 8 Summer POE10 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325

## Forecasted LDC
Option 1 - Do Nothing / Base Case
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 73.9197 | 74.5682 | 75.6918 | 78.2537 | 79.9649 | 82.1367 | 83.2619 | 84.2491 | 82.4136 | 84.5551 | 87.9243 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 77.2737 | 77.7701 | 78.8692 | 81.4712 | 82.8877 | 85.5941 | 93.83 | 87.0301 | 85.697 | 87.4862 | 91.4045 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 73.173 | 73.815 | 74.9272 | 77.4632 | 79.1572 | 81.3071 | 82.4209 | 83.3981 | 81.5812 | 83.701 | 87.0362 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 76.4931 | 76.9846 | 78.0726 | 80.6483 | 82.0504 | 84.7295 | 92.8822 | 86.151 | 84.8313 | 86.6025 | 90.4812 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 72.4263 | 73.0618 | 74.1627 | 76.6728 | 78.3495 | 80.4774 | 81.5798 | 82.5471 | 80.7487 | 82.847 | 86.1481 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 75.7126 | 76.199 | 77.2759 | 79.8254 | 81.2132 | 83.865 | 91.9344 | 85.2719 | 83.9657 | 85.7188 | 89.558 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 70.933 | 71.5553 | 72.6335 | 75.0919 | 76.734 | 78.8181 | 79.8978 | 80.8451 | 79.0838 | 81.1388 | 84.3718 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 74.1515 | 74.6279 | 75.6826 | 78.1795 | 79.5387 | 82.1358 | 90.0389 | 83.5138 | 82.2345 | 83.9514 | 87.7114 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 67.1997 | 67.7893 | 68.8107 | 71.1397 | 72.6954 | 74.6697 | 75.6926 | 76.5901 | 74.9215 | 76.8683 | 79.9312 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 70.2488 | 70.7001 | 71.6993 | 74.0648 | 75.3524 | 77.8128 | 85.3 | 79.1183 | 77.9063 | 79.5329 | 83.095 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 63.4664 | 64.0232 | 64.9879 | 67.1875 | 68.6567 | 70.5214 | 71.4875 | 72.3351 | 70.7592 | 72.5978 | 75.4906 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 66.3461 | 66.7723 | 67.716 | 69.9501 | 71.1662 | 73.4899 | 80.5611 | 74.7228 | 73.5782 | 75.1144 | 78.4786 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 59.7331 | 60.2571 | 61.1651 | 63.2353 | 64.6181 | 66.3731 | 67.2823 | 68.08 | 66.5969 | 68.3274 | 71.05 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 62.4434 | 62.8445 | 63.7327 | 65.8353 | 66.9799 | 69.167 | 75.8222 | 70.3274 | 69.2501 | 70.6959 | 73.8622 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 55.9997 | 56.4911 | 57.3423 | 59.2831 | 60.5795 | 62.2248 | 63.0772 | 63.825 | 62.4346 | 64.0569 | 66.6093 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 58.5407 | 58.9167 | 59.7494 | 61.7206 | 62.7937 | 64.844 | 71.0833 | 65.9319 | 64.9219 | 66.2774 | 69.2458 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 52.2664 | 52.725 | 53.5194 | 55.3309 | 56.5408 | 58.0765 | 58.8721 | 59.57 | 58.2723 | 59.7865 | 62.1687 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 54.638 | 54.989 | 55.7661 | 57.6059 | 58.6074 | 60.5211 | 66.3444 | 61.5365 | 60.5938 | 61.8589 | 64.6295 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 48.5331 | 48.9589 | 49.6966 | 51.3787 | 52.5022 | 53.9282 | 54.6669 | 55.315 | 54.11 | 55.516 | 57.7281 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 50.7352 | 51.0612 | 51.7828 | 53.4912 | 54.4212 | 56.1982 | 61.6055 | 57.141 | 56.2657 | 57.4405 | 60.0131 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 44.7998 | 45.1928 | 45.8738 | 47.4265 | 48.4636 | 49.7798 | 50.4618 | 51.06 | 49.9477 | 51.2455 | 53.2875 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 46.8325 | 47.1334 | 47.7995 | 49.3765 | 50.235 | 51.8752 | 56.8666 | 52.7455 | 51.9376 | 53.022 | 55.3967 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 41.0665 | 41.4268 | 42.051 | 43.4743 | 44.425 | 45.6315 | 46.2566 | 46.805 | 45.7854 | 46.9751 | 48.8469 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 42.9298 | 43.2056 | 43.8162 | 45.2618 | 46.0487 | 47.5523 | 52.1278 | 48.3501 | 47.6094 | 48.6035 | 50.7803 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 37.3332 | 37.6607 | 38.2282 | 39.5221 | 40.3863 | 41.4832 | 42.0515 | 42.55 | 41.623 | 42.7046 | 44.4062 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 39.0271 | 39.2778 | 39.833 | 41.1471 | 41.8625 | 43.2294 | 47.3889 | 43.9546 | 43.2813 | 44.185 | 46.1639 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 33.5998 | 33.8946 | 34.4054 | 35.5699 | 36.3477 | 37.3349 | 37.8463 | 38.295 | 37.4607 | 38.4342 | 39.9656 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 35.1244 | 35.35 | 35.8497 | 37.0324 | 37.6762 | 38.9064 | 42.65 | 39.5591 | 38.9532 | 39.7665 | 41.5475 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 29.8665 | 30.1286 | 30.5825 | 31.6176 | 32.3091 | 33.1866 | 33.6412 | 34.04 | 33.2984 | 34.1637 | 35.525 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 31.2217 | 31.4223 | 31.8664 | 32.9177 | 33.49 | 34.5835 | 37.9111 | 35.1637 | 34.625 | 35.348 | 36.9311 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 26.1332 | 26.3625 | 26.7597 | 27.6654 | 28.2704 | 29.0382 | 29.436 | 29.785 | 29.1361 | 29.8932 | 31.0844 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 27.319 | 27.4945 | 27.8831 | 28.803 | 29.3037 | 30.2606 | 33.1722 | 30.7682 | 30.2969 | 30.9295 | 32.3147 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 22.3999 | 22.5964 | 22.9369 | 23.7132 | 24.2318 | 24.8899 | 25.2309 | 25.53 | 24.9738 | 25.6228 | 26.6437 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 23.4163 | 23.5667 | 23.8998 | 24.6883 | 25.1175 | 25.9376 | 28.4333 | 26.3728 | 25.9688 | 26.511 | 27.6983 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 18.6666 | 18.8304 | 19.1141 | 19.761 | 20.1932 | 20.7416 | 21.0257 | 21.275 | 20.8115 | 21.3523 | 22.2031 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 19.5136 | 19.6389 | 19.9165 | 20.5735 | 20.9312 | 21.6147 | 23.6944 | 21.9773 | 21.6406 | 22.0925 | 23.0819 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.9333 | 15.0643 | 15.2913 | 15.8088 | 16.1545 | 16.5933 | 16.8206 | 17.02 | 16.6492 | 17.0818 | 17.7625 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 15.6108 | 15.7111 | 15.9332 | 16.4588 | 16.745 | 17.2917 | 18.9555 | 17.5818 | 17.3125 | 17.674 | 18.4656 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 11.1999 | 11.2982 | 11.4685 | 11.8566 | 12.1159 | 12.445 | 12.6154 | 12.765 | 12.4869 | 12.8114 | 13.3219 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.7081 | 11.7833 | 11.9499 | 12.3441 | 12.5587 | 12.9688 | 14.2167 | 13.1864 | 12.9844 | 13.2555 | 13.8492 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.4666 | 7.5321 | 7.6456 | 7.9044 | 8.0773 | 8.2966 | 8.4103 | 8.51 | 8.3246 | 8.5409 | 8.8812 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.8054 | 7.8556 | 7.9666 | 8.2294 | 8.3725 | 8.6459 | 9.4778 | 8.7909 | 8.6563 | 8.837 | 9.2328 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.7333 | 3.7661 | 3.8228 | 3.9522 | 4.0386 | 4.1483 | 4.2051 | 4.255 | 4.1623 | 4.2705 | 4.4406 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.9027 | 3.9278 | 3.9833 | 4.1147 | 4.1862 | 4.3229 | 4.7389 | 4.3955 | 4.3281 | 4.4185 | 4.6164 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.4607e-14 | 7.5261e-14 | 7.6395e-14 | 7.8981e-14 | 8.0708e-14 | 8.29e-14 | 8.4036e-14 | 8.5032e-14 | 8.318e-14 | 8.5341e-14 | 8.8741e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.7992e-14 | 7.8493e-14 | 7.9602e-14 | 8.2228e-14 | 8.3658e-14 | 8.639e-14 | 9.4702e-14 | 8.7839e-14 | 8.6493e-14 | 8.8299e-14 | 9.2254e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 78.9523 | 78.944 | 79.5082 | 80.1275 | 81.4 | 82.3146 | 82.8098 | 83.3506 | 83.8463 | 84.7437 | 85.858 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 85.0518 | 85.0691 | 85.5577 | 86.8512 | 87.7148 | 88.5615 | 89.5523 | 90.4688 | 91.3598 | 91.4592 | 92.4996 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061
98% | 0 | 55.3193 | 73.3854 | 78.3 | 78.1548 | 78.1466 | 78.7051 | 79.3181 | 80.5778 | 81.4832 | 81.9734 | 82.5086 | 82.9994 | 83.8877 | 84.9908 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 84.1927 | 84.2098 | 84.6935 | 85.9739 | 86.8287 | 87.667 | 88.6477 | 89.555 | 90.437 | 90.5354 | 91.5653 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 77.3573 | 77.3492 | 77.902 | 78.5088 | 79.7556 | 80.6517 | 81.1369 | 81.6667 | 82.1524 | 83.0317 | 84.1235 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 83.3336 | 83.3505 | 83.8292 | 85.0966 | 85.9427 | 86.7724 | 87.7432 | 88.6411 | 89.5142 | 89.6115 | 90.631 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 75.7623 | 75.7544 | 76.2958 | 76.89 | 78.1112 | 78.9888 | 79.464 | 79.9829 | 80.4586 | 81.3197 | 82.389 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 81.6153 | 81.632 | 82.1008 | 83.342 | 84.1707 | 84.9833 | 85.934 | 86.8135 | 87.6685 | 87.7639 | 88.7623 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 71.7748 | 71.7673 | 72.2802 | 72.8432 | 74 | 74.8315 | 75.2817 | 75.7732 | 76.2239 | 77.0397 | 78.0527 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 77.3198 | 77.3355 | 77.7797 | 78.9556 | 79.7407 | 80.5105 | 81.4112 | 82.2444 | 83.0544 | 83.1447 | 84.0906 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 67.7874 | 67.7802 | 68.2646 | 68.7963 | 69.8889 | 70.6742 | 71.0994 | 71.5636 | 71.9893 | 72.7598 | 73.7165 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 73.0243 | 73.0391 | 73.4586 | 74.5692 | 75.3106 | 76.0377 | 76.8883 | 77.6752 | 78.4403 | 78.5256 | 79.4189 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 63.7999 | 63.7932 | 64.2491 | 64.7495 | 65.7778 | 66.5169 | 66.917 | 67.354 | 67.7546 | 68.4798 | 69.3802 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 68.7287 | 68.7427 | 69.1375 | 70.1827 | 70.8806 | 71.5649 | 72.3655 | 73.1061 | 73.8261 | 73.9064 | 74.7472 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 59.8124 | 59.8061 | 60.2335 | 60.7027 | 61.6667 | 62.3596 | 62.7347 | 63.1444 | 63.5199 | 64.1998 | 65.044 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 64.4332 | 64.4463 | 64.8164 | 65.7963 | 66.4506 | 67.0921 | 67.8427 | 68.537 | 69.212 | 69.2873 | 70.0755 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 55.8249 | 55.819 | 56.2179 | 56.6558 | 57.5556 | 58.2023 | 58.5524 | 58.9347 | 59.2853 | 59.9198 | 60.7077 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 60.1376 | 60.1499 | 60.4953 | 61.4099 | 62.0205 | 62.6193 | 63.3198 | 63.9678 | 64.5979 | 64.6681 | 65.4038 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 51.8374 | 51.8319 | 52.2024 | 52.609 | 53.4445 | 54.045 | 54.3701 | 54.7251 | 55.0506 | 55.6398 | 56.3714 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 55.8421 | 55.8534 | 56.1742 | 57.0235 | 57.5905 | 58.1465 | 58.797 | 59.3987 | 59.9837 | 60.049 | 60.7321 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 47.8499 | 47.8449 | 48.1868 | 48.5621 | 49.3334 | 49.8876 | 50.1878 | 50.5155 | 50.8159 | 51.3598 | 52.0352 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 51.5465 | 51.557 | 51.8531 | 52.6371 | 53.1605 | 53.6736 | 54.2741 | 54.8296 | 55.3696 | 55.4298 | 56.0604 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 43.8624 | 43.8578 | 44.1712 | 44.5153 | 45.2222 | 45.7303 | 46.0055 | 46.3059 | 46.5813 | 47.0798 | 47.6989 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 47.251 | 47.2606 | 47.532 | 48.2506 | 48.7304 | 49.2008 | 49.7513 | 50.2604 | 50.7555 | 50.8107 | 51.3887 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 39.8749 | 39.8707 | 40.1557 | 40.4684 | 41.1111 | 41.573 | 41.8231 | 42.0962 | 42.3466 | 42.7999 | 43.3626 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 42.9554 | 42.9642 | 43.211 | 43.8642 | 44.3004 | 44.728 | 45.2284 | 45.6913 | 46.1413 | 46.1915 | 46.717 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 35.8874 | 35.8837 | 36.1401 | 36.4216 | 37 | 37.4157 | 37.6408 | 37.8866 | 38.112 | 38.5199 | 39.0264 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 38.6599 | 38.6678 | 38.8899 | 39.4778 | 39.8703 | 40.2552 | 40.7056 | 41.1222 | 41.5272 | 41.5724 | 42.0453 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 31.8999 | 31.8966 | 32.1245 | 32.3748 | 32.8889 | 33.2584 | 33.4585 | 33.677 | 33.8773 | 34.2399 | 34.6901 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 34.3644 | 34.3713 | 34.5688 | 35.0914 | 35.4403 | 35.7824 | 36.1827 | 36.553 | 36.9131 | 36.9532 | 37.3736 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 27.9124 | 27.9095 | 28.109 | 28.3279 | 28.7778 | 29.1011 | 29.2762 | 29.4674 | 29.6426 | 29.9599 | 30.3538 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 30.0688 | 30.0749 | 30.2477 | 30.705 | 31.0103 | 31.3096 | 31.6599 | 31.9839 | 32.2989 | 32.3341 | 32.7019 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 23.9249 | 23.9224 | 24.0934 | 24.2811 | 24.6667 | 24.9438 | 25.0939 | 25.2577 | 25.408 | 25.6799 | 26.0176 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 25.7733 | 25.7785 | 25.9266 | 26.3185 | 26.5802 | 26.8368 | 27.1371 | 27.4148 | 27.6848 | 27.7149 | 28.0302 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 19.9375 | 19.9354 | 20.0778 | 20.2342 | 20.5556 | 20.7865 | 20.9116 | 21.0481 | 21.1733 | 21.3999 | 21.6813 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 21.4777 | 21.4821 | 21.6055 | 21.9321 | 22.1502 | 22.364 | 22.6142 | 22.8457 | 23.0707 | 23.0958 | 23.3585 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.95 | 15.9483 | 16.0623 | 16.1874 | 16.4445 | 16.6292 | 16.7293 | 16.8385 | 16.9386 | 17.1199 | 17.3451 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 17.1822 | 17.1857 | 17.2844 | 17.5457 | 17.7202 | 17.8912 | 18.0914 | 18.2765 | 18.4565 | 18.4766 | 18.6868 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.9625 | 11.9612 | 12.0467 | 12.1405 | 12.3333 | 12.4719 | 12.5469 | 12.6289 | 12.704 | 12.84 | 13.0088 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.8866 | 12.8893 | 12.9633 | 13.1593 | 13.2901 | 13.4184 | 13.5685 | 13.7074 | 13.8424 | 13.8575 | 14.0151 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.975 | 7.9741 | 8.0311 | 8.0937 | 8.2222 | 8.3146 | 8.3646 | 8.4192 | 8.4693 | 8.56 | 8.6725 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.5911 | 8.5928 | 8.6422 | 8.7728 | 8.8601 | 8.9456 | 9.0457 | 9.1383 | 9.2283 | 9.2383 | 9.3434 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.9875 | 3.9871 | 4.0156 | 4.0468 | 4.1111 | 4.1573 | 4.1823 | 4.2096 | 4.2347 | 4.28 | 4.3363 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.2955 | 4.2964 | 4.3211 | 4.3864 | 4.43 | 4.4728 | 4.5228 | 4.5691 | 4.6141 | 4.6192 | 4.6717 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.9686e-14 | 7.9678e-14 | 8.0247e-14 | 8.0872e-14 | 8.2157e-14 | 8.308e-14 | 8.3579e-14 | 8.4125e-14 | 8.4626e-14 | 8.5531e-14 | 8.6656e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.5842e-14 | 8.586e-14 | 8.6353e-14 | 8.7658e-14 | 8.853e-14 | 8.9385e-14 | 9.0385e-14 | 9.131e-14 | 9.2209e-14 | 9.2309e-14 | 9.3359e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14
Option 2
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 45.6663 | 46.3214 | 47.4563 | 50.0441 | 51.7726 | 53.9664 | 55.1029 | 56.1001 | 54.2461 | 56.4092 | 59.8125 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 49.0542 | 49.5557 | 50.6659 | 53.2942 | 54.7249 | 57.4587 | 65.7777 | 58.9092 | 57.5626 | 59.3699 | 63.3278 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 45.2097 | 45.8582 | 46.9818 | 49.5437 | 51.2549 | 53.4267 | 54.5519 | 55.5391 | 53.7036 | 55.8451 | 59.2143 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 48.5637 | 49.0601 | 50.1592 | 52.7612 | 54.1777 | 56.8841 | 65.12 | 58.3201 | 56.987 | 58.7762 | 62.6945 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 44.753 | 45.395 | 46.5072 | 49.0432 | 50.7372 | 52.8871 | 54.0009 | 54.9781 | 53.1612 | 55.281 | 58.6162 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 48.0731 | 48.5646 | 49.6526 | 52.2283 | 53.6304 | 56.3095 | 64.4622 | 57.731 | 56.4113 | 58.1825 | 62.0612 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 44.2963 | 44.9318 | 46.0327 | 48.5428 | 50.2195 | 52.3474 | 53.4498 | 54.4171 | 52.6187 | 54.717 | 58.0181 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 47.5826 | 48.069 | 49.1459 | 51.6954 | 53.0832 | 55.735 | 63.8044 | 57.1419 | 55.8357 | 57.5888 | 61.428 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 43.383 | 44.0053 | 45.0835 | 47.5419 | 49.184 | 51.2681 | 52.3478 | 53.2951 | 51.5338 | 53.5888 | 56.8218 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 46.6015 | 47.0779 | 48.1326 | 50.6295 | 51.9887 | 54.5858 | 62.4889 | 55.9638 | 54.6845 | 56.4014 | 60.1614 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 41.0997 | 41.6893 | 42.7107 | 45.0397 | 46.5954 | 48.5697 | 49.5926 | 50.4901 | 48.8215 | 50.7683 | 53.8312 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 44.1488 | 44.6001 | 45.5993 | 47.9648 | 49.2524 | 51.7128 | 59.2 | 53.0183 | 51.8063 | 53.4329 | 56.995 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 38.8164 | 39.3732 | 40.3379 | 42.5375 | 44.0067 | 45.8714 | 46.8375 | 47.6851 | 46.1092 | 47.9478 | 50.8406 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 41.6961 | 42.1223 | 43.066 | 45.3001 | 46.5162 | 48.8399 | 55.9111 | 50.0728 | 48.9282 | 50.4644 | 53.8286 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 36.5331 | 37.0571 | 37.9651 | 40.0353 | 41.4181 | 43.1731 | 44.0823 | 44.88 | 43.3969 | 45.1274 | 47.85 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 39.2434 | 39.6445 | 40.5327 | 42.6353 | 43.7799 | 45.967 | 52.6222 | 47.1274 | 46.0501 | 47.4959 | 50.6622 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 34.2497 | 34.7411 | 35.5923 | 37.5331 | 38.8295 | 40.4748 | 41.3272 | 42.075 | 40.6846 | 42.3069 | 44.8593 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 36.7907 | 37.1667 | 37.9994 | 39.9706 | 41.0437 | 43.094 | 49.3333 | 44.1819 | 43.1719 | 44.5274 | 47.4958 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 31.9664 | 32.425 | 33.2194 | 35.0309 | 36.2408 | 37.7765 | 38.5721 | 39.27 | 37.9723 | 39.4865 | 41.8687 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 34.338 | 34.689 | 35.4661 | 37.3059 | 38.3074 | 40.2211 | 46.0444 | 41.2365 | 40.2938 | 41.5589 | 44.3295 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 29.6831 | 30.1089 | 30.8466 | 32.5287 | 33.6522 | 35.0782 | 35.8169 | 36.465 | 35.26 | 36.666 | 38.8781 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 31.8852 | 32.2112 | 32.9328 | 34.6412 | 35.5712 | 37.3482 | 42.7555 | 38.291 | 37.4157 | 38.5905 | 41.1631 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 27.3998 | 27.7928 | 28.4738 | 30.0265 | 31.0636 | 32.3798 | 33.0618 | 33.66 | 32.5477 | 33.8455 | 35.8875 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 29.4325 | 29.7334 | 30.3995 | 31.9765 | 32.835 | 34.4752 | 39.4666 | 35.3455 | 34.5376 | 35.622 | 37.9967 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 25.1165 | 25.4768 | 26.101 | 27.5243 | 28.475 | 29.6815 | 30.3066 | 30.855 | 29.8354 | 31.0251 | 32.8969 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 26.9798 | 27.2556 | 27.8662 | 29.3118 | 30.0987 | 31.6023 | 36.1778 | 32.4001 | 31.6594 | 32.6535 | 34.8303 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 22.8332 | 23.1607 | 23.7282 | 25.0221 | 25.8863 | 26.9832 | 27.5515 | 28.05 | 27.123 | 28.2046 | 29.9062 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 24.5271 | 24.7778 | 25.333 | 26.6471 | 27.3625 | 28.7294 | 32.8889 | 29.4546 | 28.7813 | 29.685 | 31.6639 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 20.5498 | 20.8446 | 21.3554 | 22.5199 | 23.2977 | 24.2849 | 24.7963 | 25.245 | 24.4107 | 25.3842 | 26.9156 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 22.0744 | 22.3 | 22.7997 | 23.9824 | 24.6262 | 25.8564 | 29.6 | 26.5091 | 25.9032 | 26.7165 | 28.4975 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 18.2665 | 18.5286 | 18.9825 | 20.0176 | 20.7091 | 21.5866 | 22.0412 | 22.44 | 21.6984 | 22.5637 | 23.925 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 19.6217 | 19.8223 | 20.2664 | 21.3177 | 21.89 | 22.9835 | 26.3111 | 23.5637 | 23.025 | 23.748 | 25.3311 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 15.9832 | 16.2125 | 16.6097 | 17.5154 | 18.1204 | 18.8882 | 19.286 | 19.635 | 18.9861 | 19.7432 | 20.9344 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 17.169 | 17.3445 | 17.7331 | 18.653 | 19.1537 | 20.1106 | 23.0222 | 20.6182 | 20.1469 | 20.7795 | 22.1647 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 13.6999 | 13.8964 | 14.2369 | 15.0132 | 15.5318 | 16.1899 | 16.5309 | 16.83 | 16.2738 | 16.9228 | 17.9437 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 14.7163 | 14.8667 | 15.1998 | 15.9883 | 16.4175 | 17.2376 | 19.7333 | 17.6728 | 17.2688 | 17.811 | 18.9983 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 11.4166 | 11.5804 | 11.8641 | 12.511 | 12.9432 | 13.4916 | 13.7757 | 14.025 | 13.5615 | 14.1023 | 14.9531 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 12.2636 | 12.3889 | 12.6665 | 13.3235 | 13.6812 | 14.3647 | 16.4444 | 14.7273 | 14.3906 | 14.8425 | 15.8319 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 9.1333 | 9.2643 | 9.4913 | 10.0088 | 10.3545 | 10.7933 | 11.0206 | 11.22 | 10.8492 | 11.2818 | 11.9625 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 9.8108 | 9.9111 | 10.1332 | 10.6588 | 10.945 | 11.4917 | 13.1555 | 11.7818 | 11.5125 | 11.874 | 12.6656 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 6.8499 | 6.9482 | 7.1185 | 7.5066 | 7.7659 | 8.095 | 8.2654 | 8.415 | 8.1369 | 8.4614 | 8.9719 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 7.3581 | 7.4333 | 7.5999 | 7.9941 | 8.2087 | 8.6188 | 9.8667 | 8.8364 | 8.6344 | 8.9055 | 9.4992 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 4.5666 | 4.6321 | 4.7456 | 5.0044 | 5.1773 | 5.3966 | 5.5103 | 5.61 | 5.4246 | 5.6409 | 5.9812 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 4.9054 | 4.9556 | 5.0666 | 5.3294 | 5.4725 | 5.7459 | 6.5778 | 5.8909 | 5.7563 | 5.937 | 6.3328 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 2.2833 | 2.3161 | 2.3728 | 2.5022 | 2.5886 | 2.6983 | 2.7551 | 2.805 | 2.7123 | 2.8205 | 2.9906 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 2.4527 | 2.4778 | 2.5333 | 2.6647 | 2.7362 | 2.8729 | 3.2889 | 2.9455 | 2.8781 | 2.9685 | 3.1664 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 4.563e-14 | 4.6284e-14 | 4.7418e-14 | 5.0004e-14 | 5.1731e-14 | 5.3923e-14 | 5.5059e-14 | 5.6055e-14 | 5.4203e-14 | 5.6364e-14 | 5.9765e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 4.9015e-14 | 4.9516e-14 | 5.0625e-14 | 5.3252e-14 | 5.4681e-14 | 5.7413e-14 | 6.5725e-14 | 5.8862e-14 | 5.7517e-14 | 5.9322e-14 | 6.3277e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 50.7498 | 50.7414 | 51.3113 | 51.9369 | 53.2223 | 54.1461 | 54.6463 | 55.1925 | 55.6932 | 56.5997 | 57.7253 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 56.9109 | 56.9284 | 57.4219 | 58.7284 | 59.6008 | 60.4561 | 61.4569 | 62.3826 | 63.2827 | 63.383 | 64.434 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 50.2423 | 50.234 | 50.7982 | 51.4175 | 52.69 | 53.6046 | 54.0998 | 54.6406 | 55.1363 | 56.0337 | 57.148 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 56.3418 | 56.3591 | 56.8477 | 58.1412 | 59.0048 | 59.8515 | 60.8423 | 61.7588 | 62.6498 | 62.7492 | 63.7896 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961
98% | 0 | 55.3193 | 73.3854 | 78.3 | 49.7348 | 49.7266 | 50.2851 | 50.8981 | 52.1578 | 53.0632 | 53.5534 | 54.0886 | 54.5794 | 55.4677 | 56.5708 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 55.7727 | 55.7898 | 56.2735 | 57.5539 | 58.4087 | 59.247 | 60.2277 | 61.135 | 62.017 | 62.1154 | 63.1453 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 49.2273 | 49.2192 | 49.772 | 50.3788 | 51.6256 | 52.5217 | 53.0069 | 53.5367 | 54.0224 | 54.9017 | 55.9935 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 55.2036 | 55.2205 | 55.6992 | 56.9666 | 57.8127 | 58.6424 | 59.6132 | 60.5111 | 61.3842 | 61.4815 | 62.501 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 48.2123 | 48.2044 | 48.7458 | 49.34 | 50.5612 | 51.4388 | 51.914 | 52.4329 | 52.9086 | 53.7697 | 54.839 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 54.0653 | 54.082 | 54.5508 | 55.792 | 56.6207 | 57.4333 | 58.384 | 59.2635 | 60.1185 | 60.2139 | 61.2123 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 45.6748 | 45.6673 | 46.1802 | 46.7432 | 47.9 | 48.7315 | 49.1817 | 49.6732 | 50.1239 | 50.9397 | 51.9527 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 51.2198 | 51.2355 | 51.6797 | 52.8556 | 53.6407 | 54.4105 | 55.3112 | 56.1444 | 56.9544 | 57.0447 | 57.9906 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 43.1374 | 43.1302 | 43.6146 | 44.1463 | 45.2389 | 46.0242 | 46.4494 | 46.9136 | 47.3393 | 48.1098 | 49.0665 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 48.3743 | 48.3891 | 48.8086 | 49.9192 | 50.6606 | 51.3877 | 52.2383 | 53.0252 | 53.7903 | 53.8756 | 54.7689 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 40.5999 | 40.5932 | 41.0491 | 41.5495 | 42.5778 | 43.3169 | 43.717 | 44.154 | 44.5546 | 45.2798 | 46.1802 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 45.5287 | 45.5427 | 45.9375 | 46.9827 | 47.6806 | 48.3649 | 49.1655 | 49.9061 | 50.6261 | 50.7064 | 51.5472 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 38.0624 | 38.0561 | 38.4835 | 38.9527 | 39.9167 | 40.6096 | 40.9847 | 41.3944 | 41.7699 | 42.4498 | 43.294 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 42.6832 | 42.6963 | 43.0664 | 44.0463 | 44.7006 | 45.3421 | 46.0927 | 46.787 | 47.462 | 47.5373 | 48.3255 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 35.5249 | 35.519 | 35.9179 | 36.3558 | 37.2556 | 37.9023 | 38.2524 | 38.6347 | 38.9853 | 39.6198 | 40.4077 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 39.8376 | 39.8499 | 40.1953 | 41.1099 | 41.7205 | 42.3193 | 43.0198 | 43.6678 | 44.2979 | 44.3681 | 45.1038 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 32.9874 | 32.9819 | 33.3524 | 33.759 | 34.5945 | 35.195 | 35.5201 | 35.8751 | 36.2006 | 36.7898 | 37.5214 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 36.9921 | 37.0034 | 37.3242 | 38.1735 | 38.7405 | 39.2965 | 39.947 | 40.5487 | 41.1337 | 41.199 | 41.8821 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 30.4499 | 30.4449 | 30.7868 | 31.1621 | 31.9334 | 32.4876 | 32.7878 | 33.1155 | 33.4159 | 33.9598 | 34.6352 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 34.1465 | 34.157 | 34.4531 | 35.2371 | 35.7605 | 36.2736 | 36.8741 | 37.4296 | 37.9696 | 38.0298 | 38.6604 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 27.9124 | 27.9078 | 28.2212 | 28.5653 | 29.2722 | 29.7803 | 30.0555 | 30.3559 | 30.6313 | 31.1298 | 31.7489 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 31.301 | 31.3106 | 31.582 | 32.3006 | 32.7804 | 33.2508 | 33.8013 | 34.3104 | 34.8055 | 34.8607 | 35.4387 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 25.3749 | 25.3707 | 25.6557 | 25.9684 | 26.6111 | 27.073 | 27.3231 | 27.5962 | 27.8466 | 28.2999 | 28.8626 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 28.4554 | 28.4642 | 28.711 | 29.3642 | 29.8004 | 30.228 | 30.7284 | 31.1913 | 31.6413 | 31.6915 | 32.217 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 22.8374 | 22.8337 | 23.0901 | 23.3716 | 23.95 | 24.3657 | 24.5908 | 24.8366 | 25.062 | 25.4699 | 25.9764 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 25.6099 | 25.6178 | 25.8399 | 26.4278 | 26.8203 | 27.2052 | 27.6556 | 28.0722 | 28.4772 | 28.5224 | 28.9953 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 20.2999 | 20.2966 | 20.5245 | 20.7748 | 21.2889 | 21.6584 | 21.8585 | 22.077 | 22.2773 | 22.6399 | 23.0901 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 22.7644 | 22.7713 | 22.9688 | 23.4914 | 23.8403 | 24.1824 | 24.5827 | 24.953 | 25.3131 | 25.3532 | 25.7736 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 17.7624 | 17.7595 | 17.959 | 18.1779 | 18.6278 | 18.9511 | 19.1262 | 19.3174 | 19.4926 | 19.8099 | 20.2038 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 19.9188 | 19.9249 | 20.0977 | 20.555 | 20.8603 | 21.1596 | 21.5099 | 21.8339 | 22.1489 | 22.1841 | 22.5519 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 15.2249 | 15.2224 | 15.3934 | 15.5811 | 15.9667 | 16.2438 | 16.3939 | 16.5577 | 16.708 | 16.9799 | 17.3176 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 17.0733 | 17.0785 | 17.2266 | 17.6185 | 17.8802 | 18.1368 | 18.4371 | 18.7148 | 18.9848 | 19.0149 | 19.3302 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 12.6875 | 12.6854 | 12.8278 | 12.9842 | 13.3056 | 13.5365 | 13.6616 | 13.7981 | 13.9233 | 14.1499 | 14.4313 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 14.2277 | 14.2321 | 14.3555 | 14.6821 | 14.9002 | 15.114 | 15.3642 | 15.5957 | 15.8207 | 15.8458 | 16.1085 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 10.15 | 10.1483 | 10.2623 | 10.3874 | 10.6445 | 10.8292 | 10.9293 | 11.0385 | 11.1386 | 11.3199 | 11.5451 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 11.3822 | 11.3857 | 11.4844 | 11.7457 | 11.9202 | 12.0912 | 12.2914 | 12.4765 | 12.6565 | 12.6766 | 12.8868 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 7.6125 | 7.6112 | 7.6967 | 7.7905 | 7.9833 | 8.1219 | 8.1969 | 8.2789 | 8.354 | 8.49 | 8.6588 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 8.5366 | 8.5393 | 8.6133 | 8.8093 | 8.9401 | 9.0684 | 9.2185 | 9.3574 | 9.4924 | 9.5075 | 9.6651 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 5.075 | 5.0741 | 5.1311 | 5.1937 | 5.3222 | 5.4146 | 5.4646 | 5.5192 | 5.5693 | 5.66 | 5.7725 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 5.6911 | 5.6928 | 5.7422 | 5.8728 | 5.9601 | 6.0456 | 6.1457 | 6.2383 | 6.3283 | 6.3383 | 6.4434 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 2.5375 | 2.5371 | 2.5656 | 2.5968 | 2.6611 | 2.7073 | 2.7323 | 2.7596 | 2.7847 | 2.83 | 2.8863 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 2.8455 | 2.8464 | 2.8711 | 2.9364 | 2.98 | 3.0228 | 3.0728 | 3.1191 | 3.1641 | 3.1692 | 3.2217 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 5.0709e-14 | 5.0701e-14 | 5.127e-14 | 5.1895e-14 | 5.318e-14 | 5.4103e-14 | 5.4603e-14 | 5.5148e-14 | 5.5649e-14 | 5.6554e-14 | 5.7679e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 5.6865e-14 | 5.6883e-14 | 5.7376e-14 | 5.8681e-14 | 5.9553e-14 | 6.0408e-14 | 6.1408e-14 | 6.2333e-14 | 6.3232e-14 | 6.3332e-14 | 6.4382e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14
Option 3
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 73.9197 | 74.5682 | 75.6918 | 78.2537 | 79.9649 | 82.1367 | 83.2619 | 84.2491 | 82.4136 | 84.5551 | 87.9243 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 77.2737 | 77.7701 | 78.8692 | 81.4712 | 82.8877 | 85.5941 | 93.83 | 87.0301 | 85.697 | 87.4862 | 91.4045 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 73.173 | 73.815 | 74.9272 | 77.4632 | 79.1572 | 81.3071 | 82.4209 | 83.3981 | 81.5812 | 83.701 | 87.0362 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 76.4931 | 76.9846 | 78.0726 | 80.6483 | 82.0504 | 84.7295 | 92.8822 | 86.151 | 84.8313 | 86.6025 | 90.4812 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 72.4263 | 73.0618 | 74.1627 | 76.6728 | 78.3495 | 80.4774 | 81.5798 | 82.5471 | 80.7487 | 82.847 | 86.1481 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 75.7126 | 76.199 | 77.2759 | 79.8254 | 81.2132 | 83.865 | 91.9344 | 85.2719 | 83.9657 | 85.7188 | 89.558 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 70.933 | 71.5553 | 72.6335 | 75.0919 | 76.734 | 78.8181 | 79.8978 | 80.8451 | 79.0838 | 81.1388 | 84.3718 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 74.1515 | 74.6279 | 75.6826 | 78.1795 | 79.5387 | 82.1358 | 90.0389 | 83.5138 | 82.2345 | 83.9514 | 87.7114 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 67.1997 | 67.7893 | 68.8107 | 71.1397 | 72.6954 | 74.6697 | 75.6926 | 76.5901 | 74.9215 | 76.8683 | 79.9312 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 70.2488 | 70.7001 | 71.6993 | 74.0648 | 75.3524 | 77.8128 | 85.3 | 79.1183 | 77.9063 | 79.5329 | 83.095 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 63.4664 | 64.0232 | 64.9879 | 67.1875 | 68.6567 | 70.5214 | 71.4875 | 72.3351 | 70.7592 | 72.5978 | 75.4906 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 66.3461 | 66.7723 | 67.716 | 69.9501 | 71.1662 | 73.4899 | 80.5611 | 74.7228 | 73.5782 | 75.1144 | 78.4786 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 59.7331 | 60.2571 | 61.1651 | 63.2353 | 64.6181 | 66.3731 | 67.2823 | 68.08 | 66.5969 | 68.3274 | 71.05 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 62.4434 | 62.8445 | 63.7327 | 65.8353 | 66.9799 | 69.167 | 75.8222 | 70.3274 | 69.2501 | 70.6959 | 73.8622 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 55.9997 | 56.4911 | 57.3423 | 59.2831 | 60.5795 | 62.2248 | 63.0772 | 63.825 | 62.4346 | 64.0569 | 66.6093 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 58.5407 | 58.9167 | 59.7494 | 61.7206 | 62.7937 | 64.844 | 71.0833 | 65.9319 | 64.9219 | 66.2774 | 69.2458 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 52.2664 | 52.725 | 53.5194 | 55.3309 | 56.5408 | 58.0765 | 58.8721 | 59.57 | 58.2723 | 59.7865 | 62.1687 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 54.638 | 54.989 | 55.7661 | 57.6059 | 58.6074 | 60.5211 | 66.3444 | 61.5365 | 60.5938 | 61.8589 | 64.6295 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 48.5331 | 48.9589 | 49.6966 | 51.3787 | 52.5022 | 53.9282 | 54.6669 | 55.315 | 54.11 | 55.516 | 57.7281 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 50.7352 | 51.0612 | 51.7828 | 53.4912 | 54.4212 | 56.1982 | 61.6055 | 57.141 | 56.2657 | 57.4405 | 60.0131 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 44.7998 | 45.1928 | 45.8738 | 47.4265 | 48.4636 | 49.7798 | 50.4618 | 51.06 | 49.9477 | 51.2455 | 53.2875 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 46.8325 | 47.1334 | 47.7995 | 49.3765 | 50.235 | 51.8752 | 56.8666 | 52.7455 | 51.9376 | 53.022 | 55.3967 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 41.0665 | 41.4268 | 42.051 | 43.4743 | 44.425 | 45.6315 | 46.2566 | 46.805 | 45.7854 | 46.9751 | 48.8469 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 42.9298 | 43.2056 | 43.8162 | 45.2618 | 46.0487 | 47.5523 | 52.1278 | 48.3501 | 47.6094 | 48.6035 | 50.7803 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 37.3332 | 37.6607 | 38.2282 | 39.5221 | 40.3863 | 41.4832 | 42.0515 | 42.55 | 41.623 | 42.7046 | 44.4062 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 39.0271 | 39.2778 | 39.833 | 41.1471 | 41.8625 | 43.2294 | 47.3889 | 43.9546 | 43.2813 | 44.185 | 46.1639 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 33.5998 | 33.8946 | 34.4054 | 35.5699 | 36.3477 | 37.3349 | 37.8463 | 38.295 | 37.4607 | 38.4342 | 39.9656 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 35.1244 | 35.35 | 35.8497 | 37.0324 | 37.6762 | 38.9064 | 42.65 | 39.5591 | 38.9532 | 39.7665 | 41.5475 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 29.8665 | 30.1286 | 30.5825 | 31.6176 | 32.3091 | 33.1866 | 33.6412 | 34.04 | 33.2984 | 34.1637 | 35.525 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 31.2217 | 31.4223 | 31.8664 | 32.9177 | 33.49 | 34.5835 | 37.9111 | 35.1637 | 34.625 | 35.348 | 36.9311 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 26.1332 | 26.3625 | 26.7597 | 27.6654 | 28.2704 | 29.0382 | 29.436 | 29.785 | 29.1361 | 29.8932 | 31.0844 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 27.319 | 27.4945 | 27.8831 | 28.803 | 29.3037 | 30.2606 | 33.1722 | 30.7682 | 30.2969 | 30.9295 | 32.3147 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 22.3999 | 22.5964 | 22.9369 | 23.7132 | 24.2318 | 24.8899 | 25.2309 | 25.53 | 24.9738 | 25.6228 | 26.6437 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 23.4163 | 23.5667 | 23.8998 | 24.6883 | 25.1175 | 25.9376 | 28.4333 | 26.3728 | 25.9688 | 26.511 | 27.6983 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 18.6666 | 18.8304 | 19.1141 | 19.761 | 20.1932 | 20.7416 | 21.0257 | 21.275 | 20.8115 | 21.3523 | 22.2031 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 19.5136 | 19.6389 | 19.9165 | 20.5735 | 20.9312 | 21.6147 | 23.6944 | 21.9773 | 21.6406 | 22.0925 | 23.0819 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.9333 | 15.0643 | 15.2913 | 15.8088 | 16.1545 | 16.5933 | 16.8206 | 17.02 | 16.6492 | 17.0818 | 17.7625 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 15.6108 | 15.7111 | 15.9332 | 16.4588 | 16.745 | 17.2917 | 18.9555 | 17.5818 | 17.3125 | 17.674 | 18.4656 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 11.1999 | 11.2982 | 11.4685 | 11.8566 | 12.1159 | 12.445 | 12.6154 | 12.765 | 12.4869 | 12.8114 | 13.3219 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.7081 | 11.7833 | 11.9499 | 12.3441 | 12.5587 | 12.9688 | 14.2167 | 13.1864 | 12.9844 | 13.2555 | 13.8492 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.4666 | 7.5321 | 7.6456 | 7.9044 | 8.0773 | 8.2966 | 8.4103 | 8.51 | 8.3246 | 8.5409 | 8.8812 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.8054 | 7.8556 | 7.9666 | 8.2294 | 8.3725 | 8.6459 | 9.4778 | 8.7909 | 8.6563 | 8.837 | 9.2328 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.7333 | 3.7661 | 3.8228 | 3.9522 | 4.0386 | 4.1483 | 4.2051 | 4.255 | 4.1623 | 4.2705 | 4.4406 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.9027 | 3.9278 | 3.9833 | 4.1147 | 4.1862 | 4.3229 | 4.7389 | 4.3955 | 4.3281 | 4.4185 | 4.6164 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.4607e-14 | 7.5261e-14 | 7.6395e-14 | 7.8981e-14 | 8.0708e-14 | 8.29e-14 | 8.4036e-14 | 8.5032e-14 | 8.318e-14 | 8.5341e-14 | 8.8741e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.7992e-14 | 7.8493e-14 | 7.9602e-14 | 8.2228e-14 | 8.3658e-14 | 8.639e-14 | 9.4702e-14 | 8.7839e-14 | 8.6493e-14 | 8.8299e-14 | 9.2254e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 78.9523 | 78.944 | 79.5082 | 80.1275 | 81.4 | 82.3146 | 82.8098 | 83.3506 | 83.8463 | 84.7437 | 85.858 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 85.0518 | 85.0691 | 85.5577 | 86.8512 | 87.7148 | 88.5615 | 89.5523 | 90.4688 | 91.3598 | 91.4592 | 92.4996 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061
98% | 0 | 55.3193 | 73.3854 | 78.3 | 78.1548 | 78.1466 | 78.7051 | 79.3181 | 80.5778 | 81.4832 | 81.9734 | 82.5086 | 82.9994 | 83.8877 | 84.9908 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 84.1927 | 84.2098 | 84.6935 | 85.9739 | 86.8287 | 87.667 | 88.6477 | 89.555 | 90.437 | 90.5354 | 91.5653 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 77.3573 | 77.3492 | 77.902 | 78.5088 | 79.7556 | 80.6517 | 81.1369 | 81.6667 | 82.1524 | 83.0317 | 84.1235 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 83.3336 | 83.3505 | 83.8292 | 85.0966 | 85.9427 | 86.7724 | 87.7432 | 88.6411 | 89.5142 | 89.6115 | 90.631 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 75.7623 | 75.7544 | 76.2958 | 76.89 | 78.1112 | 78.9888 | 79.464 | 79.9829 | 80.4586 | 81.3197 | 82.389 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 81.6153 | 81.632 | 82.1008 | 83.342 | 84.1707 | 84.9833 | 85.934 | 86.8135 | 87.6685 | 87.7639 | 88.7623 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 71.7748 | 71.7673 | 72.2802 | 72.8432 | 74 | 74.8315 | 75.2817 | 75.7732 | 76.2239 | 77.0397 | 78.0527 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 77.3198 | 77.3355 | 77.7797 | 78.9556 | 79.7407 | 80.5105 | 81.4112 | 82.2444 | 83.0544 | 83.1447 | 84.0906 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 67.7874 | 67.7802 | 68.2646 | 68.7963 | 69.8889 | 70.6742 | 71.0994 | 71.5636 | 71.9893 | 72.7598 | 73.7165 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 73.0243 | 73.0391 | 73.4586 | 74.5692 | 75.3106 | 76.0377 | 76.8883 | 77.6752 | 78.4403 | 78.5256 | 79.4189 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 63.7999 | 63.7932 | 64.2491 | 64.7495 | 65.7778 | 66.5169 | 66.917 | 67.354 | 67.7546 | 68.4798 | 69.3802 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 68.7287 | 68.7427 | 69.1375 | 70.1827 | 70.8806 | 71.5649 | 72.3655 | 73.1061 | 73.8261 | 73.9064 | 74.7472 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 59.8124 | 59.8061 | 60.2335 | 60.7027 | 61.6667 | 62.3596 | 62.7347 | 63.1444 | 63.5199 | 64.1998 | 65.044 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 64.4332 | 64.4463 | 64.8164 | 65.7963 | 66.4506 | 67.0921 | 67.8427 | 68.537 | 69.212 | 69.2873 | 70.0755 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 55.8249 | 55.819 | 56.2179 | 56.6558 | 57.5556 | 58.2023 | 58.5524 | 58.9347 | 59.2853 | 59.9198 | 60.7077 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 60.1376 | 60.1499 | 60.4953 | 61.4099 | 62.0205 | 62.6193 | 63.3198 | 63.9678 | 64.5979 | 64.6681 | 65.4038 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 51.8374 | 51.8319 | 52.2024 | 52.609 | 53.4445 | 54.045 | 54.3701 | 54.7251 | 55.0506 | 55.6398 | 56.3714 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 55.8421 | 55.8534 | 56.1742 | 57.0235 | 57.5905 | 58.1465 | 58.797 | 59.3987 | 59.9837 | 60.049 | 60.7321 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 47.8499 | 47.8449 | 48.1868 | 48.5621 | 49.3334 | 49.8876 | 50.1878 | 50.5155 | 50.8159 | 51.3598 | 52.0352 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 51.5465 | 51.557 | 51.8531 | 52.6371 | 53.1605 | 53.6736 | 54.2741 | 54.8296 | 55.3696 | 55.4298 | 56.0604 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 43.8624 | 43.8578 | 44.1712 | 44.5153 | 45.2222 | 45.7303 | 46.0055 | 46.3059 | 46.5813 | 47.0798 | 47.6989 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 47.251 | 47.2606 | 47.532 | 48.2506 | 48.7304 | 49.2008 | 49.7513 | 50.2604 | 50.7555 | 50.8107 | 51.3887 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 39.8749 | 39.8707 | 40.1557 | 40.4684 | 41.1111 | 41.573 | 41.8231 | 42.0962 | 42.3466 | 42.7999 | 43.3626 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 42.9554 | 42.9642 | 43.211 | 43.8642 | 44.3004 | 44.728 | 45.2284 | 45.6913 | 46.1413 | 46.1915 | 46.717 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 35.8874 | 35.8837 | 36.1401 | 36.4216 | 37 | 37.4157 | 37.6408 | 37.8866 | 38.112 | 38.5199 | 39.0264 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 38.6599 | 38.6678 | 38.8899 | 39.4778 | 39.8703 | 40.2552 | 40.7056 | 41.1222 | 41.5272 | 41.5724 | 42.0453 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 31.8999 | 31.8966 | 32.1245 | 32.3748 | 32.8889 | 33.2584 | 33.4585 | 33.677 | 33.8773 | 34.2399 | 34.6901 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 34.3644 | 34.3713 | 34.5688 | 35.0914 | 35.4403 | 35.7824 | 36.1827 | 36.553 | 36.9131 | 36.9532 | 37.3736 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 27.9124 | 27.9095 | 28.109 | 28.3279 | 28.7778 | 29.1011 | 29.2762 | 29.4674 | 29.6426 | 29.9599 | 30.3538 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 30.0688 | 30.0749 | 30.2477 | 30.705 | 31.0103 | 31.3096 | 31.6599 | 31.9839 | 32.2989 | 32.3341 | 32.7019 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 23.9249 | 23.9224 | 24.0934 | 24.2811 | 24.6667 | 24.9438 | 25.0939 | 25.2577 | 25.408 | 25.6799 | 26.0176 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 25.7733 | 25.7785 | 25.9266 | 26.3185 | 26.5802 | 26.8368 | 27.1371 | 27.4148 | 27.6848 | 27.7149 | 28.0302 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 19.9375 | 19.9354 | 20.0778 | 20.2342 | 20.5556 | 20.7865 | 20.9116 | 21.0481 | 21.1733 | 21.3999 | 21.6813 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 21.4777 | 21.4821 | 21.6055 | 21.9321 | 22.1502 | 22.364 | 22.6142 | 22.8457 | 23.0707 | 23.0958 | 23.3585 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.95 | 15.9483 | 16.0623 | 16.1874 | 16.4445 | 16.6292 | 16.7293 | 16.8385 | 16.9386 | 17.1199 | 17.3451 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 17.1822 | 17.1857 | 17.2844 | 17.5457 | 17.7202 | 17.8912 | 18.0914 | 18.2765 | 18.4565 | 18.4766 | 18.6868 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.9625 | 11.9612 | 12.0467 | 12.1405 | 12.3333 | 12.4719 | 12.5469 | 12.6289 | 12.704 | 12.84 | 13.0088 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.8866 | 12.8893 | 12.9633 | 13.1593 | 13.2901 | 13.4184 | 13.5685 | 13.7074 | 13.8424 | 13.8575 | 14.0151 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.975 | 7.9741 | 8.0311 | 8.0937 | 8.2222 | 8.3146 | 8.3646 | 8.4192 | 8.4693 | 8.56 | 8.6725 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.5911 | 8.5928 | 8.6422 | 8.7728 | 8.8601 | 8.9456 | 9.0457 | 9.1383 | 9.2283 | 9.2383 | 9.3434 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.9875 | 3.9871 | 4.0156 | 4.0468 | 4.1111 | 4.1573 | 4.1823 | 4.2096 | 4.2347 | 4.28 | 4.3363 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.2955 | 4.2964 | 4.3211 | 4.3864 | 4.43 | 4.4728 | 4.5228 | 4.5691 | 4.6141 | 4.6192 | 4.6717 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.9686e-14 | 7.9678e-14 | 8.0247e-14 | 8.0872e-14 | 8.2157e-14 | 8.308e-14 | 8.3579e-14 | 8.4125e-14 | 8.4626e-14 | 8.5531e-14 | 8.6656e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.5842e-14 | 8.586e-14 | 8.6353e-14 | 8.7658e-14 | 8.853e-14 | 8.9385e-14 | 9.0385e-14 | 9.131e-14 | 9.2209e-14 | 9.2309e-14 | 9.3359e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14
Option 4
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 60.1663 | 60.8214 | 61.9563 | 64.5441 | 66.2726 | 68.4664 | 69.6029 | 70.6001 | 68.7461 | 70.9092 | 74.3125 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 71.7221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 63.5542 | 64.0557 | 65.1659 | 67.7942 | 69.2249 | 71.9587 | 80.2777 | 73.4092 | 72.0626 | 73.8699 | 77.8278 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413 | 75.1413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 59.5647 | 60.2132 | 61.3368 | 63.8987 | 65.6099 | 67.7817 | 68.9069 | 69.8941 | 68.0586 | 70.2001 | 73.5693 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 71.0048 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 62.9187 | 63.4151 | 64.5142 | 67.1162 | 68.5327 | 71.2391 | 79.475 | 72.6751 | 71.342 | 73.1312 | 77.0495 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899 | 74.3899
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 58.963 | 59.605 | 60.7172 | 63.2532 | 64.9472 | 67.0971 | 68.2109 | 69.1881 | 67.3712 | 69.491 | 72.8262 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 70.2876 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 62.2831 | 62.7746 | 63.8626 | 66.4383 | 67.8404 | 70.5195 | 78.6722 | 71.941 | 70.6213 | 72.3925 | 76.2712 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385 | 73.6385
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 58.3613 | 58.9968 | 60.0977 | 62.6078 | 64.2845 | 66.4124 | 67.5148 | 68.4821 | 66.6837 | 68.782 | 72.0831 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 69.5704 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 61.6476 | 62.134 | 63.2109 | 65.7604 | 67.1482 | 69.8 | 77.8694 | 71.2069 | 69.9007 | 71.6538 | 75.493 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871 | 72.8871
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 57.158 | 57.7803 | 58.8585 | 61.3169 | 62.959 | 65.0431 | 66.1228 | 67.0701 | 65.3088 | 67.3638 | 70.5968 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 68.136 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 60.3765 | 60.8529 | 61.9076 | 64.4045 | 65.7637 | 68.3608 | 76.2639 | 69.7388 | 68.4595 | 70.1764 | 73.9364 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842 | 71.3842
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 54.1497 | 54.7393 | 55.7607 | 58.0897 | 59.6454 | 61.6197 | 62.6426 | 63.5401 | 61.8715 | 63.8183 | 66.8812 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 64.5499 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 57.1988 | 57.6501 | 58.6493 | 61.0148 | 62.3024 | 64.7628 | 72.25 | 66.0683 | 64.8563 | 66.4829 | 70.045 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272 | 67.6272
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 51.1414 | 51.6982 | 52.6629 | 54.8625 | 56.3317 | 58.1964 | 59.1625 | 60.0101 | 58.4342 | 60.2728 | 63.1656 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 60.9638 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 54.0211 | 54.4473 | 55.391 | 57.6251 | 58.8412 | 61.1649 | 68.2361 | 62.3978 | 61.2532 | 62.7894 | 66.1536 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701 | 63.8701
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 48.1331 | 48.6571 | 49.5651 | 51.6353 | 53.0181 | 54.7731 | 55.6823 | 56.48 | 54.9969 | 56.7274 | 59.45 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 57.3777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 50.8434 | 51.2445 | 52.1327 | 54.2353 | 55.3799 | 57.567 | 64.2222 | 58.7274 | 57.6501 | 59.0959 | 62.2622 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131 | 60.1131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 45.1247 | 45.6161 | 46.4673 | 48.4081 | 49.7045 | 51.3498 | 52.2022 | 52.95 | 51.5596 | 53.1819 | 55.7343 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 53.7915 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 47.6657 | 48.0417 | 48.8744 | 50.8456 | 51.9187 | 53.969 | 60.2083 | 55.0569 | 54.0469 | 55.4024 | 58.3708 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356 | 56.356
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 42.1164 | 42.575 | 43.3694 | 45.1809 | 46.3908 | 47.9265 | 48.7221 | 49.42 | 48.1223 | 49.6365 | 52.0187 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 50.2054 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 44.488 | 44.839 | 45.6161 | 47.4559 | 48.4574 | 50.3711 | 56.1944 | 51.3865 | 50.4438 | 51.7089 | 54.4795 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989 | 52.5989
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 39.1081 | 39.5339 | 40.2716 | 41.9537 | 43.0772 | 44.5032 | 45.2419 | 45.89 | 44.685 | 46.091 | 48.3031 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 46.6193 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 41.3102 | 41.6362 | 42.3578 | 44.0662 | 44.9962 | 46.7732 | 52.1805 | 47.716 | 46.8407 | 48.0155 | 50.5881 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419 | 48.8419
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 36.0998 | 36.4928 | 37.1738 | 38.7265 | 39.7636 | 41.0798 | 41.7618 | 42.36 | 41.2477 | 42.5455 | 44.5875 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 43.0332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 38.1325 | 38.4334 | 39.0995 | 40.6765 | 41.535 | 43.1752 | 48.1666 | 44.0455 | 43.2376 | 44.322 | 46.6967 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848 | 45.0848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 33.0915 | 33.4518 | 34.076 | 35.4993 | 36.45 | 37.6565 | 38.2816 | 38.83 | 37.8104 | 39.0001 | 40.8719 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 39.4471 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 34.9548 | 35.2306 | 35.8412 | 37.2868 | 38.0737 | 39.5773 | 44.1528 | 40.3751 | 39.6344 | 40.6285 | 42.8053 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277 | 41.3277
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 30.0832 | 30.4107 | 30.9782 | 32.2721 | 33.1363 | 34.2332 | 34.8015 | 35.3 | 34.373 | 35.4546 | 37.1562 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 35.861 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 31.7771 | 32.0278 | 32.583 | 33.8971 | 34.6125 | 35.9794 | 40.1389 | 36.7046 | 36.0313 | 36.935 | 38.9139 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707 | 37.5707
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 27.0748 | 27.3696 | 27.8804 | 29.0449 | 29.8227 | 30.8099 | 31.3213 | 31.77 | 30.9357 | 31.9092 | 33.4406 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 32.2749 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 28.5994 | 28.825 | 29.3247 | 30.5074 | 31.1512 | 32.3814 | 36.125 | 33.0341 | 32.4282 | 33.2415 | 35.0225 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136 | 33.8136
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 24.0665 | 24.3286 | 24.7825 | 25.8176 | 26.5091 | 27.3866 | 27.8412 | 28.24 | 27.4984 | 28.3637 | 29.725 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 28.6888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 25.4217 | 25.6223 | 26.0664 | 27.1177 | 27.69 | 28.7835 | 32.1111 | 29.3637 | 28.825 | 29.548 | 31.1311 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565 | 30.0565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 21.0582 | 21.2875 | 21.6847 | 22.5904 | 23.1954 | 23.9632 | 24.361 | 24.71 | 24.0611 | 24.8182 | 26.0094 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 25.1027 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 22.244 | 22.4195 | 22.8081 | 23.728 | 24.2287 | 25.1856 | 28.0972 | 25.6932 | 25.2219 | 25.8545 | 27.2397 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995 | 26.2995
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 18.0499 | 18.2464 | 18.5869 | 19.3632 | 19.8818 | 20.5399 | 20.8809 | 21.18 | 20.6238 | 21.2728 | 22.2937 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 21.5166 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 19.0663 | 19.2167 | 19.5498 | 20.3383 | 20.7675 | 21.5876 | 24.0833 | 22.0228 | 21.6188 | 22.161 | 23.3483 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424 | 22.5424
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 15.0416 | 15.2054 | 15.4891 | 16.136 | 16.5682 | 17.1166 | 17.4007 | 17.65 | 17.1865 | 17.7273 | 18.5781 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 17.9305 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 15.8886 | 16.0139 | 16.2915 | 16.9485 | 17.3062 | 17.9897 | 20.0694 | 18.3523 | 18.0156 | 18.4675 | 19.4569 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853 | 18.7853
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 12.0333 | 12.1643 | 12.3913 | 12.9088 | 13.2545 | 13.6933 | 13.9206 | 14.12 | 13.7492 | 14.1818 | 14.8625 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 14.3444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 12.7108 | 12.8111 | 13.0332 | 13.5588 | 13.845 | 14.3917 | 16.0555 | 14.6818 | 14.4125 | 14.774 | 15.5656 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283 | 15.0283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 9.0249 | 9.1232 | 9.2935 | 9.6816 | 9.9409 | 10.27 | 10.4404 | 10.59 | 10.3119 | 10.6364 | 11.1469 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 10.7583 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 9.5331 | 9.6083 | 9.7749 | 10.1691 | 10.3837 | 10.7938 | 12.0417 | 11.0114 | 10.8094 | 11.0805 | 11.6742 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712 | 11.2712
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 6.0166 | 6.0821 | 6.1956 | 6.4544 | 6.6273 | 6.8466 | 6.9603 | 7.06 | 6.8746 | 7.0909 | 7.4312 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 7.1722 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 6.3554 | 6.4056 | 6.5166 | 6.7794 | 6.9225 | 7.1959 | 8.0278 | 7.3409 | 7.2063 | 7.387 | 7.7828 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141 | 7.5141
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.0083 | 3.0411 | 3.0978 | 3.2272 | 3.3136 | 3.4233 | 3.4801 | 3.53 | 3.4373 | 3.5455 | 3.7156 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 3.5861 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.1777 | 3.2028 | 3.2583 | 3.3897 | 3.4612 | 3.5979 | 4.0139 | 3.6705 | 3.6031 | 3.6935 | 3.8914 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571 | 3.7571
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 6.0118e-14 | 6.0773e-14 | 6.1907e-14 | 6.4493e-14 | 6.622e-14 | 6.8412e-14 | 6.9547e-14 | 7.0544e-14 | 6.8691e-14 | 7.0853e-14 | 7.4253e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 7.1665e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 6.3503e-14 | 6.4004e-14 | 6.5114e-14 | 6.774e-14 | 6.917e-14 | 7.1901e-14 | 8.0214e-14 | 7.3351e-14 | 7.2005e-14 | 7.3811e-14 | 7.7766e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14 | 7.5081e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 65.2498 | 65.2414 | 65.8113 | 66.4369 | 67.7223 | 68.6461 | 69.1463 | 69.6925 | 70.1932 | 71.0997 | 72.2253 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 72.1445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 71.4109 | 71.4284 | 71.9219 | 73.2284 | 74.1008 | 74.9561 | 75.9569 | 76.8826 | 77.7827 | 77.883 | 78.934 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325 | 78.1325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 64.5973 | 64.589 | 65.1532 | 65.7725 | 67.045 | 67.9596 | 68.4548 | 68.9956 | 69.4913 | 70.3887 | 71.503 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 71.423 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 70.6968 | 70.7141 | 71.2027 | 72.4962 | 73.3598 | 74.2065 | 75.1973 | 76.1138 | 77.0048 | 77.1042 | 78.1446 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511 | 77.3511
98% | 0 | 55.3193 | 73.3854 | 78.3 | 63.9448 | 63.9366 | 64.4951 | 65.1081 | 66.3678 | 67.2732 | 67.7634 | 68.2986 | 68.7894 | 69.6777 | 70.7808 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 70.7016 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 69.9827 | 69.9998 | 70.4835 | 71.7639 | 72.6187 | 73.457 | 74.4377 | 75.345 | 76.227 | 76.3254 | 77.3553 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698 | 76.5698
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 63.2923 | 63.2842 | 63.837 | 64.4438 | 65.6906 | 66.5867 | 67.0719 | 67.6017 | 68.0874 | 68.9667 | 70.0585 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 69.9801 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 69.2686 | 69.2855 | 69.7642 | 71.0316 | 71.8777 | 72.7074 | 73.6782 | 74.5761 | 75.4492 | 75.5465 | 76.566 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885 | 75.7885
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 61.9873 | 61.9794 | 62.5208 | 63.115 | 64.3362 | 65.2138 | 65.689 | 66.2079 | 66.6836 | 67.5447 | 68.614 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 68.5372 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 67.8403 | 67.857 | 68.3258 | 69.567 | 70.3957 | 71.2083 | 72.159 | 73.0385 | 73.8935 | 73.9889 | 74.9873 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258 | 74.2258
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 58.7248 | 58.7173 | 59.2302 | 59.7932 | 60.95 | 61.7815 | 62.2317 | 62.7232 | 63.1739 | 63.9897 | 65.0027 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 64.93 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 64.2698 | 64.2855 | 64.7297 | 65.9056 | 66.6907 | 67.4605 | 68.3612 | 69.1944 | 70.0044 | 70.0947 | 71.0406 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192 | 70.3192
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 55.4624 | 55.4552 | 55.9396 | 56.4713 | 57.5639 | 58.3492 | 58.7744 | 59.2386 | 59.6643 | 60.4348 | 61.3915 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 61.3228 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 60.6993 | 60.7141 | 61.1336 | 62.2442 | 62.9856 | 63.7127 | 64.5633 | 65.3502 | 66.1153 | 66.2006 | 67.0939 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126 | 66.4126
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 52.1999 | 52.1932 | 52.6491 | 53.1495 | 54.1778 | 54.9169 | 55.317 | 55.754 | 56.1546 | 56.8798 | 57.7802 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 57.7156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 57.1287 | 57.1427 | 57.5375 | 58.5827 | 59.2806 | 59.9649 | 60.7655 | 61.5061 | 62.2261 | 62.3064 | 63.1472 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506 | 62.506
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 48.9374 | 48.9311 | 49.3585 | 49.8277 | 50.7917 | 51.4846 | 51.8597 | 52.2694 | 52.6449 | 53.3248 | 54.169 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 54.1083 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 53.5582 | 53.5713 | 53.9414 | 54.9213 | 55.5756 | 56.2171 | 56.9677 | 57.662 | 58.337 | 58.4123 | 59.2005 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994 | 58.5994
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 45.6749 | 45.669 | 46.0679 | 46.5058 | 47.4056 | 48.0523 | 48.4024 | 48.7847 | 49.1353 | 49.7698 | 50.5577 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 50.5011 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 49.9876 | 49.9999 | 50.3453 | 51.2599 | 51.8705 | 52.4693 | 53.1698 | 53.8178 | 54.4479 | 54.5181 | 55.2538 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927 | 54.6927
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 42.4124 | 42.4069 | 42.7774 | 43.184 | 44.0195 | 44.62 | 44.9451 | 45.3001 | 45.6256 | 46.2148 | 46.9464 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 46.8939 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 46.4171 | 46.4284 | 46.7492 | 47.5985 | 48.1655 | 48.7215 | 49.372 | 49.9737 | 50.5587 | 50.624 | 51.3071 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861 | 50.7861
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 39.1499 | 39.1449 | 39.4868 | 39.8621 | 40.6334 | 41.1876 | 41.4878 | 41.8155 | 42.1159 | 42.6598 | 43.3352 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 43.2867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 42.8465 | 42.857 | 43.1531 | 43.9371 | 44.4605 | 44.9736 | 45.5741 | 46.1296 | 46.6696 | 46.7298 | 47.3604 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795 | 46.8795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 35.8874 | 35.8828 | 36.1962 | 36.5403 | 37.2472 | 37.7553 | 38.0305 | 38.3309 | 38.6063 | 39.1048 | 39.7239 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 39.6795 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 39.276 | 39.2856 | 39.557 | 40.2756 | 40.7554 | 41.2258 | 41.7763 | 42.2854 | 42.7805 | 42.8357 | 43.4137 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729 | 42.9729
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 32.6249 | 32.6207 | 32.9057 | 33.2184 | 33.8611 | 34.323 | 34.5731 | 34.8462 | 35.0966 | 35.5499 | 36.1126 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 36.0722 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 35.7054 | 35.7142 | 35.961 | 36.6142 | 37.0504 | 37.478 | 37.9784 | 38.4413 | 38.8913 | 38.9415 | 39.467 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662 | 39.0662
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 29.3624 | 29.3587 | 29.6151 | 29.8966 | 30.475 | 30.8907 | 31.1158 | 31.3616 | 31.587 | 31.9949 | 32.5014 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 32.465 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 32.1349 | 32.1428 | 32.3649 | 32.9528 | 33.3453 | 33.7302 | 34.1806 | 34.5972 | 35.0022 | 35.0474 | 35.5203 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596 | 35.1596
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 26.0999 | 26.0966 | 26.3245 | 26.5748 | 27.0889 | 27.4584 | 27.6585 | 27.877 | 28.0773 | 28.4399 | 28.8901 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 28.8578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 28.5644 | 28.5713 | 28.7688 | 29.2914 | 29.6403 | 29.9824 | 30.3827 | 30.753 | 31.1131 | 31.1532 | 31.5736 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253 | 31.253
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 22.8374 | 22.8345 | 23.034 | 23.2529 | 23.7028 | 24.0261 | 24.2012 | 24.3924 | 24.5676 | 24.8849 | 25.2788 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 25.2506 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 24.9938 | 24.9999 | 25.1727 | 25.63 | 25.9353 | 26.2346 | 26.5849 | 26.9089 | 27.2239 | 27.2591 | 27.6269 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464 | 27.3464
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 19.5749 | 19.5724 | 19.7434 | 19.9311 | 20.3167 | 20.5938 | 20.7439 | 20.9077 | 21.058 | 21.3299 | 21.6676 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 21.6433 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 21.4233 | 21.4285 | 21.5766 | 21.9685 | 22.2302 | 22.4868 | 22.7871 | 23.0648 | 23.3348 | 23.3649 | 23.6802 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397 | 23.4397
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 16.3125 | 16.3104 | 16.4528 | 16.6092 | 16.9306 | 17.1615 | 17.2866 | 17.4231 | 17.5483 | 17.7749 | 18.0563 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 18.0361 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 17.8527 | 17.8571 | 17.9805 | 18.3071 | 18.5252 | 18.739 | 18.9892 | 19.2207 | 19.4457 | 19.4708 | 19.7335 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331 | 19.5331
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 13.05 | 13.0483 | 13.1623 | 13.2874 | 13.5445 | 13.7292 | 13.8293 | 13.9385 | 14.0386 | 14.2199 | 14.4451 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 14.4289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 14.2822 | 14.2857 | 14.3844 | 14.6457 | 14.8202 | 14.9912 | 15.1914 | 15.3765 | 15.5565 | 15.5766 | 15.7868 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265 | 15.6265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 9.7875 | 9.7862 | 9.8717 | 9.9655 | 10.1583 | 10.2969 | 10.3719 | 10.4539 | 10.529 | 10.665 | 10.8338 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 10.8217 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 10.7116 | 10.7143 | 10.7883 | 10.9843 | 11.1151 | 11.2434 | 11.3935 | 11.5324 | 11.6674 | 11.6825 | 11.8401 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199 | 11.7199
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 6.525 | 6.5241 | 6.5811 | 6.6437 | 6.7722 | 6.8646 | 6.9146 | 6.9692 | 7.0193 | 7.11 | 7.2225 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 7.2144 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 7.1411 | 7.1428 | 7.1922 | 7.3228 | 7.4101 | 7.4956 | 7.5957 | 7.6883 | 7.7783 | 7.7883 | 7.8934 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132 | 7.8132
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.2625 | 3.2621 | 3.2906 | 3.3218 | 3.3861 | 3.4323 | 3.4573 | 3.4846 | 3.5097 | 3.555 | 3.6113 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 3.6072 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 3.5705 | 3.5714 | 3.5961 | 3.6614 | 3.705 | 3.7478 | 3.7978 | 3.8441 | 3.8891 | 3.8942 | 3.9467 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066 | 3.9066
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 6.5198e-14 | 6.5189e-14 | 6.5759e-14 | 6.6384e-14 | 6.7668e-14 | 6.8591e-14 | 6.9091e-14 | 6.9637e-14 | 7.0137e-14 | 7.1043e-14 | 7.2168e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 7.2087e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 7.1354e-14 | 7.1371e-14 | 7.1864e-14 | 7.317e-14 | 7.4042e-14 | 7.4896e-14 | 7.5896e-14 | 7.6821e-14 | 7.7721e-14 | 7.7821e-14 | 7.8871e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14 | 7.807e-14
Option 5
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 45.6663 | 46.3214 | 47.4563 | 50.0441 | 51.7726 | 53.9664 | 55.1029 | 56.1001 | 54.2461 | 56.4092 | 59.8125 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 57.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 49.0542 | 49.5557 | 50.6659 | 53.2942 | 54.7249 | 57.4587 | 65.7777 | 58.9092 | 57.5626 | 59.3699 | 63.3278 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413 | 60.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 45.2097 | 45.8582 | 46.9818 | 49.5437 | 51.2549 | 53.4267 | 54.5519 | 55.5391 | 53.7036 | 55.8451 | 59.2143 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 56.6498 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 48.5637 | 49.0601 | 50.1592 | 52.7612 | 54.1777 | 56.8841 | 65.12 | 58.3201 | 56.987 | 58.7762 | 62.6945 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349 | 60.0349
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 44.753 | 45.395 | 46.5072 | 49.0432 | 50.7372 | 52.8871 | 54.0009 | 54.9781 | 53.1612 | 55.281 | 58.6162 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 56.0776 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 48.0731 | 48.5646 | 49.6526 | 52.2283 | 53.6304 | 56.3095 | 64.4622 | 57.731 | 56.4113 | 58.1825 | 62.0612 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285 | 59.4285
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 44.2963 | 44.9318 | 46.0327 | 48.5428 | 50.2195 | 52.3474 | 53.4498 | 54.4171 | 52.6187 | 54.717 | 58.0181 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 55.5054 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 47.5826 | 48.069 | 49.1459 | 51.6954 | 53.0832 | 55.735 | 63.8044 | 57.1419 | 55.8357 | 57.5888 | 61.428 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221 | 58.8221
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 43.383 | 44.0053 | 45.0835 | 47.5419 | 49.184 | 51.2681 | 52.3478 | 53.2951 | 51.5338 | 53.5888 | 56.8218 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 54.361 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 46.6015 | 47.0779 | 48.1326 | 50.6295 | 51.9887 | 54.5858 | 62.4889 | 55.9638 | 54.6845 | 56.4014 | 60.1614 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092 | 57.6092
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 41.0997 | 41.6893 | 42.7107 | 45.0397 | 46.5954 | 48.5697 | 49.5926 | 50.4901 | 48.8215 | 50.7683 | 53.8312 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 51.4999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 44.1488 | 44.6001 | 45.5993 | 47.9648 | 49.2524 | 51.7128 | 59.2 | 53.0183 | 51.8063 | 53.4329 | 56.995 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772 | 54.5772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 38.8164 | 39.3732 | 40.3379 | 42.5375 | 44.0067 | 45.8714 | 46.8375 | 47.6851 | 46.1092 | 47.9478 | 50.8406 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 48.6388 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 41.6961 | 42.1223 | 43.066 | 45.3001 | 46.5162 | 48.8399 | 55.9111 | 50.0728 | 48.9282 | 50.4644 | 53.8286 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451 | 51.5451
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 36.5331 | 37.0571 | 37.9651 | 40.0353 | 41.4181 | 43.1731 | 44.0823 | 44.88 | 43.3969 | 45.1274 | 47.85 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 45.7777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 39.2434 | 39.6445 | 40.5327 | 42.6353 | 43.7799 | 45.967 | 52.6222 | 47.1274 | 46.0501 | 47.4959 | 50.6622 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131 | 48.5131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 34.2497 | 34.7411 | 35.5923 | 37.5331 | 38.8295 | 40.4748 | 41.3272 | 42.075 | 40.6846 | 42.3069 | 44.8593 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 42.9165 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 36.7907 | 37.1667 | 37.9994 | 39.9706 | 41.0437 | 43.094 | 49.3333 | 44.1819 | 43.1719 | 44.5274 | 47.4958 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481 | 45.481
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 31.9664 | 32.425 | 33.2194 | 35.0309 | 36.2408 | 37.7765 | 38.5721 | 39.27 | 37.9723 | 39.4865 | 41.8687 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 40.0554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 34.338 | 34.689 | 35.4661 | 37.3059 | 38.3074 | 40.2211 | 46.0444 | 41.2365 | 40.2938 | 41.5589 | 44.3295 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489 | 42.4489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 29.6831 | 30.1089 | 30.8466 | 32.5287 | 33.6522 | 35.0782 | 35.8169 | 36.465 | 35.26 | 36.666 | 38.8781 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 37.1943 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 31.8852 | 32.2112 | 32.9328 | 34.6412 | 35.5712 | 37.3482 | 42.7555 | 38.291 | 37.4157 | 38.5905 | 41.1631 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169 | 39.4169
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 27.3998 | 27.7928 | 28.4738 | 30.0265 | 31.0636 | 32.3798 | 33.0618 | 33.66 | 32.5477 | 33.8455 | 35.8875 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 34.3332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 29.4325 | 29.7334 | 30.3995 | 31.9765 | 32.835 | 34.4752 | 39.4666 | 35.3455 | 34.5376 | 35.622 | 37.9967 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848 | 36.3848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 25.1165 | 25.4768 | 26.101 | 27.5243 | 28.475 | 29.6815 | 30.3066 | 30.855 | 29.8354 | 31.0251 | 32.8969 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 31.4721 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 26.9798 | 27.2556 | 27.8662 | 29.3118 | 30.0987 | 31.6023 | 36.1778 | 32.4001 | 31.6594 | 32.6535 | 34.8303 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527 | 33.3527
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 22.8332 | 23.1607 | 23.7282 | 25.0221 | 25.8863 | 26.9832 | 27.5515 | 28.05 | 27.123 | 28.2046 | 29.9062 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 28.611 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 24.5271 | 24.7778 | 25.333 | 26.6471 | 27.3625 | 28.7294 | 32.8889 | 29.4546 | 28.7813 | 29.685 | 31.6639 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207 | 30.3207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 20.5498 | 20.8446 | 21.3554 | 22.5199 | 23.2977 | 24.2849 | 24.7963 | 25.245 | 24.4107 | 25.3842 | 26.9156 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 25.7499 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 22.0744 | 22.3 | 22.7997 | 23.9824 | 24.6262 | 25.8564 | 29.6 | 26.5091 | 25.9032 | 26.7165 | 28.4975 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886 | 27.2886
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 18.2665 | 18.5286 | 18.9825 | 20.0176 | 20.7091 | 21.5866 | 22.0412 | 22.44 | 21.6984 | 22.5637 | 23.925 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 22.8888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 19.6217 | 19.8223 | 20.2664 | 21.3177 | 21.89 | 22.9835 | 26.3111 | 23.5637 | 23.025 | 23.748 | 25.3311 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565 | 24.2565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 15.9832 | 16.2125 | 16.6097 | 17.5154 | 18.1204 | 18.8882 | 19.286 | 19.635 | 18.9861 | 19.7432 | 20.9344 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 20.0277 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 17.169 | 17.3445 | 17.7331 | 18.653 | 19.1537 | 20.1106 | 23.0222 | 20.6182 | 20.1469 | 20.7795 | 22.1647 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245 | 21.2245
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 13.6999 | 13.8964 | 14.2369 | 15.0132 | 15.5318 | 16.1899 | 16.5309 | 16.83 | 16.2738 | 16.9228 | 17.9437 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 17.1666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 14.7163 | 14.8667 | 15.1998 | 15.9883 | 16.4175 | 17.2376 | 19.7333 | 17.6728 | 17.2688 | 17.811 | 18.9983 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924 | 18.1924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 11.4166 | 11.5804 | 11.8641 | 12.511 | 12.9432 | 13.4916 | 13.7757 | 14.025 | 13.5615 | 14.1023 | 14.9531 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 14.3055 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 12.2636 | 12.3889 | 12.6665 | 13.3235 | 13.6812 | 14.3647 | 16.4444 | 14.7273 | 14.3906 | 14.8425 | 15.8319 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603 | 15.1603
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 9.1333 | 9.2643 | 9.4913 | 10.0088 | 10.3545 | 10.7933 | 11.0206 | 11.22 | 10.8492 | 11.2818 | 11.9625 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 11.4444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 9.8108 | 9.9111 | 10.1332 | 10.6588 | 10.945 | 11.4917 | 13.1555 | 11.7818 | 11.5125 | 11.874 | 12.6656 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283 | 12.1283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 6.8499 | 6.9482 | 7.1185 | 7.5066 | 7.7659 | 8.095 | 8.2654 | 8.415 | 8.1369 | 8.4614 | 8.9719 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 8.5833 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 7.3581 | 7.4333 | 7.5999 | 7.9941 | 8.2087 | 8.6188 | 9.8667 | 8.8364 | 8.6344 | 8.9055 | 9.4992 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962 | 9.0962
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 4.5666 | 4.6321 | 4.7456 | 5.0044 | 5.1773 | 5.3966 | 5.5103 | 5.61 | 5.4246 | 5.6409 | 5.9812 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 5.7222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 4.9054 | 4.9556 | 5.0666 | 5.3294 | 5.4725 | 5.7459 | 6.5778 | 5.8909 | 5.7563 | 5.937 | 6.3328 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641 | 6.0641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 2.2833 | 2.3161 | 2.3728 | 2.5022 | 2.5886 | 2.6983 | 2.7551 | 2.805 | 2.7123 | 2.8205 | 2.9906 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 2.8611 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 2.4527 | 2.4778 | 2.5333 | 2.6647 | 2.7362 | 2.8729 | 3.2889 | 2.9455 | 2.8781 | 2.9685 | 3.1664 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321 | 3.0321
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 4.563e-14 | 4.6284e-14 | 4.7418e-14 | 5.0004e-14 | 5.1731e-14 | 5.3923e-14 | 5.5059e-14 | 5.6055e-14 | 5.4203e-14 | 5.6364e-14 | 5.9765e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 5.7176e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 4.9015e-14 | 4.9516e-14 | 5.0625e-14 | 5.3252e-14 | 5.4681e-14 | 5.7413e-14 | 6.5725e-14 | 5.8862e-14 | 5.7517e-14 | 5.9322e-14 | 6.3277e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14 | 6.0593e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 50.7498 | 50.7414 | 51.3113 | 51.9369 | 53.2223 | 54.1461 | 54.6463 | 55.1925 | 55.6932 | 56.5997 | 57.7253 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 57.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 56.9109 | 56.9284 | 57.4219 | 58.7284 | 59.6008 | 60.4561 | 61.4569 | 62.3826 | 63.2827 | 63.383 | 64.434 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325 | 63.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 50.2423 | 50.234 | 50.7982 | 51.4175 | 52.69 | 53.6046 | 54.0998 | 54.6406 | 55.1363 | 56.0337 | 57.148 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 57.068 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 56.3418 | 56.3591 | 56.8477 | 58.1412 | 59.0048 | 59.8515 | 60.8423 | 61.7588 | 62.6498 | 62.7492 | 63.7896 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961 | 62.9961
98% | 0 | 55.3193 | 73.3854 | 78.3 | 49.7348 | 49.7266 | 50.2851 | 50.8981 | 52.1578 | 53.0632 | 53.5534 | 54.0886 | 54.5794 | 55.4677 | 56.5708 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 56.4916 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 55.7727 | 55.7898 | 56.2735 | 57.5539 | 58.4087 | 59.247 | 60.2277 | 61.135 | 62.017 | 62.1154 | 63.1453 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598 | 62.3598
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 49.2273 | 49.2192 | 49.772 | 50.3788 | 51.6256 | 52.5217 | 53.0069 | 53.5367 | 54.0224 | 54.9017 | 55.9935 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 55.9151 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 55.2036 | 55.2205 | 55.6992 | 56.9666 | 57.8127 | 58.6424 | 59.6132 | 60.5111 | 61.3842 | 61.4815 | 62.501 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235 | 61.7235
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 48.2123 | 48.2044 | 48.7458 | 49.34 | 50.5612 | 51.4388 | 51.914 | 52.4329 | 52.9086 | 53.7697 | 54.839 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 54.7622 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 54.0653 | 54.082 | 54.5508 | 55.792 | 56.6207 | 57.4333 | 58.384 | 59.2635 | 60.1185 | 60.2139 | 61.2123 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508 | 60.4508
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 45.6748 | 45.6673 | 46.1802 | 46.7432 | 47.9 | 48.7315 | 49.1817 | 49.6732 | 50.1239 | 50.9397 | 51.9527 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 51.88 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 51.2198 | 51.2355 | 51.6797 | 52.8556 | 53.6407 | 54.4105 | 55.3112 | 56.1444 | 56.9544 | 57.0447 | 57.9906 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692 | 57.2692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 43.1374 | 43.1302 | 43.6146 | 44.1463 | 45.2389 | 46.0242 | 46.4494 | 46.9136 | 47.3393 | 48.1098 | 49.0665 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 48.9978 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 48.3743 | 48.3891 | 48.8086 | 49.9192 | 50.6606 | 51.3877 | 52.2383 | 53.0252 | 53.7903 | 53.8756 | 54.7689 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876 | 54.0876
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 40.5999 | 40.5932 | 41.0491 | 41.5495 | 42.5778 | 43.3169 | 43.717 | 44.154 | 44.5546 | 45.2798 | 46.1802 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 46.1156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 45.5287 | 45.5427 | 45.9375 | 46.9827 | 47.6806 | 48.3649 | 49.1655 | 49.9061 | 50.6261 | 50.7064 | 51.5472 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906 | 50.906
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 38.0624 | 38.0561 | 38.4835 | 38.9527 | 39.9167 | 40.6096 | 40.9847 | 41.3944 | 41.7699 | 42.4498 | 43.294 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 43.2333 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 42.6832 | 42.6963 | 43.0664 | 44.0463 | 44.7006 | 45.3421 | 46.0927 | 46.787 | 47.462 | 47.5373 | 48.3255 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244 | 47.7244
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 35.5249 | 35.519 | 35.9179 | 36.3558 | 37.2556 | 37.9023 | 38.2524 | 38.6347 | 38.9853 | 39.6198 | 40.4077 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 40.3511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 39.8376 | 39.8499 | 40.1953 | 41.1099 | 41.7205 | 42.3193 | 43.0198 | 43.6678 | 44.2979 | 44.3681 | 45.1038 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427 | 44.5427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 32.9874 | 32.9819 | 33.3524 | 33.759 | 34.5945 | 35.195 | 35.5201 | 35.8751 | 36.2006 | 36.7898 | 37.5214 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 37.4689 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 36.9921 | 37.0034 | 37.3242 | 38.1735 | 38.7405 | 39.2965 | 39.947 | 40.5487 | 41.1337 | 41.199 | 41.8821 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611 | 41.3611
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 30.4499 | 30.4449 | 30.7868 | 31.1621 | 31.9334 | 32.4876 | 32.7878 | 33.1155 | 33.4159 | 33.9598 | 34.6352 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 34.5867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 34.1465 | 34.157 | 34.4531 | 35.2371 | 35.7605 | 36.2736 | 36.8741 | 37.4296 | 37.9696 | 38.0298 | 38.6604 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795 | 38.1795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 27.9124 | 27.9078 | 28.2212 | 28.5653 | 29.2722 | 29.7803 | 30.0555 | 30.3559 | 30.6313 | 31.1298 | 31.7489 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 31.7045 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 31.301 | 31.3106 | 31.582 | 32.3006 | 32.7804 | 33.2508 | 33.8013 | 34.3104 | 34.8055 | 34.8607 | 35.4387 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979 | 34.9979
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 25.3749 | 25.3707 | 25.6557 | 25.9684 | 26.6111 | 27.073 | 27.3231 | 27.5962 | 27.8466 | 28.2999 | 28.8626 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 28.8222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 28.4554 | 28.4642 | 28.711 | 29.3642 | 29.8004 | 30.228 | 30.7284 | 31.1913 | 31.6413 | 31.6915 | 32.217 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162 | 31.8162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 22.8374 | 22.8337 | 23.0901 | 23.3716 | 23.95 | 24.3657 | 24.5908 | 24.8366 | 25.062 | 25.4699 | 25.9764 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 25.94 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 25.6099 | 25.6178 | 25.8399 | 26.4278 | 26.8203 | 27.2052 | 27.6556 | 28.0722 | 28.4772 | 28.5224 | 28.9953 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346 | 28.6346
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 20.2999 | 20.2966 | 20.5245 | 20.7748 | 21.2889 | 21.6584 | 21.8585 | 22.077 | 22.2773 | 22.6399 | 23.0901 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 23.0578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 22.7644 | 22.7713 | 22.9688 | 23.4914 | 23.8403 | 24.1824 | 24.5827 | 24.953 | 25.3131 | 25.3532 | 25.7736 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453 | 25.453
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 17.7624 | 17.7595 | 17.959 | 18.1779 | 18.6278 | 18.9511 | 19.1262 | 19.3174 | 19.4926 | 19.8099 | 20.2038 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 20.1756 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 19.9188 | 19.9249 | 20.0977 | 20.555 | 20.8603 | 21.1596 | 21.5099 | 21.8339 | 22.1489 | 22.1841 | 22.5519 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714 | 22.2714
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 15.2249 | 15.2224 | 15.3934 | 15.5811 | 15.9667 | 16.2438 | 16.3939 | 16.5577 | 16.708 | 16.9799 | 17.3176 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 17.2933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 17.0733 | 17.0785 | 17.2266 | 17.6185 | 17.8802 | 18.1368 | 18.4371 | 18.7148 | 18.9848 | 19.0149 | 19.3302 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897 | 19.0897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 12.6875 | 12.6854 | 12.8278 | 12.9842 | 13.3056 | 13.5365 | 13.6616 | 13.7981 | 13.9233 | 14.1499 | 14.4313 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 14.4111 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 14.2277 | 14.2321 | 14.3555 | 14.6821 | 14.9002 | 15.114 | 15.3642 | 15.5957 | 15.8207 | 15.8458 | 16.1085 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081 | 15.9081
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 10.15 | 10.1483 | 10.2623 | 10.3874 | 10.6445 | 10.8292 | 10.9293 | 11.0385 | 11.1386 | 11.3199 | 11.5451 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 11.5289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 11.3822 | 11.3857 | 11.4844 | 11.7457 | 11.9202 | 12.0912 | 12.2914 | 12.4765 | 12.6565 | 12.6766 | 12.8868 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265 | 12.7265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 7.6125 | 7.6112 | 7.6967 | 7.7905 | 7.9833 | 8.1219 | 8.1969 | 8.2789 | 8.354 | 8.49 | 8.6588 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 8.6467 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 8.5366 | 8.5393 | 8.6133 | 8.8093 | 8.9401 | 9.0684 | 9.2185 | 9.3574 | 9.4924 | 9.5075 | 9.6651 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449 | 9.5449
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 5.075 | 5.0741 | 5.1311 | 5.1937 | 5.3222 | 5.4146 | 5.4646 | 5.5192 | 5.5693 | 5.66 | 5.7725 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 5.7644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 5.6911 | 5.6928 | 5.7422 | 5.8728 | 5.9601 | 6.0456 | 6.1457 | 6.2383 | 6.3283 | 6.3383 | 6.4434 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632 | 6.3632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 2.5375 | 2.5371 | 2.5656 | 2.5968 | 2.6611 | 2.7073 | 2.7323 | 2.7596 | 2.7847 | 2.83 | 2.8863 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 2.8822 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 2.8455 | 2.8464 | 2.8711 | 2.9364 | 2.98 | 3.0228 | 3.0728 | 3.1191 | 3.1641 | 3.1692 | 3.2217 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816 | 3.1816
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 5.0709e-14 | 5.0701e-14 | 5.127e-14 | 5.1895e-14 | 5.318e-14 | 5.4103e-14 | 5.4603e-14 | 5.5148e-14 | 5.5649e-14 | 5.6554e-14 | 5.7679e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 5.7598e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 5.6865e-14 | 5.6883e-14 | 5.7376e-14 | 5.8681e-14 | 5.9553e-14 | 6.0408e-14 | 6.1408e-14 | 6.2333e-14 | 6.3232e-14 | 6.3332e-14 | 6.4382e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14 | 6.3582e-14
Option 6
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 41.9587 | 58.8911 | 63.2865 | 64.1679 | 64.8245 | 65.9027 | 68.3362 | 69.9637 | 72.0573 | 73.0762 | 73.966 | 72.0065 | 74.16 | 77.4396 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 74.9477 | 100% | 0 | 45.442 | 62.1329 | 66.7226 | 67.5558 | 68.0587 | 69.1122 | 71.5862 | 72.916 | 75.5496 | 83.7511 | 76.7751 | 75.323 | 77.1207 | 80.9549 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367 | 78.367
99% | 1.486 | 41.5391 | 58.3022 | 62.6536 | 63.5262 | 64.1762 | 65.2436 | 67.6528 | 69.2641 | 71.3367 | 72.3455 | 73.2263 | 71.2864 | 73.4184 | 76.6652 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 74.1982 | 99% | 1.486 | 44.9876 | 61.5116 | 66.0554 | 66.8802 | 67.3782 | 68.4211 | 70.8704 | 72.1868 | 74.7941 | 82.9135 | 76.0074 | 74.5698 | 76.3495 | 80.1454 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833 | 77.5833
98% | 3.2692 | 41.1195 | 57.7133 | 62.0207 | 62.8845 | 63.528 | 64.5846 | 66.9694 | 68.5644 | 70.6161 | 71.6147 | 72.4867 | 70.5664 | 72.6768 | 75.8908 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 73.4488 | 98% | 3.2692 | 44.5332 | 60.8903 | 65.3881 | 66.2047 | 66.6976 | 67.73 | 70.1545 | 71.4577 | 74.0386 | 82.076 | 75.2396 | 73.8165 | 75.5783 | 79.3358 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996 | 76.7996
97% | 6.8356 | 40.6999 | 57.1243 | 61.3879 | 62.2429 | 62.8797 | 63.9256 | 66.2861 | 67.8648 | 69.8956 | 70.884 | 71.747 | 69.8463 | 71.9352 | 75.1164 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 72.6993 | 97% | 6.8356 | 44.0787 | 60.2689 | 64.7209 | 65.5291 | 66.017 | 67.0388 | 69.4387 | 70.7285 | 73.2831 | 81.2385 | 74.4719 | 73.0633 | 74.8071 | 78.5263 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016 | 76.016
95% | 17.5347 | 39.8607 | 55.9465 | 60.1221 | 60.9595 | 61.5833 | 62.6075 | 64.9194 | 66.4655 | 68.4544 | 69.4224 | 70.2677 | 68.4062 | 70.452 | 73.5676 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 71.2003 | 95% | 17.5347 | 43.1699 | 59.0263 | 63.3865 | 64.178 | 64.6558 | 65.6566 | 68.0069 | 69.2702 | 71.7721 | 79.5635 | 72.9364 | 71.5568 | 73.2647 | 76.9072 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486 | 74.4486
90% | 78.7576 | 37.7628 | 53.002 | 56.9578 | 57.7511 | 58.342 | 59.3124 | 61.5026 | 62.9673 | 64.8516 | 65.7686 | 66.5694 | 64.8058 | 66.744 | 69.6957 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 67.4529 | 90% | 78.7576 | 40.8978 | 55.9196 | 60.0503 | 60.8002 | 61.2529 | 62.201 | 64.4276 | 65.6244 | 67.9947 | 75.376 | 69.0976 | 67.7907 | 69.4086 | 72.8595 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303 | 70.5303
85% | 236.8672 | 35.6649 | 50.0574 | 53.7935 | 54.5427 | 55.1008 | 56.0173 | 58.0857 | 59.4691 | 61.2487 | 62.1148 | 62.8711 | 61.2055 | 63.036 | 65.8237 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 63.7056 | 85% | 236.8672 | 38.6257 | 52.813 | 56.7142 | 57.4224 | 57.8499 | 58.7454 | 60.8483 | 61.9786 | 64.2172 | 71.1884 | 65.2589 | 64.0245 | 65.5526 | 68.8117 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119 | 66.6119
80% | 497.5104 | 33.5669 | 47.1129 | 50.6292 | 51.3343 | 51.8596 | 52.7221 | 54.6689 | 55.971 | 57.6458 | 58.461 | 59.1728 | 57.6052 | 59.328 | 61.9517 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 59.9582 | 80% | 497.5104 | 36.3536 | 49.7063 | 53.3781 | 54.0446 | 54.447 | 55.2898 | 57.269 | 58.3328 | 60.4397 | 67.0008 | 61.4201 | 60.2584 | 61.6966 | 64.764 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936 | 62.6936
75% | 803.6248 | 31.469 | 44.1683 | 47.4648 | 48.1259 | 48.6184 | 49.427 | 51.2521 | 52.4728 | 54.043 | 54.8072 | 55.4745 | 54.0049 | 55.62 | 58.0797 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 56.2108 | 75% | 803.6248 | 34.0815 | 46.5997 | 50.0419 | 50.6669 | 51.0441 | 51.8342 | 53.6897 | 54.687 | 56.6622 | 62.8133 | 57.5814 | 56.4922 | 57.8405 | 60.7162 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752 | 58.7752
70% | 1155.2107 | 29.3711 | 41.2238 | 44.3005 | 44.9175 | 45.3771 | 46.1319 | 47.8353 | 48.9746 | 50.4401 | 51.1534 | 51.7762 | 50.4045 | 51.912 | 54.2077 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 52.4634 | 70% | 1155.2107 | 31.8094 | 43.493 | 46.7058 | 47.2891 | 47.6411 | 48.3785 | 50.1104 | 51.0412 | 52.8847 | 58.6257 | 53.7426 | 52.7261 | 53.9845 | 56.6685 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569 | 54.8569
65% | 1553.1596 | 27.2731 | 38.2792 | 41.1362 | 41.7091 | 42.1359 | 42.8367 | 44.4185 | 45.4764 | 46.8372 | 47.4996 | 48.0779 | 46.8042 | 48.204 | 50.3358 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 48.716 | 65% | 1553.1596 | 29.5373 | 40.3864 | 43.3697 | 43.9113 | 44.2382 | 44.9229 | 46.5311 | 47.3954 | 49.1073 | 54.4382 | 49.9038 | 48.9599 | 50.1284 | 52.6207 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385 | 50.9385
60% | 2026.2996 | 25.1752 | 35.3346 | 37.9719 | 38.5007 | 38.8947 | 39.5416 | 41.0017 | 41.9782 | 43.2344 | 43.8457 | 44.3796 | 43.2039 | 44.496 | 46.4638 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 44.9686 | 60% | 2026.2996 | 27.2652 | 37.2798 | 40.0336 | 40.5335 | 40.8352 | 41.4673 | 42.9517 | 43.7496 | 45.3298 | 50.2506 | 46.0651 | 45.1938 | 46.2724 | 48.573 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202 | 47.0202
55% | 2598.4068 | 23.0773 | 32.3901 | 34.8075 | 35.2923 | 35.6535 | 36.2465 | 37.5849 | 38.48 | 39.6315 | 40.1919 | 40.6813 | 39.6036 | 40.788 | 42.5918 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 41.2212 | 55% | 2598.4068 | 24.9931 | 34.1731 | 36.6974 | 37.1557 | 37.4323 | 38.0117 | 39.3724 | 40.1038 | 41.5523 | 46.0631 | 42.2263 | 41.4276 | 42.4164 | 44.5252 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018 | 43.1018
50% | 3233.5201 | 20.9793 | 29.4455 | 31.6432 | 32.084 | 32.4122 | 32.9513 | 34.1681 | 34.9818 | 36.0286 | 36.5381 | 36.983 | 36.0032 | 37.08 | 38.7198 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 37.4739 | 50% | 3233.5201 | 22.721 | 31.0665 | 33.3613 | 33.7779 | 34.0294 | 34.5561 | 35.7931 | 36.458 | 37.7748 | 41.8755 | 38.3876 | 37.6615 | 38.5603 | 40.4775 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835 | 39.1835
45% | 3775.313 | 18.8814 | 26.501 | 28.4789 | 28.8756 | 29.171 | 29.6562 | 30.7513 | 31.4837 | 32.4258 | 32.8843 | 33.2847 | 32.4029 | 33.372 | 34.8478 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 33.7265 | 45% | 3775.313 | 20.4489 | 27.9598 | 30.0252 | 30.4001 | 30.6264 | 31.1005 | 32.2138 | 32.8122 | 33.9973 | 37.688 | 34.5488 | 33.8953 | 34.7043 | 36.4297 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651 | 35.2651
40% | 4072.8088 | 16.7835 | 23.5564 | 25.3146 | 25.6672 | 25.9298 | 26.3611 | 27.3345 | 27.9855 | 28.8229 | 29.2305 | 29.5864 | 28.8026 | 29.664 | 30.9758 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 29.9791 | 40% | 4072.8088 | 18.1768 | 24.8532 | 26.689 | 27.0223 | 27.2235 | 27.6449 | 28.6345 | 29.1664 | 30.2198 | 33.5004 | 30.7101 | 30.1292 | 30.8483 | 32.382 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468 | 31.3468
35% | 4198.821 | 14.6855 | 20.6119 | 22.1503 | 22.4588 | 22.6886 | 23.0659 | 23.9177 | 24.4873 | 25.2201 | 25.5767 | 25.8881 | 25.2023 | 25.956 | 27.1039 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 26.2317 | 35% | 4198.821 | 15.9047 | 21.7465 | 23.3529 | 23.6445 | 23.8206 | 24.1893 | 25.0552 | 25.5206 | 26.4424 | 29.3129 | 26.8713 | 26.363 | 26.9922 | 28.3342 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284 | 27.4284
30% | 4271.3374 | 12.5876 | 17.6673 | 18.9859 | 19.2504 | 19.4473 | 19.7708 | 20.5009 | 20.9891 | 21.6172 | 21.9229 | 22.1898 | 21.6019 | 22.248 | 23.2319 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 22.4843 | 30% | 4271.3374 | 13.6326 | 18.6399 | 20.0168 | 20.2667 | 20.4176 | 20.7337 | 21.4759 | 21.8748 | 22.6649 | 25.1253 | 23.0325 | 22.5969 | 23.1362 | 24.2865 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101 | 23.5101
25% | 4321.8611 | 10.4897 | 14.7228 | 15.8216 | 16.042 | 16.2061 | 16.4757 | 17.084 | 17.4909 | 18.0143 | 18.2691 | 18.4915 | 18.0016 | 18.54 | 19.3599 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 18.7369 | 25% | 4321.8611 | 11.3605 | 15.5332 | 16.6806 | 16.889 | 17.0147 | 17.2781 | 17.8966 | 18.229 | 18.8874 | 20.9378 | 19.1938 | 18.8307 | 19.2802 | 20.2387 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917 | 19.5917
20% | 4353.067 | 8.3917 | 11.7782 | 12.6573 | 12.8336 | 12.9649 | 13.1805 | 13.6672 | 13.9927 | 14.4115 | 14.6152 | 14.7932 | 14.4013 | 14.832 | 15.4879 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 14.9895 | 20% | 4353.067 | 9.0884 | 12.4266 | 13.3445 | 13.5112 | 13.6117 | 13.8224 | 14.3172 | 14.5832 | 15.1099 | 16.7502 | 15.355 | 15.0646 | 15.4241 | 16.191 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734 | 15.6734
15% | 4369.4129 | 6.2938 | 8.8337 | 9.493 | 9.6252 | 9.7237 | 9.8854 | 10.2504 | 10.4946 | 10.8086 | 10.9614 | 11.0949 | 10.801 | 11.124 | 11.6159 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 11.2422 | 15% | 4369.4129 | 6.8163 | 9.3199 | 10.0084 | 10.1334 | 10.2088 | 10.3668 | 10.7379 | 10.9374 | 11.3324 | 12.5627 | 11.5163 | 11.2984 | 11.5681 | 12.1432 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755 | 11.755
10% | 4378.6261 | 4.1959 | 5.8891 | 6.3286 | 6.4168 | 6.4824 | 6.5903 | 6.8336 | 6.9964 | 7.2057 | 7.3076 | 7.3966 | 7.2006 | 7.416 | 7.744 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 7.4948 | 10% | 4378.6261 | 4.5442 | 6.2133 | 6.6723 | 6.7556 | 6.8059 | 6.9112 | 7.1586 | 7.2916 | 7.555 | 8.3751 | 7.6775 | 7.5323 | 7.7121 | 8.0955 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367 | 7.8367
5% | 4391.7028 | 2.0979 | 2.9446 | 3.1643 | 3.2084 | 3.2412 | 3.2951 | 3.4168 | 3.4982 | 3.6029 | 3.6538 | 3.6983 | 3.6003 | 3.708 | 3.872 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 3.7474 | 5% | 4391.7028 | 2.2721 | 3.1066 | 3.3361 | 3.3778 | 3.4029 | 3.4556 | 3.5793 | 3.6458 | 3.7775 | 4.1876 | 3.8388 | 3.7661 | 3.856 | 4.0477 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183 | 3.9183
9.992e-14% | 4391.7028 | 4.1925e-14 | 5.8844e-14 | 6.3236e-14 | 6.4117e-14 | 6.4773e-14 | 6.585e-14 | 6.8282e-14 | 6.9908e-14 | 7.2e-14 | 7.3018e-14 | 7.3907e-14 | 7.1949e-14 | 7.4101e-14 | 7.7378e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 7.4888e-14 | 9.992e-14% | 4391.7028 | 4.5406e-14 | 6.2083e-14 | 6.6669e-14 | 6.7502e-14 | 6.8004e-14 | 6.9057e-14 | 7.1529e-14 | 7.2858e-14 | 7.5489e-14 | 8.3684e-14 | 7.6714e-14 | 7.5263e-14 | 7.7059e-14 | 8.089e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14 | 7.8304e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 48.7027 | 64.9228 | 69.3621 | 69.2514 | 69.2445 | 69.7576 | 70.2289 | 71.4133 | 72.237 | 72.6196 | 73.0584 | 73.4536 | 74.3505 | 75.3524 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 75.3701 | 100% | 0 | 55.1554 | 71.4125 | 75.6672 | 75.4125 | 75.4315 | 75.8682 | 77.0205 | 77.7918 | 78.547 | 79.4302 | 80.2485 | 81.0431 | 81.1338 | 82.0611 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581 | 81.3581
99% | 0 | 48.2157 | 64.2736 | 68.6685 | 68.5589 | 68.5521 | 69.0601 | 69.5266 | 70.6992 | 71.5146 | 71.8934 | 72.3278 | 72.7191 | 73.607 | 74.5989 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 74.6164 | 99% | 1.5127 | 54.6039 | 70.6983 | 74.9105 | 74.6583 | 74.6771 | 75.1095 | 76.2503 | 77.0139 | 77.7615 | 78.6359 | 79.446 | 80.2326 | 80.3224 | 81.2405 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445 | 80.5445
98% | 0 | 47.7287 | 63.6243 | 67.9749 | 67.8664 | 67.8596 | 68.3625 | 68.8244 | 69.9851 | 70.7922 | 71.1672 | 71.5972 | 71.9846 | 72.8635 | 73.8454 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 73.8627 | 98% | 2.269 | 54.0523 | 69.9842 | 74.1538 | 73.9042 | 73.9228 | 74.3508 | 75.4801 | 76.236 | 76.9761 | 77.8416 | 78.6436 | 79.4222 | 79.5111 | 80.4199 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731 | 79.731
97% | 0.37816 | 47.2417 | 62.9751 | 67.2813 | 67.1739 | 67.1672 | 67.6649 | 68.1221 | 69.2709 | 70.0699 | 70.441 | 70.8666 | 71.25 | 72.12 | 73.0919 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 73.109 | 97% | 3.7816 | 53.5008 | 69.2701 | 73.3971 | 73.1501 | 73.1685 | 73.5922 | 74.7099 | 75.4581 | 76.1906 | 77.0473 | 77.8411 | 78.6118 | 78.6998 | 79.5993 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174 | 78.9174
95% | 2.269 | 46.2676 | 61.6767 | 65.894 | 65.7888 | 65.7823 | 66.2698 | 66.7175 | 67.8427 | 68.6251 | 68.9886 | 69.4055 | 69.781 | 70.6329 | 71.5848 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 71.6016 | 95% | 6.0506 | 52.3977 | 67.8418 | 71.8838 | 71.6418 | 71.6599 | 72.0748 | 73.1695 | 73.9022 | 74.6196 | 75.4587 | 76.2361 | 76.9909 | 77.0771 | 77.9581 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902 | 77.2902
90% | 5.6725 | 43.8325 | 58.4305 | 62.4259 | 62.3263 | 62.3201 | 62.7819 | 63.206 | 64.272 | 65.0133 | 65.3577 | 65.7526 | 66.1083 | 66.9154 | 67.8172 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 67.8331 | 90% | 16.2611 | 49.6399 | 64.2712 | 68.1004 | 67.8712 | 67.8883 | 68.2814 | 69.3184 | 70.0126 | 70.6923 | 71.4872 | 72.2237 | 72.9388 | 73.0204 | 73.855 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223 | 73.2223
85% | 15.8829 | 41.3973 | 55.1844 | 58.9578 | 58.8637 | 58.8578 | 59.294 | 59.6946 | 60.7013 | 61.4014 | 61.7267 | 62.0996 | 62.4356 | 63.1979 | 64.0496 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 64.0646 | 85% | 26.4715 | 46.8821 | 60.7006 | 64.3171 | 64.1006 | 64.1167 | 64.488 | 65.4674 | 66.1231 | 66.7649 | 67.5157 | 68.2113 | 68.8866 | 68.9637 | 69.752 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544 | 69.1544
80% | 31.0095 | 38.9622 | 51.9382 | 55.4897 | 55.4011 | 55.3956 | 55.8061 | 56.1831 | 57.1307 | 57.7896 | 58.0957 | 58.4467 | 58.7629 | 59.4804 | 60.2819 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 60.2961 | 80% | 34.0348 | 44.1243 | 57.13 | 60.5337 | 60.33 | 60.3452 | 60.6946 | 61.6164 | 62.2335 | 62.8376 | 63.5441 | 64.1988 | 64.8345 | 64.907 | 65.6489 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865 | 65.0865
75% | 72.9857 | 36.5271 | 48.6921 | 52.0216 | 51.9386 | 51.9334 | 52.3182 | 52.6717 | 53.56 | 54.1777 | 54.4647 | 54.7938 | 55.0902 | 55.7629 | 56.5143 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 56.5276 | 75% | 48.405 | 41.3666 | 53.5594 | 56.7504 | 56.5594 | 56.5736 | 56.9012 | 57.7654 | 58.3439 | 58.9102 | 59.5726 | 60.1864 | 60.7823 | 60.8503 | 61.5458 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186 | 61.0186
70% | 150.5094 | 34.0919 | 45.446 | 48.5535 | 48.476 | 48.4712 | 48.8303 | 49.1603 | 49.9893 | 50.5659 | 50.8337 | 51.1409 | 51.4175 | 52.0453 | 52.7467 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 52.7591 | 70% | 76.3892 | 38.6088 | 49.9887 | 52.967 | 52.7887 | 52.802 | 53.1077 | 53.9143 | 54.4543 | 54.9829 | 55.6011 | 56.174 | 56.7301 | 56.7936 | 57.4428 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507 | 56.9507
65% | 359.6342 | 31.6568 | 42.1998 | 45.0854 | 45.0134 | 45.0089 | 45.3425 | 45.6488 | 46.4187 | 46.954 | 47.2027 | 47.488 | 47.7449 | 48.3278 | 48.9791 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 48.9906 | 65% | 114.2056 | 35.851 | 46.4181 | 49.1837 | 49.0181 | 49.0304 | 49.3143 | 50.0633 | 50.5647 | 51.0555 | 51.6296 | 52.1615 | 52.678 | 52.737 | 53.3397 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828 | 52.8828
60% | 689.7717 | 29.2216 | 38.9537 | 41.6173 | 41.5508 | 41.5467 | 41.8546 | 42.1374 | 42.848 | 43.3422 | 43.5718 | 43.835 | 44.0722 | 44.6103 | 45.2115 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 45.2221 | 60% | 178.1154 | 33.0933 | 42.8475 | 45.4003 | 45.2475 | 45.2589 | 45.5209 | 46.2123 | 46.6751 | 47.1282 | 47.6581 | 48.1491 | 48.6258 | 48.6803 | 49.2367 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149 | 48.8149
55% | 1095.5419 | 26.7865 | 35.7075 | 38.1492 | 38.0883 | 38.0845 | 38.3667 | 38.6259 | 39.2773 | 39.7303 | 39.9408 | 40.1821 | 40.3995 | 40.8928 | 41.4438 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 41.4536 | 55% | 311.6074 | 30.3355 | 39.2769 | 41.6169 | 41.4769 | 41.4873 | 41.7275 | 42.3613 | 42.7855 | 43.2008 | 43.6866 | 44.1367 | 44.5737 | 44.6236 | 45.1336 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747 | 44.747
50% | 1666.1918 | 24.3514 | 32.4614 | 34.6811 | 34.6257 | 34.6223 | 34.8788 | 35.1145 | 35.7067 | 36.1185 | 36.3098 | 36.5292 | 36.7268 | 37.1752 | 37.6762 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 37.6851 | 50% | 636.0723 | 27.5777 | 35.7062 | 37.8336 | 37.7062 | 37.7157 | 37.9341 | 38.5102 | 38.8959 | 39.2735 | 39.7151 | 40.1243 | 40.5215 | 40.5669 | 41.0306 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791 | 40.6791
45% | 2506.0947 | 21.9162 | 29.2153 | 31.213 | 31.1631 | 31.16 | 31.3909 | 31.603 | 32.136 | 32.5066 | 32.6788 | 32.8763 | 33.0541 | 33.4577 | 33.9086 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 33.9165 | 45% | 1179.4944 | 24.8199 | 32.1356 | 34.0502 | 33.9356 | 33.9442 | 34.1407 | 34.6592 | 35.0063 | 35.3461 | 35.7436 | 36.1118 | 36.4694 | 36.5102 | 36.9275 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112 | 36.6112
40% | 3164.4787 | 19.4811 | 25.9691 | 27.7449 | 27.7006 | 27.6978 | 27.9031 | 28.0916 | 28.5653 | 28.8948 | 29.0478 | 29.2234 | 29.3815 | 29.7402 | 30.141 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 30.148 | 40% | 1808.3816 | 22.0622 | 28.565 | 30.2669 | 30.165 | 30.1726 | 30.3473 | 30.8082 | 31.1167 | 31.4188 | 31.7721 | 32.0994 | 32.4172 | 32.4535 | 32.8244 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432 | 32.5432
35% | 3551.3408 | 17.046 | 22.723 | 24.2767 | 24.238 | 24.2356 | 24.4152 | 24.5801 | 24.9947 | 25.2829 | 25.4169 | 25.5704 | 25.7088 | 26.0227 | 26.3733 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 26.3795 | 35% | 2779.1293 | 19.3044 | 24.9944 | 26.4835 | 26.3944 | 26.401 | 26.5539 | 26.9572 | 27.2271 | 27.4914 | 27.8006 | 28.087 | 28.3651 | 28.3968 | 28.7214 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753 | 28.4753
30% | 3758.953 | 14.6108 | 19.4768 | 20.8086 | 20.7754 | 20.7734 | 20.9273 | 21.0687 | 21.424 | 21.6711 | 21.7859 | 21.9175 | 22.0361 | 22.3051 | 22.6057 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 22.611 | 30% | 3814.165 | 16.5466 | 21.4237 | 22.7001 | 22.6237 | 22.6294 | 22.7605 | 23.1061 | 23.3375 | 23.5641 | 23.8291 | 24.0746 | 24.3129 | 24.3401 | 24.6183 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074 | 24.4074
25% | 3926.4798 | 12.1757 | 16.2307 | 17.3405 | 17.3129 | 17.3111 | 17.4394 | 17.5572 | 17.8533 | 18.0592 | 18.1549 | 18.2646 | 18.3634 | 18.5876 | 18.8381 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 18.8425 | 25% | 4166.9923 | 13.7889 | 17.8531 | 18.9168 | 18.8531 | 18.8579 | 18.9671 | 19.2551 | 19.448 | 19.6367 | 19.8575 | 20.0621 | 20.2608 | 20.2834 | 20.5153 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395 | 20.3395
20% | 4050.5177 | 9.7405 | 12.9846 | 13.8724 | 13.8503 | 13.8489 | 13.9515 | 14.0458 | 14.2827 | 14.4474 | 14.5239 | 14.6117 | 14.6907 | 14.8701 | 15.0705 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 15.074 | 20% | 4282.7105 | 11.0311 | 14.2825 | 15.1334 | 15.0825 | 15.0863 | 15.1736 | 15.4041 | 15.5584 | 15.7094 | 15.886 | 16.0497 | 16.2086 | 16.2268 | 16.4122 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716 | 16.2716
15% | 4152.622 | 7.3054 | 9.7384 | 10.4043 | 10.3877 | 10.3867 | 10.4636 | 10.5343 | 10.712 | 10.8355 | 10.8929 | 10.9588 | 11.018 | 11.1526 | 11.3029 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 11.3055 | 15% | 4364.7722 | 8.2733 | 10.7119 | 11.3501 | 11.3119 | 11.3147 | 11.3802 | 11.5531 | 11.6688 | 11.782 | 11.9145 | 12.0373 | 12.1565 | 12.1701 | 12.3092 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037 | 12.2037
10% | 4248.2976 | 4.8703 | 6.4923 | 6.9362 | 6.9251 | 6.9245 | 6.9758 | 7.0229 | 7.1413 | 7.2237 | 7.262 | 7.3058 | 7.3454 | 7.435 | 7.5352 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 7.537 | 10% | 4391.6218 | 5.5155 | 7.1412 | 7.5667 | 7.5412 | 7.5431 | 7.5868 | 7.702 | 7.7792 | 7.8547 | 7.943 | 8.0249 | 8.1043 | 8.1134 | 8.2061 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358 | 8.1358
5% | 4361.7469 | 2.4351 | 3.2461 | 3.4681 | 3.4626 | 3.4622 | 3.4879 | 3.5114 | 3.5707 | 3.6118 | 3.631 | 3.6529 | 3.6727 | 3.7175 | 3.7676 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 3.7685 | 5% | 4391.6218 | 2.7578 | 3.5706 | 3.7834 | 3.7706 | 3.7716 | 3.7934 | 3.851 | 3.8896 | 3.9273 | 3.9715 | 4.0124 | 4.0522 | 4.0567 | 4.1031 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679 | 4.0679
9.992e-14% | 4391.6218 | 4.8664e-14 | 6.4871e-14 | 6.9307e-14 | 6.9196e-14 | 6.9189e-14 | 6.9702e-14 | 7.0173e-14 | 7.1356e-14 | 7.2179e-14 | 7.2562e-14 | 7.3e-14 | 7.3395e-14 | 7.4291e-14 | 7.5292e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 7.531e-14 | 9.992e-14% | 4391.6218 | 5.5111e-14 | 7.1355e-14 | 7.5607e-14 | 7.5352e-14 | 7.5371e-14 | 7.5808e-14 | 7.6959e-14 | 7.773e-14 | 7.8484e-14 | 7.9367e-14 | 8.0184e-14 | 8.0978e-14 | 8.1069e-14 | 8.1996e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14 | 8.1293e-14
Option 7
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 73.9197 | 74.5682 | 75.6918 | 78.2537 | 79.9649 | 82.1367 | 83.2619 | 84.2491 | 82.4136 | 84.5551 | 87.9243 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 77.2737 | 77.7701 | 78.8692 | 81.4712 | 82.8877 | 85.5941 | 93.83 | 87.0301 | 85.697 | 87.4862 | 91.4045 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 73.173 | 73.815 | 74.9272 | 77.4632 | 79.1572 | 81.3071 | 82.4209 | 83.3981 | 81.5812 | 83.701 | 87.0362 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 76.4931 | 76.9846 | 78.0726 | 80.6483 | 82.0504 | 84.7295 | 92.8822 | 86.151 | 84.8313 | 86.6025 | 90.4812 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 72.4263 | 73.0618 | 74.1627 | 76.6728 | 78.3495 | 80.4774 | 81.5798 | 82.5471 | 80.7487 | 82.847 | 86.1481 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 75.7126 | 76.199 | 77.2759 | 79.8254 | 81.2132 | 83.865 | 91.9344 | 85.2719 | 83.9657 | 85.7188 | 89.558 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 70.933 | 71.5553 | 72.6335 | 75.0919 | 76.734 | 78.8181 | 79.8978 | 80.8451 | 79.0838 | 81.1388 | 84.3718 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 74.1515 | 74.6279 | 75.6826 | 78.1795 | 79.5387 | 82.1358 | 90.0389 | 83.5138 | 82.2345 | 83.9514 | 87.7114 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 67.1997 | 67.7893 | 68.8107 | 71.1397 | 72.6954 | 74.6697 | 75.6926 | 76.5901 | 74.9215 | 76.8683 | 79.9312 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 70.2488 | 70.7001 | 71.6993 | 74.0648 | 75.3524 | 77.8128 | 85.3 | 79.1183 | 77.9063 | 79.5329 | 83.095 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 63.4664 | 64.0232 | 64.9879 | 67.1875 | 68.6567 | 70.5214 | 71.4875 | 72.3351 | 70.7592 | 72.5978 | 75.4906 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 66.3461 | 66.7723 | 67.716 | 69.9501 | 71.1662 | 73.4899 | 80.5611 | 74.7228 | 73.5782 | 75.1144 | 78.4786 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 59.7331 | 60.2571 | 61.1651 | 63.2353 | 64.6181 | 66.3731 | 67.2823 | 68.08 | 66.5969 | 68.3274 | 71.05 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 62.4434 | 62.8445 | 63.7327 | 65.8353 | 66.9799 | 69.167 | 75.8222 | 70.3274 | 69.2501 | 70.6959 | 73.8622 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 55.9997 | 56.4911 | 57.3423 | 59.2831 | 60.5795 | 62.2248 | 63.0772 | 63.825 | 62.4346 | 64.0569 | 66.6093 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 58.5407 | 58.9167 | 59.7494 | 61.7206 | 62.7937 | 64.844 | 71.0833 | 65.9319 | 64.9219 | 66.2774 | 69.2458 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 52.2664 | 52.725 | 53.5194 | 55.3309 | 56.5408 | 58.0765 | 58.8721 | 59.57 | 58.2723 | 59.7865 | 62.1687 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 54.638 | 54.989 | 55.7661 | 57.6059 | 58.6074 | 60.5211 | 66.3444 | 61.5365 | 60.5938 | 61.8589 | 64.6295 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 48.5331 | 48.9589 | 49.6966 | 51.3787 | 52.5022 | 53.9282 | 54.6669 | 55.315 | 54.11 | 55.516 | 57.7281 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 50.7352 | 51.0612 | 51.7828 | 53.4912 | 54.4212 | 56.1982 | 61.6055 | 57.141 | 56.2657 | 57.4405 | 60.0131 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 44.7998 | 45.1928 | 45.8738 | 47.4265 | 48.4636 | 49.7798 | 50.4618 | 51.06 | 49.9477 | 51.2455 | 53.2875 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 46.8325 | 47.1334 | 47.7995 | 49.3765 | 50.235 | 51.8752 | 56.8666 | 52.7455 | 51.9376 | 53.022 | 55.3967 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 41.0665 | 41.4268 | 42.051 | 43.4743 | 44.425 | 45.6315 | 46.2566 | 46.805 | 45.7854 | 46.9751 | 48.8469 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 42.9298 | 43.2056 | 43.8162 | 45.2618 | 46.0487 | 47.5523 | 52.1278 | 48.3501 | 47.6094 | 48.6035 | 50.7803 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 37.3332 | 37.6607 | 38.2282 | 39.5221 | 40.3863 | 41.4832 | 42.0515 | 42.55 | 41.623 | 42.7046 | 44.4062 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 39.0271 | 39.2778 | 39.833 | 41.1471 | 41.8625 | 43.2294 | 47.3889 | 43.9546 | 43.2813 | 44.185 | 46.1639 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 33.5998 | 33.8946 | 34.4054 | 35.5699 | 36.3477 | 37.3349 | 37.8463 | 38.295 | 37.4607 | 38.4342 | 39.9656 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 35.1244 | 35.35 | 35.8497 | 37.0324 | 37.6762 | 38.9064 | 42.65 | 39.5591 | 38.9532 | 39.7665 | 41.5475 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 29.8665 | 30.1286 | 30.5825 | 31.6176 | 32.3091 | 33.1866 | 33.6412 | 34.04 | 33.2984 | 34.1637 | 35.525 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 31.2217 | 31.4223 | 31.8664 | 32.9177 | 33.49 | 34.5835 | 37.9111 | 35.1637 | 34.625 | 35.348 | 36.9311 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 26.1332 | 26.3625 | 26.7597 | 27.6654 | 28.2704 | 29.0382 | 29.436 | 29.785 | 29.1361 | 29.8932 | 31.0844 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 27.319 | 27.4945 | 27.8831 | 28.803 | 29.3037 | 30.2606 | 33.1722 | 30.7682 | 30.2969 | 30.9295 | 32.3147 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 22.3999 | 22.5964 | 22.9369 | 23.7132 | 24.2318 | 24.8899 | 25.2309 | 25.53 | 24.9738 | 25.6228 | 26.6437 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 23.4163 | 23.5667 | 23.8998 | 24.6883 | 25.1175 | 25.9376 | 28.4333 | 26.3728 | 25.9688 | 26.511 | 27.6983 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 18.6666 | 18.8304 | 19.1141 | 19.761 | 20.1932 | 20.7416 | 21.0257 | 21.275 | 20.8115 | 21.3523 | 22.2031 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 19.5136 | 19.6389 | 19.9165 | 20.5735 | 20.9312 | 21.6147 | 23.6944 | 21.9773 | 21.6406 | 22.0925 | 23.0819 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.9333 | 15.0643 | 15.2913 | 15.8088 | 16.1545 | 16.5933 | 16.8206 | 17.02 | 16.6492 | 17.0818 | 17.7625 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 15.6108 | 15.7111 | 15.9332 | 16.4588 | 16.745 | 17.2917 | 18.9555 | 17.5818 | 17.3125 | 17.674 | 18.4656 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 11.1999 | 11.2982 | 11.4685 | 11.8566 | 12.1159 | 12.445 | 12.6154 | 12.765 | 12.4869 | 12.8114 | 13.3219 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.7081 | 11.7833 | 11.9499 | 12.3441 | 12.5587 | 12.9688 | 14.2167 | 13.1864 | 12.9844 | 13.2555 | 13.8492 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.4666 | 7.5321 | 7.6456 | 7.9044 | 8.0773 | 8.2966 | 8.4103 | 8.51 | 8.3246 | 8.5409 | 8.8812 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.8054 | 7.8556 | 7.9666 | 8.2294 | 8.3725 | 8.6459 | 9.4778 | 8.7909 | 8.6563 | 8.837 | 9.2328 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.7333 | 3.7661 | 3.8228 | 3.9522 | 4.0386 | 4.1483 | 4.2051 | 4.255 | 4.1623 | 4.2705 | 4.4406 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.9027 | 3.9278 | 3.9833 | 4.1147 | 4.1862 | 4.3229 | 4.7389 | 4.3955 | 4.3281 | 4.4185 | 4.6164 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.4607e-14 | 7.5261e-14 | 7.6395e-14 | 7.8981e-14 | 8.0708e-14 | 8.29e-14 | 8.4036e-14 | 8.5032e-14 | 8.318e-14 | 8.5341e-14 | 8.8741e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.7992e-14 | 7.8493e-14 | 7.9602e-14 | 8.2228e-14 | 8.3658e-14 | 8.639e-14 | 9.4702e-14 | 8.7839e-14 | 8.6493e-14 | 8.8299e-14 | 9.2254e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 78.9523 | 78.944 | 79.5082 | 80.1275 | 81.4 | 82.3146 | 82.8098 | 83.3506 | 83.8463 | 84.7437 | 85.858 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 85.0518 | 85.0691 | 85.5577 | 86.8512 | 87.7148 | 88.5615 | 89.5523 | 90.4688 | 91.3598 | 91.4592 | 92.4996 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061
98% | 0 | 55.3193 | 73.3854 | 78.3 | 78.1548 | 78.1466 | 78.7051 | 79.3181 | 80.5778 | 81.4832 | 81.9734 | 82.5086 | 82.9994 | 83.8877 | 84.9908 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 84.1927 | 84.2098 | 84.6935 | 85.9739 | 86.8287 | 87.667 | 88.6477 | 89.555 | 90.437 | 90.5354 | 91.5653 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 77.3573 | 77.3492 | 77.902 | 78.5088 | 79.7556 | 80.6517 | 81.1369 | 81.6667 | 82.1524 | 83.0317 | 84.1235 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 83.3336 | 83.3505 | 83.8292 | 85.0966 | 85.9427 | 86.7724 | 87.7432 | 88.6411 | 89.5142 | 89.6115 | 90.631 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 75.7623 | 75.7544 | 76.2958 | 76.89 | 78.1112 | 78.9888 | 79.464 | 79.9829 | 80.4586 | 81.3197 | 82.389 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 81.6153 | 81.632 | 82.1008 | 83.342 | 84.1707 | 84.9833 | 85.934 | 86.8135 | 87.6685 | 87.7639 | 88.7623 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 71.7748 | 71.7673 | 72.2802 | 72.8432 | 74 | 74.8315 | 75.2817 | 75.7732 | 76.2239 | 77.0397 | 78.0527 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 77.3198 | 77.3355 | 77.7797 | 78.9556 | 79.7407 | 80.5105 | 81.4112 | 82.2444 | 83.0544 | 83.1447 | 84.0906 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 67.7874 | 67.7802 | 68.2646 | 68.7963 | 69.8889 | 70.6742 | 71.0994 | 71.5636 | 71.9893 | 72.7598 | 73.7165 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 73.0243 | 73.0391 | 73.4586 | 74.5692 | 75.3106 | 76.0377 | 76.8883 | 77.6752 | 78.4403 | 78.5256 | 79.4189 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 63.7999 | 63.7932 | 64.2491 | 64.7495 | 65.7778 | 66.5169 | 66.917 | 67.354 | 67.7546 | 68.4798 | 69.3802 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 68.7287 | 68.7427 | 69.1375 | 70.1827 | 70.8806 | 71.5649 | 72.3655 | 73.1061 | 73.8261 | 73.9064 | 74.7472 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 59.8124 | 59.8061 | 60.2335 | 60.7027 | 61.6667 | 62.3596 | 62.7347 | 63.1444 | 63.5199 | 64.1998 | 65.044 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 64.4332 | 64.4463 | 64.8164 | 65.7963 | 66.4506 | 67.0921 | 67.8427 | 68.537 | 69.212 | 69.2873 | 70.0755 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 55.8249 | 55.819 | 56.2179 | 56.6558 | 57.5556 | 58.2023 | 58.5524 | 58.9347 | 59.2853 | 59.9198 | 60.7077 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 60.1376 | 60.1499 | 60.4953 | 61.4099 | 62.0205 | 62.6193 | 63.3198 | 63.9678 | 64.5979 | 64.6681 | 65.4038 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 51.8374 | 51.8319 | 52.2024 | 52.609 | 53.4445 | 54.045 | 54.3701 | 54.7251 | 55.0506 | 55.6398 | 56.3714 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 55.8421 | 55.8534 | 56.1742 | 57.0235 | 57.5905 | 58.1465 | 58.797 | 59.3987 | 59.9837 | 60.049 | 60.7321 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 47.8499 | 47.8449 | 48.1868 | 48.5621 | 49.3334 | 49.8876 | 50.1878 | 50.5155 | 50.8159 | 51.3598 | 52.0352 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 51.5465 | 51.557 | 51.8531 | 52.6371 | 53.1605 | 53.6736 | 54.2741 | 54.8296 | 55.3696 | 55.4298 | 56.0604 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 43.8624 | 43.8578 | 44.1712 | 44.5153 | 45.2222 | 45.7303 | 46.0055 | 46.3059 | 46.5813 | 47.0798 | 47.6989 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 47.251 | 47.2606 | 47.532 | 48.2506 | 48.7304 | 49.2008 | 49.7513 | 50.2604 | 50.7555 | 50.8107 | 51.3887 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 39.8749 | 39.8707 | 40.1557 | 40.4684 | 41.1111 | 41.573 | 41.8231 | 42.0962 | 42.3466 | 42.7999 | 43.3626 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 42.9554 | 42.9642 | 43.211 | 43.8642 | 44.3004 | 44.728 | 45.2284 | 45.6913 | 46.1413 | 46.1915 | 46.717 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 35.8874 | 35.8837 | 36.1401 | 36.4216 | 37 | 37.4157 | 37.6408 | 37.8866 | 38.112 | 38.5199 | 39.0264 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 38.6599 | 38.6678 | 38.8899 | 39.4778 | 39.8703 | 40.2552 | 40.7056 | 41.1222 | 41.5272 | 41.5724 | 42.0453 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 31.8999 | 31.8966 | 32.1245 | 32.3748 | 32.8889 | 33.2584 | 33.4585 | 33.677 | 33.8773 | 34.2399 | 34.6901 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 34.3644 | 34.3713 | 34.5688 | 35.0914 | 35.4403 | 35.7824 | 36.1827 | 36.553 | 36.9131 | 36.9532 | 37.3736 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 27.9124 | 27.9095 | 28.109 | 28.3279 | 28.7778 | 29.1011 | 29.2762 | 29.4674 | 29.6426 | 29.9599 | 30.3538 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 30.0688 | 30.0749 | 30.2477 | 30.705 | 31.0103 | 31.3096 | 31.6599 | 31.9839 | 32.2989 | 32.3341 | 32.7019 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 23.9249 | 23.9224 | 24.0934 | 24.2811 | 24.6667 | 24.9438 | 25.0939 | 25.2577 | 25.408 | 25.6799 | 26.0176 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 25.7733 | 25.7785 | 25.9266 | 26.3185 | 26.5802 | 26.8368 | 27.1371 | 27.4148 | 27.6848 | 27.7149 | 28.0302 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 19.9375 | 19.9354 | 20.0778 | 20.2342 | 20.5556 | 20.7865 | 20.9116 | 21.0481 | 21.1733 | 21.3999 | 21.6813 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 21.4777 | 21.4821 | 21.6055 | 21.9321 | 22.1502 | 22.364 | 22.6142 | 22.8457 | 23.0707 | 23.0958 | 23.3585 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.95 | 15.9483 | 16.0623 | 16.1874 | 16.4445 | 16.6292 | 16.7293 | 16.8385 | 16.9386 | 17.1199 | 17.3451 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 17.1822 | 17.1857 | 17.2844 | 17.5457 | 17.7202 | 17.8912 | 18.0914 | 18.2765 | 18.4565 | 18.4766 | 18.6868 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.9625 | 11.9612 | 12.0467 | 12.1405 | 12.3333 | 12.4719 | 12.5469 | 12.6289 | 12.704 | 12.84 | 13.0088 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.8866 | 12.8893 | 12.9633 | 13.1593 | 13.2901 | 13.4184 | 13.5685 | 13.7074 | 13.8424 | 13.8575 | 14.0151 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.975 | 7.9741 | 8.0311 | 8.0937 | 8.2222 | 8.3146 | 8.3646 | 8.4192 | 8.4693 | 8.56 | 8.6725 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.5911 | 8.5928 | 8.6422 | 8.7728 | 8.8601 | 8.9456 | 9.0457 | 9.1383 | 9.2283 | 9.2383 | 9.3434 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.9875 | 3.9871 | 4.0156 | 4.0468 | 4.1111 | 4.1573 | 4.1823 | 4.2096 | 4.2347 | 4.28 | 4.3363 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.2955 | 4.2964 | 4.3211 | 4.3864 | 4.43 | 4.4728 | 4.5228 | 4.5691 | 4.6141 | 4.6192 | 4.6717 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.9686e-14 | 7.9678e-14 | 8.0247e-14 | 8.0872e-14 | 8.2157e-14 | 8.308e-14 | 8.3579e-14 | 8.4125e-14 | 8.4626e-14 | 8.5531e-14 | 8.6656e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.5842e-14 | 8.586e-14 | 8.6353e-14 | 8.7658e-14 | 8.853e-14 | 8.9385e-14 | 9.0385e-14 | 9.131e-14 | 9.2209e-14 | 9.2309e-14 | 9.3359e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14
Option 8
Winter Season | [31 empty] | Winter Season
P50 | [31 empty] | P10
% of MD | Winter - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Winter - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 49.7042 | 68.8514 | 73.8223 | 74.6663 | 75.3214 | 76.4563 | 79.0441 | 80.7726 | 82.9664 | 84.1029 | 85.1001 | 83.2461 | 85.4092 | 88.8125 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 86.2221 | 100% | 0 | 53.1876 | 72.0932 | 77.2584 | 78.0542 | 78.5557 | 79.6659 | 82.2942 | 83.7249 | 86.4587 | 94.7777 | 87.9092 | 86.5626 | 88.3699 | 92.3278 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413 | 89.6413
99% | 1.486 | 49.2072 | 68.1629 | 73.0841 | 73.9197 | 74.5682 | 75.6918 | 78.2537 | 79.9649 | 82.1367 | 83.2619 | 84.2491 | 82.4136 | 84.5551 | 87.9243 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 85.3598 | 99% | 1.486 | 52.6557 | 71.3723 | 76.4858 | 77.2737 | 77.7701 | 78.8692 | 81.4712 | 82.8877 | 85.5941 | 93.83 | 87.0301 | 85.697 | 87.4862 | 91.4045 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449 | 88.7449
98% | 3.2692 | 48.7101 | 67.4743 | 72.3458 | 73.173 | 73.815 | 74.9272 | 77.4632 | 79.1572 | 81.3071 | 82.4209 | 83.3981 | 81.5812 | 83.701 | 87.0362 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 84.4976 | 98% | 3.2692 | 52.1238 | 70.6514 | 75.7133 | 76.4931 | 76.9846 | 78.0726 | 80.6483 | 82.0504 | 84.7295 | 92.8822 | 86.151 | 84.8313 | 86.6025 | 90.4812 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485 | 87.8485
97% | 6.8356 | 48.2131 | 66.7858 | 71.6076 | 72.4263 | 73.0618 | 74.1627 | 76.6728 | 78.3495 | 80.4774 | 81.5798 | 82.5471 | 80.7487 | 82.847 | 86.1481 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 83.6354 | 97% | 6.8356 | 51.5919 | 69.9304 | 74.9407 | 75.7126 | 76.199 | 77.2759 | 79.8254 | 81.2132 | 83.865 | 91.9344 | 85.2719 | 83.9657 | 85.7188 | 89.558 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521 | 86.9521
95% | 17.5347 | 47.219 | 65.4088 | 70.1312 | 70.933 | 71.5553 | 72.6335 | 75.0919 | 76.734 | 78.8181 | 79.8978 | 80.8451 | 79.0838 | 81.1388 | 84.3718 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 81.911 | 95% | 17.5347 | 50.5282 | 68.4886 | 73.3955 | 74.1515 | 74.6279 | 75.6826 | 78.1795 | 79.5387 | 82.1358 | 90.0389 | 83.5138 | 82.2345 | 83.9514 | 87.7114 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592 | 85.1592
90% | 78.7576 | 44.7338 | 61.9662 | 66.4401 | 67.1997 | 67.7893 | 68.8107 | 71.1397 | 72.6954 | 74.6697 | 75.6926 | 76.5901 | 74.9215 | 76.8683 | 79.9312 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 77.5999 | 90% | 78.7576 | 47.8688 | 64.8839 | 69.5326 | 70.2488 | 70.7001 | 71.6993 | 74.0648 | 75.3524 | 77.8128 | 85.3 | 79.1183 | 77.9063 | 79.5329 | 83.095 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772 | 80.6772
85% | 236.8672 | 42.2486 | 58.5237 | 62.7489 | 63.4664 | 64.0232 | 64.9879 | 67.1875 | 68.6567 | 70.5214 | 71.4875 | 72.3351 | 70.7592 | 72.5978 | 75.4906 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 73.2888 | 85% | 236.8672 | 45.2094 | 61.2792 | 65.6697 | 66.3461 | 66.7723 | 67.716 | 69.9501 | 71.1662 | 73.4899 | 80.5611 | 74.7228 | 73.5782 | 75.1144 | 78.4786 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951 | 76.1951
80% | 497.5104 | 39.7634 | 55.0811 | 59.0578 | 59.7331 | 60.2571 | 61.1651 | 63.2353 | 64.6181 | 66.3731 | 67.2823 | 68.08 | 66.5969 | 68.3274 | 71.05 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 68.9777 | 80% | 497.5104 | 42.55 | 57.6746 | 61.8067 | 62.4434 | 62.8445 | 63.7327 | 65.8353 | 66.9799 | 69.167 | 75.8222 | 70.3274 | 69.2501 | 70.6959 | 73.8622 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131 | 71.7131
75% | 803.6248 | 37.2782 | 51.6385 | 55.3667 | 55.9997 | 56.4911 | 57.3423 | 59.2831 | 60.5795 | 62.2248 | 63.0772 | 63.825 | 62.4346 | 64.0569 | 66.6093 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 64.6665 | 75% | 803.6248 | 39.8907 | 54.0699 | 57.9438 | 58.5407 | 58.9167 | 59.7494 | 61.7206 | 62.7937 | 64.844 | 71.0833 | 65.9319 | 64.9219 | 66.2774 | 69.2458 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231 | 67.231
70% | 1155.2107 | 34.793 | 48.196 | 51.6756 | 52.2664 | 52.725 | 53.5194 | 55.3309 | 56.5408 | 58.0765 | 58.8721 | 59.57 | 58.2723 | 59.7865 | 62.1687 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 60.3554 | 70% | 1155.2107 | 37.2313 | 50.4653 | 54.0809 | 54.638 | 54.989 | 55.7661 | 57.6059 | 58.6074 | 60.5211 | 66.3444 | 61.5365 | 60.5938 | 61.8589 | 64.6295 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489 | 62.7489
65% | 1553.1596 | 32.3077 | 44.7534 | 47.9845 | 48.5331 | 48.9589 | 49.6966 | 51.3787 | 52.5022 | 53.9282 | 54.6669 | 55.315 | 54.11 | 55.516 | 57.7281 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 56.0443 | 65% | 1553.1596 | 34.5719 | 46.8606 | 50.218 | 50.7352 | 51.0612 | 51.7828 | 53.4912 | 54.4212 | 56.1982 | 61.6055 | 57.141 | 56.2657 | 57.4405 | 60.0131 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669 | 58.2669
60% | 2026.2996 | 29.8225 | 41.3108 | 44.2934 | 44.7998 | 45.1928 | 45.8738 | 47.4265 | 48.4636 | 49.7798 | 50.4618 | 51.06 | 49.9477 | 51.2455 | 53.2875 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 51.7332 | 60% | 2026.2996 | 31.9125 | 43.2559 | 46.3551 | 46.8325 | 47.1334 | 47.7995 | 49.3765 | 50.235 | 51.8752 | 56.8666 | 52.7455 | 51.9376 | 53.022 | 55.3967 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848 | 53.7848
55% | 2598.4068 | 27.3373 | 37.8683 | 40.6023 | 41.0665 | 41.4268 | 42.051 | 43.4743 | 44.425 | 45.6315 | 46.2566 | 46.805 | 45.7854 | 46.9751 | 48.8469 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 47.4221 | 55% | 2598.4068 | 29.2532 | 39.6513 | 42.4921 | 42.9298 | 43.2056 | 43.8162 | 45.2618 | 46.0487 | 47.5523 | 52.1278 | 48.3501 | 47.6094 | 48.6035 | 50.7803 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027 | 49.3027
50% | 3233.5201 | 24.8521 | 34.4257 | 36.9111 | 37.3332 | 37.6607 | 38.2282 | 39.5221 | 40.3863 | 41.4832 | 42.0515 | 42.55 | 41.623 | 42.7046 | 44.4062 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 43.111 | 50% | 3233.5201 | 26.5938 | 36.0466 | 38.6292 | 39.0271 | 39.2778 | 39.833 | 41.1471 | 41.8625 | 43.2294 | 47.3889 | 43.9546 | 43.2813 | 44.185 | 46.1639 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207 | 44.8207
45% | 3775.313 | 22.3669 | 30.9831 | 33.22 | 33.5998 | 33.8946 | 34.4054 | 35.5699 | 36.3477 | 37.3349 | 37.8463 | 38.295 | 37.4607 | 38.4342 | 39.9656 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 38.7999 | 45% | 3775.313 | 23.9344 | 32.442 | 34.7663 | 35.1244 | 35.35 | 35.8497 | 37.0324 | 37.6762 | 38.9064 | 42.65 | 39.5591 | 38.9532 | 39.7665 | 41.5475 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386 | 40.3386
40% | 4072.8088 | 19.8817 | 27.5405 | 29.5289 | 29.8665 | 30.1286 | 30.5825 | 31.6176 | 32.3091 | 33.1866 | 33.6412 | 34.04 | 33.2984 | 34.1637 | 35.525 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 34.4888 | 40% | 4072.8088 | 21.275 | 28.8373 | 30.9034 | 31.2217 | 31.4223 | 31.8664 | 32.9177 | 33.49 | 34.5835 | 37.9111 | 35.1637 | 34.625 | 35.348 | 36.9311 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565 | 35.8565
35% | 4198.821 | 17.3965 | 24.098 | 25.8378 | 26.1332 | 26.3625 | 26.7597 | 27.6654 | 28.2704 | 29.0382 | 29.436 | 29.785 | 29.1361 | 29.8932 | 31.0844 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 30.1777 | 35% | 4198.821 | 18.6156 | 25.2326 | 27.0405 | 27.319 | 27.4945 | 27.8831 | 28.803 | 29.3037 | 30.2606 | 33.1722 | 30.7682 | 30.2969 | 30.9295 | 32.3147 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745 | 31.3745
30% | 4271.3374 | 14.9113 | 20.6554 | 22.1467 | 22.3999 | 22.5964 | 22.9369 | 23.7132 | 24.2318 | 24.8899 | 25.2309 | 25.53 | 24.9738 | 25.6228 | 26.6437 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 25.8666 | 30% | 4271.3374 | 15.9563 | 21.628 | 23.1775 | 23.4163 | 23.5667 | 23.8998 | 24.6883 | 25.1175 | 25.9376 | 28.4333 | 26.3728 | 25.9688 | 26.511 | 27.6983 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924 | 26.8924
25% | 4321.8611 | 12.4261 | 17.2128 | 18.4556 | 18.6666 | 18.8304 | 19.1141 | 19.761 | 20.1932 | 20.7416 | 21.0257 | 21.275 | 20.8115 | 21.3523 | 22.2031 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 21.5555 | 25% | 4321.8611 | 13.2969 | 18.0233 | 19.3146 | 19.5136 | 19.6389 | 19.9165 | 20.5735 | 20.9312 | 21.6147 | 23.6944 | 21.9773 | 21.6406 | 22.0925 | 23.0819 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103 | 22.4103
20% | 4353.067 | 9.9408 | 13.7703 | 14.7645 | 14.9333 | 15.0643 | 15.2913 | 15.8088 | 16.1545 | 16.5933 | 16.8206 | 17.02 | 16.6492 | 17.0818 | 17.7625 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 17.2444 | 20% | 4353.067 | 10.6375 | 14.4186 | 15.4517 | 15.6108 | 15.7111 | 15.9332 | 16.4588 | 16.745 | 17.2917 | 18.9555 | 17.5818 | 17.3125 | 17.674 | 18.4656 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283 | 17.9283
15% | 4369.4129 | 7.4556 | 10.3277 | 11.0733 | 11.1999 | 11.2982 | 11.4685 | 11.8566 | 12.1159 | 12.445 | 12.6154 | 12.765 | 12.4869 | 12.8114 | 13.3219 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 12.9333 | 15% | 4369.4129 | 7.9781 | 10.814 | 11.5888 | 11.7081 | 11.7833 | 11.9499 | 12.3441 | 12.5587 | 12.9688 | 14.2167 | 13.1864 | 12.9844 | 13.2555 | 13.8492 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462 | 13.4462
10% | 4378.6261 | 4.9704 | 6.8851 | 7.3822 | 7.4666 | 7.5321 | 7.6456 | 7.9044 | 8.0773 | 8.2966 | 8.4103 | 8.51 | 8.3246 | 8.5409 | 8.8812 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 8.6222 | 10% | 4378.6261 | 5.3188 | 7.2093 | 7.7258 | 7.8054 | 7.8556 | 7.9666 | 8.2294 | 8.3725 | 8.6459 | 9.4778 | 8.7909 | 8.6563 | 8.837 | 9.2328 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641 | 8.9641
5% | 4391.7028 | 2.4852 | 3.4426 | 3.6911 | 3.7333 | 3.7661 | 3.8228 | 3.9522 | 4.0386 | 4.1483 | 4.2051 | 4.255 | 4.1623 | 4.2705 | 4.4406 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 4.3111 | 5% | 4391.7028 | 2.6594 | 3.6047 | 3.8629 | 3.9027 | 3.9278 | 3.9833 | 4.1147 | 4.1862 | 4.3229 | 4.7389 | 4.3955 | 4.3281 | 4.4185 | 4.6164 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821 | 4.4821
9.992e-14% | 4391.7028 | 4.9664e-14 | 6.8796e-14 | 7.3763e-14 | 7.4607e-14 | 7.5261e-14 | 7.6395e-14 | 7.8981e-14 | 8.0708e-14 | 8.29e-14 | 8.4036e-14 | 8.5032e-14 | 8.318e-14 | 8.5341e-14 | 8.8741e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 8.6153e-14 | 9.992e-14% | 4391.7028 | 5.3145e-14 | 7.2036e-14 | 7.7197e-14 | 7.7992e-14 | 7.8493e-14 | 7.9602e-14 | 8.2228e-14 | 8.3658e-14 | 8.639e-14 | 9.4702e-14 | 8.7839e-14 | 8.6493e-14 | 8.8299e-14 | 9.2254e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14 | 8.957e-14
Summer Season | [31 empty] | Summer Season
P50 | [31 empty] | P10
% of MD | Summer - AD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 | % of MD | Summer - MD - Hours | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
100% | 0 | 56.4483 | 74.8831 | 79.898 | 79.7498 | 79.7414 | 80.3113 | 80.9369 | 82.2223 | 83.1461 | 83.6463 | 84.1925 | 84.6932 | 85.5997 | 86.7253 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 86.6445 | 100% | 0 | 62.901 | 81.3728 | 86.203 | 85.9109 | 85.9284 | 86.4219 | 87.7284 | 88.6008 | 89.4561 | 90.4569 | 91.3826 | 92.2827 | 92.383 | 93.434 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325 | 92.6325
99% | 0 | 55.8838 | 74.1343 | 79.099 | 78.9523 | 78.944 | 79.5082 | 80.1275 | 81.4 | 82.3146 | 82.8098 | 83.3506 | 83.8463 | 84.7437 | 85.858 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 85.778 | 99% | 1.5127 | 62.272 | 80.559 | 85.341 | 85.0518 | 85.0691 | 85.5577 | 86.8512 | 87.7148 | 88.5615 | 89.5523 | 90.4688 | 91.3598 | 91.4592 | 92.4996 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061 | 91.7061
98% | 0 | 55.3193 | 73.3854 | 78.3 | 78.1548 | 78.1466 | 78.7051 | 79.3181 | 80.5778 | 81.4832 | 81.9734 | 82.5086 | 82.9994 | 83.8877 | 84.9908 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 84.9116 | 98% | 2.269 | 61.643 | 79.7453 | 84.4789 | 84.1927 | 84.2098 | 84.6935 | 85.9739 | 86.8287 | 87.667 | 88.6477 | 89.555 | 90.437 | 90.5354 | 91.5653 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798 | 90.7798
97% | 0.37816 | 54.7549 | 72.6366 | 77.501 | 77.3573 | 77.3492 | 77.902 | 78.5088 | 79.7556 | 80.6517 | 81.1369 | 81.6667 | 82.1524 | 83.0317 | 84.1235 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 84.0451 | 97% | 3.7816 | 61.014 | 78.9316 | 83.6169 | 83.3336 | 83.3505 | 83.8292 | 85.0966 | 85.9427 | 86.7724 | 87.7432 | 88.6411 | 89.5142 | 89.6115 | 90.631 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535 | 89.8535
95% | 2.269 | 53.6259 | 71.1389 | 75.9031 | 75.7623 | 75.7544 | 76.2958 | 76.89 | 78.1112 | 78.9888 | 79.464 | 79.9829 | 80.4586 | 81.3197 | 82.389 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 82.3122 | 95% | 6.0506 | 59.7559 | 77.3041 | 81.8928 | 81.6153 | 81.632 | 82.1008 | 83.342 | 84.1707 | 84.9833 | 85.934 | 86.8135 | 87.6685 | 87.7639 | 88.7623 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008 | 88.0008
90% | 5.6725 | 50.8035 | 67.3948 | 71.9082 | 71.7748 | 71.7673 | 72.2802 | 72.8432 | 74 | 74.8315 | 75.2817 | 75.7732 | 76.2239 | 77.0397 | 78.0527 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 77.98 | 90% | 16.2611 | 56.6109 | 73.2355 | 77.5827 | 77.3198 | 77.3355 | 77.7797 | 78.9556 | 79.7407 | 80.5105 | 81.4112 | 82.2444 | 83.0544 | 83.1447 | 84.0906 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692 | 83.3692
85% | 15.8829 | 47.9811 | 63.6506 | 67.9133 | 67.7874 | 67.7802 | 68.2646 | 68.7963 | 69.8889 | 70.6742 | 71.0994 | 71.5636 | 71.9893 | 72.7598 | 73.7165 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 73.6478 | 85% | 26.4715 | 53.4658 | 69.1669 | 73.2725 | 73.0243 | 73.0391 | 73.4586 | 74.5692 | 75.3106 | 76.0377 | 76.8883 | 77.6752 | 78.4403 | 78.5256 | 79.4189 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376 | 78.7376
80% | 31.0095 | 45.1586 | 59.9065 | 63.9184 | 63.7999 | 63.7932 | 64.2491 | 64.7495 | 65.7778 | 66.5169 | 66.917 | 67.354 | 67.7546 | 68.4798 | 69.3802 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 69.3156 | 80% | 34.0348 | 50.3208 | 65.0982 | 68.9624 | 68.7287 | 68.7427 | 69.1375 | 70.1827 | 70.8806 | 71.5649 | 72.3655 | 73.1061 | 73.8261 | 73.9064 | 74.7472 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106 | 74.106
75% | 72.9857 | 42.3362 | 56.1623 | 59.9235 | 59.8124 | 59.8061 | 60.2335 | 60.7027 | 61.6667 | 62.3596 | 62.7347 | 63.1444 | 63.5199 | 64.1998 | 65.044 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 64.9833 | 75% | 48.405 | 47.1757 | 61.0296 | 64.6522 | 64.4332 | 64.4463 | 64.8164 | 65.7963 | 66.4506 | 67.0921 | 67.8427 | 68.537 | 69.212 | 69.2873 | 70.0755 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744 | 69.4744
70% | 150.5094 | 39.5138 | 52.4182 | 55.9286 | 55.8249 | 55.819 | 56.2179 | 56.6558 | 57.5556 | 58.2023 | 58.5524 | 58.9347 | 59.2853 | 59.9198 | 60.7077 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 60.6511 | 70% | 76.3892 | 44.0307 | 56.9609 | 60.3421 | 60.1376 | 60.1499 | 60.4953 | 61.4099 | 62.0205 | 62.6193 | 63.3198 | 63.9678 | 64.5979 | 64.6681 | 65.4038 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427 | 64.8427
65% | 359.6342 | 36.6914 | 48.674 | 51.9337 | 51.8374 | 51.8319 | 52.2024 | 52.609 | 53.4445 | 54.045 | 54.3701 | 54.7251 | 55.0506 | 55.6398 | 56.3714 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 56.3189 | 65% | 114.2056 | 40.8856 | 52.8923 | 56.0319 | 55.8421 | 55.8534 | 56.1742 | 57.0235 | 57.5905 | 58.1465 | 58.797 | 59.3987 | 59.9837 | 60.049 | 60.7321 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111 | 60.2111
60% | 689.7717 | 33.869 | 44.9299 | 47.9388 | 47.8499 | 47.8449 | 48.1868 | 48.5621 | 49.3334 | 49.8876 | 50.1878 | 50.5155 | 50.8159 | 51.3598 | 52.0352 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 51.9867 | 60% | 178.1154 | 37.7406 | 48.8237 | 51.7218 | 51.5465 | 51.557 | 51.8531 | 52.6371 | 53.1605 | 53.6736 | 54.2741 | 54.8296 | 55.3696 | 55.4298 | 56.0604 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795 | 55.5795
55% | 1095.5419 | 31.0466 | 41.1857 | 43.9439 | 43.8624 | 43.8578 | 44.1712 | 44.5153 | 45.2222 | 45.7303 | 46.0055 | 46.3059 | 46.5813 | 47.0798 | 47.6989 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 47.6545 | 55% | 311.6074 | 34.5955 | 44.755 | 47.4116 | 47.251 | 47.2606 | 47.532 | 48.2506 | 48.7304 | 49.2008 | 49.7513 | 50.2604 | 50.7555 | 50.8107 | 51.3887 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479 | 50.9479
50% | 1666.1918 | 28.2242 | 37.4415 | 39.949 | 39.8749 | 39.8707 | 40.1557 | 40.4684 | 41.1111 | 41.573 | 41.8231 | 42.0962 | 42.3466 | 42.7999 | 43.3626 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 43.3222 | 50% | 636.0723 | 31.4505 | 40.6864 | 43.1015 | 42.9554 | 42.9642 | 43.211 | 43.8642 | 44.3004 | 44.728 | 45.2284 | 45.6913 | 46.1413 | 46.1915 | 46.717 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162 | 46.3162
45% | 2506.0947 | 25.4017 | 33.6974 | 35.9541 | 35.8874 | 35.8837 | 36.1401 | 36.4216 | 37 | 37.4157 | 37.6408 | 37.8866 | 38.112 | 38.5199 | 39.0264 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 38.99 | 45% | 1179.4944 | 28.3054 | 36.6177 | 38.7913 | 38.6599 | 38.6678 | 38.8899 | 39.4778 | 39.8703 | 40.2552 | 40.7056 | 41.1222 | 41.5272 | 41.5724 | 42.0453 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846 | 41.6846
40% | 3164.4787 | 22.5793 | 29.9532 | 31.9592 | 31.8999 | 31.8966 | 32.1245 | 32.3748 | 32.8889 | 33.2584 | 33.4585 | 33.677 | 33.8773 | 34.2399 | 34.6901 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 34.6578 | 40% | 1808.3816 | 25.1604 | 32.5491 | 34.4812 | 34.3644 | 34.3713 | 34.5688 | 35.0914 | 35.4403 | 35.7824 | 36.1827 | 36.553 | 36.9131 | 36.9532 | 37.3736 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053 | 37.053
35% | 3551.3408 | 19.7569 | 26.2091 | 27.9643 | 27.9124 | 27.9095 | 28.109 | 28.3279 | 28.7778 | 29.1011 | 29.2762 | 29.4674 | 29.6426 | 29.9599 | 30.3538 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 30.3256 | 35% | 2779.1293 | 22.0153 | 28.4805 | 30.171 | 30.0688 | 30.0749 | 30.2477 | 30.705 | 31.0103 | 31.3096 | 31.6599 | 31.9839 | 32.2989 | 32.3341 | 32.7019 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214 | 32.4214
30% | 3758.953 | 16.9345 | 22.4649 | 23.9694 | 23.9249 | 23.9224 | 24.0934 | 24.2811 | 24.6667 | 24.9438 | 25.0939 | 25.2577 | 25.408 | 25.6799 | 26.0176 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 25.9933 | 30% | 3814.165 | 18.8703 | 24.4118 | 25.8609 | 25.7733 | 25.7785 | 25.9266 | 26.3185 | 26.5802 | 26.8368 | 27.1371 | 27.4148 | 27.6848 | 27.7149 | 28.0302 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897
25% | 3926.4798 | 14.1121 | 18.7208 | 19.9745 | 19.9375 | 19.9354 | 20.0778 | 20.2342 | 20.5556 | 20.7865 | 20.9116 | 21.0481 | 21.1733 | 21.3999 | 21.6813 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 21.6611 | 25% | 4166.9923 | 15.7252 | 20.3432 | 21.5507 | 21.4777 | 21.4821 | 21.6055 | 21.9321 | 22.1502 | 22.364 | 22.6142 | 22.8457 | 23.0707 | 23.0958 | 23.3585 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581 | 23.1581
20% | 4050.5177 | 11.2897 | 14.9766 | 15.9796 | 15.95 | 15.9483 | 16.0623 | 16.1874 | 16.4445 | 16.6292 | 16.7293 | 16.8385 | 16.9386 | 17.1199 | 17.3451 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 17.3289 | 20% | 4282.7105 | 12.5802 | 16.2746 | 17.2406 | 17.1822 | 17.1857 | 17.2844 | 17.5457 | 17.7202 | 17.8912 | 18.0914 | 18.2765 | 18.4565 | 18.4766 | 18.6868 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265 | 18.5265
15% | 4152.622 | 8.4672 | 11.2325 | 11.9847 | 11.9625 | 11.9612 | 12.0467 | 12.1405 | 12.3333 | 12.4719 | 12.5469 | 12.6289 | 12.704 | 12.84 | 13.0088 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 12.9967 | 15% | 4364.7722 | 9.4351 | 12.2059 | 12.9304 | 12.8866 | 12.8893 | 12.9633 | 13.1593 | 13.2901 | 13.4184 | 13.5685 | 13.7074 | 13.8424 | 13.8575 | 14.0151 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949 | 13.8949
10% | 4248.2976 | 5.6448 | 7.4883 | 7.9898 | 7.975 | 7.9741 | 8.0311 | 8.0937 | 8.2222 | 8.3146 | 8.3646 | 8.4192 | 8.4693 | 8.56 | 8.6725 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 8.6644 | 10% | 4391.6218 | 6.2901 | 8.1373 | 8.6203 | 8.5911 | 8.5928 | 8.6422 | 8.7728 | 8.8601 | 8.9456 | 9.0457 | 9.1383 | 9.2283 | 9.2383 | 9.3434 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632 | 9.2632
5% | 4361.7469 | 2.8224 | 3.7442 | 3.9949 | 3.9875 | 3.9871 | 4.0156 | 4.0468 | 4.1111 | 4.1573 | 4.1823 | 4.2096 | 4.2347 | 4.28 | 4.3363 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 4.3322 | 5% | 4391.6218 | 3.145 | 4.0686 | 4.3101 | 4.2955 | 4.2964 | 4.3211 | 4.3864 | 4.43 | 4.4728 | 4.5228 | 4.5691 | 4.6141 | 4.6192 | 4.6717 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316 | 4.6316
9.992e-14% | 4391.6218 | 5.6403e-14 | 7.4823e-14 | 7.9834e-14 | 7.9686e-14 | 7.9678e-14 | 8.0247e-14 | 8.0872e-14 | 8.2157e-14 | 8.308e-14 | 8.3579e-14 | 8.4125e-14 | 8.4626e-14 | 8.5531e-14 | 8.6656e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 8.6575e-14 | 9.992e-14% | 4391.6218 | 6.2851e-14 | 8.1308e-14 | 8.6134e-14 | 8.5842e-14 | 8.586e-14 | 8.6353e-14 | 8.7658e-14 | 8.853e-14 | 8.9385e-14 | 9.0385e-14 | 9.131e-14 | 9.2209e-14 | 9.2309e-14 | 9.3359e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14 | 9.2558e-14

## Locational VCR
Base case |  | Energy Usage (CY 2024 kWh) | Energy Usage (CY 2024 %) | Tailored VCR
Dec 24 AER VCR ($/kWh) - Res | 49.23 | 67934749.1441 | 34.06% | 16.7657
Dec 24 AER VCR ($/kWh) - Com | 34.39 | 101368150.4504 | 50.82% | 17.4756
Dec 24 AER VCR ($/kWh) - Ind | 33.49 | 17726336.2671 | 8.886% | 2.976
Dec 24 AER VCR ($/kWh) - Agr | 22.25 | 12451243.5083 | 6.242% | 1.3888
|  | 199480479.3698 |  | 38.6062 | KW/h
|  |  |  | 38606.1513 | MW/h

## E@R N
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [42 empty] | 0.12002 | 0.191 | 1.6137 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
98% | [44 empty] | 0.14553
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12002 | 0.191 | 1.7592 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
Option 1 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 1 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036006 | 0.057301 | 0.52777 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 2 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 4 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 5 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 6 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [42 empty] | 0.12002 | 0.191 | 1.6137 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
98% | [44 empty] | 0.14553
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12002 | 0.191 | 1.7592 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
Option 7 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 7 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036006 | 0.057301 | 0.52777 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99%
98%
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 8 Winter POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Winter POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | [42 empty] | 0.12002 | 0.191 | 1.6137 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
98% | [44 empty] | 0.14553
97%
95%
90%
85%
80%
75%
70%
65%
60%
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12002 | 0.191 | 1.7592 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805 | 0.43805
Option 8 Summer POE50 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 8 Summer POE10 W E @ R (MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036006 | 0.057301 | 0.52777 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142 | 0.13142

## E@R N-1
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 37.4366 | 38.4052 | 40.0833 | 43.9094 | 46.4652 | 49.7088 | 51.3892 | 52.8635 | 50.1223 | 53.3207 | 58.3526 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 |  | 5.6789 | 33.6321 | 41.2692 | 42.4458 | 43.1872 | 44.8288 | 48.7149 | 50.8303 | 54.8724 | 67.1726 | 57.0171 | 55.026 | 57.6982 | 63.5502 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781
98% | 0.020606 | 33.3788 | 42.11 | 43.5925 | 44.7431 | 46.7365 | 51.2818 | 54.3179 | 58.1711 | 60.1673 | 61.9187 | 58.6624 | 62.4618 | 68.4394 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 |  | 5.8662 | 39.073 | 48.1454 | 49.5431 | 50.4239 | 52.374 | 56.9904 | 59.5034 | 64.3051 | 78.9171 | 66.8529 | 64.4876 | 67.6621 | 74.6138 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952
97% |  | 64.3022 | 81.5872 | 84.5221 | 86.7999 | 90.7464 | 99.7446 | 105.7551 | 113.3832 | 117.3353 | 120.8025 | 114.3559 | 121.8775 | 133.7114 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 |  | 9.8356 | 75.5748 | 93.5354 | 96.3025 | 98.0462 | 101.9067 | 111.0458 | 116.0208 | 125.5268 | 154.454 | 130.5706 | 125.888 | 132.1725 | 145.9349 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934
95% |  | 181.8568 | 232.914 | 241.5832 | 248.3116 | 259.9688 | 286.5483 | 304.3023 | 326.8347 | 338.5083 | 348.75 | 329.7076 | 351.9256 | 386.8808 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 |  | 20.9709 | 215.1544 | 268.2072 | 276.3809 | 281.5313 | 292.9348 | 319.9304 | 334.6257 | 362.705 | 448.1513 | 377.6034 | 363.7719 | 382.3354 | 422.9874 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941
90% |  | 893.0903 | 1174.5993 | 1222.3975 | 1259.4956 | 1323.7687 | 1470.3172 | 1568.2056 | 1692.4401 | 1756.8041 | 1813.2726 | 1708.2805 | 1830.7812 | 2023.5105 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 |  | 23.4784 | 1076.68 | 1369.1919 | 1414.2584 | 1442.6557 | 1505.5298 | 1654.3725 | 1735.397 | 1890.2148 | 2361.3315 | 1972.3588 | 1896.0974 | 1998.4489 | 2222.5876 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492
85% |  | 1762.1242 | 2449.8304 | 2566.598 | 2657.2259 | 2814.2407 | 3172.248 | 3411.3825 | 3714.8785 | 3872.1151 | 4010.0635 | 3753.5754 | 4052.8358 | 4523.6597 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 |  |  | 2210.6207 | 2925.2063 | 3035.3005 | 3104.6731 | 3258.27 | 3621.8821 | 3819.8191 | 4198.028 | 5348.9323 | 4398.6997 | 4212.3987 | 4462.436 | 5009.9908 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275
80% |  | 2007.5732 | 3076.4726 | 3257.9641 | 3398.8267 | 3642.8742 | 4199.3237 | 4571.0097 | 5042.7323 | 5287.1246 | 5501.5374 | 5102.8788 | 5568.0182 | 6299.8181 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 |  |  | 2704.6698 | 3815.3477 | 3986.4666 | 4094.2922 | 4333.0273 | 4898.1884 | 5205.8411 | 5793.6899 | 7582.5364 | 6105.5932 | 5816.0263 | 6204.6584 | 7055.7208 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459
75% |  | 1303.991 | 2483.2854 | 2683.5211 | 2838.9319 | 3108.1844 | 3722.1035 | 4132.1769 | 4652.6186 | 4922.2514 | 5158.8086 | 4718.9769 | 5232.1555 | 6039.5351 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 |  |  | 2073.0831 | 3298.4708 | 3487.2627 | 3606.2244 | 3869.6159 | 4493.1463 | 4832.5731 | 5481.1343 | 7454.7312 | 5825.2508 | 5505.7776 | 5934.5473 | 6873.5067 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17
70% |  | 329.0664 | 1554.418 | 1769.5601 | 1936.5403 | 2225.837 | 2885.4588 | 3326.0597 | 3885.2453 | 4174.9507 | 4429.1182 | 3956.5436 | 4507.9253 | 5375.4095 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 |  |  | 1113.6786 | 2430.2892 | 2633.1355 | 2760.9532 | 3043.9527 | 3713.9012 | 4078.5963 | 4775.4391 | 6895.9587 | 5145.173 | 4801.917 | 5262.606 | 6271.4654 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828
65% |  |  | 357.6004 | 534.3679 | 694.2568 | 998.0683 | 1693.1832 | 2157.4921 | 2746.7664 | 3052.0604 | 3319.9042 | 2821.9012 | 3402.9518 | 4317.1138 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 |  |  | 102.8871 | 1213.5217 | 1427.2829 | 1561.9782 | 1860.2054 | 2566.2027 | 2950.5214 | 3684.8601 | 5919.4811 | 4074.4887 | 3712.7627 | 4198.2405 | 5261.3849 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553
60% | [5 empty] | 22.0281 | 310.8024 | 678.0302 | 1303.0236 | 1639.1146 | 1933.9776 | 1385.7376 | 2025.4028 | 3031.7826 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 |  |  |  | 76.5442 | 162.0907 | 231.6582 | 427.4699 | 1104.2451 | 1527.3326 | 2335.7491 | 4795.7916 | 2764.6822 | 2366.4664 | 2900.9178 | 4071.3088 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835
55% | [8 empty] | 31.8697 | 126.1441 | 258.2709 | 49.3804 | 308.3505 | 1129.5587 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | [7 empty] | 5.3153 | 88.0196 | 509.6432 | 3087.7799 | 864.8984 | 532.1518 | 995.8136 | 2281.8383 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09
50% | [40 empty] | 614.3108 |  |  |  | 194.216 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 12441.5431 | 13203.537 | 14572.5364 | 17934.9211 | 20355.1972 | 23617.6722 | 25397.9652 | 27009.2878 | 24050.1225 | 27518.0067 | 33387.7721 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 16610.4697 | 17275.6237 | 18790.1152 | 22593.9352 | 24799.0804 | 29276.1679 | 44809.5484 | 31783.1886 | 29452.7715 | 32597.5368 | 39949.1057 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767
Option 1 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 8709.0802 | 9242.4759 | 10200.7755 | 12554.4447 | 14248.638 | 16532.3706 | 17778.5756 | 18906.5014 | 16835.0857 | 19262.6047 | 23371.4405 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | Option 1 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 4983.1409 | 5182.6871 | 5637.0346 | 6778.1806 | 7439.7241 | 8782.8504 | 13442.8645 | 9534.9566 | 8835.8314 | 9779.261 | 11984.7317 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 61.2344 | 61.2607 | 62.0035 | 63.97 | 65.2829 | 66.5702 | 68.0765 | 69.4698 | 70.8245 | 70.9755 | 72.5573 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 29.9674 | 29.9804 | 30.3481 | 31.3215 | 31.9713 | 32.6085 | 33.3541 | 34.0438 | 34.7143 | 34.789 | 35.572 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749
97% | 3.7957 | 10.5928 | 12.4418 | 12.3872 | 12.3841 | 12.5942 | 12.8249 | 13.2988 | 13.6394 | 13.8238 | 14.0252 | 14.2099 | 14.5441 | 14.9591 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 |  | 24.6994 | 51.9423 | 59.0661 | 58.6353 | 58.6611 | 59.389 | 61.3159 | 62.6024 | 63.8639 | 65.3399 | 66.7052 | 68.0327 | 68.1807 | 69.7307 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486
95% | 17.3774 | 50.84 | 59.9429 | 59.674 | 59.6588 | 60.6932 | 61.8287 | 64.162 | 65.8388 | 66.7468 | 67.7383 | 68.6472 | 70.2926 | 72.3358 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 |  | 34.9082 | 75.1439 | 85.6653 | 85.029 | 85.0671 | 86.1421 | 88.988 | 90.8882 | 92.7512 | 94.9312 | 96.9477 | 98.9082 | 99.1268 | 101.416 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701
90% | 24.555 | 82.5918 | 98.3797 | 97.9133 | 97.8869 | 99.681 | 101.6504 | 105.6971 | 108.6054 | 110.1802 | 111.8997 | 113.4762 | 116.33 | 119.8735 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 |  | 134.6084 | 309.068 | 354.6878 | 351.9289 | 352.0941 | 356.7553 | 369.095 | 377.3339 | 385.4121 | 394.8642 | 403.6075 | 412.1082 | 413.0559 | 422.9818 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119
85% | 44.847 | 209.5458 | 254.3493 | 253.0259 | 252.9509 | 258.0423 | 263.6311 | 275.1149 | 283.3684 | 287.8374 | 292.7171 | 297.1909 | 305.2894 | 315.3454 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 |  | 102.4961 | 267.5254 | 310.6793 | 308.0696 | 308.2258 | 312.635 | 324.3078 | 332.1012 | 339.7428 | 348.684 | 356.9547 | 364.9959 | 365.8924 | 375.2817 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121
80% | 23.7465 | 253.802 | 316.3847 | 314.536 | 314.4314 | 321.5432 | 329.3497 | 345.3906 | 356.9192 | 363.1617 | 369.9778 | 376.2269 | 387.5391 | 401.5855 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 |  | 52.1361 | 167.3947 | 197.5339 | 195.7112 | 195.8203 | 198.8998 | 207.0522 | 212.4953 | 217.8322 | 224.0769 | 229.8532 | 235.4693 | 236.0954 | 242.6531 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519
75% | 0.18716 | 547.1351 | 710.2768 | 705.4576 | 705.1848 | 723.724 | 744.0742 | 785.8898 | 815.9429 | 832.2159 | 849.9842 | 866.2744 | 895.7633 | 932.3798 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 |  | 53.8635 | 259.5826 | 313.3765 | 310.1233 | 310.3181 | 315.8145 | 330.3652 | 340.0803 | 349.6059 | 360.7517 | 371.0616 | 381.0855 | 382.203 | 393.9074 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811
70% |  | 720.2141 | 1002.0732 | 993.7472 | 993.2758 | 1025.3059 | 1060.4649 | 1132.7095 | 1184.6321 | 1212.7469 | 1243.4451 | 1271.5896 | 1322.5375 | 1385.7996 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 |  | 21.0605 | 391.6455 | 489.6437 | 483.7172 | 484.0719 | 494.0849 | 520.5925 | 538.2908 | 555.6439 | 575.9484 | 594.7305 | 612.9912 | 615.027 | 636.3493 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088
65% |  | 1159.8257 | 1867.7211 | 1846.81 | 1845.6263 | 1926.0704 | 2014.373 | 2195.817 | 2326.2218 | 2396.8327 | 2473.9318 | 2544.6175 | 2672.5742 | 2831.4585 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 |  |  | 375.3893 | 498.6861 | 491.2298 | 491.676 | 504.2739 | 537.6246 | 559.8917 | 581.7247 | 607.2709 | 630.9016 | 653.8765 | 656.4378 | 683.2646 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054
60% |  | 595.1039 | 1629.6346 | 1599.0683 | 1597.338 | 1714.9251 | 1843.9992 | 2109.2202 | 2299.836 | 2403.0496 | 2515.7473 | 2619.0702 | 2806.1076 | 3038.3525 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 |  |  | 374.3821 | 567.3189 | 555.6511 | 556.3494 | 576.0627 | 628.2504 | 663.0943 | 697.2588 | 737.234 | 774.2116 | 810.1631 | 814.1711 | 856.15 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351
55% |  |  | 438.6107 | 413.2466 | 411.832 | 513.1119 | 636.1403 | 924.2646 | 1139.8067 | 1256.5173 | 1383.9522 | 1500.7863 | 1712.2821 | 1974.8972 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 |  |  | 239.8473 | 609.6211 | 587.1995 | 588.5414 | 626.4237 | 726.7105 | 793.6685 | 859.321 | 936.1395 | 1007.1978 | 1076.2842 | 1083.9862 | 1164.6552 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336
50% | [7 empty] | 3.4281 | 36.6085 | 68.9695 | 115.5831 | 168.4762 | 288.3744 | 479.2895 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 |  |  |  | 218.9141 | 191.3668 | 192.9659 | 240.7061 | 390.8095 | 509.6193 | 640.0757 | 807.8717 | 965.5671 | 1118.8862 | 1135.9788 | 1315.0026 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715
45% | [40 empty] | 3.1349 | 28.4196 | 76.7087 | 83.5101 | 171.461 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 6295.8662 | 6290.5691 | 6655.6913 | 7068.3364 | 7954.9925 | 8631.4193 | 9012.0818 | 9439.0017 | 9840.5652 | 10591.6343 | 11566.2763 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 3709.8635 | 3715.0322 | 3863.5385 | 4280.4031 | 4577.3201 | 4882.411 | 5257.6779 | 5629.6718 | 6015.0485 | 6059.4299 | 6540.9827 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785
Option 1 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 4407.1063 | 4403.3984 | 4658.9839 | 4947.8355 | 5568.4947 | 6041.9935 | 6308.4573 | 6607.3012 | 6888.3957 | 7414.144 | 8096.3934 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | Option 1 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 1112.959 | 1114.5097 | 1159.0616 | 1284.1209 | 1373.196 | 1464.7233 | 1577.3034 | 1688.9015 | 1804.5146 | 1817.829 | 1962.2948 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 |  |  |  | 1.0311 | 3.5869 | 6.8304 | 8.5109 | 9.9852 | 7.244 | 10.4423 | 15.4742 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 |  | 5.6789 | 33.6321 | 41.2692 |  | 0.3113 | 1.9505 | 5.8366 | 7.952 | 11.9941 | 24.2943 | 14.1387 | 12.1477 | 14.8199 | 20.6719 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997
98% | 0.020606 | 33.3788 | 42.11 |  |  |  | 0.3507 | 3.381 | 7.2342 | 9.2305 | 10.9819 | 7.7255 | 11.5249 | 17.5025 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 |  | 5.8662 | 39.073 | 48.1454 |  |  | 1.4371 | 6.0535 | 8.5665 | 13.3683 | 27.9802 | 15.916 | 13.5507 | 16.7252 | 23.677 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583
97% |  | 64.3022 | 81.5872 |  |  |  |  | 4.9156 | 12.5438 | 16.4958 | 19.963 | 13.5164 | 21.0381 | 32.8719 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 |  | 9.8356 | 75.5748 | 93.5354 |  |  | 1.0673 | 10.2064 | 15.1814 | 24.6874 | 53.6145 | 29.7311 | 25.0486 | 31.3331 | 45.0955 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754
95% |  | 181.8568 | 232.914 |  |  |  |  | 6.438 | 28.9704 | 40.6441 | 50.8858 | 31.8434 | 54.0613 | 89.0165 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 |  | 20.9709 | 215.1544 | 268.2072 |  |  | 0.011134 | 22.0661 | 36.7615 | 64.8408 | 150.2871 | 79.7392 | 65.9077 | 84.4711 | 125.1231 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298
90% |  | 893.0903 | 1174.5993 |  |  |  |  | 0.083453 | 53.3256 | 114.4998 | 170.9683 | 66.8517 | 188.4769 | 381.2062 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 |  | 23.4784 | 1076.68 | 1369.1919 |  |  |  | 26.8732 | 93.0927 | 247.9106 | 719.0273 | 330.0545 | 253.7932 | 356.1446 | 580.2833 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449
85% |  | 1762.1242 | 2449.8304 | [6 empty] | 6.9637 | 54.4575 |  | 78.0116 | 511.628 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 |  |  | 2210.6207 | 2925.2063 |  |  |  |  | 0.67131 | 187.8578 | 1336.9006 | 386.668 | 201.1777 | 450.4044 | 997.9591 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959
80% | FY26: 2007.5732; FY27: 3076.4726; FY38: 132.0232 |  |  | 2704.6698 | 3815.3477 | [6 empty] | 1346.6497 | 41.874 |  | 81.7309 | 819.8342 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667
75% | FY26: 1303.991; FY27: 2483.2854 |  |  | 2073.0831 | 3298.4708 | [6 empty] | 574.808 |  |  |  | 117.9727
70% | FY26: 329.0664; FY27: 1554.418 |  |  | 1113.6786 | 2430.2892 | [6 empty] | 2.9095
65% | FY27: 357.6004 |  |  | 102.8871 | 1213.5217
60% | [33 empty] | 76.5442
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 0 | 0 | 0 | 1.3818 | 18.405 | 108.9044 | 196.3448 | 317.2417 | 127.181 | 363.5552 | 1179.7227 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 0 | 0.3113 | 4.466 | 71.0357 | 162.2254 | 550.6588 | 4236.4712 | 898.1216 | 571.6256 | 1035.6292 | 2730.6169 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493
Option 2 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 0 | 0 | 0 | 0.96727 | 12.8835 | 76.2331 | 137.4414 | 222.0692 | 89.0267 | 254.4886 | 825.8059 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | Option 2 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 0 | 0.093391 | 1.3398 | 21.3107 | 48.6676 | 165.1977 | 1270.9414 | 269.4365 | 171.4877 | 310.6888 | 819.1851 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 17.5867 | 17.613 | 18.3558 | 20.3222 | 21.6352 | 22.9225 | 24.4288 | 25.8221 | 27.1768 | 27.3278 | 28.9096 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 8.3629 | 8.3759 | 8.7436 | 9.7169 | 10.3668 | 11.004 | 11.7496 | 12.4392 | 13.1098 | 13.1845 | 13.9675 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704
97% | 3.7957 | 10.5928 | 12.4418 | 1.6946 | 1.6915 | 1.9016 | 2.1323 | 2.6062 | 2.9468 | 3.1313 | 3.3326 | 3.5173 | 3.8515 | 4.2665 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 |  | 24.6994 | 51.9423 | 59.0661 | 15.8649 | 15.8907 | 16.6186 | 18.5455 | 19.8321 | 21.0935 | 22.5695 | 23.9349 | 25.2623 | 25.4103 | 26.9603 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782
95% | 17.3774 | 50.84 | 59.9429 | 7.0335 | 7.0183 | 8.0528 | 9.1883 | 11.5215 | 13.1984 | 14.1064 | 15.0978 | 16.0068 | 17.6522 | 19.6953 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 |  | 34.9082 | 75.1439 | 85.6653 | 21.8604 | 21.8985 | 22.9735 | 25.8195 | 27.7196 | 29.5827 | 31.7626 | 33.7791 | 35.7396 | 35.9582 | 38.2474 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016
90% | 24.555 | 82.5918 | 98.3797 | 6.615 | 6.5886 | 8.3827 | 10.3521 | 14.3987 | 17.3071 | 18.8819 | 20.6014 | 22.1779 | 25.0317 | 28.5752 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 |  | 134.6084 | 309.068 | 354.6878 | 78.034 | 78.1991 | 82.8603 | 95.2001 | 103.4389 | 111.5171 | 120.9692 | 129.7126 | 138.2133 | 139.161 | 149.0869 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517
85% | 44.847 | 209.5458 | 254.3493 | 0.91627 | 0.89603 | 2.7716 | 5.9739 | 16.0251 | 24.2786 | 28.7476 | 33.6273 | 38.1011 | 46.1996 | 56.2556 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 |  | 102.4961 | 267.5254 | 310.6793 | 48.9798 | 49.1359 | 53.5452 | 65.2179 | 73.0114 | 80.653 | 89.5942 | 97.8649 | 105.9061 | 106.8026 | 116.1919 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312
80% | 23.7465 | 253.802 | 316.3847 |  |  |  |  | 0.16225 | 2.9303 | 5.8147 | 10.0362 | 14.8625 | 25.6359 | 39.6823 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 |  | 52.1361 | 167.3947 | 197.5339 | 14.7596 | 14.8687 | 17.9482 | 26.1006 | 31.5437 | 36.8806 | 43.1252 | 48.9016 | 54.5177 | 55.1438 | 61.7015 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003
75% | 0.18716 | 547.1351 | 710.2768 | [9 empty] | 0.58047 | 10.1289 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 |  | 53.8635 | 259.5826 | 313.3765 | 0.70584 | 0.74345 | 2.1996 | 9.6195 | 17.3253 | 26.6347 | 37.7805 | 48.0904 | 58.1143 | 59.2318 | 70.9362 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099
70% | FY26: 720.2141; FY27: 1002.0732 |  | 21.0605 | 391.6455 | 489.6437 | [5 empty] | 0.5416 | 5.4364 | 14.3245 | 26.8044 | 28.423 | 47.9824 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407
65% | FY26: 1159.8257; FY27: 1867.7211 |  |  | 375.3893 | 498.6861 | [10 empty] | 0.063209
60% | FY26: 595.1039; FY27: 1629.6346 |  |  | 374.3821 | 567.3189
55% | FY27: 438.6107 |  |  | 239.8473 | 609.6211
50% | [33 empty] | 218.9141
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 16.2594 | 16.1944 | 21.1087 | 27.6465 | 44.7138 | 60.6612 | 70.6819 | 82.6953 | 94.6655 | 118.9513 | 158.6038 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 206.1542 | 206.7254 | 223.2449 | 270.5423 | 304.8729 | 340.8297 | 387.416 | 434.8694 | 484.8443 | 490.643 | 554.0469 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525
Option 2 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 11.3816 | 11.3361 | 14.7761 | 19.3526 | 31.2996 | 42.4628 | 49.4773 | 57.8867 | 66.2658 | 83.2659 | 111.0226 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | Option 2 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 61.8462 | 62.0176 | 66.9735 | 81.1627 | 91.4619 | 102.2489 | 116.2248 | 130.4608 | 145.4533 | 147.1929 | 166.2141 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | FY25: 0.52857; FY26: 28.8388; FY27: 36.1886 |  | 5.6789 | 33.6321 | 41.2692 | [6 empty] | 0.36009
98% | FY25: 0.020606; FY26: 33.3788; FY27: 42.11 |  | 5.8662 | 39.073 | 48.1454
97% | FY26: 64.3022; FY27: 81.5872 |  | 9.8356 | 75.5748 | 93.5354
95% | FY26: 181.8568; FY27: 232.914 |  | 20.9709 | 215.1544 | 268.2072
90% | FY26: 893.0903; FY27: 1174.5993 |  | 23.4784 | 1076.68 | 1369.1919
85% | FY26: 1762.1242; FY27: 2449.8304 |  |  | 2210.6207 | 2925.2063
80% | FY26: 2007.5732; FY27: 3076.4726 |  |  | 2704.6698 | 3815.3477
75% | FY26: 1303.991; FY27: 2483.2854 |  |  | 2073.0831 | 3298.4708
70% | FY26: 329.0664; FY27: 1554.418 |  |  | 1113.6786 | 2430.2892
65% | FY27: 357.6004 |  |  | 102.8871 | 1213.5217
60% | [33 empty] | 76.5442
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | FY25: 0; FY26: 0; FY27: 0 |  | 26.6023 | 54.4041 | 61.674 | [6 empty] | 0.17453 | 1.4003 | 2.7549 | 2.906 | 4.4878 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814 | 3.2814
98% | FY25: 0; FY26: 0; FY27: 0 |  | 12.8254 | 26.5866 | 30.185 | [7 empty] | 0.090945 | 0.67951 | 0.75426 | 1.5372 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401 | 0.9401
97% | FY25: 3.7957; FY26: 10.5928; FY27: 12.4418 |  | 24.6994 | 51.9423 | 59.0661 | [8 empty] | 0.15653 | 0.23464 | 1.6611 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652 | 0.49652
95% | FY25: 17.3774; FY26: 50.84; FY27: 59.9429 |  | 34.9082 | 75.1439 | 85.6653 | [10 empty] | 0.24169
90% | FY25: 24.555; FY26: 82.5918; FY27: 98.3797 |  | 134.6084 | 309.068 | 354.6878
85% | FY25: 44.847; FY26: 209.5458; FY27: 254.3493 |  | 102.4961 | 267.5254 | 310.6793
80% | FY25: 23.7465; FY26: 253.802; FY27: 316.3847 |  | 52.1361 | 167.3947 | 197.5339
75% | FY25: 0.18716; FY26: 547.1351; FY27: 710.2768 |  | 53.8635 | 259.5826 | 313.3765
70% | FY26: 720.2141; FY27: 1002.0732 |  | 21.0605 | 391.6455 | 489.6437
65% | FY26: 1159.8257; FY27: 1867.7211 |  |  | 375.3893 | 498.6861
60% | FY26: 595.1039; FY27: 1629.6346 |  |  | 374.3821 | 567.3189
55% | FY27: 438.6107 |  |  | 239.8473 | 609.6211
50% | [33 empty] | 218.9141
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17453 | 1.4912 | 3.591 | 3.8949 | 7.9277 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718 | 4.718
Option 3 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Option 3 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052358 | 0.44737 | 1.0773 | 1.1685 | 2.3783 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154 | 1.4154
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 15.9974 | 16.966 | 18.6441 | 22.4703 | 25.026 | 28.2696 | 29.9501 | 31.4244 | 28.6832 | 31.8815 | 36.9134 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 | 33.0833 |  | 5.6789 | 33.6321 | 41.2692 | 21.0067 | 21.7481 | 23.3896 | 27.2757 | 29.3912 | 33.4332 | 45.7334 | 35.5779 | 33.5868 | 36.2591 | 42.111 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389 | 38.1389
98% | 0.020606 | 33.3788 | 42.11 | 18.124 | 19.2747 | 21.2681 | 25.8134 | 28.8494 | 32.7026 | 34.6989 | 36.4503 | 33.1939 | 36.9934 | 42.9709 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 | 38.4211 |  | 5.8662 | 39.073 | 48.1454 | 24.0747 | 24.9555 | 26.9055 | 31.522 | 34.035 | 38.8367 | 53.4486 | 41.3845 | 39.0192 | 42.1936 | 49.1454 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268 | 44.4268
97% |  | 64.3022 | 81.5872 | 34.1023 | 36.3802 | 40.3266 | 49.3249 | 55.3354 | 62.9635 | 66.9155 | 70.3828 | 63.9361 | 71.4578 | 83.2916 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 | 74.2842 |  | 9.8356 | 75.5748 | 93.5354 | 45.8828 | 47.6264 | 51.487 | 60.6261 | 65.6011 | 75.1071 | 104.0342 | 80.1508 | 75.4683 | 81.7528 | 95.5152 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737 | 86.1737
95% |  | 181.8568 | 232.914 | 92.651 | 99.3795 | 111.0367 | 137.6162 | 155.3702 | 177.9025 | 189.5762 | 199.8179 | 180.7755 | 202.9934 | 237.9487 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 | 211.3422 |  | 20.9709 | 215.1544 | 268.2072 | 127.4488 | 132.5992 | 144.0027 | 170.9982 | 185.6936 | 213.7729 | 299.2192 | 228.6713 | 214.8398 | 233.4033 | 274.0552 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619 | 246.4619
90% |  | 893.0903 | 1174.5993 | 401.2454 | 438.3434 | 502.6166 | 649.165 | 747.0535 | 871.288 | 935.652 | 992.1204 | 887.1284 | 1009.6291 | 1202.3584 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 | 1055.6609 |  | 23.4784 | 1076.68 | 1369.1919 | 593.1063 | 621.5036 | 684.3777 | 833.2204 | 914.2449 | 1069.0627 | 1540.1794 | 1151.2066 | 1074.9453 | 1177.2968 | 1401.4355 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297 | 1249.297
85% |  | 1762.1242 | 2449.8304 | 560.5822 | 651.2101 | 808.2248 | 1166.2322 | 1405.3667 | 1708.8626 | 1866.0992 | 2004.0477 | 1747.5595 | 2046.82 | 2517.6439 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 | 2159.2724 |  |  | 2210.6207 | 2925.2063 | 1029.2846 | 1098.6572 | 1252.2541 | 1615.8663 | 1813.8032 | 2192.0121 | 3342.9164 | 2392.6839 | 2206.3829 | 2456.4202 | 3003.975 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117 | 2632.3117
80% |  | 2007.5732 | 3076.4726 | 180.5247 | 289.2889 | 524.9309 | 1081.3804 | 1453.0664 | 1924.789 | 2169.1813 | 2383.5941 | 1984.9355 | 2450.0749 | 3181.8748 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 | 2624.8593 |  |  | 2704.6698 | 3815.3477 | 868.5233 | 976.3489 | 1215.084 | 1780.2451 | 2087.8978 | 2675.7466 | 4464.5931 | 2987.6499 | 2698.083 | 3086.7151 | 3937.7775 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026 | 3360.1026
75% |  | 1303.991 | 2483.2854 |  |  | 10.6867 | 304.8475 | 692.2152 | 1212.657 | 1482.2898 | 1718.847 | 1279.0153 | 1792.1939 | 2599.5734 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 | 1985.0299 |  |  | 2073.0831 | 3298.4708 | 146.3935 | 219.7814 | 432.0445 | 1053.1847 | 1392.6114 | 2041.1727 | 4014.7696 | 2385.2891 | 2065.816 | 2494.5856 | 3433.5451 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084 | 2796.2084
70% |  | 329.0664 | 1554.418 |  |  |  |  | 19.3847 | 259.9188 | 486.1197 | 733.0717 | 309.3874 | 811.8788 | 1679.363 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 | 1019.0703 |  |  | 1113.6786 | 2430.2892 |  |  |  | 158.0329 | 403.5193 | 1079.3926 | 3199.9122 | 1449.1265 | 1105.8705 | 1566.5595 | 2575.4189 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363 | 1890.6363
65% |  |  | 357.6004 | [7 empty] | 5.7734 |  | 16.151 | 456.1967 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 | 67.8029 |  |  | 102.8871 | 1213.5217 | [5 empty] | 89.3519 | 2024.5568 | 283.4015 | 99.723 | 366.6825 | 1366.4606 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603 | 648.3603
60% | [33 empty] | 76.5442 | [6 empty] | 559.3031 |  |  |  | 134.6166
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 1303.2271 | 1550.8427 | 2037.7346 | 3436.8499 | 4581.6675 | 6279.3537 | 7260.4827 | 8175.5297 | 6514.6148 | 8470.0737 | 12038.1349 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | 9268.8265 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 2855.7207 | 3143.2203 | 3829.5452 | 5730.9714 | 6926.7975 | 9507.8885 | 19648.6661 | 11035.142 | 9613.7348 | 11541.8685 | 16314.0562 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176 | 12992.1176
Option 4 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 912.259 | 1085.5899 | 1426.4142 | 2405.7949 | 3207.1673 | 4395.5476 | 5082.3379 | 5722.8708 | 4560.2304 | 5929.0516 | 8426.6944 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | 6488.1786 | Option 4 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 856.7162 | 942.9661 | 1148.8636 | 1719.2914 | 2078.0392 | 2852.3666 | 5894.5998 | 3310.5426 | 2884.1204 | 3462.5605 | 4894.2169 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353 | 3897.6353
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 39.4105 | 39.4368 | 40.1796 | 42.1461 | 43.459 | 44.7464 | 46.2527 | 47.646 | 49.0007 | 49.1517 | 50.7335 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271 | 49.5271
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 19.1652 | 19.1782 | 19.5459 | 20.5192 | 21.1691 | 21.8063 | 22.5518 | 23.2415 | 23.912 | 23.9868 | 24.7697 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726
97% | 3.7957 | 10.5928 | 12.4418 | 7.0409 | 7.0378 | 7.2479 | 7.4786 | 7.9525 | 8.2931 | 8.4776 | 8.6789 | 8.8636 | 9.1978 | 9.6128 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 | 9.583 |  | 24.6994 | 51.9423 | 59.0661 | 37.2501 | 37.2759 | 38.0038 | 39.9307 | 41.2173 | 42.4787 | 43.9547 | 45.32 | 46.6475 | 46.7955 | 48.3455 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634 | 47.1634
95% | 17.3774 | 50.84 | 59.9429 | 33.3538 | 33.3386 | 34.373 | 35.5085 | 37.8417 | 39.5186 | 40.4266 | 41.418 | 42.327 | 43.9724 | 46.0155 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 | 45.8688 |  | 34.9082 | 75.1439 | 85.6653 | 53.4447 | 53.4828 | 54.5578 | 57.4037 | 59.3039 | 61.167 | 63.3469 | 65.3634 | 67.3239 | 67.5425 | 69.8317 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858 | 68.0858
90% | 24.555 | 82.5918 | 98.3797 | 52.2641 | 52.2377 | 54.0318 | 56.0012 | 60.0479 | 62.9563 | 64.5311 | 66.2506 | 67.8271 | 70.6808 | 74.2243 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 | 73.9699 |  | 134.6084 | 309.068 | 354.6878 | 214.9815 | 215.1466 | 219.8078 | 232.1476 | 240.3864 | 248.4646 | 257.9167 | 266.66 | 275.1608 | 276.1085 | 286.0343 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644 | 278.4644
85% | 44.847 | 209.5458 | 254.3493 | 123.4809 | 123.406 | 128.4974 | 134.0862 | 145.57 | 153.8235 | 158.2925 | 163.1722 | 167.646 | 175.7445 | 185.8005 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 | 185.0785 |  | 102.4961 | 267.5254 | 310.6793 | 178.5247 | 178.6809 | 183.0901 | 194.7629 | 202.5563 | 210.1979 | 219.1391 | 227.4098 | 235.451 | 236.3475 | 245.7368 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761 | 238.5761
80% | 23.7465 | 253.802 | 316.3847 | 133.5844 | 133.4798 | 140.5916 | 148.3981 | 164.439 | 175.9676 | 182.2101 | 189.0262 | 195.2753 | 206.5875 | 220.6339 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 | 219.6254 |  | 52.1361 | 167.3947 | 197.5339 | 105.2354 | 105.3445 | 108.424 | 116.5764 | 122.0195 | 127.3564 | 133.6011 | 139.3774 | 144.9935 | 145.6196 | 152.1773 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761 | 147.1761
75% | 0.18716 | 547.1351 | 710.2768 | 233.7497 | 233.4769 | 252.016 | 272.3663 | 314.1819 | 344.235 | 360.508 | 378.2762 | 394.5665 | 424.0554 | 460.6719 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 | 458.0428 |  | 53.8635 | 259.5826 | 313.3765 | 148.6377 | 148.8324 | 154.3288 | 168.8796 | 178.5947 | 188.1203 | 199.2661 | 209.576 | 219.5999 | 220.7174 | 232.4218 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955 | 223.4955
70% |  | 720.2141 | 1002.0732 | 178.7795 | 178.3082 | 210.3382 | 245.4972 | 317.7418 | 369.6644 | 397.7792 | 428.4774 | 456.6219 | 507.5698 | 570.8319 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 | 566.2898 |  | 21.0605 | 391.6455 | 489.6437 | 189.5338 | 189.8885 | 199.9014 | 226.4091 | 244.1073 | 261.4605 | 281.765 | 300.547 | 318.8078 | 320.8436 | 342.1659 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046 | 325.9046
65% |  | 1159.8257 | 1867.7211 | 14.5976 | 14.3466 | 36.2401 | 71.3741 | 178.6964 | 283.8125 | 350.1144 | 427.1224 | 497.808 | 625.7647 | 784.649 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 | 773.2412 |  |  | 375.3893 | 498.6861 | 121.1015 | 121.5477 | 134.1456 | 167.4963 | 189.7634 | 211.5964 | 237.1426 | 260.7733 | 283.7482 | 286.3095 | 313.1363 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771 | 292.6771
60% |  | 595.1039 | 1629.6346 | [7 empty] | 4.2666 | 18.4076 | 68.5241 | 173.1739 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 | 164.1365 |  |  | 374.3821 | 567.3189 | 17.9718 | 18.2567 | 27.1896 | 58.9288 | 86.4228 | 118.0825 | 158.0518 | 195.0294 | 230.9808 | 234.9888 | 276.9677 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529 | 244.9529
55% | FY27: 438.6107 |  |  | 239.8473 | 609.6211 | [6 empty] | 5.7929 | 22.1541 | 47.8409 | 51.2872 | 94.2227 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531 | 60.3531
50% | [33 empty] | 218.9141
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 776.851 | 775.6316 | 863.3362 | 970.7101 | 1226.4712 | 1438.271 | 1562.3394 | 1706.6885 | 1849.3429 | 2132.097 | 2525.6137 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | 2495.8359 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 1125.2568 | 1127.071 | 1179.1745 | 1325.2004 | 1428.9997 | 1535.4769 | 1668.7813 | 1803.098 | 1943.467 | 1959.6985 | 2136.5432 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488 | 2000.5488
Option 4 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 543.7957 | 542.9421 | 604.3353 | 679.4971 | 858.5299 | 1006.7897 | 1093.6376 | 1194.682 | 1294.54 | 1492.4679 | 1767.9296 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | 1747.0851 | Option 4 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 337.577 | 338.1213 | 353.7523 | 397.5601 | 428.6999 | 460.6431 | 500.6344 | 540.9294 | 583.0401 | 587.9096 | 640.963 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646 | 600.1646
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 |  |  |  | 1.0311 | 3.5869 | 6.8304 | 8.5109 | 9.9852 | 7.244 | 10.4423 | 15.4742 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 | 11.6442 |  | 5.6789 | 33.6321 | 41.2692 |  | 0.3113 | 1.9505 | 5.8366 | 7.952 | 11.9941 | 24.2943 | 14.1387 | 12.1477 | 14.8199 | 20.6719 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997 | 16.6997
98% | 0.020606 | 33.3788 | 42.11 |  |  |  | 0.3507 | 3.381 | 7.2342 | 9.2305 | 10.9819 | 7.7255 | 11.5249 | 17.5025 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 | 12.9526 |  | 5.8662 | 39.073 | 48.1454 |  |  | 1.4371 | 6.0535 | 8.5665 | 13.3683 | 27.9802 | 15.916 | 13.5507 | 16.7252 | 23.677 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583
97% |  | 64.3022 | 81.5872 |  |  |  |  | 4.9156 | 12.5438 | 16.4958 | 19.963 | 13.5164 | 21.0381 | 32.8719 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 | 23.8645 |  | 9.8356 | 75.5748 | 93.5354 |  |  | 1.0673 | 10.2064 | 15.1814 | 24.6874 | 53.6145 | 29.7311 | 25.0486 | 31.3331 | 45.0955 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754 | 35.754
95% |  | 181.8568 | 232.914 |  |  |  |  | 6.438 | 28.9704 | 40.6441 | 50.8858 | 31.8434 | 54.0613 | 89.0165 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 | 62.4101 |  | 20.9709 | 215.1544 | 268.2072 |  |  | 0.011134 | 22.0661 | 36.7615 | 64.8408 | 150.2871 | 79.7392 | 65.9077 | 84.4711 | 125.1231 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298 | 97.5298
90% |  | 893.0903 | 1174.5993 |  |  |  |  | 0.083453 | 53.3256 | 114.4998 | 170.9683 | 66.8517 | 188.4769 | 381.2062 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 | 234.5087 |  | 23.4784 | 1076.68 | 1369.1919 |  |  |  | 26.8732 | 93.0927 | 247.9106 | 719.0273 | 330.0545 | 253.7932 | 356.1446 | 580.2833 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449 | 428.1449
85% |  | 1762.1242 | 2449.8304 | [6 empty] | 6.9637 | 54.4575 |  | 78.0116 | 511.628 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 | 159.135 |  |  | 2210.6207 | 2925.2063 |  |  |  |  | 0.67131 | 187.8578 | 1336.9006 | 386.668 | 201.1777 | 450.4044 | 997.9591 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959 | 626.2959
80% | FY26: 2007.5732; FY27: 3076.4726; FY38: 132.0232 |  |  | 2704.6698 | 3815.3477 | [6 empty] | 1346.6497 | 41.874 |  | 81.7309 | 819.8342 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667 | 256.9667
75% | FY26: 1303.991; FY27: 2483.2854 |  |  | 2073.0831 | 3298.4708 | [6 empty] | 574.808 |  |  |  | 117.9727
70% | FY26: 329.0664; FY27: 1554.418 |  |  | 1113.6786 | 2430.2892 | [6 empty] | 2.9095
65% | FY27: 357.6004 |  |  | 102.8871 | 1213.5217
60% | [33 empty] | 76.5442
55%
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 0 | 0 | 0 | 1.3818 | 18.405 | 108.9044 | 196.3448 | 317.2417 | 127.181 | 363.5552 | 1179.7227 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | 504.5151 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 0 | 0.3113 | 4.466 | 71.0357 | 162.2254 | 550.6588 | 4236.4712 | 898.1216 | 571.6256 | 1035.6292 | 2730.6169 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493 | 1480.3493
Option 5 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 0 | 0 | 0 | 0.96727 | 12.8835 | 76.2331 | 137.4414 | 222.0692 | 89.0267 | 254.4886 | 825.8059 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | 353.1605 | Option 5 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 0 | 0.093391 | 1.3398 | 21.3107 | 48.6676 | 165.1977 | 1270.9414 | 269.4365 | 171.4877 | 310.6888 | 819.1851 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048 | 444.1048
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 17.5867 | 17.613 | 18.3558 | 20.3222 | 21.6352 | 22.9225 | 24.4288 | 25.8221 | 27.1768 | 27.3278 | 28.9096 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033 | 27.7033
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 8.3629 | 8.3759 | 8.7436 | 9.7169 | 10.3668 | 11.004 | 11.7496 | 12.4392 | 13.1098 | 13.1845 | 13.9675 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704 | 13.3704
97% | 3.7957 | 10.5928 | 12.4418 | 1.6946 | 1.6915 | 1.9016 | 2.1323 | 2.6062 | 2.9468 | 3.1313 | 3.3326 | 3.5173 | 3.8515 | 4.2665 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 | 4.2367 |  | 24.6994 | 51.9423 | 59.0661 | 15.8649 | 15.8907 | 16.6186 | 18.5455 | 19.8321 | 21.0935 | 22.5695 | 23.9349 | 25.2623 | 25.4103 | 26.9603 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782 | 25.7782
95% | 17.3774 | 50.84 | 59.9429 | 7.0335 | 7.0183 | 8.0528 | 9.1883 | 11.5215 | 13.1984 | 14.1064 | 15.0978 | 16.0068 | 17.6522 | 19.6953 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 | 19.5486 |  | 34.9082 | 75.1439 | 85.6653 | 21.8604 | 21.8985 | 22.9735 | 25.8195 | 27.7196 | 29.5827 | 31.7626 | 33.7791 | 35.7396 | 35.9582 | 38.2474 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016 | 36.5016
90% | 24.555 | 82.5918 | 98.3797 | 6.615 | 6.5886 | 8.3827 | 10.3521 | 14.3987 | 17.3071 | 18.8819 | 20.6014 | 22.1779 | 25.0317 | 28.5752 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 | 28.3208 |  | 134.6084 | 309.068 | 354.6878 | 78.034 | 78.1991 | 82.8603 | 95.2001 | 103.4389 | 111.5171 | 120.9692 | 129.7126 | 138.2133 | 139.161 | 149.0869 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517 | 141.517
85% | 44.847 | 209.5458 | 254.3493 | 0.91627 | 0.89603 | 2.7716 | 5.9739 | 16.0251 | 24.2786 | 28.7476 | 33.6273 | 38.1011 | 46.1996 | 56.2556 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 | 55.5336 |  | 102.4961 | 267.5254 | 310.6793 | 48.9798 | 49.1359 | 53.5452 | 65.2179 | 73.0114 | 80.653 | 89.5942 | 97.8649 | 105.9061 | 106.8026 | 116.1919 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312 | 109.0312
80% | 23.7465 | 253.802 | 316.3847 |  |  |  |  | 0.16225 | 2.9303 | 5.8147 | 10.0362 | 14.8625 | 25.6359 | 39.6823 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 | 38.6738 |  | 52.1361 | 167.3947 | 197.5339 | 14.7596 | 14.8687 | 17.9482 | 26.1006 | 31.5437 | 36.8806 | 43.1252 | 48.9016 | 54.5177 | 55.1438 | 61.7015 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003 | 56.7003
75% | 0.18716 | 547.1351 | 710.2768 | [9 empty] | 0.58047 | 10.1289 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 | 9.0623 |  | 53.8635 | 259.5826 | 313.3765 | 0.70584 | 0.74345 | 2.1996 | 9.6195 | 17.3253 | 26.6347 | 37.7805 | 48.0904 | 58.1143 | 59.2318 | 70.9362 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099 | 62.0099
70% | FY26: 720.2141; FY27: 1002.0732 |  | 21.0605 | 391.6455 | 489.6437 | [5 empty] | 0.5416 | 5.4364 | 14.3245 | 26.8044 | 28.423 | 47.9824 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407 | 32.6407
65% | FY26: 1159.8257; FY27: 1867.7211 |  |  | 375.3893 | 498.6861 | [10 empty] | 0.063209
60% | FY26: 595.1039; FY27: 1629.6346 |  |  | 374.3821 | 567.3189
55% | FY27: 438.6107 |  |  | 239.8473 | 609.6211
50% | [33 empty] | 218.9141
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 16.2594 | 16.1944 | 21.1087 | 27.6465 | 44.7138 | 60.6612 | 70.6819 | 82.6953 | 94.6655 | 118.9513 | 158.6038 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | 155.3757 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 206.1542 | 206.7254 | 223.2449 | 270.5423 | 304.8729 | 340.8297 | 387.416 | 434.8694 | 484.8443 | 490.643 | 554.0469 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525 | 505.2525
Option 5 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 11.3816 | 11.3361 | 14.7761 | 19.3526 | 31.2996 | 42.4628 | 49.4773 | 57.8867 | 66.2658 | 83.2659 | 111.0226 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | 108.763 | Option 5 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 61.8462 | 62.0176 | 66.9735 | 81.1627 | 91.4619 | 102.2489 | 116.2248 | 130.4608 | 145.4533 | 147.1929 | 166.2141 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758 | 151.5758
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% |  | 14.1119 | 20.6108 | 21.914 | 22.8848 | 24.479 | 28.0771 | 30.4835 | 33.579 | 35.0856 | 36.4011 | 33.5039 | 36.688 | 41.5371 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 | 37.8527 |  |  | 18.9052 | 25.6913 | 26.9233 | 27.6669 | 29.2245 | 32.8825 | 34.8486 | 38.7426 | 50.869 | 40.5546 | 38.4075 | 41.0655 | 46.7347 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082 | 42.9082
98% |  | 15.8841 | 23.6044 | 25.1526 | 26.3058 | 28.1996 | 32.4739 | 35.3326 | 39.0099 | 40.7996 | 42.3624 | 38.9206 | 42.7031 | 48.4636 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 | 44.0867 |  |  | 21.5783 | 29.6398 | 31.1033 | 31.9866 | 33.837 | 38.1825 | 40.5181 | 45.1439 | 59.5493 | 47.2965 | 44.7459 | 47.9034 | 54.6381 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924 | 50.0924
97% |  | 29.668 | 44.9517 | 48.0167 | 50.2998 | 54.0488 | 62.5107 | 68.17 | 75.4499 | 78.993 | 82.0868 | 75.2732 | 82.7614 | 94.1654 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 | 85.5005 |  |  | 40.9406 | 56.8999 | 59.7972 | 61.5461 | 65.2092 | 73.8119 | 78.4358 | 87.5935 | 116.1117 | 91.8549 | 86.8054 | 93.0564 | 106.389 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39 | 97.39
95% |  | 79.5528 | 124.6985 | 133.752 | 140.4959 | 151.57 | 176.565 | 193.2817 | 214.7854 | 225.2512 | 234.3898 | 214.2636 | 236.3826 | 270.0682 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 | 244.4734 |  |  | 112.8504 | 159.9917 | 168.5498 | 173.7156 | 184.5359 | 209.9471 | 223.6052 | 250.6557 | 334.8942 | 263.2432 | 248.3279 | 266.7924 | 306.1748 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932 | 279.5932
90% |  | 329.0269 | 577.9423 | 627.8597 | 665.0428 | 726.1007 | 863.9136 | 956.0826 | 1074.6453 | 1132.3497 | 1182.7361 | 1071.7684 | 1193.7236 | 1379.4528 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 | 1238.3333 |  |  | 512.6166 | 772.5349 | 819.7206 | 848.2029 | 907.8618 | 1047.9689 | 1123.274 | 1272.42 | 1736.8772 | 1341.8223 | 1259.5854 | 1361.3913 | 1578.5299 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694 | 1431.9694
85% |  | 384.1576 | 992.2401 | 1114.1848 | 1205.0204 | 1354.1805 | 1690.8475 | 1916.0099 | 2205.65 | 2346.6178 | 2469.7081 | 2198.6221 | 2496.5498 | 2950.2728 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 | 2605.528 |  |  | 832.6541 | 1467.616 | 1582.8873 | 1652.4675 | 1798.2098 | 2140.4816 | 2324.4464 | 2688.7995 | 3823.435 | 2858.3443 | 2657.4454 | 2906.15 | 3436.6039 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673 | 3078.5673
80% |  | 40.5692 | 810.9452 | 1000.4834 | 1141.6687 | 1373.5078 | 1896.7881 | 2246.7573 | 2696.9439 | 2916.0496 | 3107.3684 | 2686.0203 | 3149.0884 | 3854.3085 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 | 3318.4728 |  |  | 562.9012 | 1549.8203 | 1728.9859 | 1837.1342 | 2063.6609 | 2595.6528 | 2881.5887 | 3447.9014 | 5211.4613 | 3711.4242 | 3399.1679 | 3785.7286 | 4610.2112 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161 | 4053.7161
75% |  |  | 113.1047 | 238.1536 | 359.611 | 604.4399 | 1181.7641 | 1567.8778 | 2064.5593 | 2306.294 | 2517.3721 | 2052.5075 | 2563.4009 | 3341.4554 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 | 2750.2791 |  |  | 18.1131 | 798.9618 | 996.6315 | 1115.9492 | 1365.8714 | 1952.8069 | 2268.274 | 2893.075 | 4838.7738 | 3183.8142 | 2839.3083 | 3265.7926 | 4175.427 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576 | 3561.4576
70% | [5 empty] | 5.7042 | 238.2956 | 571.6541 | 1104.5202 | 1364.2506 | 1591.0422 | 1091.5713 | 1640.4976 | 2476.4737 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 | 1841.2878 |  |  |  | 46.753 | 127.7688 | 195.2392 | 380.2977 | 984.4485 | 1323.4003 | 1994.714 | 4085.2586 | 2307.0971 | 1936.9447 | 2395.1783 | 3372.5296 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538 | 2712.8538
65% | [8 empty] | 99.1807 | 229.6074 | 385.3242 | 94.0533 | 424.3131 | 1262.1913 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | 600.6561 | [7 empty] | 56.7487 | 205.6554 | 754.509 | 2957.5422 | 1083.7008 | 694.6676 | 1176.5216 | 2206.4625 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906 | 1511.2906
60% | FY38: 93.3017 | [9 empty] | 0.0032958 | 1535.0617 | 39.8205 |  | 64.8908 | 724.4493 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782 | 204.0782
55% | [40 empty] | 90.4405
50%
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0 | 892.9705 | 2708.0977 | 3209.517 | 3611.3293 | 4322.2303 | 6171.2356 | 7585.6495 | 9608.3235 | 10675.2985 | 11648.7911 | 9556.5043 | 11866.1086 | 15811.6905 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | 12766.4703 | E @ R (MWh) | 0 | 2120.5595 | 4907.9088 | 5542.3676 | 5943.9082 | 6828.7081 | 9132.9315 | 10504.0465 | 13473.5581 | 24840.2744 | 14968.9725 | 13205.406 | 15404.4711 | 20618.15 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168 | 17023.9168
Option 6 Winter POE50 W E @ R (MWh) N 1 | 0 | 625.0793 | 1895.6684 | 2246.6619 | 2527.9305 | 3025.5612 | 4319.8649 | 5309.9547 | 6725.8265 | 7472.709 | 8154.1538 | 6689.553 | 8306.276 | 11068.1834 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | 8936.5292 | Option 6 Winter POE10 W E @ R (MWh) N 1 | 0 | 636.1679 | 1472.3726 | 1662.7103 | 1783.1725 | 2048.6124 | 2739.8795 | 3151.214 | 4042.0674 | 7452.0823 | 4490.6918 | 3961.6218 | 4621.3413 | 6185.445 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751 | 5107.1751
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 14.9445 | 39.4129 | 45.8166 | 45.4333 | 45.4619 | 46.1192 | 47.8535 | 49.0144 | 50.151 | 51.4803 | 52.712 | 53.9079 | 54.0444 | 55.4401 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382 | 54.382
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.0551 | 19.1663 | 22.336 | 22.1463 | 22.1604 | 22.4858 | 23.3442 | 23.9189 | 24.4814 | 25.1394 | 25.7491 | 26.341 | 26.4086 | 27.0994 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757 | 26.5757
97% | 0.93981 | 6.9203 | 8.5571 | 8.5163 | 8.5138 | 8.703 | 8.8767 | 9.3134 | 9.6171 | 9.7582 | 9.92 | 10.0657 | 10.3964 | 10.7658 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 | 10.7723 |  | 13.2759 | 37.2524 | 43.5274 | 43.1518 | 43.1798 | 43.824 | 45.5234 | 46.661 | 47.7747 | 49.0773 | 50.2842 | 51.456 | 51.5898 | 52.9575 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207 | 51.9207
95% | 3.3177 | 32.7602 | 40.8184 | 40.6174 | 40.6049 | 41.5363 | 42.3918 | 44.5417 | 46.0368 | 46.7313 | 47.5278 | 48.2452 | 49.8732 | 51.6919 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 | 51.724 |  | 18.0366 | 53.4482 | 62.7158 | 62.1611 | 62.2024 | 63.1538 | 65.6637 | 67.3438 | 68.9888 | 70.9126 | 72.6951 | 74.4258 | 74.6234 | 76.6433 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112 | 75.112
90% | 1.1229 | 51.2346 | 65.2106 | 64.862 | 64.8403 | 66.4557 | 67.9394 | 71.6682 | 74.2612 | 75.4658 | 76.8472 | 78.0915 | 80.9149 | 84.0693 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 | 84.125 |  | 61.4543 | 214.9964 | 255.1805 | 252.775 | 252.9543 | 257.0793 | 267.9622 | 275.2472 | 282.3795 | 290.7209 | 298.4499 | 305.9541 | 306.8108 | 315.5692 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296 | 308.9296
85% |  | 120.5592 | 160.2208 | 159.2316 | 159.1701 | 163.7543 | 167.9649 | 178.5464 | 185.9051 | 189.3235 | 193.2437 | 196.7748 | 204.7873 | 213.7389 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 | 213.8968 |  | 33.2962 | 178.5388 | 216.5507 | 214.2753 | 214.4449 | 218.3469 | 228.6416 | 235.5328 | 242.2795 | 250.1701 | 257.4813 | 264.5798 | 265.3902 | 273.6752 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945 | 267.3945
80% |  | 129.5033 | 184.9036 | 183.5219 | 183.4359 | 189.8392 | 195.7208 | 210.5013 | 220.7801 | 225.555 | 231.0308 | 235.9631 | 247.1551 | 259.659 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 | 259.8796 |  | 4.8575 | 105.2453 | 131.7933 | 130.2042 | 130.3226 | 133.0478 | 140.2377 | 145.0506 | 149.7626 | 155.2735 | 160.3798 | 165.3375 | 165.9035 | 171.6898 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033 | 167.3033
75% |  | 223.1109 | 367.5293 | 363.9275 | 363.7035 | 380.3957 | 395.7278 | 434.2579 | 461.0529 | 473.5003 | 487.7747 | 500.6323 | 529.8079 | 562.4031 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 | 562.9783 |  |  | 148.6553 | 196.0396 | 193.2031 | 193.4145 | 198.2786 | 211.1115 | 219.7018 | 228.112 | 237.9481 | 247.062 | 255.9107 | 256.921 | 267.2487 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194 | 259.4194
70% |  | 160.3989 | 409.9099 | 403.6871 | 403.3001 | 432.1391 | 458.6284 | 525.1967 | 571.4902 | 592.9956 | 617.6574 | 639.8714 | 690.2779 | 746.5926 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 | 747.5864 |  |  | 189.5658 | 275.8872 | 270.7199 | 271.1051 | 279.9662 | 303.3442 | 318.9934 | 334.3146 | 352.2333 | 368.8364 | 384.9564 | 386.7967 | 405.6112 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482 | 391.3482
65% |  | 6.4062 | 380.4898 | 364.8611 | 363.8892 | 436.3189 | 502.8472 | 670.035 | 786.3022 | 840.3134 | 902.2523 | 958.0432 | 1084.6401 | 1226.0757 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 | 1228.5717 |  |  | 121.1418 | 229.7474 | 223.2462 | 223.7308 | 234.8794 | 264.2926 | 283.9818 | 303.2582 | 325.8027 | 346.6919 | 366.9734 | 369.2888 | 392.9603 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153 | 375.0153
60% |  |  | 0.34701 | 0.0085845 | 0.0038137 | 5.5505 | 19.7884 | 93.0408 | 174.5028 | 220.5821 | 279.712 | 338.6275 | 491.7302 | 691.7261 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 | 695.3745 |  |  | 17.9974 | 146.4796 | 136.3065 | 137.0647 | 154.5102 | 200.5365 | 231.3463 | 261.5104 | 296.7883 | 329.4761 | 361.2128 | 364.836 | 401.8775 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797 | 373.797
55% | FY38: 2.4078; FY39: 2.6549; FY40: 2.6549; FY41: 2.6549; FY42: 2.6549; FY43: 2.6549; FY44: 2.6549; FY45: 2.6549; FY46: 2.6549; FY47: 2.6549; FY48: 2.6549; FY49: 2.6549; FY50: 2.6549; FY51: 2.6549; FY52: 2.6549; FY53: 2.6549; FY54: 2.6549 |  |  |  | 2.8269 | 1.0842 | 1.186 | 4.7747 | 25.4721 | 48.1504 | 76.9747 | 118.7451 | 164.9667 | 216.5495 | 222.8498 | 291.6995 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888 | 238.7888
50% | [44 empty] | 0.70593
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 5.3804 | 730.8936 | 1617.9864 | 1589.2335 | 1587.4617 | 1724.6926 | 1859.8855 | 2237.1014 | 2529.9483 | 2674.2253 | 2845.966 | 3006.3147 | 3389.5829 | 3849.1303 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | 3857.5636 | E @ R (MWh) | 152.9201 | 1125.4206 | 1628.901 | 1594.7069 | 1597.2275 | 1656.466 | 1823.9833 | 1944.9425 | 2069.9875 | 2224.2918 | 2374.7845 | 2527.6047 | 2545.463 | 2733.1777 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865 | 2589.9865
Option 6 Summer POE50 W E @ R (MWh) N 1 | 3.7663 | 511.6255 | 1132.5905 | 1112.4634 | 1111.2232 | 1207.2849 | 1301.9198 | 1565.971 | 1770.9638 | 1871.9577 | 1992.1762 | 2104.4203 | 2372.7081 | 2694.3912 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | 2700.2945 | Option 6 Summer POE10 W E @ R (MWh) N 1 | 45.876 | 337.6262 | 488.6703 | 478.4121 | 479.1683 | 496.9398 | 547.195 | 583.4827 | 620.9963 | 667.2875 | 712.4354 | 758.2814 | 763.6389 | 819.9533 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996 | 776.996
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 37.4366 | 38.4052 | 40.0833 | 43.9094 | 46.4652 | 49.7088 | 51.3892 | 52.8635 | 50.1223 | 53.3207 | 58.3526 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 |  | 5.6789 | 33.6321 | 41.2692 | 42.4458 | 43.1872 | 44.8288 | 48.7149 | 50.8303 | 54.8724 | 67.1726 | 57.0171 | 55.026 | 57.6982 | 63.5502 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781
98% | 0.020606 | 33.3788 | 42.11 | 43.5925 | 44.7431 | 46.7365 | 51.2818 | 54.3179 | 58.1711 | 60.1673 | 61.9187 | 58.6624 | 62.4618 | 68.4394 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 |  | 5.8662 | 39.073 | 48.1454 | 49.5431 | 50.4239 | 52.374 | 56.9904 | 59.5034 | 64.3051 | 78.9171 | 66.8529 | 64.4876 | 67.6621 | 74.6138 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952
97% |  | 64.3022 | 81.5872 | 84.5221 | 86.7999 | 90.7464 | 99.7446 | 105.7551 | 113.3832 | 117.3353 | 120.8025 | 114.3559 | 121.8775 | 133.7114 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 |  | 9.8356 | 75.5748 | 93.5354 | 96.3025 | 98.0462 | 101.9067 | 111.0458 | 116.0208 | 125.5268 | 154.454 | 130.5706 | 125.888 | 132.1725 | 145.9349 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934
95% |  | 181.8568 | 232.914 | 241.5832 | 248.3116 | 259.9688 | 286.5483 | 304.3023 | 326.8347 | 338.5083 | 348.75 | 329.7076 | 351.9256 | 386.8808 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 |  | 20.9709 | 215.1544 | 268.2072 | 276.3809 | 281.5313 | 292.9348 | 319.9304 | 334.6257 | 362.705 | 448.1513 | 377.6034 | 363.7719 | 382.3354 | 422.9874 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941
90% |  | 893.0903 | 1174.5993 | 1222.3975 | 1259.4956 | 1323.7687 | 1470.3172 | 1568.2056 | 1692.4401 | 1756.8041 | 1813.2726 | 1708.2805 | 1830.7812 | 2023.5105 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 |  | 23.4784 | 1076.68 | 1369.1919 | 1414.2584 | 1442.6557 | 1505.5298 | 1654.3725 | 1735.397 | 1890.2148 | 2361.3315 | 1972.3588 | 1896.0974 | 1998.4489 | 2222.5876 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492
85% |  | 1762.1242 | 2449.8304 | 2566.598 | 2657.2259 | 2814.2407 | 3172.248 | 3411.3825 | 3714.8785 | 3872.1151 | 4010.0635 | 3753.5754 | 4052.8358 | 4523.6597 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 |  |  | 2210.6207 | 2925.2063 | 3035.3005 | 3104.6731 | 3258.27 | 3621.8821 | 3819.8191 | 4198.028 | 5348.9323 | 4398.6997 | 4212.3987 | 4462.436 | 5009.9908 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275
80% |  | 2007.5732 | 3076.4726 | 3257.9641 | 3398.8267 | 3642.8742 | 4199.3237 | 4571.0097 | 5042.7323 | 5287.1246 | 5501.5374 | 5102.8788 | 5568.0182 | 6299.8181 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 |  |  | 2704.6698 | 3815.3477 | 3986.4666 | 4094.2922 | 4333.0273 | 4898.1884 | 5205.8411 | 5793.6899 | 7582.5364 | 6105.5932 | 5816.0263 | 6204.6584 | 7055.7208 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459
75% |  | 1303.991 | 2483.2854 | 2683.5211 | 2838.9319 | 3108.1844 | 3722.1035 | 4132.1769 | 4652.6186 | 4922.2514 | 5158.8086 | 4718.9769 | 5232.1555 | 6039.5351 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 |  |  | 2073.0831 | 3298.4708 | 3487.2627 | 3606.2244 | 3869.6159 | 4493.1463 | 4832.5731 | 5481.1343 | 7454.7312 | 5825.2508 | 5505.7776 | 5934.5473 | 6873.5067 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17
70% |  | 329.0664 | 1554.418 | 1769.5601 | 1936.5403 | 2225.837 | 2885.4588 | 3326.0597 | 3885.2453 | 4174.9507 | 4429.1182 | 3956.5436 | 4507.9253 | 5375.4095 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 |  |  | 1113.6786 | 2430.2892 | 2633.1355 | 2760.9532 | 3043.9527 | 3713.9012 | 4078.5963 | 4775.4391 | 6895.9587 | 5145.173 | 4801.917 | 5262.606 | 6271.4654 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828
65% |  |  | 357.6004 | 534.3679 | 694.2568 | 998.0683 | 1693.1832 | 2157.4921 | 2746.7664 | 3052.0604 | 3319.9042 | 2821.9012 | 3402.9518 | 4317.1138 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 |  |  | 102.8871 | 1213.5217 | 1427.2829 | 1561.9782 | 1860.2054 | 2566.2027 | 2950.5214 | 3684.8601 | 5919.4811 | 4074.4887 | 3712.7627 | 4198.2405 | 5261.3849 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553
60% | [5 empty] | 22.0281 | 310.8024 | 678.0302 | 1303.0236 | 1639.1146 | 1933.9776 | 1385.7376 | 2025.4028 | 3031.7826 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 |  |  |  | 76.5442 | 162.0907 | 231.6582 | 427.4699 | 1104.2451 | 1527.3326 | 2335.7491 | 4795.7916 | 2764.6822 | 2366.4664 | 2900.9178 | 4071.3088 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835
55% | [8 empty] | 31.8697 | 126.1441 | 258.2709 | 49.3804 | 308.3505 | 1129.5587 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | [7 empty] | 5.3153 | 88.0196 | 509.6432 | 3087.7799 | 864.8984 | 532.1518 | 995.8136 | 2281.8383 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09
50% | [40 empty] | 614.3108 |  |  |  | 194.216 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 12441.5431 | 13203.537 | 14572.5364 | 17934.9211 | 20355.1972 | 23617.6722 | 25397.9652 | 27009.2878 | 24050.1225 | 27518.0067 | 33387.7721 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 16610.4697 | 17275.6237 | 18790.1152 | 22593.9352 | 24799.0804 | 29276.1679 | 44809.5484 | 31783.1886 | 29452.7715 | 32597.5368 | 39949.1057 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767
Option 7 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 8709.0802 | 9242.4759 | 10200.7755 | 12554.4447 | 14248.638 | 16532.3706 | 17778.5756 | 18906.5014 | 16835.0857 | 19262.6047 | 23371.4405 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | Option 7 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 4983.1409 | 5182.6871 | 5637.0346 | 6778.1806 | 7439.7241 | 8782.8504 | 13442.8645 | 9534.9566 | 8835.8314 | 9779.261 | 11984.7317 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 61.2344 | 61.2607 | 62.0035 | 63.97 | 65.2829 | 66.5702 | 68.0765 | 69.4698 | 70.8245 | 70.9755 | 72.5573 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 29.9674 | 29.9804 | 30.3481 | 31.3215 | 31.9713 | 32.6085 | 33.3541 | 34.0438 | 34.7143 | 34.789 | 35.572 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749
97% | 3.7957 | 10.5928 | 12.4418 | 12.3872 | 12.3841 | 12.5942 | 12.8249 | 13.2988 | 13.6394 | 13.8238 | 14.0252 | 14.2099 | 14.5441 | 14.9591 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 |  | 24.6994 | 51.9423 | 59.0661 | 58.6353 | 58.6611 | 59.389 | 61.3159 | 62.6024 | 63.8639 | 65.3399 | 66.7052 | 68.0327 | 68.1807 | 69.7307 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486
95% | 17.3774 | 50.84 | 59.9429 | 59.674 | 59.6588 | 60.6932 | 61.8287 | 64.162 | 65.8388 | 66.7468 | 67.7383 | 68.6472 | 70.2926 | 72.3358 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 |  | 34.9082 | 75.1439 | 85.6653 | 85.029 | 85.0671 | 86.1421 | 88.988 | 90.8882 | 92.7512 | 94.9312 | 96.9477 | 98.9082 | 99.1268 | 101.416 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701
90% | 24.555 | 82.5918 | 98.3797 | 97.9133 | 97.8869 | 99.681 | 101.6504 | 105.6971 | 108.6054 | 110.1802 | 111.8997 | 113.4762 | 116.33 | 119.8735 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 |  | 134.6084 | 309.068 | 354.6878 | 351.9289 | 352.0941 | 356.7553 | 369.095 | 377.3339 | 385.4121 | 394.8642 | 403.6075 | 412.1082 | 413.0559 | 422.9818 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119
85% | 44.847 | 209.5458 | 254.3493 | 253.0259 | 252.9509 | 258.0423 | 263.6311 | 275.1149 | 283.3684 | 287.8374 | 292.7171 | 297.1909 | 305.2894 | 315.3454 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 |  | 102.4961 | 267.5254 | 310.6793 | 308.0696 | 308.2258 | 312.635 | 324.3078 | 332.1012 | 339.7428 | 348.684 | 356.9547 | 364.9959 | 365.8924 | 375.2817 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121
80% | 23.7465 | 253.802 | 316.3847 | 314.536 | 314.4314 | 321.5432 | 329.3497 | 345.3906 | 356.9192 | 363.1617 | 369.9778 | 376.2269 | 387.5391 | 401.5855 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 |  | 52.1361 | 167.3947 | 197.5339 | 195.7112 | 195.8203 | 198.8998 | 207.0522 | 212.4953 | 217.8322 | 224.0769 | 229.8532 | 235.4693 | 236.0954 | 242.6531 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519
75% | 0.18716 | 547.1351 | 710.2768 | 705.4576 | 705.1848 | 723.724 | 744.0742 | 785.8898 | 815.9429 | 832.2159 | 849.9842 | 866.2744 | 895.7633 | 932.3798 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 |  | 53.8635 | 259.5826 | 313.3765 | 310.1233 | 310.3181 | 315.8145 | 330.3652 | 340.0803 | 349.6059 | 360.7517 | 371.0616 | 381.0855 | 382.203 | 393.9074 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811
70% |  | 720.2141 | 1002.0732 | 993.7472 | 993.2758 | 1025.3059 | 1060.4649 | 1132.7095 | 1184.6321 | 1212.7469 | 1243.4451 | 1271.5896 | 1322.5375 | 1385.7996 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 |  | 21.0605 | 391.6455 | 489.6437 | 483.7172 | 484.0719 | 494.0849 | 520.5925 | 538.2908 | 555.6439 | 575.9484 | 594.7305 | 612.9912 | 615.027 | 636.3493 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088
65% |  | 1159.8257 | 1867.7211 | 1846.81 | 1845.6263 | 1926.0704 | 2014.373 | 2195.817 | 2326.2218 | 2396.8327 | 2473.9318 | 2544.6175 | 2672.5742 | 2831.4585 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 |  |  | 375.3893 | 498.6861 | 491.2298 | 491.676 | 504.2739 | 537.6246 | 559.8917 | 581.7247 | 607.2709 | 630.9016 | 653.8765 | 656.4378 | 683.2646 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054
60% |  | 595.1039 | 1629.6346 | 1599.0683 | 1597.338 | 1714.9251 | 1843.9992 | 2109.2202 | 2299.836 | 2403.0496 | 2515.7473 | 2619.0702 | 2806.1076 | 3038.3525 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 |  |  | 374.3821 | 567.3189 | 555.6511 | 556.3494 | 576.0627 | 628.2504 | 663.0943 | 697.2588 | 737.234 | 774.2116 | 810.1631 | 814.1711 | 856.15 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351
55% |  |  | 438.6107 | 413.2466 | 411.832 | 513.1119 | 636.1403 | 924.2646 | 1139.8067 | 1256.5173 | 1383.9522 | 1500.7863 | 1712.2821 | 1974.8972 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 |  |  | 239.8473 | 609.6211 | 587.1995 | 588.5414 | 626.4237 | 726.7105 | 793.6685 | 859.321 | 936.1395 | 1007.1978 | 1076.2842 | 1083.9862 | 1164.6552 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336
50% | [7 empty] | 3.4281 | 36.6085 | 68.9695 | 115.5831 | 168.4762 | 288.3744 | 479.2895 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 |  |  |  | 218.9141 | 191.3668 | 192.9659 | 240.7061 | 390.8095 | 509.6193 | 640.0757 | 807.8717 | 965.5671 | 1118.8862 | 1135.9788 | 1315.0026 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715
45% | [40 empty] | 3.1349 | 28.4196 | 76.7087 | 83.5101 | 171.461 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 6295.8662 | 6290.5691 | 6655.6913 | 7068.3364 | 7954.9925 | 8631.4193 | 9012.0818 | 9439.0017 | 9840.5652 | 10591.6343 | 11566.2763 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 3709.8635 | 3715.0322 | 3863.5385 | 4280.4031 | 4577.3201 | 4882.411 | 5257.6779 | 5629.6718 | 6015.0485 | 6059.4299 | 6540.9827 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785
Option 7 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 4407.1063 | 4403.3984 | 4658.9839 | 4947.8355 | 5568.4947 | 6041.9935 | 6308.4573 | 6607.3012 | 6888.3957 | 7414.144 | 8096.3934 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | Option 7 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 1112.959 | 1114.5097 | 1159.0616 | 1284.1209 | 1373.196 | 1464.7233 | 1577.3034 | 1688.9015 | 1804.5146 | 1817.829 | 1962.2948 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 0.52857 | 28.8388 | 36.1886 | 37.4366 | 38.4052 | 40.0833 | 43.9094 | 46.4652 | 49.7088 | 51.3892 | 52.8635 | 50.1223 | 53.3207 | 58.3526 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 | 54.5225 |  | 5.6789 | 33.6321 | 41.2692 | 42.4458 | 43.1872 | 44.8288 | 48.7149 | 50.8303 | 54.8724 | 67.1726 | 57.0171 | 55.026 | 57.6982 | 63.5502 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781 | 59.5781
98% | 0.020606 | 33.3788 | 42.11 | 43.5925 | 44.7431 | 46.7365 | 51.2818 | 54.3179 | 58.1711 | 60.1673 | 61.9187 | 58.6624 | 62.4618 | 68.4394 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 | 63.8895 |  | 5.8662 | 39.073 | 48.1454 | 49.5431 | 50.4239 | 52.374 | 56.9904 | 59.5034 | 64.3051 | 78.9171 | 66.8529 | 64.4876 | 67.6621 | 74.6138 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952 | 69.8952
97% |  | 64.3022 | 81.5872 | 84.5221 | 86.7999 | 90.7464 | 99.7446 | 105.7551 | 113.3832 | 117.3353 | 120.8025 | 114.3559 | 121.8775 | 133.7114 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 | 124.704 |  | 9.8356 | 75.5748 | 93.5354 | 96.3025 | 98.0462 | 101.9067 | 111.0458 | 116.0208 | 125.5268 | 154.454 | 130.5706 | 125.888 | 132.1725 | 145.9349 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934 | 136.5934
95% |  | 181.8568 | 232.914 | 241.5832 | 248.3116 | 259.9688 | 286.5483 | 304.3023 | 326.8347 | 338.5083 | 348.75 | 329.7076 | 351.9256 | 386.8808 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 | 360.2743 |  | 20.9709 | 215.1544 | 268.2072 | 276.3809 | 281.5313 | 292.9348 | 319.9304 | 334.6257 | 362.705 | 448.1513 | 377.6034 | 363.7719 | 382.3354 | 422.9874 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941 | 395.3941
90% |  | 893.0903 | 1174.5993 | 1222.3975 | 1259.4956 | 1323.7687 | 1470.3172 | 1568.2056 | 1692.4401 | 1756.8041 | 1813.2726 | 1708.2805 | 1830.7812 | 2023.5105 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 | 1876.813 |  | 23.4784 | 1076.68 | 1369.1919 | 1414.2584 | 1442.6557 | 1505.5298 | 1654.3725 | 1735.397 | 1890.2148 | 2361.3315 | 1972.3588 | 1896.0974 | 1998.4489 | 2222.5876 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492 | 2070.4492
85% |  | 1762.1242 | 2449.8304 | 2566.598 | 2657.2259 | 2814.2407 | 3172.248 | 3411.3825 | 3714.8785 | 3872.1151 | 4010.0635 | 3753.5754 | 4052.8358 | 4523.6597 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 | 4165.2882 |  |  | 2210.6207 | 2925.2063 | 3035.3005 | 3104.6731 | 3258.27 | 3621.8821 | 3819.8191 | 4198.028 | 5348.9323 | 4398.6997 | 4212.3987 | 4462.436 | 5009.9908 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275 | 4638.3275
80% |  | 2007.5732 | 3076.4726 | 3257.9641 | 3398.8267 | 3642.8742 | 4199.3237 | 4571.0097 | 5042.7323 | 5287.1246 | 5501.5374 | 5102.8788 | 5568.0182 | 6299.8181 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 | 5742.8026 |  |  | 2704.6698 | 3815.3477 | 3986.4666 | 4094.2922 | 4333.0273 | 4898.1884 | 5205.8411 | 5793.6899 | 7582.5364 | 6105.5932 | 5816.0263 | 6204.6584 | 7055.7208 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459 | 6478.0459
75% |  | 1303.991 | 2483.2854 | 2683.5211 | 2838.9319 | 3108.1844 | 3722.1035 | 4132.1769 | 4652.6186 | 4922.2514 | 5158.8086 | 4718.9769 | 5232.1555 | 6039.5351 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 | 5424.9915 |  |  | 2073.0831 | 3298.4708 | 3487.2627 | 3606.2244 | 3869.6159 | 4493.1463 | 4832.5731 | 5481.1343 | 7454.7312 | 5825.2508 | 5505.7776 | 5934.5473 | 6873.5067 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17 | 6236.17
70% |  | 329.0664 | 1554.418 | 1769.5601 | 1936.5403 | 2225.837 | 2885.4588 | 3326.0597 | 3885.2453 | 4174.9507 | 4429.1182 | 3956.5436 | 4507.9253 | 5375.4095 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 | 4715.1168 |  |  | 1113.6786 | 2430.2892 | 2633.1355 | 2760.9532 | 3043.9527 | 3713.9012 | 4078.5963 | 4775.4391 | 6895.9587 | 5145.173 | 4801.917 | 5262.606 | 6271.4654 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828 | 5586.6828
65% |  |  | 357.6004 | 534.3679 | 694.2568 | 998.0683 | 1693.1832 | 2157.4921 | 2746.7664 | 3052.0604 | 3319.9042 | 2821.9012 | 3402.9518 | 4317.1138 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 | 3621.2919 |  |  | 102.8871 | 1213.5217 | 1427.2829 | 1561.9782 | 1860.2054 | 2566.2027 | 2950.5214 | 3684.8601 | 5919.4811 | 4074.4887 | 3712.7627 | 4198.2405 | 5261.3849 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553 | 4539.7553
60% | [5 empty] | 22.0281 | 310.8024 | 678.0302 | 1303.0236 | 1639.1146 | 1933.9776 | 1385.7376 | 2025.4028 | 3031.7826 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 | 2265.7684 |  |  |  | 76.5442 | 162.0907 | 231.6582 | 427.4699 | 1104.2451 | 1527.3326 | 2335.7491 | 4795.7916 | 2764.6822 | 2366.4664 | 2900.9178 | 4071.3088 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835 | 3276.8835
55% | [8 empty] | 31.8697 | 126.1441 | 258.2709 | 49.3804 | 308.3505 | 1129.5587 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | 460.0863 | [7 empty] | 5.3153 | 88.0196 | 509.6432 | 3087.7799 | 864.8984 | 532.1518 | 995.8136 | 2281.8383 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09 | 1398.09
50% | [40 empty] | 614.3108 |  |  |  | 194.216 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117 | 2.9117
45%
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 0.54918 | 6604.2219 | 11489.0059 | 12441.5431 | 13203.537 | 14572.5364 | 17934.9211 | 20355.1972 | 23617.6722 | 25397.9652 | 27009.2878 | 24050.1225 | 27518.0067 | 33387.7721 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | 28875.549 | E @ R (MWh) | 65.83 | 9645.0538 | 15579.729 | 16610.4697 | 17275.6237 | 18790.1152 | 22593.9352 | 24799.0804 | 29276.1679 | 44809.5484 | 31783.1886 | 29452.7715 | 32597.5368 | 39949.1057 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767 | 34888.7767
Option 8 Winter POE50 W E @ R (MWh) N 1 | 0.38442 | 4622.9553 | 8042.3041 | 8709.0802 | 9242.4759 | 10200.7755 | 12554.4447 | 14248.638 | 16532.3706 | 17778.5756 | 18906.5014 | 16835.0857 | 19262.6047 | 23371.4405 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | 20212.8843 | Option 8 Winter POE10 W E @ R (MWh) N 1 | 19.749 | 2893.5161 | 4673.9187 | 4983.1409 | 5182.6871 | 5637.0346 | 6778.1806 | 7439.7241 | 8782.8504 | 13442.8645 | 9534.9566 | 8835.8314 | 9779.261 | 11984.7317 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633 | 10466.633
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.6023 | 54.4041 | 61.674 | 61.2344 | 61.2607 | 62.0035 | 63.97 | 65.2829 | 66.5702 | 68.0765 | 69.4698 | 70.8245 | 70.9755 | 72.5573 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12.8254 | 26.5866 | 30.185 | 29.9674 | 29.9804 | 30.3481 | 31.3215 | 31.9713 | 32.6085 | 33.3541 | 34.0438 | 34.7143 | 34.789 | 35.572 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749
97% | 3.7957 | 10.5928 | 12.4418 | 12.3872 | 12.3841 | 12.5942 | 12.8249 | 13.2988 | 13.6394 | 13.8238 | 14.0252 | 14.2099 | 14.5441 | 14.9591 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 |  | 24.6994 | 51.9423 | 59.0661 | 58.6353 | 58.6611 | 59.389 | 61.3159 | 62.6024 | 63.8639 | 65.3399 | 66.7052 | 68.0327 | 68.1807 | 69.7307 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486
95% | 17.3774 | 50.84 | 59.9429 | 59.674 | 59.6588 | 60.6932 | 61.8287 | 64.162 | 65.8388 | 66.7468 | 67.7383 | 68.6472 | 70.2926 | 72.3358 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 |  | 34.9082 | 75.1439 | 85.6653 | 85.029 | 85.0671 | 86.1421 | 88.988 | 90.8882 | 92.7512 | 94.9312 | 96.9477 | 98.9082 | 99.1268 | 101.416 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701
90% | 24.555 | 82.5918 | 98.3797 | 97.9133 | 97.8869 | 99.681 | 101.6504 | 105.6971 | 108.6054 | 110.1802 | 111.8997 | 113.4762 | 116.33 | 119.8735 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 |  | 134.6084 | 309.068 | 354.6878 | 351.9289 | 352.0941 | 356.7553 | 369.095 | 377.3339 | 385.4121 | 394.8642 | 403.6075 | 412.1082 | 413.0559 | 422.9818 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119
85% | 44.847 | 209.5458 | 254.3493 | 253.0259 | 252.9509 | 258.0423 | 263.6311 | 275.1149 | 283.3684 | 287.8374 | 292.7171 | 297.1909 | 305.2894 | 315.3454 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 |  | 102.4961 | 267.5254 | 310.6793 | 308.0696 | 308.2258 | 312.635 | 324.3078 | 332.1012 | 339.7428 | 348.684 | 356.9547 | 364.9959 | 365.8924 | 375.2817 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121
80% | 23.7465 | 253.802 | 316.3847 | 314.536 | 314.4314 | 321.5432 | 329.3497 | 345.3906 | 356.9192 | 363.1617 | 369.9778 | 376.2269 | 387.5391 | 401.5855 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 |  | 52.1361 | 167.3947 | 197.5339 | 195.7112 | 195.8203 | 198.8998 | 207.0522 | 212.4953 | 217.8322 | 224.0769 | 229.8532 | 235.4693 | 236.0954 | 242.6531 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519
75% | 0.18716 | 547.1351 | 710.2768 | 705.4576 | 705.1848 | 723.724 | 744.0742 | 785.8898 | 815.9429 | 832.2159 | 849.9842 | 866.2744 | 895.7633 | 932.3798 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 |  | 53.8635 | 259.5826 | 313.3765 | 310.1233 | 310.3181 | 315.8145 | 330.3652 | 340.0803 | 349.6059 | 360.7517 | 371.0616 | 381.0855 | 382.203 | 393.9074 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811
70% |  | 720.2141 | 1002.0732 | 993.7472 | 993.2758 | 1025.3059 | 1060.4649 | 1132.7095 | 1184.6321 | 1212.7469 | 1243.4451 | 1271.5896 | 1322.5375 | 1385.7996 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 |  | 21.0605 | 391.6455 | 489.6437 | 483.7172 | 484.0719 | 494.0849 | 520.5925 | 538.2908 | 555.6439 | 575.9484 | 594.7305 | 612.9912 | 615.027 | 636.3493 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088
65% |  | 1159.8257 | 1867.7211 | 1846.81 | 1845.6263 | 1926.0704 | 2014.373 | 2195.817 | 2326.2218 | 2396.8327 | 2473.9318 | 2544.6175 | 2672.5742 | 2831.4585 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 |  |  | 375.3893 | 498.6861 | 491.2298 | 491.676 | 504.2739 | 537.6246 | 559.8917 | 581.7247 | 607.2709 | 630.9016 | 653.8765 | 656.4378 | 683.2646 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054
60% |  | 595.1039 | 1629.6346 | 1599.0683 | 1597.338 | 1714.9251 | 1843.9992 | 2109.2202 | 2299.836 | 2403.0496 | 2515.7473 | 2619.0702 | 2806.1076 | 3038.3525 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 |  |  | 374.3821 | 567.3189 | 555.6511 | 556.3494 | 576.0627 | 628.2504 | 663.0943 | 697.2588 | 737.234 | 774.2116 | 810.1631 | 814.1711 | 856.15 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351
55% |  |  | 438.6107 | 413.2466 | 411.832 | 513.1119 | 636.1403 | 924.2646 | 1139.8067 | 1256.5173 | 1383.9522 | 1500.7863 | 1712.2821 | 1974.8972 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 |  |  | 239.8473 | 609.6211 | 587.1995 | 588.5414 | 626.4237 | 726.7105 | 793.6685 | 859.321 | 936.1395 | 1007.1978 | 1076.2842 | 1083.9862 | 1164.6552 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336
50% | [7 empty] | 3.4281 | 36.6085 | 68.9695 | 115.5831 | 168.4762 | 288.3744 | 479.2895 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 |  |  |  | 218.9141 | 191.3668 | 192.9659 | 240.7061 | 390.8095 | 509.6193 | 640.0757 | 807.8717 | 965.5671 | 1118.8862 | 1135.9788 | 1315.0026 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715
45% | [40 empty] | 3.1349 | 28.4196 | 76.7087 | 83.5101 | 171.461 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343
40%
35%
30%
25%
20%
15%
10%
5%
9.992e-14%
E @ R (MWh) | 114.5088 | 3629.6513 | 6389.8148 | 6295.8662 | 6290.5691 | 6655.6913 | 7068.3364 | 7954.9925 | 8631.4193 | 9012.0818 | 9439.0017 | 9840.5652 | 10591.6343 | 11566.2763 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | E @ R (MWh) | 463.1998 | 2592.9116 | 3797.0519 | 3709.8635 | 3715.0322 | 3863.5385 | 4280.4031 | 4577.3201 | 4882.411 | 5257.6779 | 5629.6718 | 6015.0485 | 6059.4299 | 6540.9827 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785
Option 8 Summer POE50 W E @ R (MWh) N 1 | 80.1561 | 2540.7559 | 4472.8704 | 4407.1063 | 4403.3984 | 4658.9839 | 4947.8355 | 5568.4947 | 6041.9935 | 6308.4573 | 6607.3012 | 6888.3957 | 7414.144 | 8096.3934 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | Option 8 Summer POE10 W E @ R (MWh) N 1 | 138.9599 | 777.8735 | 1139.1156 | 1112.959 | 1114.5097 | 1159.0616 | 1284.1209 | 1373.196 | 1464.7233 | 1577.3034 | 1688.9015 | 1804.5146 | 1817.829 | 1962.2948 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936

## E@R N-2
Option 1 - Do Nothing / Base Case
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 110.3988 | 111.3674 | 113.0455 | 116.8717 | 119.4274 | 122.671 | 124.3515 | 125.8258 | 123.0846 | 126.2829 | 131.3148 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 |  | 78.6411 | 106.5944 | 114.2314 | 115.4081 | 116.1495 | 117.791 | 121.6771 | 123.7926 | 127.8346 | 140.1348 | 129.9793 | 127.9882 | 130.6605 | 136.5124 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403
98% | 87.3027 | 120.9335 | 129.6647 | 131.1472 | 132.2978 | 134.2912 | 138.8365 | 141.8726 | 145.7258 | 147.722 | 149.4734 | 146.2171 | 150.0165 | 155.9941 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 |  | 93.4209 | 126.6277 | 135.7001 | 137.0978 | 137.9786 | 139.9286 | 144.5451 | 147.0581 | 151.8598 | 166.4717 | 154.4076 | 152.0423 | 155.2168 | 162.1685 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499
97% | 172.8327 | 239.4116 | 256.6966 | 259.6314 | 261.9093 | 265.8557 | 274.854 | 280.8645 | 288.4926 | 292.4446 | 295.9119 | 289.4652 | 296.9869 | 308.8207 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 |  | 184.945 | 250.6842 | 268.6448 | 271.4119 | 273.1556 | 277.0161 | 286.1552 | 291.1302 | 300.6362 | 329.5634 | 305.68 | 300.9974 | 307.2819 | 321.0443 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028
95% | 510.5211 | 707.185 | 758.2422 | 766.9113 | 773.6398 | 785.297 | 811.8764 | 829.6304 | 852.1628 | 863.8365 | 874.0782 | 855.0358 | 877.2537 | 912.2089 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 |  | 546.299 | 740.4826 | 793.5354 | 801.7091 | 806.8595 | 818.2629 | 845.2585 | 859.9539 | 888.0332 | 973.4795 | 902.9316 | 889.1001 | 907.6635 | 948.3155 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222
90% | 2814.8088 | 3899.1347 | 4180.6436 | 4228.4418 | 4265.5399 | 4329.8131 | 4476.3615 | 4574.25 | 4698.4845 | 4762.8484 | 4819.3169 | 4714.3248 | 4836.8255 | 5029.5548 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 |  | 3012.0741 | 4082.7244 | 4375.2363 | 4420.3027 | 4448.7 | 4511.5741 | 4660.4169 | 4741.4413 | 4896.2592 | 5367.3759 | 4978.4031 | 4902.1418 | 5004.4932 | 5228.6319 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935
85% | 6876.3763 | 9525.3066 | 10213.0129 | 10329.7805 | 10420.4084 | 10577.4231 | 10935.4305 | 11174.565 | 11478.0609 | 11635.2975 | 11773.246 | 11516.7578 | 11816.0183 | 12286.8422 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 |  | 7358.2813 | 9973.8032 | 10688.3888 | 10798.4829 | 10867.8555 | 11021.4524 | 11385.0646 | 11583.0015 | 11961.2104 | 13112.1147 | 12161.8821 | 11975.5812 | 12225.6185 | 12773.1733 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51
80% | 10687.9274 | 14805.1503 | 15874.0497 | 16055.5412 | 16196.4038 | 16440.4513 | 16996.9008 | 17368.5868 | 17840.3094 | 18084.7017 | 18299.1145 | 17900.4559 | 18365.5953 | 19097.3952 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 |  | 11436.9506 | 15502.2469 | 16612.9248 | 16784.0437 | 16891.8693 | 17130.6044 | 17695.7655 | 18003.4182 | 18591.267 | 20380.1135 | 18903.1703 | 18613.6034 | 19002.2355 | 19853.298 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623
75% | 11791.7667 | 16334.2127 | 17513.507 | 17713.7428 | 17869.1536 | 18138.406 | 18752.3252 | 19162.3985 | 19682.8403 | 19952.4731 | 20189.0303 | 19749.1986 | 20262.3772 | 21069.7567 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 |  | 12618.1483 | 17103.3048 | 18328.6925 | 18517.4844 | 18636.4461 | 18899.8376 | 19523.368 | 19862.7948 | 20511.356 | 22484.9529 | 20855.4725 | 20535.9993 | 20964.769 | 21903.7284 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917
70% | 12669.5942 | 17550.1984 | 18817.2842 | 19032.4264 | 19199.4066 | 19488.7033 | 20148.3251 | 20588.926 | 21148.1115 | 21437.817 | 21691.9844 | 21219.4098 | 21770.7916 | 22638.2758 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 |  | 13557.495 | 18376.5449 | 19693.1554 | 19896.0018 | 20023.8195 | 20306.8189 | 20976.7675 | 21341.4626 | 22038.3054 | 24158.8249 | 22408.0393 | 22064.7832 | 22525.4722 | 23534.3317 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549
65% | 13351.323 | 18494.5441 | 19829.8096 | 20056.5282 | 20232.4932 | 20537.3565 | 21232.4714 | 21696.7803 | 22286.0546 | 22591.3486 | 22859.1924 | 22361.1894 | 22942.24 | 23856.402 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 |  | 14287.0002 | 19365.3548 | 20752.8099 | 20966.571 | 21101.2664 | 21399.4935 | 22105.4909 | 22489.8096 | 23224.1482 | 25458.7693 | 23613.7769 | 23252.0508 | 23737.5287 | 24800.6731 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435
60% | 14698.1621 | 20360.2151 | 21830.1779 | 22079.7671 | 22273.483 | 22609.0999 | 23374.3358 | 23885.4827 | 24534.2012 | 24870.2922 | 25165.1552 | 24616.9152 | 25256.5804 | 26262.9602 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 |  | 15728.2275 | 21318.8704 | 22846.2875 | 23081.6122 | 23229.8952 | 23558.2066 | 24335.4227 | 24758.5102 | 25566.9267 | 28026.9692 | 25995.8598 | 25597.644 | 26132.0954 | 27302.4864 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611
55% | 16350.7821 | 22649.4603 | 24284.7017 | 24562.354 | 24777.8508 | 25151.2035 | 26002.4804 | 26571.0991 | 27292.7577 | 27666.6379 | 27994.6544 | 27384.7719 | 28096.3592 | 29215.8935 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 |  | 17496.6651 | 23715.9042 | 25415.0598 | 25676.8438 | 25841.7993 | 26207.0251 | 27071.6291 | 27542.2874 | 28441.6 | 31178.2427 | 28918.7611 | 28475.7711 | 29070.3146 | 30372.3011 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529
50% | 16573.101 | 22957.4214 | 24614.8968 | 24896.3244 | 25114.7512 | 25493.1803 | 26356.0319 | 26932.3821 | 27663.8529 | 28042.8167 | 28375.2932 | 27757.1182 | 28478.3809 | 29613.1373 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 |  | 17734.5645 | 24038.3655 | 25760.6242 | 26025.9676 | 26193.1661 | 26563.3577 | 27439.7177 | 27916.7755 | 28828.3158 | 31602.1683 | 29311.9648 | 28862.9515 | 29465.579 | 30785.2684 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039
45% | 12791.4633 | 17719.0143 | 18998.2882 | 19215.4999 | 19384.0862 | 19676.1657 | 20342.1324 | 20786.9714 | 21351.5358 | 21644.0279 | 21900.6402 | 21423.5199 | 21980.2054 | 22856.034 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 |  | 13687.9049 | 18553.3094 | 19882.5844 | 20087.382 | 20216.4292 | 20502.1508 | 21178.5436 | 21546.7467 | 22250.2924 | 24391.2093 | 22623.5828 | 22277.025 | 22742.1454 | 23760.7091 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395
40% | 6284.3875 | 8705.2708 | 9333.7723 | 9440.4874 | 9523.3131 | 9666.8104 | 9993.9968 | 10212.5442 | 10489.9121 | 10633.6121 | 10759.6846 | 10525.2775 | 10798.7746 | 11229.0652 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 |  | 6724.8052 | 9115.1562 | 9768.223 | 9868.8391 | 9932.2394 | 10072.6131 | 10404.9218 | 10585.8183 | 10931.4671 | 11983.2898 | 11114.863 | 10944.6007 | 11173.1122 | 11673.5279 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612
35% | 2348.7515 | 3253.5419 | 3488.4405 | 3528.3246 | 3559.2802 | 3612.9114 | 3735.1954 | 3816.8761 | 3920.5407 | 3974.2477 | 4021.3665 | 3933.7583 | 4035.9762 | 4196.7946 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 |  | 2513.3549 | 3406.7341 | 3650.8138 | 3688.4184 | 3712.1139 | 3764.5777 | 3888.7761 | 3956.3851 | 4085.5692 | 4478.6815 | 4154.1123 | 4090.4778 | 4175.8826 | 4362.9099 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1759.7242 | 1775.163 | 1801.9112 | 1862.8993 | 1903.637 | 1955.3388 | 1982.1248 | 2005.6249 | 1961.931 | 2012.9114 | 2093.1183 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 |  | 1253.516 | 1699.0818 | 1820.8147 | 1839.5697 | 1851.3876 | 1877.5536 | 1939.4965 | 1973.2159 | 2037.6455 | 2233.7072 | 2071.8308 | 2040.0936 | 2082.6886 | 2175.967 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525
25% | 690.592 | 956.6232 | 1025.6893 | 1037.4162 | 1046.5179 | 1062.2869 | 1098.2414 | 1122.2576 | 1152.7376 | 1168.5288 | 1182.3829 | 1156.6239 | 1186.6785 | 1233.9632 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 |  | 738.9896 | 1001.6655 | 1073.4311 | 1084.4878 | 1091.4549 | 1106.8806 | 1143.398 | 1163.2767 | 1201.2601 | 1316.845 | 1221.4135 | 1202.7034 | 1227.8145 | 1282.8053 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793
20% | 348.989 | 483.4272 | 518.3296 | 524.2558 | 528.8553 | 536.8241 | 554.9937 | 567.1302 | 582.5332 | 590.5132 | 597.5144 | 584.4971 | 599.6851 | 623.5803 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 |  | 373.4466 | 506.1893 | 542.4558 | 548.0433 | 551.5641 | 559.3594 | 577.8134 | 587.8591 | 607.0539 | 665.4645 | 617.2384 | 607.7833 | 620.4731 | 648.2626 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999
15% | 142.1807 | 196.9518 | 211.1713 | 213.5857 | 215.4596 | 218.7061 | 226.1085 | 231.053 | 237.3283 | 240.5795 | 243.4318 | 238.1285 | 244.3162 | 254.0512 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 |  | 152.1449 | 206.2253 | 221.0005 | 223.2769 | 224.7113 | 227.8872 | 235.4055 | 239.4982 | 247.3183 | 271.1152 | 251.4675 | 247.6154 | 252.7853 | 264.107 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222
10% | 57.2416 | 79.2923 | 85.017 | 85.989 | 86.7435 | 88.0505 | 91.0307 | 93.0214 | 95.5478 | 96.8567 | 98.005 | 95.8699 | 98.3611 | 102.2804 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 |  | 61.2531 | 83.0258 | 88.9742 | 89.8907 | 90.4682 | 91.7468 | 94.7736 | 96.4213 | 99.5697 | 109.1503 | 101.2402 | 99.6893 | 101.7707 | 106.3288 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349
5% | 48.7477 | 67.5263 | 72.4016 | 73.2294 | 73.8719 | 74.985 | 77.5229 | 79.2182 | 81.3697 | 82.4844 | 83.4623 | 81.644 | 83.7655 | 87.1033 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 |  | 52.164 | 70.7058 | 75.7716 | 76.5521 | 77.0439 | 78.1327 | 80.7104 | 82.1137 | 84.7948 | 92.9538 | 86.2174 | 84.8967 | 86.6693 | 90.551 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 196101.5072 | 197821.9953 | 200802.7777 | 207599.2223 | 212138.9744 | 217900.5692 | 220885.5628 | 223504.3892 | 218635.1944 | 224316.3823 | 233254.5468 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 204999.3971 | 206316.373 | 209232.2711 | 216135.1177 | 219892.7708 | 227072.7236 | 248921.5973 | 230882.2942 | 227345.5395 | 232092.2705 | 242487.1014 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111
Option 1 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 137271.0551 | 138475.3967 | 140561.9444 | 145319.4556 | 148497.2821 | 152530.3985 | 154619.8939 | 156453.0725 | 153044.6361 | 157021.4676 | 163278.1828 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | Option 1 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 61499.8191 | 61894.9119 | 62769.6813 | 64840.5353 | 65967.8312 | 68121.8171 | 74676.4792 | 69264.6882 | 68203.6618 | 69627.6812 | 72746.1304 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 129.304 | 129.3303 | 130.0731 | 132.0395 | 133.3525 | 134.6398 | 136.1461 | 137.5394 | 138.8941 | 139.0451 | 140.6269 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 64.0022 | 64.0152 | 64.3829 | 65.3562 | 66.0061 | 66.6433 | 67.3889 | 68.0786 | 68.7491 | 68.8238 | 69.6068 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097
97% | 20.8131 | 27.6102 | 29.4592 | 29.4046 | 29.4015 | 29.6116 | 29.8423 | 30.3162 | 30.6568 | 30.8412 | 31.0426 | 31.2273 | 31.5615 | 31.9765 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 |  | 92.7689 | 120.0119 | 127.1357 | 126.7049 | 126.7307 | 127.4585 | 129.3855 | 130.672 | 131.9335 | 133.4095 | 134.7748 | 136.1022 | 136.2502 | 137.8002 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181
95% | 102.4643 | 135.9269 | 145.0299 | 144.761 | 144.7458 | 145.7802 | 146.9157 | 149.2489 | 150.9258 | 151.8338 | 152.8252 | 153.7342 | 155.3796 | 157.4227 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 |  | 137.0126 | 177.2483 | 187.7696 | 187.1334 | 187.1714 | 188.2465 | 191.0924 | 192.9925 | 194.8556 | 197.0355 | 199.052 | 201.0125 | 201.2311 | 203.5203 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745
90% | 177.7116 | 235.7483 | 251.5362 | 251.0698 | 251.0434 | 252.8375 | 254.8069 | 258.8536 | 261.762 | 263.3368 | 265.0563 | 266.6327 | 269.4865 | 273.03 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 |  | 594.078 | 768.5376 | 814.1574 | 811.3985 | 811.5637 | 816.2249 | 828.5646 | 836.8035 | 844.8817 | 854.3338 | 863.0771 | 871.5778 | 872.5255 | 882.4514 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815
85% | 504.3166 | 669.0154 | 713.8189 | 712.4955 | 712.4205 | 717.5119 | 723.1007 | 734.5845 | 742.838 | 747.307 | 752.1867 | 756.6605 | 764.759 | 774.815 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 |  | 561.9657 | 726.995 | 770.1489 | 767.5392 | 767.6954 | 772.1046 | 783.7774 | 791.5709 | 799.2124 | 808.1536 | 816.4243 | 824.4655 | 825.362 | 834.7513 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906
80% | 704.4422 | 934.4978 | 997.0804 | 995.2318 | 995.1271 | 1002.2389 | 1010.0454 | 1026.0863 | 1037.6149 | 1043.8574 | 1050.6735 | 1056.9226 | 1068.2348 | 1082.2812 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 |  | 392.484 | 507.7425 | 537.8818 | 536.0591 | 536.1682 | 539.2477 | 547.4001 | 552.8431 | 558.1801 | 564.4247 | 570.2011 | 575.8172 | 576.4433 | 583.0009 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998
75% | 1836.3528 | 2436.0657 | 2599.2074 | 2594.3882 | 2594.1154 | 2612.6546 | 2633.0048 | 2674.8204 | 2704.8735 | 2721.1465 | 2738.9148 | 2755.205 | 2784.6939 | 2821.3104 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 |  | 700.5244 | 906.2435 | 960.0375 | 956.7843 | 956.979 | 962.4754 | 977.0262 | 986.7412 | 996.2669 | 1007.4126 | 1017.7226 | 1027.7464 | 1028.8639 | 1040.5683 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421
70% | 3172.6584 | 4208.7797 | 4490.6388 | 4482.3127 | 4481.8414 | 4513.8714 | 4549.0304 | 4621.275 | 4673.1976 | 4701.3124 | 4732.0106 | 4760.1551 | 4811.103 | 4874.3651 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1743.0043 | 1743.359 | 1753.372 | 1779.8796 | 1797.5778 | 1814.931 | 1835.2355 | 1854.0175 | 1872.2783 | 1874.3141 | 1895.6364 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751
65% | 7968.2023 | 10570.444 | 11278.3393 | 11257.4282 | 11256.2445 | 11336.6886 | 11424.9912 | 11606.4352 | 11736.84 | 11807.4509 | 11884.55 | 11955.2357 | 12083.1924 | 12242.0767 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 |  | 1605.6162 | 2077.1285 | 2200.4254 | 2192.969 | 2193.4153 | 2206.0132 | 2239.3639 | 2261.631 | 2283.4639 | 2309.0102 | 2332.6409 | 2355.6158 | 2358.1771 | 2385.0038 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446
60% | 11647.312 | 15451.0709 | 16485.8185 | 16455.2522 | 16453.5219 | 16571.109 | 16700.1831 | 16965.4041 | 17156.0199 | 17259.2335 | 17371.9312 | 17475.2541 | 17662.2915 | 17894.5364 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 |  | 2512.492 | 3250.3215 | 3443.2583 | 3431.5904 | 3432.2888 | 3452.0021 | 3504.1898 | 3539.0337 | 3573.1982 | 3613.1734 | 3650.151 | 3686.1024 | 3690.1105 | 3732.0893 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745
55% | 13170.4015 | 17471.5683 | 18641.6273 | 18607.0639 | 18605.1073 | 18738.071 | 18884.0238 | 19183.9271 | 19399.4692 | 19516.1798 | 19643.6146 | 19760.4488 | 19971.9446 | 20234.5597 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 |  | 4828.1473 | 6246.0024 | 6616.7608 | 6594.3391 | 6595.6811 | 6633.5633 | 6733.8501 | 6800.8082 | 6866.4607 | 6943.2792 | 7014.3375 | 7083.4238 | 7091.1259 | 7171.7949 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733
50% | 16911.4168 | 22434.3178 | 23936.7286 | 23892.3477 | 23889.8353 | 24060.567 | 24247.9772 | 24633.0672 | 24909.8334 | 25059.6953 | 25223.3277 | 25373.3483 | 25644.9189 | 25982.129 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 |  | 10714.812 | 13861.3711 | 14684.1724 | 14634.4134 | 14637.3915 | 14721.4613 | 14944.0217 | 15092.6176 | 15238.3161 | 15408.7947 | 15566.4901 | 15719.8092 | 15736.9019 | 15915.9256 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945
45% | 22520.2713 | 29874.9022 | 31875.6039 | 31816.5035 | 31813.1579 | 32040.5146 | 32290.0814 | 32802.8907 | 33171.4494 | 33371.0147 | 33588.9175 | 33788.694 | 34150.3339 | 34599.3834 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 |  | 16236.3476 | 21004.3853 | 22251.1909 | 22175.7903 | 22180.3031 | 22307.6955 | 22644.9453 | 22870.1153 | 23090.8949 | 23349.2243 | 23588.1829 | 23820.5101 | 23846.4109 | 24117.6889 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008
40% | 15794.9825 | 20953.2804 | 22356.5072 | 22315.0562 | 22312.7097 | 22472.1702 | 22647.2082 | 23006.8759 | 23265.371 | 23405.3395 | 23558.1694 | 23698.2861 | 23951.9286 | 24266.8772 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 |  | 16811.9908 | 21749.0744 | 23040.0842 | 22962.0103 | 22966.6831 | 23098.592 | 23447.7987 | 23680.9519 | 23909.559 | 24177.0472 | 24424.4778 | 24665.0419 | 24691.8611 | 24972.7569 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339
35% | 8189.141 | 10863.5364 | 11591.06 | 11569.5691 | 11568.3525 | 11651.0272 | 11741.7782 | 11928.2532 | 12062.2738 | 12134.8425 | 12214.0795 | 12286.725 | 12418.2297 | 12581.5194 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 |  | 22897.8708 | 29622.1608 | 31380.5115 | 31274.1752 | 31280.5395 | 31460.199 | 31935.8172 | 32253.3711 | 32564.7331 | 32929.051 | 33266.0507 | 33593.6981 | 33630.2257 | 34012.8048 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338
30% | 3808.7911 | 5052.6595 | 5391.0326 | 5381.0371 | 5380.4713 | 5418.9235 | 5461.132 | 5547.8621 | 5610.1954 | 5643.9473 | 5680.8006 | 5714.5882 | 5775.7514 | 5851.6979 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 |  | 21159.0479 | 27372.7075 | 28997.5323 | 28899.2709 | 28905.152 | 29071.1685 | 29510.6691 | 29804.1085 | 30091.8262 | 30428.4785 | 30739.887 | 31042.6535 | 31076.4072 | 31429.934 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195
25% | 2600.5659 | 3449.8542 | 3680.8886 | 3674.0639 | 3673.6775 | 3699.9319 | 3728.7511 | 3787.9686 | 3830.5285 | 3853.5736 | 3878.7363 | 3901.8059 | 3943.5668 | 3995.4216 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 |  | 6103.1255 | 7895.3963 | 8364.0615 | 8335.719 | 8337.4153 | 8385.3012 | 8512.071 | 8596.7107 | 8679.7002 | 8776.8043 | 8866.6271 | 8953.9572 | 8963.6932 | 9065.6646 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969
20% | 1575.389 | 2089.8768 | 2229.8344 | 2225.7001 | 2225.4661 | 2241.3706 | 2258.8289 | 2294.7021 | 2320.4843 | 2334.4448 | 2349.688 | 2363.6632 | 2388.9615 | 2420.3744 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 |  | 1637.7285 | 2118.6711 | 2244.4339 | 2236.8284 | 2237.2836 | 2250.1334 | 2284.1512 | 2306.8636 | 2329.1332 | 2355.1904 | 2379.2937 | 2402.7281 | 2405.3406 | 2432.7039 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1424.9909 | 1424.8411 | 1435.0239 | 1446.2014 | 1469.169 | 1485.676 | 1494.614 | 1504.3734 | 1513.321 | 1529.518 | 1549.63 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 |  | 903.3078 | 1168.5771 | 1237.943 | 1233.7481 | 1233.9992 | 1241.0867 | 1259.8495 | 1272.3769 | 1284.6599 | 1299.032 | 1312.3265 | 1325.252 | 1326.693 | 1341.7855 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753
10% | 675.0905 | 895.5604 | 955.5354 | 953.7638 | 953.6635 | 960.4789 | 967.9602 | 983.3327 | 994.381 | 1000.3634 | 1006.8954 | 1012.8841 | 1023.725 | 1037.1862 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 |  | 211.1088 | 273.1039 | 289.3152 | 288.3348 | 288.3935 | 290.0499 | 294.4349 | 297.3626 | 300.2332 | 303.5921 | 306.6991 | 309.7199 | 310.0566 | 313.5838 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938
5% | 480.3015 | 637.1576 | 679.8276 | 678.5671 | 678.4957 | 683.3447 | 688.6673 | 699.6043 | 707.4647 | 711.721 | 716.3683 | 720.629 | 728.3419 | 737.919 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 59.5631 | 59.5568 | 59.9825 | 60.4497 | 61.4097 | 62.0997 | 62.4733 | 62.8812 | 63.2552 | 63.9322 | 64.7729 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 159520.5704 | 159503.7964 | 160643.7099 | 161894.98 | 164466.0868 | 166313.955 | 167314.5287 | 168407.043 | 169408.6762 | 171221.8548 | 173473.2847 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 149581.1188 | 149611.5589 | 150470.8515 | 152745.6837 | 154264.5107 | 155753.7228 | 157496.2176 | 159108.0516 | 160675.1553 | 160849.8627 | 162679.6988 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885
Option 1 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 111664.3993 | 111652.6574 | 112450.5969 | 113326.486 | 115126.2607 | 116419.7685 | 117120.1701 | 117884.9301 | 118586.0733 | 119855.2983 | 121431.2993 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | Option 1 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 44874.3356 | 44883.4677 | 45141.2555 | 45823.7051 | 46279.3532 | 46726.1168 | 47248.8653 | 47732.4155 | 48202.5466 | 48254.9588 | 48803.9096 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566
Option 2 - 1A New PHS ZSS + Four new feeders
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 67.5205 | 68.4891 | 70.1672 | 73.9934 | 76.5491 | 79.7927 | 81.4731 | 82.9475 | 80.2063 | 83.4046 | 88.4365 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 |  | 78.6411 | 106.5944 | 114.2314 | 72.5297 | 73.2712 | 74.9127 | 78.7988 | 80.9142 | 84.9563 | 97.2565 | 87.101 | 85.1099 | 87.7822 | 93.6341 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662
98% | 87.3027 | 120.9335 | 129.6647 | 80.2103 | 81.3609 | 83.3544 | 87.8996 | 90.9357 | 94.7889 | 96.7852 | 98.5366 | 95.2802 | 99.0796 | 105.0572 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 |  | 93.4209 | 126.6277 | 135.7001 | 86.161 | 87.0417 | 88.9918 | 93.6082 | 96.1212 | 100.923 | 115.5349 | 103.4707 | 101.1054 | 104.2799 | 111.2317 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513
97% | 172.8327 | 239.4116 | 256.6966 | 158.792 | 161.0698 | 165.0163 | 174.0145 | 180.025 | 187.6532 | 191.6052 | 195.0724 | 188.6258 | 196.1475 | 207.9813 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 |  | 184.945 | 250.6842 | 268.6448 | 170.5725 | 172.3161 | 176.1766 | 185.3158 | 190.2908 | 199.7968 | 228.7239 | 204.8405 | 200.158 | 206.4425 | 220.2048 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634
95% | 510.5211 | 707.185 | 758.2422 | 469.047 | 475.7755 | 487.4327 | 514.0122 | 531.7662 | 554.2985 | 565.9722 | 576.2139 | 557.1715 | 579.3894 | 614.3447 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 |  | 546.299 | 740.4826 | 793.5354 | 503.8448 | 508.9952 | 520.3987 | 547.3942 | 562.0896 | 590.1689 | 675.6152 | 605.0673 | 591.2358 | 609.7993 | 650.4512 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579
90% | 2814.8088 | 3899.1347 | 4180.6436 | 2586.1376 | 2623.2356 | 2687.5088 | 2834.0572 | 2931.9457 | 3056.1802 | 3120.5442 | 3177.0126 | 3072.0206 | 3194.5213 | 3387.2506 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 |  | 3012.0741 | 4082.7244 | 4375.2363 | 2777.9985 | 2806.3958 | 2869.2699 | 3018.1126 | 3099.1371 | 3253.9549 | 3725.0716 | 3336.0988 | 3259.8375 | 3362.189 | 3586.3277 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892
85% | 6876.3763 | 9525.3066 | 10213.0129 | 6317.7488 | 6408.3767 | 6565.3915 | 6923.3988 | 7162.5333 | 7466.0293 | 7623.2658 | 7761.2143 | 7504.7262 | 7803.9866 | 8274.8105 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 |  | 7358.2813 | 9973.8032 | 10688.3888 | 6786.4512 | 6855.8238 | 7009.4208 | 7373.0329 | 7570.9698 | 7949.1788 | 9100.0831 | 8149.8505 | 7963.5495 | 8213.5868 | 8761.1416 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783
80% | 10687.9274 | 14805.1503 | 15874.0497 | 9819.6546 | 9960.5172 | 10204.5647 | 10761.0142 | 11132.7002 | 11604.4228 | 11848.8151 | 12063.2279 | 11664.5693 | 12129.7087 | 12861.5086 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 |  | 11436.9506 | 15502.2469 | 16612.9248 | 10548.1571 | 10655.9827 | 10894.7178 | 11459.8789 | 11767.5316 | 12355.3804 | 14144.2269 | 12667.2837 | 12377.7168 | 12766.3489 | 13617.4113 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364
75% | 11791.7667 | 16334.2127 | 17513.507 | 10833.8196 | 10989.2303 | 11258.4828 | 11872.4019 | 12282.4753 | 12802.917 | 13072.5499 | 13309.107 | 12869.2753 | 13382.4539 | 14189.8335 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 |  | 12618.1483 | 17103.3048 | 18328.6925 | 11637.5611 | 11756.5228 | 12019.9143 | 12643.4447 | 12982.8715 | 13631.4327 | 15605.0297 | 13975.5492 | 13656.0761 | 14084.8457 | 15023.8051 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684
70% | 12669.5942 | 17550.1984 | 18817.2842 | 11640.3335 | 11807.3136 | 12096.6104 | 12756.2322 | 13196.833 | 13756.0186 | 14045.724 | 14299.8915 | 13827.3169 | 14378.6986 | 15246.1828 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 |  | 13557.495 | 18376.5449 | 19693.1554 | 12503.9088 | 12631.7266 | 12914.726 | 13584.6745 | 13949.3696 | 14646.2124 | 16766.732 | 15015.9463 | 14672.6903 | 15133.3793 | 16142.2387 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561
65% | 13351.323 | 18494.5441 | 19829.8096 | 12266.6796 | 12442.6447 | 12747.5079 | 13442.6228 | 13906.9317 | 14496.206 | 14801.5 | 15069.3438 | 14571.3408 | 15152.3914 | 16066.5534 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 |  | 14287.0002 | 19365.3548 | 20752.8099 | 13176.7224 | 13311.4178 | 13609.6449 | 14315.6423 | 14699.961 | 15434.2996 | 17668.9207 | 15823.9283 | 15462.2022 | 15947.6801 | 17010.8245 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949
60% | 14698.1621 | 20360.2151 | 21830.1779 | 13504.1033 | 13697.8192 | 14033.4361 | 14798.672 | 15309.8188 | 15958.5373 | 16294.6284 | 16589.4914 | 16041.2514 | 16680.9166 | 17687.2964 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 |  | 15728.2275 | 21318.8704 | 22846.2875 | 14505.9484 | 14654.2314 | 14982.5428 | 15759.7589 | 16182.8464 | 16991.2629 | 19451.3054 | 17420.196 | 17021.9802 | 17556.4315 | 18726.8226 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973
55% | 16350.7821 | 22649.4603 | 24284.7017 | 15022.4667 | 15237.9634 | 15611.3162 | 16462.593 | 17031.2118 | 17752.8704 | 18126.7506 | 18454.7671 | 17844.8846 | 18556.4719 | 19676.0062 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 |  | 17496.6651 | 23715.9042 | 25415.0598 | 16136.9564 | 16301.912 | 16667.1377 | 17531.7418 | 18002.4001 | 18901.7126 | 21638.3554 | 19378.8738 | 18935.8837 | 19530.4273 | 20832.4138 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655
50% | 16573.101 | 22957.4214 | 24614.8968 | 15226.7247 | 15445.1515 | 15823.5807 | 16686.4322 | 17262.7824 | 17994.2533 | 18373.217 | 18705.6936 | 18087.5186 | 18808.7812 | 19943.5377 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 |  | 17734.5645 | 24038.3655 | 25760.6242 | 16356.368 | 16523.5664 | 16893.7581 | 17770.118 | 18247.1758 | 19158.7162 | 21932.5686 | 19642.3652 | 19193.3519 | 19795.9793 | 21115.6687 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043
45% | 12791.4633 | 17719.0143 | 18998.2882 | 11752.3022 | 11920.8885 | 12212.968 | 12878.9347 | 13323.7738 | 13888.3381 | 14180.8302 | 14437.4425 | 13960.3222 | 14517.0077 | 15392.8363 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 |  | 13687.9049 | 18553.3094 | 19882.5844 | 12624.1843 | 12753.2315 | 13038.9531 | 13715.3459 | 14083.549 | 14787.0948 | 16928.0117 | 15160.3851 | 14813.8273 | 15278.9477 | 16297.5114 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418
40% | 6284.3875 | 8705.2708 | 9333.7723 | 5773.8524 | 5856.6781 | 6000.1754 | 6327.3618 | 6545.9092 | 6823.2771 | 6966.9772 | 7093.0496 | 6858.6426 | 7132.1396 | 7562.4302 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 |  | 6724.8052 | 9115.1562 | 9768.223 | 6202.2041 | 6265.6044 | 6405.9781 | 6738.2868 | 6919.1833 | 7264.8322 | 8316.6549 | 7448.228 | 7277.9657 | 7506.4773 | 8006.893 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262
35% | 2348.7515 | 3253.5419 | 3488.4405 | 2157.9421 | 2188.8977 | 2242.529 | 2364.8129 | 2446.4937 | 2550.1582 | 2603.8652 | 2650.9841 | 2563.3759 | 2665.5937 | 2826.4122 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 |  | 2513.3549 | 3406.7341 | 3650.8138 | 2318.036 | 2341.7315 | 2394.1953 | 2518.3936 | 2586.0026 | 2715.1867 | 3108.299 | 2783.7298 | 2720.0953 | 2805.5001 | 2992.5274 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1076.2567 | 1091.6955 | 1118.4437 | 1179.4318 | 1220.1695 | 1271.8714 | 1298.6573 | 1322.1575 | 1278.4636 | 1329.4439 | 1409.6509 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 |  | 1253.516 | 1699.0818 | 1820.8147 | 1156.1022 | 1167.9202 | 1194.0861 | 1256.029 | 1289.7485 | 1354.178 | 1550.2397 | 1388.3634 | 1356.6262 | 1399.2211 | 1492.4995 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185
25% | 690.592 | 956.6232 | 1025.6893 | 634.4893 | 643.591 | 659.3599 | 695.3145 | 719.3307 | 749.8107 | 765.6019 | 779.456 | 753.697 | 783.7516 | 831.0363 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 |  | 738.9896 | 1001.6655 | 1073.4311 | 681.5609 | 688.528 | 703.9536 | 740.4711 | 760.3498 | 798.3332 | 913.9181 | 818.4866 | 799.7765 | 824.8876 | 879.8783 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523
20% | 348.989 | 483.4272 | 518.3296 | 320.6376 | 325.2372 | 333.206 | 351.3755 | 363.512 | 378.915 | 386.8951 | 393.8962 | 380.879 | 396.067 | 419.9622 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 |  | 373.4466 | 506.1893 | 542.4558 | 344.4252 | 347.9459 | 355.7413 | 374.1953 | 384.241 | 403.4358 | 461.8463 | 413.6202 | 404.1651 | 416.855 | 444.6444 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818
15% | 142.1807 | 196.9518 | 211.1713 | 130.6301 | 132.504 | 135.7506 | 143.153 | 148.0975 | 154.3728 | 157.6239 | 160.4762 | 155.1729 | 161.3606 | 171.0957 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 |  | 152.1449 | 206.2253 | 221.0005 | 140.3214 | 141.7558 | 144.9316 | 152.4499 | 156.5426 | 164.3627 | 188.1596 | 168.5119 | 164.6599 | 169.8298 | 181.1514 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667
10% | 57.2416 | 79.2923 | 85.017 | 52.5914 | 53.3458 | 54.6528 | 57.633 | 59.6237 | 62.1501 | 63.459 | 64.6073 | 62.4722 | 64.9634 | 68.8827 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 |  | 61.2531 | 83.0258 | 88.9742 | 56.493 | 57.0705 | 58.3491 | 61.3759 | 63.0236 | 66.172 | 75.7526 | 67.8425 | 66.2916 | 68.373 | 72.9311 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372
5% | 48.7477 | 67.5263 | 72.4016 | 44.7875 | 45.43 | 46.5431 | 49.081 | 50.7763 | 52.9278 | 54.0425 | 55.0204 | 53.2021 | 55.3236 | 58.6614 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 |  | 52.164 | 70.7058 | 75.7716 | 48.1102 | 48.602 | 49.6908 | 52.2685 | 53.6718 | 56.3529 | 64.5119 | 57.7755 | 56.4548 | 58.2274 | 62.1091 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 119936.7274 | 121657.2155 | 124637.9979 | 131434.4425 | 135974.1946 | 141735.7894 | 144720.783 | 147339.6094 | 142470.4146 | 148151.6025 | 157089.767 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 128834.6173 | 130151.5932 | 133067.4913 | 139970.3379 | 143727.991 | 150907.9438 | 172756.8175 | 154717.5144 | 151180.7597 | 155927.4907 | 166322.3216 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313
Option 2 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 83955.7092 | 85160.0509 | 87246.5985 | 92004.1098 | 95181.9362 | 99215.0526 | 101304.5481 | 103137.7266 | 99729.2902 | 103706.1218 | 109962.8369 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | Option 2 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 38650.3852 | 39045.4779 | 39920.2474 | 41991.1014 | 43118.3973 | 45272.3831 | 51827.0452 | 46415.2543 | 45354.2279 | 46778.2472 | 49896.6965 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 85.6562 | 85.6825 | 86.4254 | 88.3918 | 89.7047 | 90.9921 | 92.4984 | 93.8917 | 95.2464 | 95.3974 | 96.9792 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 42.3977 | 42.4107 | 42.7784 | 43.7517 | 44.4016 | 45.0388 | 45.7844 | 46.474 | 47.1446 | 47.2193 | 48.0023 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051
97% | 20.8131 | 27.6102 | 29.4592 | 18.712 | 18.7089 | 18.919 | 19.1497 | 19.6236 | 19.9642 | 20.1486 | 20.35 | 20.5347 | 20.8689 | 21.2839 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 |  | 92.7689 | 120.0119 | 127.1357 | 83.9345 | 83.9603 | 84.6882 | 86.6151 | 87.9016 | 89.1631 | 90.6391 | 92.0044 | 93.3319 | 93.4799 | 95.0298 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478
95% | 102.4643 | 135.9269 | 145.0299 | 92.1205 | 92.1053 | 93.1397 | 94.2752 | 96.6084 | 98.2853 | 99.1933 | 100.1848 | 101.0937 | 102.7391 | 104.7823 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 |  | 137.0126 | 177.2483 | 187.7696 | 123.9648 | 124.0029 | 125.0779 | 127.9238 | 129.824 | 131.687 | 133.867 | 135.8835 | 137.844 | 138.0626 | 140.3518 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059
90% | 177.7116 | 235.7483 | 251.5362 | 159.7715 | 159.7451 | 161.5392 | 163.5086 | 167.5553 | 170.4636 | 172.0384 | 173.758 | 175.3344 | 178.1882 | 181.7317 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 |  | 594.078 | 768.5376 | 814.1574 | 537.5036 | 537.6687 | 542.3299 | 554.6697 | 562.9085 | 570.9867 | 580.4388 | 589.1822 | 597.6829 | 598.6306 | 608.5565 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866
85% | 504.3166 | 669.0154 | 713.8189 | 453.4057 | 453.3307 | 458.4221 | 464.0109 | 475.4947 | 483.7482 | 488.2172 | 493.0969 | 497.5707 | 505.6692 | 515.7252 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 |  | 561.9657 | 726.995 | 770.1489 | 508.4494 | 508.6056 | 513.0148 | 524.6876 | 532.481 | 540.1226 | 549.0638 | 557.3345 | 565.3757 | 566.2722 | 575.6615 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008
80% | 704.4422 | 934.4978 | 997.0804 | 633.3285 | 633.2239 | 640.3357 | 648.1422 | 664.1831 | 675.7117 | 681.9542 | 688.7703 | 695.0194 | 706.3316 | 720.378 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 |  | 392.484 | 507.7425 | 537.8818 | 355.1075 | 355.2166 | 358.2961 | 366.4485 | 371.8915 | 377.2285 | 383.4731 | 389.2495 | 394.8656 | 395.4917 | 402.0493 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482
75% | 1836.3528 | 2436.0657 | 2599.2074 | 1650.9723 | 1650.6995 | 1669.2387 | 1689.5889 | 1731.4045 | 1761.4576 | 1777.7306 | 1795.4989 | 1811.7891 | 1841.278 | 1877.8945 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 |  | 700.5244 | 906.2435 | 960.0375 | 633.8131 | 634.0078 | 639.5042 | 654.055 | 663.77 | 673.2957 | 684.4414 | 694.7514 | 704.7752 | 705.8927 | 717.5971 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709
70% | 3172.6584 | 4208.7797 | 4490.6388 | 2852.3774 | 2851.906 | 2883.9361 | 2919.0951 | 2991.3397 | 3043.2623 | 3071.3771 | 3102.0752 | 3130.2198 | 3181.1677 | 3244.4298 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1154.6374 | 1154.9921 | 1165.0051 | 1191.5127 | 1209.2109 | 1226.5641 | 1246.8686 | 1265.6506 | 1283.9114 | 1285.9472 | 1307.2695 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082
65% | 7968.2023 | 10570.444 | 11278.3393 | 7163.8093 | 7162.6256 | 7243.0697 | 7331.3723 | 7512.8163 | 7643.2211 | 7713.832 | 7790.9311 | 7861.6168 | 7989.5735 | 8148.4577 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 |  | 1605.6162 | 2077.1285 | 2200.4254 | 1452.7125 | 1453.1587 | 1465.7566 | 1499.1073 | 1521.3744 | 1543.2074 | 1568.7536 | 1592.3843 | 1615.3592 | 1617.9205 | 1644.7473 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881
60% | 11647.312 | 15451.0709 | 16485.8185 | 10471.5115 | 10469.7812 | 10587.3683 | 10716.4423 | 10981.6634 | 11172.2792 | 11275.4928 | 11388.1904 | 11491.5133 | 11678.5507 | 11910.7957 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 |  | 2512.492 | 3250.3215 | 3443.2583 | 2273.226 | 2273.9243 | 2293.6376 | 2345.8253 | 2380.6692 | 2414.8337 | 2454.8089 | 2491.7865 | 2527.738 | 2531.746 | 2573.7249 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71
55% | 13170.4015 | 17471.5683 | 18641.6273 | 11840.8446 | 11838.888 | 11971.8517 | 12117.8044 | 12417.7077 | 12633.2498 | 12749.9604 | 12877.3953 | 12994.2294 | 13205.7252 | 13468.3403 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 |  | 4828.1473 | 6246.0024 | 6616.7608 | 4368.3602 | 4369.7021 | 4407.5844 | 4507.8712 | 4574.8292 | 4640.4817 | 4717.3002 | 4788.3585 | 4857.4449 | 4865.1469 | 4945.8159 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943
50% | 16911.4168 | 22434.3178 | 23936.7286 | 15204.2029 | 15201.6905 | 15372.4222 | 15559.8324 | 15944.9224 | 16221.6886 | 16371.5505 | 16535.1829 | 16685.2035 | 16956.7741 | 17293.9842 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 |  | 10714.812 | 13861.3711 | 14684.1724 | 9694.4344 | 9697.4126 | 9781.4823 | 10004.0427 | 10152.6386 | 10298.3371 | 10468.8158 | 10626.5111 | 10779.8302 | 10796.9229 | 10975.9467 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156
45% | 22520.2713 | 29874.9022 | 31875.6039 | 20246.8414 | 20243.4958 | 20470.8525 | 20720.4193 | 21233.2285 | 21601.7873 | 21801.3525 | 22019.2554 | 22219.0319 | 22580.6718 | 23029.7213 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 |  | 16236.3476 | 21004.3853 | 22251.1909 | 14690.1512 | 14694.664 | 14822.0564 | 15159.3061 | 15384.4762 | 15605.2558 | 15863.5852 | 16102.5438 | 16334.871 | 16360.7718 | 16632.0497 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617
40% | 15794.9825 | 20953.2804 | 22356.5072 | 14200.4731 | 14198.1266 | 14357.5872 | 14532.6252 | 14892.2928 | 15150.7879 | 15290.7564 | 15443.5864 | 15583.7031 | 15837.3455 | 16152.2941 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 |  | 16811.9908 | 21749.0744 | 23040.0842 | 15210.9755 | 15215.6483 | 15347.5572 | 15696.7639 | 15929.9171 | 16158.5242 | 16426.0124 | 16673.443 | 16914.0071 | 16940.8263 | 17221.7221 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991
35% | 8189.141 | 10863.5364 | 11591.06 | 7362.4442 | 7361.2276 | 7443.9022 | 7534.6533 | 7721.1283 | 7855.1489 | 7927.7176 | 8006.9545 | 8079.6001 | 8211.1047 | 8374.3945 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 |  | 22897.8708 | 29622.1608 | 31380.5115 | 20717.2937 | 20723.6581 | 20903.3176 | 21378.9358 | 21696.4896 | 22007.8517 | 22372.1696 | 22709.1692 | 23036.8167 | 23073.3442 | 23455.9234 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524
30% | 3808.7911 | 5052.6595 | 5391.0326 | 3424.2922 | 3423.7264 | 3462.1786 | 3504.3871 | 3591.1171 | 3653.4505 | 3687.2024 | 3724.0557 | 3757.8433 | 3819.0065 | 3894.953 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 |  | 21159.0479 | 27372.7075 | 28997.5323 | 19144.0599 | 19149.941 | 19315.9575 | 19755.4581 | 20048.8975 | 20336.6152 | 20673.2675 | 20984.676 | 21287.4425 | 21321.1963 | 21674.723 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086
25% | 2600.5659 | 3449.8542 | 3680.8886 | 2338.0378 | 2337.6515 | 2363.9059 | 2392.725 | 2451.9425 | 2494.5025 | 2517.5476 | 2542.7103 | 2565.7798 | 2607.5408 | 2659.3955 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 |  | 6103.1255 | 7895.3963 | 8364.0615 | 5521.9215 | 5523.6178 | 5571.5037 | 5698.2734 | 5782.9132 | 5865.9027 | 5963.0068 | 6052.8296 | 6140.1597 | 6149.8956 | 6251.8671 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994
20% | 1575.389 | 2089.8768 | 2229.8344 | 1416.3529 | 1416.1189 | 1432.0234 | 1449.4817 | 1485.3549 | 1511.1371 | 1525.0976 | 1540.3408 | 1554.316 | 1579.6143 | 1611.0272 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 |  | 1637.7285 | 2118.6711 | 2244.4339 | 1481.7667 | 1482.2219 | 1495.0717 | 1529.0894 | 1551.8019 | 1574.0715 | 1600.1287 | 1624.232 | 1647.6664 | 1650.2789 | 1677.6422 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738
15% | 1008.6332 | 1338.0309 | 1427.6379 | 906.8113 | 906.6615 | 916.8443 | 928.0218 | 950.9894 | 967.4963 | 976.4344 | 986.1938 | 995.1414 | 1011.3384 | 1031.4503 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 |  | 903.3078 | 1168.5771 | 1237.943 | 817.2853 | 817.5363 | 824.6238 | 843.3867 | 855.914 | 868.197 | 882.5692 | 895.8636 | 908.7891 | 910.2301 | 925.3226 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124
10% | 675.0905 | 895.5604 | 955.5354 | 606.9398 | 606.8396 | 613.655 | 621.1363 | 636.5088 | 647.5571 | 653.5394 | 660.0715 | 666.0602 | 676.9011 | 690.3623 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 |  | 211.1088 | 273.1039 | 289.3152 | 191.0048 | 191.0635 | 192.7198 | 197.1048 | 200.0326 | 202.9032 | 206.262 | 209.369 | 212.3898 | 212.7266 | 216.2538 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638
5% | 480.3015 | 637.1576 | 679.8276 | 431.8149 | 431.7436 | 436.5925 | 441.9151 | 452.8521 | 460.7125 | 464.9688 | 469.6161 | 473.8768 | 481.5897 | 491.1668 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 37.9038 | 37.8975 | 38.3231 | 38.7903 | 39.7504 | 40.4403 | 40.8139 | 41.2219 | 41.5959 | 42.2729 | 43.1135 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 101512.9676 | 101496.1935 | 102636.107 | 103887.3772 | 106458.4839 | 108306.3522 | 109306.9259 | 110399.4401 | 111401.0734 | 113214.252 | 115465.6819 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 99088.6557 | 99119.0958 | 99978.3884 | 102253.2205 | 103772.0476 | 105261.2597 | 107003.7545 | 108615.5885 | 110182.6921 | 110357.3996 | 112187.2356 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254
Option 2 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 71059.0773 | 71047.3355 | 71845.2749 | 72721.164 | 74520.9387 | 75814.4465 | 76514.8481 | 77279.6081 | 77980.7514 | 79249.9764 | 80825.9773 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | Option 2 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 29726.5967 | 29735.7287 | 29993.5165 | 30675.9662 | 31131.6143 | 31578.3779 | 32101.1263 | 32584.6765 | 33054.8076 | 33107.2199 | 33656.1707 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 43.5292 | 44.4977 | 46.1758 | 50.002 | 52.5577 | 55.8013 | 57.4818 | 58.9561 | 56.2149 | 59.4132 | 64.4451 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 | 60.6151 |  | 78.6411 | 106.5944 | 114.2314 | 48.5384 | 49.2798 | 50.9214 | 54.8074 | 56.9229 | 60.965 | 73.2652 | 63.1096 | 61.1185 | 63.7908 | 69.6428 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706 | 65.6706
98% | 87.3027 | 120.9335 | 129.6647 | 50.9036 | 52.0542 | 54.0476 | 58.5929 | 61.629 | 65.4822 | 67.4784 | 69.2298 | 65.9734 | 69.7729 | 75.7505 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 | 71.2006 |  | 93.4209 | 126.6277 | 135.7001 | 56.8542 | 57.735 | 59.685 | 64.3015 | 66.8145 | 71.6162 | 86.2281 | 74.164 | 71.7987 | 74.9732 | 81.9249 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063 | 77.2063
97% | 172.8327 | 239.4116 | 256.6966 | 99.1442 | 101.4221 | 105.3685 | 114.3668 | 120.3773 | 128.0054 | 131.9574 | 135.4247 | 128.978 | 136.4997 | 148.3335 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 | 139.3261 |  | 184.945 | 250.6842 | 268.6448 | 110.9247 | 112.6683 | 116.5289 | 125.668 | 130.643 | 140.149 | 169.0761 | 145.1927 | 140.5102 | 146.7947 | 160.5571 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156 | 151.2156
95% | 510.5211 | 707.185 | 758.2422 | 285.4497 | 292.1781 | 303.8353 | 330.4148 | 348.1688 | 370.7012 | 382.3748 | 392.6165 | 373.5741 | 395.7921 | 430.7473 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 | 404.1408 |  | 546.299 | 740.4826 | 793.5354 | 320.2474 | 325.3978 | 336.8013 | 363.7969 | 378.4923 | 406.5715 | 492.0178 | 421.4699 | 407.6384 | 426.2019 | 466.8539 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606 | 439.2606
90% | 2814.8088 | 3899.1347 | 4180.6436 | 1473.4114 | 1510.5094 | 1574.7826 | 1721.331 | 1819.2195 | 1943.454 | 2007.818 | 2064.2865 | 1959.2944 | 2081.7951 | 2274.5244 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 | 2127.8269 |  | 3012.0741 | 4082.7244 | 4375.2363 | 1665.2723 | 1693.6696 | 1756.5437 | 1905.3864 | 1986.4109 | 2141.2287 | 2612.3454 | 2223.3727 | 2147.1113 | 2249.4628 | 2473.6015 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631 | 2321.4631
85% | 6876.3763 | 9525.3066 | 10213.0129 | 3214.8475 | 3305.4754 | 3462.4901 | 3820.4975 | 4059.632 | 4363.1279 | 4520.3645 | 4658.313 | 4401.8248 | 4701.0853 | 5171.9092 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 | 4813.5377 |  | 7358.2813 | 9973.8032 | 10688.3888 | 3683.5499 | 3752.9225 | 3906.5194 | 4270.1316 | 4468.0685 | 4846.2774 | 5997.1817 | 5046.9491 | 4860.6482 | 5110.6855 | 5658.2403 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577 | 5286.577
80% | 10687.9274 | 14805.1503 | 15874.0497 | 4326.6009 | 4467.4635 | 4711.511 | 5267.9605 | 5639.6465 | 6111.3691 | 6355.7614 | 6570.1742 | 6171.5156 | 6636.655 | 7368.4549 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 | 6811.4394 |  | 11436.9506 | 15502.2469 | 16612.9248 | 5055.1034 | 5162.929 | 5401.6641 | 5966.8252 | 6274.4779 | 6862.3266 | 8651.1731 | 7174.23 | 6884.6631 | 7273.2952 | 8124.3576 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827 | 7546.6827
75% | 11791.7667 | 16334.2127 | 17513.507 | 3938.5906 | 4094.0013 | 4363.2538 | 4977.1729 | 5387.2463 | 5907.688 | 6177.3209 | 6413.878 | 5974.0463 | 6487.2249 | 7294.6045 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 | 6680.0609 |  | 12618.1483 | 17103.3048 | 18328.6925 | 4742.3321 | 4861.2939 | 5124.6853 | 5748.2157 | 6087.6425 | 6736.2038 | 8709.8007 | 7080.3202 | 6760.8471 | 7189.6167 | 8128.5761 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395 | 7491.2395
70% | 12669.5942 | 17550.1984 | 18817.2842 | 3211.0622 | 3378.0424 | 3667.3391 | 4326.9609 | 4767.5618 | 5326.7473 | 5616.4528 | 5870.6202 | 5398.0456 | 5949.4274 | 6816.9116 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 | 6156.6189 |  | 13557.495 | 18376.5449 | 19693.1554 | 4074.6376 | 4202.4553 | 4485.4547 | 5155.4033 | 5520.0984 | 6216.9412 | 8337.4607 | 6586.6751 | 6243.419 | 6704.1081 | 7712.9675 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848 | 7028.1848
65% | 13351.323 | 18494.5441 | 19829.8096 | 2148.8302 | 2324.7953 | 2629.6586 | 3324.7735 | 3789.0824 | 4378.3567 | 4683.6507 | 4951.4944 | 4453.4914 | 5034.5421 | 5948.7041 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 | 5252.8822 |  | 14287.0002 | 19365.3548 | 20752.8099 | 3058.8731 | 3193.5685 | 3491.7956 | 4197.7929 | 4582.1116 | 5316.4503 | 7551.0713 | 5706.0789 | 5344.3529 | 5829.8308 | 6892.9752 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456 | 6171.3456
60% | 14698.1621 | 20360.2151 | 21830.1779 | 791.0038 | 982.1797 | 1317.7966 | 2083.0325 | 2594.1794 | 3242.8979 | 3578.9889 | 3873.8519 | 3325.6119 | 3965.2771 | 4971.6569 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 | 4205.6427 |  | 15728.2275 | 21318.8704 | 22846.2875 | 1790.3089 | 1938.592 | 2266.9033 | 3044.1194 | 3467.2069 | 4275.6234 | 6735.6659 | 4704.5565 | 4306.3407 | 4840.7921 | 6011.1831 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578 | 5216.7578
55% | 16350.7821 | 22649.4603 | 24284.7017 |  | 2.8246 | 57.1339 | 426.1445 | 849.6977 | 1547.9343 | 1921.8145 | 2249.8311 | 1639.9485 | 2351.5358 | 3471.0701 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 | 2618.9274 |  | 17496.6651 | 23715.9042 | 25415.0598 | 246.1412 | 331.4696 | 562.8318 | 1326.8057 | 1797.4641 | 2696.7766 | 5433.4194 | 3173.9377 | 2730.9477 | 3325.4912 | 4627.4777 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295 | 3743.7295
50% | 16573.101 | 22957.4214 | 24614.8968 | [5 empty] | 30.529 | 119.2458 | 243.1596 | 47.0563 | 290.0774 | 1058.252 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 | 432.145 |  | 17734.5645 | 24038.3655 | 25760.6242 |  |  |  | 5.2896 | 83.4268 | 478.5238 | 3022.0708 | 810.8211 | 499.5863 | 933.2237 | 2205.1709 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853 | 1311.6853
45% | FY25: 12791.4633; FY26: 17719.0143; FY27: 18998.2882 |  | 13687.9049 | 18553.3094 | 19882.5844 | [6 empty] | 326.2222 |  |  |  | 79.4931
40% | FY25: 6284.3875; FY26: 8705.2708; FY27: 9333.7723 |  | 6724.8052 | 9115.1562 | 9768.223
35% | FY25: 2348.7515; FY26: 3253.5419; FY27: 3488.4405 |  | 2513.3549 | 3406.7341 | 3650.8138
30% | FY25: 1171.4214; FY26: 1622.6784; FY27: 1739.8323 |  | 1253.516 | 1699.0818 | 1820.8147
25% | FY25: 690.592; FY26: 956.6232; FY27: 1025.6893 |  | 738.9896 | 1001.6655 | 1073.4311
20% | FY25: 348.989; FY26: 483.4272; FY27: 518.3296 |  | 373.4466 | 506.1893 | 542.4558
15% | FY25: 142.1807; FY26: 196.9518; FY27: 211.1713 |  | 152.1449 | 206.2253 | 221.0005
10% | FY25: 57.2416; FY26: 79.2923; FY27: 85.017 |  | 61.2531 | 83.0258 | 88.9742
5% | FY25: 48.7477; FY26: 67.5263; FY27: 72.4016 |  | 52.164 | 70.7058 | 75.7716
9.992e-14% | FY25: 0; FY26: 0; FY27: 0 |  | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 19583.3732 | 20555.4438 | 22293.393 | 26501.2499 | 29488.9982 | 33472.0944 | 35620.7099 | 37551.8361 | 33995.5753 | 38159.0979 | 45095.3641 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | 39774.3636 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 24852.7833 | 25681.9812 | 27560.3346 | 32228.5437 | 34899.7802 | 40249.6535 | 58196.9985 | 43210.8776 | 40458.9821 | 44168.2665 | 52693.0217 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183 | 46851.0183
Option 3 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 13708.3613 | 14388.8107 | 15605.3751 | 18550.8749 | 20642.2988 | 23430.4661 | 24934.4969 | 26286.2852 | 23796.9027 | 26711.3686 | 31566.7548 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | 27842.0545 | Option 3 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 7455.835 | 7704.5944 | 8268.1004 | 9668.5631 | 10469.9341 | 12074.8961 | 17459.0996 | 12963.2633 | 12137.6946 | 13250.48 | 15807.9065 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055 | 14055.3055
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 61.2344 | 61.2607 | 62.0035 | 63.97 | 65.2829 | 66.5702 | 68.0765 | 69.4698 | 70.8245 | 70.9755 | 72.5573 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351 | 71.351
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 29.9674 | 29.9804 | 30.3481 | 31.3215 | 31.9713 | 32.6085 | 33.3541 | 34.0438 | 34.7143 | 34.789 | 35.572 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749 | 34.9749
97% | 20.8131 | 27.6102 | 29.4592 | 12.3872 | 12.3841 | 12.5942 | 12.8249 | 13.2988 | 13.6394 | 13.8238 | 14.0252 | 14.2099 | 14.5441 | 14.9591 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 | 14.9293 |  | 92.7689 | 120.0119 | 127.1357 | 58.6353 | 58.6611 | 59.389 | 61.3159 | 62.6024 | 63.8639 | 65.3399 | 66.7052 | 68.0327 | 68.1807 | 69.7307 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486 | 68.5486
95% | 102.4643 | 135.9269 | 145.0299 | 59.674 | 59.6588 | 60.6932 | 61.8287 | 64.162 | 65.8388 | 66.7468 | 67.7383 | 68.6472 | 70.2926 | 72.3358 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 | 72.1891 |  | 137.0126 | 177.2483 | 187.7696 | 85.029 | 85.0671 | 86.1421 | 88.988 | 90.8882 | 92.7512 | 94.9312 | 96.9477 | 98.9082 | 99.1268 | 101.416 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701 | 99.6701
90% | 177.7116 | 235.7483 | 251.5362 | 97.9133 | 97.8869 | 99.681 | 101.6504 | 105.6971 | 108.6054 | 110.1802 | 111.8997 | 113.4762 | 116.33 | 119.8735 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 | 119.6191 |  | 594.078 | 768.5376 | 814.1574 | 351.9289 | 352.0941 | 356.7553 | 369.095 | 377.3339 | 385.4121 | 394.8642 | 403.6075 | 412.1082 | 413.0559 | 422.9818 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119 | 415.4119
85% | 504.3166 | 669.0154 | 713.8189 | 253.0259 | 252.9509 | 258.0423 | 263.6311 | 275.1149 | 283.3684 | 287.8374 | 292.7171 | 297.1909 | 305.2894 | 315.3454 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 | 314.6234 |  | 561.9657 | 726.995 | 770.1489 | 308.0696 | 308.2258 | 312.635 | 324.3078 | 332.1012 | 339.7428 | 348.684 | 356.9547 | 364.9959 | 365.8924 | 375.2817 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121 | 368.121
80% | 704.4422 | 934.4978 | 997.0804 | 314.536 | 314.4314 | 321.5432 | 329.3497 | 345.3906 | 356.9192 | 363.1617 | 369.9778 | 376.2269 | 387.5391 | 401.5855 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 | 400.577 |  | 392.484 | 507.7425 | 537.8818 | 195.7112 | 195.8203 | 198.8998 | 207.0522 | 212.4953 | 217.8322 | 224.0769 | 229.8532 | 235.4693 | 236.0954 | 242.6531 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519 | 237.6519
75% | 1836.3528 | 2436.0657 | 2599.2074 | 705.4576 | 705.1848 | 723.724 | 744.0742 | 785.8898 | 815.9429 | 832.2159 | 849.9842 | 866.2744 | 895.7633 | 932.3798 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 | 929.7508 |  | 700.5244 | 906.2435 | 960.0375 | 310.1233 | 310.3181 | 315.8145 | 330.3652 | 340.0803 | 349.6059 | 360.7517 | 371.0616 | 381.0855 | 382.203 | 393.9074 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811 | 384.9811
70% | 3172.6584 | 4208.7797 | 4490.6388 | 993.7472 | 993.2758 | 1025.3059 | 1060.4649 | 1132.7095 | 1184.6321 | 1212.7469 | 1243.4451 | 1271.5896 | 1322.5375 | 1385.7996 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 | 1381.2574 |  | 1276.1675 | 1650.9325 | 1748.9307 | 483.7172 | 484.0719 | 494.0849 | 520.5925 | 538.2908 | 555.6439 | 575.9484 | 594.7305 | 612.9912 | 615.027 | 636.3493 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088 | 620.088
65% | 7968.2023 | 10570.444 | 11278.3393 | 1846.81 | 1845.6263 | 1926.0704 | 2014.373 | 2195.817 | 2326.2218 | 2396.8327 | 2473.9318 | 2544.6175 | 2672.5742 | 2831.4585 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 | 2820.0507 |  | 1605.6162 | 2077.1285 | 2200.4254 | 491.2298 | 491.676 | 504.2739 | 537.6246 | 559.8917 | 581.7247 | 607.2709 | 630.9016 | 653.8765 | 656.4378 | 683.2646 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054 | 662.8054
60% | 11647.312 | 15451.0709 | 16485.8185 | 1599.0683 | 1597.338 | 1714.9251 | 1843.9992 | 2109.2202 | 2299.836 | 2403.0496 | 2515.7473 | 2619.0702 | 2806.1076 | 3038.3525 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 | 3021.6775 |  | 2512.492 | 3250.3215 | 3443.2583 | 555.6511 | 556.3494 | 576.0627 | 628.2504 | 663.0943 | 697.2588 | 737.234 | 774.2116 | 810.1631 | 814.1711 | 856.15 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351 | 824.1351
55% | 13170.4015 | 17471.5683 | 18641.6273 | 413.2466 | 411.832 | 513.1119 | 636.1403 | 924.2646 | 1139.8067 | 1256.5173 | 1383.9522 | 1500.7863 | 1712.2821 | 1974.8972 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 | 1956.0416 |  | 4828.1473 | 6246.0024 | 6616.7608 | 587.1995 | 588.5414 | 626.4237 | 726.7105 | 793.6685 | 859.321 | 936.1395 | 1007.1978 | 1076.2842 | 1083.9862 | 1164.6552 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336 | 1103.1336
50% | 16911.4168 | 22434.3178 | 23936.7286 |  |  |  |  | 3.4281 | 36.6085 | 68.9695 | 115.5831 | 168.4762 | 288.3744 | 479.2895 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 | 464.0651 |  | 10714.812 | 13861.3711 | 14684.1724 | 191.3668 | 192.9659 | 240.7061 | 390.8095 | 509.6193 | 640.0757 | 807.8717 | 965.5671 | 1118.8862 | 1135.9788 | 1315.0026 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715 | 1178.4715
45% | FY25: 22520.2713; FY26: 29874.9022; FY27: 31875.6039 |  | 16236.3476 | 21004.3853 | 22251.1909 | [6 empty] | 3.1349 | 28.4196 | 76.7087 | 83.5101 | 171.461 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343 | 101.6343
40% | FY25: 15794.9825; FY26: 20953.2804; FY27: 22356.5072 |  | 16811.9908 | 21749.0744 | 23040.0842
35% | FY25: 8189.141; FY26: 10863.5364; FY27: 11591.06 |  | 22897.8708 | 29622.1608 | 31380.5115
30% | FY25: 3808.7911; FY26: 5052.6595; FY27: 5391.0326 |  | 21159.0479 | 27372.7075 | 28997.5323
25% | FY25: 2600.5659; FY26: 3449.8542; FY27: 3680.8886 |  | 6103.1255 | 7895.3963 | 8364.0615
20% | FY25: 1575.389; FY26: 2089.8768; FY27: 2229.8344 |  | 1637.7285 | 2118.6711 | 2244.4339
15% | FY25: 1008.6332; FY26: 1338.0309; FY27: 1427.6379 |  | 903.3078 | 1168.5771 | 1237.943
10% | FY25: 675.0905; FY26: 895.5604; FY27: 955.5354 |  | 211.1088 | 273.1039 | 289.3152
5% | FY25: 480.3015; FY26: 637.1576; FY27: 679.8276 |  | 0 | 0 | 0
9.992e-14% | FY25: 42.1598; FY26: 55.9283; FY27: 59.6738 |  | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 6295.8662 | 6290.5691 | 6655.6913 | 7068.3364 | 7954.9925 | 8631.4193 | 9012.0818 | 9439.0017 | 9840.5652 | 10591.6343 | 11566.2763 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | 11494.7808 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 3709.8635 | 3715.0322 | 3863.5385 | 4280.4031 | 4577.3201 | 4882.411 | 5257.6779 | 5629.6718 | 6015.0485 | 6059.4299 | 6540.9827 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785 | 6170.9785
Option 3 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 4407.1063 | 4403.3984 | 4658.9839 | 4947.8355 | 5568.4947 | 6041.9935 | 6308.4573 | 6607.3012 | 6888.3957 | 7414.144 | 8096.3934 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | 8046.3465 | Option 3 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 1112.959 | 1114.5097 | 1159.0616 | 1284.1209 | 1373.196 | 1464.7233 | 1577.3034 | 1688.9015 | 1804.5146 | 1817.829 | 1962.2948 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936 | 1851.2936
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 88.9597 | 89.9283 | 91.6063 | 95.4325 | 97.9883 | 101.2318 | 102.9123 | 104.3866 | 101.6454 | 104.8437 | 109.8756 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 | 106.0456 |  | 78.6411 | 106.5944 | 114.2314 | 93.9689 | 94.7103 | 96.3519 | 100.238 | 102.3534 | 106.3955 | 118.6957 | 108.5401 | 106.5491 | 109.2213 | 115.0733 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011 | 111.1011
98% | 87.3027 | 120.9335 | 129.6647 | 105.6787 | 106.8293 | 108.8228 | 113.3681 | 116.4041 | 120.2573 | 122.2536 | 124.005 | 120.7486 | 124.548 | 130.5256 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 | 125.9757 |  | 93.4209 | 126.6277 | 135.7001 | 111.6294 | 112.5101 | 114.4602 | 119.0766 | 121.5897 | 126.3914 | 141.0033 | 128.9391 | 126.5739 | 129.7483 | 136.7001 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815 | 131.9815
97% | 172.8327 | 239.4116 | 256.6966 | 209.2117 | 211.4896 | 215.436 | 224.4343 | 230.4447 | 238.0729 | 242.0249 | 245.4921 | 239.0455 | 246.5672 | 258.401 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 | 249.3936 |  | 184.945 | 250.6842 | 268.6448 | 220.9922 | 222.7358 | 226.5964 | 235.7355 | 240.7105 | 250.2165 | 279.1436 | 255.2602 | 250.5777 | 256.8622 | 270.6246 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831 | 261.2831
95% | 510.5211 | 707.185 | 758.2422 | 617.9792 | 624.7076 | 636.3648 | 662.9443 | 680.6983 | 703.2307 | 714.9043 | 725.146 | 706.1036 | 728.3216 | 763.2768 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 | 736.6703 |  | 546.299 | 740.4826 | 793.5354 | 652.7769 | 657.9273 | 669.3308 | 696.3264 | 711.0218 | 739.101 | 824.5473 | 753.9994 | 740.1679 | 758.7314 | 799.3834 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901 | 771.7901
90% | 2814.8088 | 3899.1347 | 4180.6436 | 3407.2897 | 3444.3878 | 3508.6609 | 3655.2094 | 3753.0978 | 3877.3323 | 3941.6963 | 3998.1648 | 3893.1727 | 4015.6734 | 4208.4027 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 | 4061.7052 |  | 3012.0741 | 4082.7244 | 4375.2363 | 3599.1506 | 3627.5479 | 3690.422 | 3839.2647 | 3920.2892 | 4075.107 | 4546.2237 | 4157.251 | 4080.9896 | 4183.3411 | 4407.4798 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414 | 4255.3414
85% | 6876.3763 | 9525.3066 | 10213.0129 | 8323.7647 | 8414.3925 | 8571.4073 | 8929.4146 | 9168.5492 | 9472.0451 | 9629.2817 | 9767.2301 | 9510.742 | 9810.0024 | 10280.8263 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 | 9922.4549 |  | 7358.2813 | 9973.8032 | 10688.3888 | 8792.4671 | 8861.8397 | 9015.4366 | 9379.0487 | 9576.9857 | 9955.1946 | 11106.0989 | 10155.8663 | 9969.5654 | 10219.6026 | 10767.1574 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941 | 10395.4941
80% | 10687.9274 | 14805.1503 | 15874.0497 | 12937.5979 | 13078.4605 | 13322.508 | 13878.9575 | 14250.6435 | 14722.3661 | 14966.7584 | 15181.1712 | 14782.5126 | 15247.652 | 15979.4519 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 | 15422.4364 |  | 11436.9506 | 15502.2469 | 16612.9248 | 13666.1004 | 13773.926 | 14012.6611 | 14577.8222 | 14885.4749 | 15473.3237 | 17262.1702 | 15785.227 | 15495.6601 | 15884.2922 | 16735.3547 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797 | 16157.6797
75% | 11791.7667 | 16334.2127 | 17513.507 | 14273.7812 | 14429.192 | 14698.4444 | 15312.3636 | 15722.4369 | 16242.8786 | 16512.5115 | 16749.0687 | 16309.2369 | 16822.4156 | 17629.7951 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 | 17015.2515 |  | 12618.1483 | 17103.3048 | 18328.6925 | 15077.5228 | 15196.4845 | 15459.876 | 16083.4064 | 16422.8331 | 17071.3944 | 19044.9913 | 17415.5108 | 17096.0377 | 17524.8073 | 18463.7668 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301 | 17826.4301
70% | 12669.5942 | 17550.1984 | 18817.2842 | 15336.3799 | 15503.3601 | 15792.6568 | 16452.2786 | 16892.8795 | 17452.0651 | 17741.7705 | 17995.9379 | 17523.3633 | 18074.7451 | 18942.2293 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 | 18281.9366 |  | 13557.495 | 18376.5449 | 19693.1554 | 16199.9553 | 16327.773 | 16610.7725 | 17280.721 | 17645.4161 | 18342.2589 | 20462.7785 | 18711.9928 | 18368.7368 | 18829.4258 | 19838.2852 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026 | 19153.5026
65% | 13351.323 | 18494.5441 | 19829.8096 | 16161.6039 | 16337.5689 | 16642.4322 | 17337.5471 | 17801.856 | 18391.1303 | 18696.4243 | 18964.2681 | 18466.2651 | 19047.3157 | 19961.4777 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 | 19265.6558 |  | 14287.0002 | 19365.3548 | 20752.8099 | 17071.6467 | 17206.3421 | 17504.5692 | 18210.5666 | 18594.8853 | 19329.2239 | 21563.845 | 19718.8526 | 19357.1265 | 19842.6044 | 20905.7488 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192 | 20184.1192
60% | 14698.1621 | 20360.2151 | 21830.1779 | 17791.9352 | 17985.6511 | 18321.268 | 19086.5039 | 19597.6508 | 20246.3692 | 20582.4603 | 20877.3233 | 20329.0833 | 20968.7485 | 21975.1283 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 | 21209.114 |  | 15728.2275 | 21318.8704 | 22846.2875 | 18793.7803 | 18942.0633 | 19270.3747 | 20047.5908 | 20470.6783 | 21279.0948 | 23739.1373 | 21708.0279 | 21309.8121 | 21844.2634 | 23014.6545 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292 | 22220.2292
55% | 16350.7821 | 22649.4603 | 24284.7017 | 19792.4103 | 20007.9071 | 20381.2598 | 21232.5367 | 21801.1555 | 22522.814 | 22896.6942 | 23224.7108 | 22614.8282 | 23326.4156 | 24445.9499 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 | 23593.8071 |  | 17496.6651 | 23715.9042 | 25415.0598 | 20906.9001 | 21071.8556 | 21437.0814 | 22301.6855 | 22772.3438 | 23671.6563 | 26408.2991 | 24148.8175 | 23705.8274 | 24300.371 | 25602.3575 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092 | 24718.6092
50% | 16573.101 | 22957.4214 | 24614.8968 | 20061.5245 | 20279.9514 | 20658.3805 | 21521.2321 | 22097.5822 | 22829.0531 | 23208.0169 | 23540.4934 | 22922.3184 | 23643.5811 | 24778.3375 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 | 23914.6083 |  | 17734.5645 | 24038.3655 | 25760.6242 | 21191.1678 | 21358.3662 | 21728.5579 | 22604.9179 | 23081.9756 | 23993.516 | 26767.3684 | 24477.165 | 24028.1517 | 24630.7792 | 25950.4686 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041 | 25054.7041
45% | 12791.4633 | 17719.0143 | 18998.2882 | 15483.901 | 15652.4874 | 15944.5668 | 16610.5336 | 17055.3726 | 17619.937 | 17912.4291 | 18169.0414 | 17691.9211 | 18248.6066 | 19124.4351 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 | 18457.791 |  | 13687.9049 | 18553.3094 | 19882.5844 | 16355.7831 | 16484.8303 | 16770.552 | 17446.9448 | 17815.1479 | 18518.6936 | 20659.6105 | 18891.984 | 18545.4262 | 19010.5466 | 20029.1102 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406 | 19337.7406
40% | 6284.3875 | 8705.2708 | 9333.7723 | 7607.1699 | 7689.9956 | 7833.4929 | 8160.6793 | 8379.2267 | 8656.5946 | 8800.2946 | 8926.3671 | 8691.9601 | 8965.4571 | 9395.7477 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 | 9068.2285 |  | 6724.8052 | 9115.1562 | 9768.223 | 8035.5216 | 8098.9219 | 8239.2956 | 8571.6043 | 8752.5008 | 9098.1496 | 10149.9723 | 9281.5455 | 9111.2832 | 9339.7947 | 9840.2104 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437 | 9500.5437
35% | 2348.7515 | 3253.5419 | 3488.4405 | 2843.1334 | 2874.089 | 2927.7202 | 3050.0041 | 3131.6849 | 3235.3495 | 3289.0565 | 3336.1753 | 3248.5671 | 3350.7849 | 3511.6034 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 | 3389.1951 |  | 2513.3549 | 3406.7341 | 3650.8138 | 3003.2272 | 3026.9227 | 3079.3865 | 3203.5849 | 3271.1938 | 3400.378 | 3793.4903 | 3468.921 | 3405.2866 | 3490.6913 | 3677.7187 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703 | 3550.7703
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1417.9904 | 1433.4293 | 1460.1774 | 1521.1656 | 1561.9032 | 1613.6051 | 1640.3911 | 1663.8912 | 1620.1973 | 1671.1776 | 1751.3846 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 | 1690.3344 |  | 1253.516 | 1699.0818 | 1820.8147 | 1497.836 | 1509.6539 | 1535.8198 | 1597.7628 | 1631.4822 | 1695.9118 | 1891.9735 | 1730.0971 | 1698.3599 | 1740.9549 | 1834.2333 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188 | 1770.9188
25% | 690.592 | 956.6232 | 1025.6893 | 835.9527 | 845.0545 | 860.8234 | 896.7779 | 920.7941 | 951.2741 | 967.0653 | 980.9195 | 955.1604 | 985.2151 | 1032.4997 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 | 996.5086 |  | 738.9896 | 1001.6655 | 1073.4311 | 883.0244 | 889.9914 | 905.4171 | 941.9345 | 961.8133 | 999.7967 | 1115.3816 | 1019.9501 | 1001.2399 | 1026.3511 | 1081.3418 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158 | 1044.0158
20% | 348.989 | 483.4272 | 518.3296 | 422.4467 | 427.0462 | 435.015 | 453.1846 | 465.3211 | 480.7241 | 488.7041 | 495.7053 | 482.688 | 497.8761 | 521.7713 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 | 503.5832 |  | 373.4466 | 506.1893 | 542.4558 | 446.2342 | 449.755 | 457.5504 | 476.0044 | 486.05 | 505.2448 | 563.6554 | 515.4293 | 505.9742 | 518.664 | 546.4535 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909 | 527.5909
15% | 142.1807 | 196.9518 | 211.1713 | 172.1079 | 173.9818 | 177.2283 | 184.6308 | 189.5753 | 195.8506 | 199.1017 | 201.954 | 196.6507 | 202.8384 | 212.5735 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 | 205.1635 |  | 152.1449 | 206.2253 | 221.0005 | 181.7991 | 183.2335 | 186.4094 | 193.9277 | 198.0204 | 205.8405 | 229.6374 | 209.9897 | 206.1376 | 211.3076 | 222.6292 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444 | 214.9444
10% | 57.2416 | 79.2923 | 85.017 | 69.2902 | 70.0446 | 71.3517 | 74.3319 | 76.3225 | 78.8489 | 80.1578 | 81.3062 | 79.1711 | 81.6622 | 85.5815 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 | 82.5983 |  | 61.2531 | 83.0258 | 88.9742 | 73.1919 | 73.7693 | 75.0479 | 78.0748 | 79.7225 | 82.8708 | 92.4514 | 84.5413 | 82.9905 | 85.0719 | 89.6299 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361 | 86.5361
5% | 48.7477 | 67.5263 | 72.4016 | 59.0084 | 59.6509 | 60.764 | 63.302 | 64.9972 | 67.1488 | 68.2634 | 69.2414 | 67.4231 | 69.5446 | 72.8823 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 | 70.3418 |  | 52.164 | 70.7058 | 75.7716 | 62.3311 | 62.8229 | 63.9118 | 66.4895 | 67.8927 | 70.5739 | 78.7328 | 71.9965 | 70.6758 | 72.4483 | 76.33 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952 | 73.6952
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 158019.1173 | 159739.6054 | 162720.3878 | 169516.8324 | 174056.5845 | 179818.1793 | 182803.1729 | 185421.9993 | 180552.8045 | 186233.9924 | 195172.1569 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | 188368.7997 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 166917.0072 | 168233.9831 | 171149.8812 | 178052.7278 | 181810.3809 | 188990.3337 | 210839.2074 | 192799.9043 | 189263.1496 | 194009.8806 | 204404.7115 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212 | 197349.0212
Option 4 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 110613.3821 | 111817.7238 | 113904.2715 | 118661.7827 | 121839.6091 | 125872.7255 | 127962.221 | 129795.3995 | 126386.9632 | 130363.7947 | 136620.5099 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | 131858.1598 | Option 4 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 50075.1022 | 50470.1949 | 51344.9643 | 53415.8183 | 54543.1143 | 56697.1001 | 63251.7622 | 57839.9713 | 56778.9449 | 58202.9642 | 61321.4135 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063 | 59204.7063
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 107.4801 | 107.5064 | 108.2492 | 110.2157 | 111.5286 | 112.8159 | 114.3222 | 115.7156 | 117.0702 | 117.2212 | 118.803 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967 | 117.5967
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 53.1999 | 53.213 | 53.5806 | 54.554 | 55.2039 | 55.8411 | 56.5866 | 57.2763 | 57.9468 | 58.0216 | 58.8045 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074 | 58.2074
97% | 20.8131 | 27.6102 | 29.4592 | 24.0583 | 24.0552 | 24.2653 | 24.496 | 24.9699 | 25.3105 | 25.4949 | 25.6963 | 25.881 | 26.2152 | 26.6302 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 | 26.6004 |  | 92.7689 | 120.0119 | 127.1357 | 105.3197 | 105.3455 | 106.0733 | 108.0003 | 109.2868 | 110.5483 | 112.0243 | 113.3896 | 114.7171 | 114.865 | 116.415 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329 | 115.2329
95% | 102.4643 | 135.9269 | 145.0299 | 118.4407 | 118.4255 | 119.46 | 120.5955 | 122.9287 | 124.6056 | 125.5136 | 126.505 | 127.414 | 129.0594 | 131.1025 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 | 130.9558 |  | 137.0126 | 177.2483 | 187.7696 | 155.5491 | 155.5872 | 156.6622 | 159.5081 | 161.4082 | 163.2713 | 165.4513 | 167.4677 | 169.4283 | 169.6468 | 171.936 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902 | 170.1902
90% | 177.7116 | 235.7483 | 251.5362 | 205.4207 | 205.3943 | 207.1884 | 209.1578 | 213.2044 | 216.1128 | 217.6876 | 219.4071 | 220.9836 | 223.8374 | 227.3809 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 | 227.1265 |  | 594.078 | 768.5376 | 814.1574 | 674.4511 | 674.6162 | 679.2774 | 691.6172 | 699.856 | 707.9342 | 717.3863 | 726.1297 | 734.6304 | 735.5781 | 745.504 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934 | 737.934
85% | 504.3166 | 669.0154 | 713.8189 | 582.9506 | 582.8756 | 587.967 | 593.5558 | 605.0396 | 613.2931 | 617.7621 | 622.6418 | 627.1156 | 635.2141 | 645.2701 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 | 644.5481 |  | 561.9657 | 726.995 | 770.1489 | 637.9943 | 638.1505 | 642.5597 | 654.2325 | 662.0259 | 669.6675 | 678.6087 | 686.8794 | 694.9206 | 695.8171 | 705.2064 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457 | 698.0457
80% | 704.4422 | 934.4978 | 997.0804 | 814.2801 | 814.1755 | 821.2873 | 829.0938 | 845.1347 | 856.6633 | 862.9058 | 869.7219 | 875.971 | 887.2832 | 901.3296 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 | 900.3211 |  | 392.484 | 507.7425 | 537.8818 | 445.5833 | 445.6924 | 448.7719 | 456.9243 | 462.3673 | 467.7043 | 473.9489 | 479.7253 | 485.3414 | 485.9675 | 492.5251 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524 | 487.524
75% | 1836.3528 | 2436.0657 | 2599.2074 | 2122.6803 | 2122.4075 | 2140.9466 | 2161.2969 | 2203.1125 | 2233.1656 | 2249.4386 | 2267.2068 | 2283.4971 | 2312.986 | 2349.6025 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 | 2346.9734 |  | 700.5244 | 906.2435 | 960.0375 | 795.2987 | 795.4934 | 800.9898 | 815.5406 | 825.2556 | 834.7813 | 845.927 | 856.237 | 866.2608 | 867.3783 | 879.0827 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565 | 870.1565
70% | 3172.6584 | 4208.7797 | 4490.6388 | 3667.345 | 3666.8737 | 3698.9037 | 3734.0627 | 3806.3074 | 3858.23 | 3886.3447 | 3917.0429 | 3945.1875 | 3996.1353 | 4059.3975 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 | 4054.8553 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1448.8208 | 1449.1755 | 1459.1885 | 1485.6961 | 1503.3944 | 1520.7475 | 1541.0521 | 1559.8341 | 1578.0949 | 1580.1306 | 1601.4529 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917 | 1585.1917
65% | 7968.2023 | 10570.444 | 11278.3393 | 9210.6188 | 9209.435 | 9289.8792 | 9378.1818 | 9559.6258 | 9690.0306 | 9760.6414 | 9837.7406 | 9908.4262 | 10036.3829 | 10195.2672 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 | 10183.8594 |  | 1605.6162 | 2077.1285 | 2200.4254 | 1822.8407 | 1823.287 | 1835.8849 | 1869.2356 | 1891.5027 | 1913.3357 | 1938.8819 | 1962.5126 | 1985.4875 | 1988.0488 | 2014.8755 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163 | 1994.4163
60% | 11647.312 | 15451.0709 | 16485.8185 | 13463.3819 | 13461.6516 | 13579.2387 | 13708.3127 | 13973.5338 | 14164.1495 | 14267.3631 | 14380.0608 | 14483.3837 | 14670.4211 | 14902.6661 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 | 14885.991 |  | 2512.492 | 3250.3215 | 3443.2583 | 2852.4082 | 2853.1065 | 2872.8199 | 2925.0075 | 2959.8515 | 2994.016 | 3033.9911 | 3070.9688 | 3106.9202 | 3110.9282 | 3152.9071 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922 | 3120.8922
55% | 13170.4015 | 17471.5683 | 18641.6273 | 15223.9542 | 15221.9977 | 15354.9613 | 15500.9141 | 15800.8174 | 16016.3595 | 16133.0701 | 16260.505 | 16377.3391 | 16588.8349 | 16851.45 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 | 16832.5944 |  | 4828.1473 | 6246.0024 | 6616.7608 | 5481.3496 | 5482.6916 | 5520.5738 | 5620.8607 | 5687.8187 | 5753.4712 | 5830.2897 | 5901.348 | 5970.4344 | 5978.1364 | 6058.8054 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838 | 5997.2838
50% | 16911.4168 | 22434.3178 | 23936.7286 | 19548.2753 | 19545.7629 | 19716.4946 | 19903.9048 | 20288.9948 | 20565.761 | 20715.6229 | 20879.2553 | 21029.2759 | 21300.8465 | 21638.0566 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 | 21613.8451 |  | 10714.812 | 13861.3711 | 14684.1724 | 12164.4239 | 12167.4021 | 12251.4718 | 12474.0322 | 12622.6281 | 12768.3266 | 12938.8053 | 13096.5006 | 13249.8197 | 13266.9124 | 13445.9362 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051 | 13309.4051
45% | 22520.2713 | 29874.9022 | 31875.6039 | 26031.6725 | 26028.3269 | 26255.6835 | 26505.2503 | 27018.0596 | 27386.6184 | 27586.1836 | 27804.0864 | 28003.863 | 28365.5029 | 28814.5523 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 | 28782.3109 |  | 16236.3476 | 21004.3853 | 22251.1909 | 18432.9707 | 18437.4835 | 18564.8759 | 18902.1257 | 19127.2958 | 19348.0753 | 19606.4047 | 19845.3633 | 20077.6905 | 20103.5913 | 20374.8693 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813 | 20167.9813
40% | 15794.9825 | 20953.2804 | 22356.5072 | 18257.7646 | 18255.4181 | 18414.8787 | 18589.9167 | 18949.5844 | 19208.0794 | 19348.048 | 19500.8779 | 19640.9946 | 19894.637 | 20209.5857 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 | 20186.9725 |  | 16811.9908 | 21749.0744 | 23040.0842 | 19086.4929 | 19091.1657 | 19223.0746 | 19572.2813 | 19805.4345 | 20034.0416 | 20301.5298 | 20548.9604 | 20789.5245 | 20816.3437 | 21097.2395 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165 | 20883.0165
35% | 8189.141 | 10863.5364 | 11591.06 | 9466.0066 | 9464.7901 | 9547.4647 | 9638.2157 | 9824.6907 | 9958.7113 | 10031.2801 | 10110.517 | 10183.1626 | 10314.6672 | 10477.957 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 | 10466.2329 |  | 22897.8708 | 29622.1608 | 31380.5115 | 25995.7345 | 26002.0988 | 26181.7583 | 26657.3765 | 26974.9304 | 27286.2924 | 27650.6103 | 27987.6099 | 28315.2574 | 28351.785 | 28734.3641 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931 | 28442.5931
30% | 3808.7911 | 5052.6595 | 5391.0326 | 4402.6647 | 4402.0988 | 4440.551 | 4482.7596 | 4569.4896 | 4631.8229 | 4665.5748 | 4702.4281 | 4736.2158 | 4797.3789 | 4873.3254 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 | 4867.8725 |  | 21159.0479 | 27372.7075 | 28997.5323 | 24021.6654 | 24027.5465 | 24193.563 | 24633.0636 | 24926.503 | 25214.2207 | 25550.873 | 25862.2815 | 26165.048 | 26198.8017 | 26552.3285 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141 | 26282.7141
25% | 2600.5659 | 3449.8542 | 3680.8886 | 3006.0509 | 3005.6645 | 3031.9189 | 3060.738 | 3119.9556 | 3162.5155 | 3185.5606 | 3210.7233 | 3233.7928 | 3275.5538 | 3327.4086 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 | 3323.6854 |  | 6103.1255 | 7895.3963 | 8364.0615 | 6928.8202 | 6930.5166 | 6978.4024 | 7105.1722 | 7189.812 | 7272.8014 | 7369.9056 | 7459.7284 | 7547.0585 | 7556.7944 | 7658.7658 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981 | 7580.9981
20% | 1575.389 | 2089.8768 | 2229.8344 | 1821.0265 | 1820.7925 | 1836.697 | 1854.1553 | 1890.0285 | 1915.8107 | 1929.7712 | 1945.0144 | 1958.9896 | 1984.2879 | 2015.7008 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 | 2013.4454 |  | 1637.7285 | 2118.6711 | 2244.4339 | 1859.2976 | 1859.7528 | 1872.6026 | 1906.6203 | 1929.3328 | 1951.6024 | 1977.6595 | 2001.7628 | 2025.1972 | 2027.8098 | 2055.1731 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047 | 2034.3047
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1165.9011 | 1165.7513 | 1175.9341 | 1187.1116 | 1210.0792 | 1226.5861 | 1235.5242 | 1245.2836 | 1254.2312 | 1270.4282 | 1290.5402 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 | 1289.0961 |  | 903.3078 | 1168.5771 | 1237.943 | 1025.5167 | 1025.7678 | 1032.8552 | 1051.6181 | 1064.1454 | 1076.4285 | 1090.8006 | 1104.095 | 1117.0205 | 1118.4615 | 1133.5541 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439 | 1122.0439
10% | 675.0905 | 895.5604 | 955.5354 | 780.3518 | 780.2515 | 787.067 | 794.5483 | 809.9207 | 820.969 | 826.9514 | 833.4835 | 839.4722 | 850.3131 | 863.7742 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 | 862.8077 |  | 211.1088 | 273.1039 | 289.3152 | 239.6698 | 239.7285 | 241.3849 | 245.7699 | 248.6976 | 251.5682 | 254.9271 | 258.0341 | 261.0548 | 261.3916 | 264.9188 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288 | 262.2288
5% | 480.3015 | 637.1576 | 679.8276 | 555.191 | 555.1197 | 559.9686 | 565.2912 | 576.2282 | 584.0886 | 588.3449 | 592.9922 | 597.2529 | 604.9658 | 614.5429 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 | 613.8553 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 48.7334 | 48.7272 | 49.1528 | 49.62 | 50.58 | 51.27 | 51.6436 | 52.0515 | 52.4255 | 53.1026 | 53.9432 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 | 53.8829 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 130516.769 | 130499.9949 | 131639.9084 | 132891.1786 | 135462.2853 | 137310.1536 | 138310.7273 | 139403.2415 | 140404.8748 | 142218.0534 | 144469.4833 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | 144307.832 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 124334.8872 | 124365.3273 | 125224.6199 | 127499.4521 | 129018.2791 | 130507.4913 | 132249.986 | 133861.82 | 135428.9237 | 135603.6312 | 137433.4672 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957 | 136037.957
Option 4 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 91361.7383 | 91349.9965 | 92147.9359 | 93023.825 | 94823.5997 | 96117.1075 | 96817.5091 | 97582.2691 | 98283.4123 | 99552.6374 | 101128.6383 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | 101015.4824 | Option 4 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 37300.4662 | 37309.5982 | 37567.386 | 38249.8356 | 38705.4837 | 39152.2474 | 39674.9958 | 40158.546 | 40628.6771 | 40681.0894 | 41230.0402 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871 | 40811.3871
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 67.5205 | 68.4891 | 70.1672 | 73.9934 | 76.5491 | 79.7927 | 81.4731 | 82.9475 | 80.2063 | 83.4046 | 88.4365 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 | 84.6064 |  | 78.6411 | 106.5944 | 114.2314 | 72.5297 | 73.2712 | 74.9127 | 78.7988 | 80.9142 | 84.9563 | 97.2565 | 87.101 | 85.1099 | 87.7822 | 93.6341 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662 | 89.662
98% | 87.3027 | 120.9335 | 129.6647 | 80.2103 | 81.3609 | 83.3544 | 87.8996 | 90.9357 | 94.7889 | 96.7852 | 98.5366 | 95.2802 | 99.0796 | 105.0572 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 | 100.5073 |  | 93.4209 | 126.6277 | 135.7001 | 86.161 | 87.0417 | 88.9918 | 93.6082 | 96.1212 | 100.923 | 115.5349 | 103.4707 | 101.1054 | 104.2799 | 111.2317 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513 | 106.513
97% | 172.8327 | 239.4116 | 256.6966 | 158.792 | 161.0698 | 165.0163 | 174.0145 | 180.025 | 187.6532 | 191.6052 | 195.0724 | 188.6258 | 196.1475 | 207.9813 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 | 198.9739 |  | 184.945 | 250.6842 | 268.6448 | 170.5725 | 172.3161 | 176.1766 | 185.3158 | 190.2908 | 199.7968 | 228.7239 | 204.8405 | 200.158 | 206.4425 | 220.2048 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634 | 210.8634
95% | 510.5211 | 707.185 | 758.2422 | 469.047 | 475.7755 | 487.4327 | 514.0122 | 531.7662 | 554.2985 | 565.9722 | 576.2139 | 557.1715 | 579.3894 | 614.3447 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 | 587.7382 |  | 546.299 | 740.4826 | 793.5354 | 503.8448 | 508.9952 | 520.3987 | 547.3942 | 562.0896 | 590.1689 | 675.6152 | 605.0673 | 591.2358 | 609.7993 | 650.4512 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579 | 622.8579
90% | 2814.8088 | 3899.1347 | 4180.6436 | 2586.1376 | 2623.2356 | 2687.5088 | 2834.0572 | 2931.9457 | 3056.1802 | 3120.5442 | 3177.0126 | 3072.0206 | 3194.5213 | 3387.2506 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 | 3240.5531 |  | 3012.0741 | 4082.7244 | 4375.2363 | 2777.9985 | 2806.3958 | 2869.2699 | 3018.1126 | 3099.1371 | 3253.9549 | 3725.0716 | 3336.0988 | 3259.8375 | 3362.189 | 3586.3277 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892 | 3434.1892
85% | 6876.3763 | 9525.3066 | 10213.0129 | 6317.7488 | 6408.3767 | 6565.3915 | 6923.3988 | 7162.5333 | 7466.0293 | 7623.2658 | 7761.2143 | 7504.7262 | 7803.9866 | 8274.8105 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 | 7916.439 |  | 7358.2813 | 9973.8032 | 10688.3888 | 6786.4512 | 6855.8238 | 7009.4208 | 7373.0329 | 7570.9698 | 7949.1788 | 9100.0831 | 8149.8505 | 7963.5495 | 8213.5868 | 8761.1416 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783 | 8389.4783
80% | 10687.9274 | 14805.1503 | 15874.0497 | 9819.6546 | 9960.5172 | 10204.5647 | 10761.0142 | 11132.7002 | 11604.4228 | 11848.8151 | 12063.2279 | 11664.5693 | 12129.7087 | 12861.5086 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 | 12304.4931 |  | 11436.9506 | 15502.2469 | 16612.9248 | 10548.1571 | 10655.9827 | 10894.7178 | 11459.8789 | 11767.5316 | 12355.3804 | 14144.2269 | 12667.2837 | 12377.7168 | 12766.3489 | 13617.4113 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364 | 13039.7364
75% | 11791.7667 | 16334.2127 | 17513.507 | 10833.8196 | 10989.2303 | 11258.4828 | 11872.4019 | 12282.4753 | 12802.917 | 13072.5499 | 13309.107 | 12869.2753 | 13382.4539 | 14189.8335 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 | 13575.2899 |  | 12618.1483 | 17103.3048 | 18328.6925 | 11637.5611 | 11756.5228 | 12019.9143 | 12643.4447 | 12982.8715 | 13631.4327 | 15605.0297 | 13975.5492 | 13656.0761 | 14084.8457 | 15023.8051 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684 | 14386.4684
70% | 12669.5942 | 17550.1984 | 18817.2842 | 11640.3335 | 11807.3136 | 12096.6104 | 12756.2322 | 13196.833 | 13756.0186 | 14045.724 | 14299.8915 | 13827.3169 | 14378.6986 | 15246.1828 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 | 14585.8901 |  | 13557.495 | 18376.5449 | 19693.1554 | 12503.9088 | 12631.7266 | 12914.726 | 13584.6745 | 13949.3696 | 14646.2124 | 16766.732 | 15015.9463 | 14672.6903 | 15133.3793 | 16142.2387 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561 | 15457.4561
65% | 13351.323 | 18494.5441 | 19829.8096 | 12266.6796 | 12442.6447 | 12747.5079 | 13442.6228 | 13906.9317 | 14496.206 | 14801.5 | 15069.3438 | 14571.3408 | 15152.3914 | 16066.5534 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 | 15370.7315 |  | 14287.0002 | 19365.3548 | 20752.8099 | 13176.7224 | 13311.4178 | 13609.6449 | 14315.6423 | 14699.961 | 15434.2996 | 17668.9207 | 15823.9283 | 15462.2022 | 15947.6801 | 17010.8245 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949 | 16289.1949
60% | 14698.1621 | 20360.2151 | 21830.1779 | 13504.1033 | 13697.8192 | 14033.4361 | 14798.672 | 15309.8188 | 15958.5373 | 16294.6284 | 16589.4914 | 16041.2514 | 16680.9166 | 17687.2964 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 | 16921.2821 |  | 15728.2275 | 21318.8704 | 22846.2875 | 14505.9484 | 14654.2314 | 14982.5428 | 15759.7589 | 16182.8464 | 16991.2629 | 19451.3054 | 17420.196 | 17021.9802 | 17556.4315 | 18726.8226 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973 | 17932.3973
55% | 16350.7821 | 22649.4603 | 24284.7017 | 15022.4667 | 15237.9634 | 15611.3162 | 16462.593 | 17031.2118 | 17752.8704 | 18126.7506 | 18454.7671 | 17844.8846 | 18556.4719 | 19676.0062 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 | 18823.8635 |  | 17496.6651 | 23715.9042 | 25415.0598 | 16136.9564 | 16301.912 | 16667.1377 | 17531.7418 | 18002.4001 | 18901.7126 | 21638.3554 | 19378.8738 | 18935.8837 | 19530.4273 | 20832.4138 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655 | 19948.6655
50% | 16573.101 | 22957.4214 | 24614.8968 | 15226.7247 | 15445.1515 | 15823.5807 | 16686.4322 | 17262.7824 | 17994.2533 | 18373.217 | 18705.6936 | 18087.5186 | 18808.7812 | 19943.5377 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 | 19079.8085 |  | 17734.5645 | 24038.3655 | 25760.6242 | 16356.368 | 16523.5664 | 16893.7581 | 17770.118 | 18247.1758 | 19158.7162 | 21932.5686 | 19642.3652 | 19193.3519 | 19795.9793 | 21115.6687 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043 | 20219.9043
45% | 12791.4633 | 17719.0143 | 18998.2882 | 11752.3022 | 11920.8885 | 12212.968 | 12878.9347 | 13323.7738 | 13888.3381 | 14180.8302 | 14437.4425 | 13960.3222 | 14517.0077 | 15392.8363 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 | 14726.1922 |  | 13687.9049 | 18553.3094 | 19882.5844 | 12624.1843 | 12753.2315 | 13038.9531 | 13715.3459 | 14083.549 | 14787.0948 | 16928.0117 | 15160.3851 | 14813.8273 | 15278.9477 | 16297.5114 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418 | 15606.1418
40% | 6284.3875 | 8705.2708 | 9333.7723 | 5773.8524 | 5856.6781 | 6000.1754 | 6327.3618 | 6545.9092 | 6823.2771 | 6966.9772 | 7093.0496 | 6858.6426 | 7132.1396 | 7562.4302 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 | 7234.911 |  | 6724.8052 | 9115.1562 | 9768.223 | 6202.2041 | 6265.6044 | 6405.9781 | 6738.2868 | 6919.1833 | 7264.8322 | 8316.6549 | 7448.228 | 7277.9657 | 7506.4773 | 8006.893 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262 | 7667.2262
35% | 2348.7515 | 3253.5419 | 3488.4405 | 2157.9421 | 2188.8977 | 2242.529 | 2364.8129 | 2446.4937 | 2550.1582 | 2603.8652 | 2650.9841 | 2563.3759 | 2665.5937 | 2826.4122 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 | 2704.0039 |  | 2513.3549 | 3406.7341 | 3650.8138 | 2318.036 | 2341.7315 | 2394.1953 | 2518.3936 | 2586.0026 | 2715.1867 | 3108.299 | 2783.7298 | 2720.0953 | 2805.5001 | 2992.5274 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791 | 2865.5791
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1076.2567 | 1091.6955 | 1118.4437 | 1179.4318 | 1220.1695 | 1271.8714 | 1298.6573 | 1322.1575 | 1278.4636 | 1329.4439 | 1409.6509 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 | 1348.6007 |  | 1253.516 | 1699.0818 | 1820.8147 | 1156.1022 | 1167.9202 | 1194.0861 | 1256.029 | 1289.7485 | 1354.178 | 1550.2397 | 1388.3634 | 1356.6262 | 1399.2211 | 1492.4995 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185 | 1429.185
25% | 690.592 | 956.6232 | 1025.6893 | 634.4893 | 643.591 | 659.3599 | 695.3145 | 719.3307 | 749.8107 | 765.6019 | 779.456 | 753.697 | 783.7516 | 831.0363 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 | 795.0452 |  | 738.9896 | 1001.6655 | 1073.4311 | 681.5609 | 688.528 | 703.9536 | 740.4711 | 760.3498 | 798.3332 | 913.9181 | 818.4866 | 799.7765 | 824.8876 | 879.8783 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523 | 842.5523
20% | 348.989 | 483.4272 | 518.3296 | 320.6376 | 325.2372 | 333.206 | 351.3755 | 363.512 | 378.915 | 386.8951 | 393.8962 | 380.879 | 396.067 | 419.9622 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 | 401.7742 |  | 373.4466 | 506.1893 | 542.4558 | 344.4252 | 347.9459 | 355.7413 | 374.1953 | 384.241 | 403.4358 | 461.8463 | 413.6202 | 404.1651 | 416.855 | 444.6444 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818 | 425.7818
15% | 142.1807 | 196.9518 | 211.1713 | 130.6301 | 132.504 | 135.7506 | 143.153 | 148.0975 | 154.3728 | 157.6239 | 160.4762 | 155.1729 | 161.3606 | 171.0957 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 | 163.6858 |  | 152.1449 | 206.2253 | 221.0005 | 140.3214 | 141.7558 | 144.9316 | 152.4499 | 156.5426 | 164.3627 | 188.1596 | 168.5119 | 164.6599 | 169.8298 | 181.1514 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667 | 173.4667
10% | 57.2416 | 79.2923 | 85.017 | 52.5914 | 53.3458 | 54.6528 | 57.633 | 59.6237 | 62.1501 | 63.459 | 64.6073 | 62.4722 | 64.9634 | 68.8827 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 | 65.8995 |  | 61.2531 | 83.0258 | 88.9742 | 56.493 | 57.0705 | 58.3491 | 61.3759 | 63.0236 | 66.172 | 75.7526 | 67.8425 | 66.2916 | 68.373 | 72.9311 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372 | 69.8372
5% | 48.7477 | 67.5263 | 72.4016 | 44.7875 | 45.43 | 46.5431 | 49.081 | 50.7763 | 52.9278 | 54.0425 | 55.0204 | 53.2021 | 55.3236 | 58.6614 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 | 56.1208 |  | 52.164 | 70.7058 | 75.7716 | 48.1102 | 48.602 | 49.6908 | 52.2685 | 53.6718 | 56.3529 | 64.5119 | 57.7755 | 56.4548 | 58.2274 | 62.1091 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743 | 59.4743
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 119936.7274 | 121657.2155 | 124637.9979 | 131434.4425 | 135974.1946 | 141735.7894 | 144720.783 | 147339.6094 | 142470.4146 | 148151.6025 | 157089.767 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | 150286.4098 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 128834.6173 | 130151.5932 | 133067.4913 | 139970.3379 | 143727.991 | 150907.9438 | 172756.8175 | 154717.5144 | 151180.7597 | 155927.4907 | 166322.3216 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313 | 159266.6313
Option 5 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 83955.7092 | 85160.0509 | 87246.5985 | 92004.1098 | 95181.9362 | 99215.0526 | 101304.5481 | 103137.7266 | 99729.2902 | 103706.1218 | 109962.8369 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | 105200.4869 | Option 5 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 38650.3852 | 39045.4779 | 39920.2474 | 41991.1014 | 43118.3973 | 45272.3831 | 51827.0452 | 46415.2543 | 45354.2279 | 46778.2472 | 49896.6965 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894 | 47779.9894
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 85.6562 | 85.6825 | 86.4254 | 88.3918 | 89.7047 | 90.9921 | 92.4984 | 93.8917 | 95.2464 | 95.3974 | 96.9792 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728 | 95.7728
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 42.3977 | 42.4107 | 42.7784 | 43.7517 | 44.4016 | 45.0388 | 45.7844 | 46.474 | 47.1446 | 47.2193 | 48.0023 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051 | 47.4051
97% | 20.8131 | 27.6102 | 29.4592 | 18.712 | 18.7089 | 18.919 | 19.1497 | 19.6236 | 19.9642 | 20.1486 | 20.35 | 20.5347 | 20.8689 | 21.2839 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 | 21.2541 |  | 92.7689 | 120.0119 | 127.1357 | 83.9345 | 83.9603 | 84.6882 | 86.6151 | 87.9016 | 89.1631 | 90.6391 | 92.0044 | 93.3319 | 93.4799 | 95.0298 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478 | 93.8478
95% | 102.4643 | 135.9269 | 145.0299 | 92.1205 | 92.1053 | 93.1397 | 94.2752 | 96.6084 | 98.2853 | 99.1933 | 100.1848 | 101.0937 | 102.7391 | 104.7823 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 | 104.6356 |  | 137.0126 | 177.2483 | 187.7696 | 123.9648 | 124.0029 | 125.0779 | 127.9238 | 129.824 | 131.687 | 133.867 | 135.8835 | 137.844 | 138.0626 | 140.3518 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059 | 138.6059
90% | 177.7116 | 235.7483 | 251.5362 | 159.7715 | 159.7451 | 161.5392 | 163.5086 | 167.5553 | 170.4636 | 172.0384 | 173.758 | 175.3344 | 178.1882 | 181.7317 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 | 181.4773 |  | 594.078 | 768.5376 | 814.1574 | 537.5036 | 537.6687 | 542.3299 | 554.6697 | 562.9085 | 570.9867 | 580.4388 | 589.1822 | 597.6829 | 598.6306 | 608.5565 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866 | 600.9866
85% | 504.3166 | 669.0154 | 713.8189 | 453.4057 | 453.3307 | 458.4221 | 464.0109 | 475.4947 | 483.7482 | 488.2172 | 493.0969 | 497.5707 | 505.6692 | 515.7252 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 | 515.0032 |  | 561.9657 | 726.995 | 770.1489 | 508.4494 | 508.6056 | 513.0148 | 524.6876 | 532.481 | 540.1226 | 549.0638 | 557.3345 | 565.3757 | 566.2722 | 575.6615 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008 | 568.5008
80% | 704.4422 | 934.4978 | 997.0804 | 633.3285 | 633.2239 | 640.3357 | 648.1422 | 664.1831 | 675.7117 | 681.9542 | 688.7703 | 695.0194 | 706.3316 | 720.378 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 | 719.3695 |  | 392.484 | 507.7425 | 537.8818 | 355.1075 | 355.2166 | 358.2961 | 366.4485 | 371.8915 | 377.2285 | 383.4731 | 389.2495 | 394.8656 | 395.4917 | 402.0493 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482 | 397.0482
75% | 1836.3528 | 2436.0657 | 2599.2074 | 1650.9723 | 1650.6995 | 1669.2387 | 1689.5889 | 1731.4045 | 1761.4576 | 1777.7306 | 1795.4989 | 1811.7891 | 1841.278 | 1877.8945 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 | 1875.2655 |  | 700.5244 | 906.2435 | 960.0375 | 633.8131 | 634.0078 | 639.5042 | 654.055 | 663.77 | 673.2957 | 684.4414 | 694.7514 | 704.7752 | 705.8927 | 717.5971 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709 | 708.6709
70% | 3172.6584 | 4208.7797 | 4490.6388 | 2852.3774 | 2851.906 | 2883.9361 | 2919.0951 | 2991.3397 | 3043.2623 | 3071.3771 | 3102.0752 | 3130.2198 | 3181.1677 | 3244.4298 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 | 3239.8876 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1154.6374 | 1154.9921 | 1165.0051 | 1191.5127 | 1209.2109 | 1226.5641 | 1246.8686 | 1265.6506 | 1283.9114 | 1285.9472 | 1307.2695 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082 | 1291.0082
65% | 7968.2023 | 10570.444 | 11278.3393 | 7163.8093 | 7162.6256 | 7243.0697 | 7331.3723 | 7512.8163 | 7643.2211 | 7713.832 | 7790.9311 | 7861.6168 | 7989.5735 | 8148.4577 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 | 8137.05 |  | 1605.6162 | 2077.1285 | 2200.4254 | 1452.7125 | 1453.1587 | 1465.7566 | 1499.1073 | 1521.3744 | 1543.2074 | 1568.7536 | 1592.3843 | 1615.3592 | 1617.9205 | 1644.7473 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881 | 1624.2881
60% | 11647.312 | 15451.0709 | 16485.8185 | 10471.5115 | 10469.7812 | 10587.3683 | 10716.4423 | 10981.6634 | 11172.2792 | 11275.4928 | 11388.1904 | 11491.5133 | 11678.5507 | 11910.7957 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 | 11894.1206 |  | 2512.492 | 3250.3215 | 3443.2583 | 2273.226 | 2273.9243 | 2293.6376 | 2345.8253 | 2380.6692 | 2414.8337 | 2454.8089 | 2491.7865 | 2527.738 | 2531.746 | 2573.7249 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71 | 2541.71
55% | 13170.4015 | 17471.5683 | 18641.6273 | 11840.8446 | 11838.888 | 11971.8517 | 12117.8044 | 12417.7077 | 12633.2498 | 12749.9604 | 12877.3953 | 12994.2294 | 13205.7252 | 13468.3403 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 | 13449.4847 |  | 4828.1473 | 6246.0024 | 6616.7608 | 4368.3602 | 4369.7021 | 4407.5844 | 4507.8712 | 4574.8292 | 4640.4817 | 4717.3002 | 4788.3585 | 4857.4449 | 4865.1469 | 4945.8159 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943 | 4884.2943
50% | 16911.4168 | 22434.3178 | 23936.7286 | 15204.2029 | 15201.6905 | 15372.4222 | 15559.8324 | 15944.9224 | 16221.6886 | 16371.5505 | 16535.1829 | 16685.2035 | 16956.7741 | 17293.9842 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 | 17269.7727 |  | 10714.812 | 13861.3711 | 14684.1724 | 9694.4344 | 9697.4126 | 9781.4823 | 10004.0427 | 10152.6386 | 10298.3371 | 10468.8158 | 10626.5111 | 10779.8302 | 10796.9229 | 10975.9467 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156 | 10839.4156
45% | 22520.2713 | 29874.9022 | 31875.6039 | 20246.8414 | 20243.4958 | 20470.8525 | 20720.4193 | 21233.2285 | 21601.7873 | 21801.3525 | 22019.2554 | 22219.0319 | 22580.6718 | 23029.7213 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 | 22997.4798 |  | 16236.3476 | 21004.3853 | 22251.1909 | 14690.1512 | 14694.664 | 14822.0564 | 15159.3061 | 15384.4762 | 15605.2558 | 15863.5852 | 16102.5438 | 16334.871 | 16360.7718 | 16632.0497 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617 | 16425.1617
40% | 15794.9825 | 20953.2804 | 22356.5072 | 14200.4731 | 14198.1266 | 14357.5872 | 14532.6252 | 14892.2928 | 15150.7879 | 15290.7564 | 15443.5864 | 15583.7031 | 15837.3455 | 16152.2941 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 | 16129.681 |  | 16811.9908 | 21749.0744 | 23040.0842 | 15210.9755 | 15215.6483 | 15347.5572 | 15696.7639 | 15929.9171 | 16158.5242 | 16426.0124 | 16673.443 | 16914.0071 | 16940.8263 | 17221.7221 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991 | 17007.4991
35% | 8189.141 | 10863.5364 | 11591.06 | 7362.4442 | 7361.2276 | 7443.9022 | 7534.6533 | 7721.1283 | 7855.1489 | 7927.7176 | 8006.9545 | 8079.6001 | 8211.1047 | 8374.3945 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 | 8362.6704 |  | 22897.8708 | 29622.1608 | 31380.5115 | 20717.2937 | 20723.6581 | 20903.3176 | 21378.9358 | 21696.4896 | 22007.8517 | 22372.1696 | 22709.1692 | 23036.8167 | 23073.3442 | 23455.9234 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524 | 23164.1524
30% | 3808.7911 | 5052.6595 | 5391.0326 | 3424.2922 | 3423.7264 | 3462.1786 | 3504.3871 | 3591.1171 | 3653.4505 | 3687.2024 | 3724.0557 | 3757.8433 | 3819.0065 | 3894.953 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 | 3889.5001 |  | 21159.0479 | 27372.7075 | 28997.5323 | 19144.0599 | 19149.941 | 19315.9575 | 19755.4581 | 20048.8975 | 20336.6152 | 20673.2675 | 20984.676 | 21287.4425 | 21321.1963 | 21674.723 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086 | 21405.1086
25% | 2600.5659 | 3449.8542 | 3680.8886 | 2338.0378 | 2337.6515 | 2363.9059 | 2392.725 | 2451.9425 | 2494.5025 | 2517.5476 | 2542.7103 | 2565.7798 | 2607.5408 | 2659.3955 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 | 2655.6724 |  | 6103.1255 | 7895.3963 | 8364.0615 | 5521.9215 | 5523.6178 | 5571.5037 | 5698.2734 | 5782.9132 | 5865.9027 | 5963.0068 | 6052.8296 | 6140.1597 | 6149.8956 | 6251.8671 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994 | 6174.0994
20% | 1575.389 | 2089.8768 | 2229.8344 | 1416.3529 | 1416.1189 | 1432.0234 | 1449.4817 | 1485.3549 | 1511.1371 | 1525.0976 | 1540.3408 | 1554.316 | 1579.6143 | 1611.0272 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 | 1608.7718 |  | 1637.7285 | 2118.6711 | 2244.4339 | 1481.7667 | 1482.2219 | 1495.0717 | 1529.0894 | 1551.8019 | 1574.0715 | 1600.1287 | 1624.232 | 1647.6664 | 1650.2789 | 1677.6422 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738 | 1656.7738
15% | 1008.6332 | 1338.0309 | 1427.6379 | 906.8113 | 906.6615 | 916.8443 | 928.0218 | 950.9894 | 967.4963 | 976.4344 | 986.1938 | 995.1414 | 1011.3384 | 1031.4503 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 | 1030.0063 |  | 903.3078 | 1168.5771 | 1237.943 | 817.2853 | 817.5363 | 824.6238 | 843.3867 | 855.914 | 868.197 | 882.5692 | 895.8636 | 908.7891 | 910.2301 | 925.3226 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124 | 913.8124
10% | 675.0905 | 895.5604 | 955.5354 | 606.9398 | 606.8396 | 613.655 | 621.1363 | 636.5088 | 647.5571 | 653.5394 | 660.0715 | 666.0602 | 676.9011 | 690.3623 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 | 689.3958 |  | 211.1088 | 273.1039 | 289.3152 | 191.0048 | 191.0635 | 192.7198 | 197.1048 | 200.0326 | 202.9032 | 206.262 | 209.369 | 212.3898 | 212.7266 | 216.2538 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638 | 213.5638
5% | 480.3015 | 637.1576 | 679.8276 | 431.8149 | 431.7436 | 436.5925 | 441.9151 | 452.8521 | 460.7125 | 464.9688 | 469.6161 | 473.8768 | 481.5897 | 491.1668 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 | 490.4792 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 37.9038 | 37.8975 | 38.3231 | 38.7903 | 39.7504 | 40.4403 | 40.8139 | 41.2219 | 41.5959 | 42.2729 | 43.1135 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 | 43.0532 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 101512.9676 | 101496.1935 | 102636.107 | 103887.3772 | 106458.4839 | 108306.3522 | 109306.9259 | 110399.4401 | 111401.0734 | 113214.252 | 115465.6819 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | 115304.0306 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 99088.6557 | 99119.0958 | 99978.3884 | 102253.2205 | 103772.0476 | 105261.2597 | 107003.7545 | 108615.5885 | 110182.6921 | 110357.3996 | 112187.2356 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254 | 110791.7254
Option 5 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 71059.0773 | 71047.3355 | 71845.2749 | 72721.164 | 74520.9387 | 75814.4465 | 76514.8481 | 77279.6081 | 77980.7514 | 79249.9764 | 80825.9773 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | 80712.8214 | Option 5 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 29726.5967 | 29735.7287 | 29993.5165 | 30675.9662 | 31131.6143 | 31578.3779 | 32101.1263 | 32584.6765 | 33054.8076 | 33107.2199 | 33656.1707 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176 | 33237.5176
Option 6 - Non Network
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 62.0385 | 87.0741 | 93.573 | 94.8763 | 95.8471 | 97.4412 | 101.0393 | 103.4457 | 106.5412 | 108.0478 | 109.3633 | 106.4661 | 109.6502 | 114.4993 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 | 110.8149 |  | 67.1888 | 91.8674 | 98.6535 | 99.8855 | 100.6291 | 102.1867 | 105.8447 | 107.8109 | 111.7049 | 123.8312 | 113.5169 | 111.3698 | 114.0278 | 119.697 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705 | 115.8705
98% | 73.698 | 103.4388 | 111.1591 | 112.7073 | 113.8605 | 115.7543 | 120.0286 | 122.8873 | 126.5646 | 128.3543 | 129.917 | 126.4753 | 130.2578 | 136.0183 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 | 131.6414 |  | 79.8163 | 109.133 | 117.1945 | 118.6579 | 119.5413 | 121.3917 | 125.7372 | 128.0728 | 132.6986 | 147.104 | 134.8512 | 132.3006 | 135.4581 | 142.1928 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471 | 137.6471
97% | 145.8996 | 204.7774 | 220.0611 | 223.1261 | 225.4092 | 229.1582 | 237.6201 | 243.2794 | 250.5593 | 254.1024 | 257.1962 | 250.3826 | 257.8708 | 269.2748 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 | 260.6099 |  | 158.0119 | 216.05 | 232.0093 | 234.9066 | 236.6554 | 240.3186 | 248.9213 | 253.5451 | 262.7029 | 291.2211 | 266.9643 | 261.9148 | 268.1658 | 281.4984 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994 | 272.4994
95% | 430.965 | 604.8809 | 650.0266 | 659.0802 | 665.824 | 676.8981 | 701.8932 | 718.6099 | 740.1135 | 750.5794 | 759.7179 | 739.5918 | 761.7107 | 795.3964 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 | 769.8016 |  | 466.743 | 638.1785 | 685.3199 | 693.8779 | 699.0437 | 709.864 | 735.2752 | 748.9333 | 775.9839 | 860.2223 | 788.5714 | 773.6561 | 792.1206 | 831.5029 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213 | 804.9213
90% | 2376.1686 | 3335.0712 | 3583.9866 | 3633.9041 | 3671.0871 | 3732.145 | 3869.9579 | 3962.127 | 4080.6896 | 4138.3941 | 4188.7804 | 4077.8128 | 4199.768 | 4385.4971 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 | 4244.3776 |  | 2573.4339 | 3518.6609 | 3778.5793 | 3825.765 | 3854.2473 | 3913.9061 | 4054.0133 | 4129.3183 | 4278.4644 | 4742.9215 | 4347.8666 | 4265.6297 | 4367.4357 | 4584.5742 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138 | 4438.0138
85% | 5804.8097 | 8147.34 | 8755.4226 | 8877.3673 | 8968.2028 | 9117.3629 | 9454.0299 | 9679.1924 | 9968.8325 | 10109.8002 | 10232.8906 | 9961.8045 | 10259.7323 | 10713.4553 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 | 10368.7104 |  | 6286.7147 | 8595.8366 | 9230.7985 | 9346.0697 | 9415.6499 | 9561.3922 | 9903.664 | 10087.6289 | 10451.982 | 11586.6175 | 10621.5267 | 10420.6279 | 10669.3325 | 11199.7864 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497 | 10841.7497
80% | 9022.3952 | 12663.3817 | 13608.5223 | 13798.0605 | 13939.2458 | 14171.0849 | 14694.3652 | 15044.3344 | 15494.521 | 15713.6267 | 15904.9455 | 15483.5974 | 15946.6655 | 16651.8856 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 | 16116.0499 |  | 9771.4184 | 13360.4783 | 14347.3974 | 14526.563 | 14634.7113 | 14861.238 | 15393.2299 | 15679.1658 | 16245.4785 | 18009.0384 | 16509.0013 | 16196.745 | 16583.3057 | 17407.7883 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932 | 16851.2932
75% | 9954.2199 | 13971.2442 | 15013.998 | 15223.1116 | 15378.8784 | 15634.6615 | 16211.9858 | 16598.0995 | 17094.7809 | 17336.5157 | 17547.5937 | 17082.7292 | 17593.6225 | 18371.6771 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 | 17780.5008 |  | 10780.6016 | 14740.3363 | 15829.1835 | 16026.8532 | 16146.1709 | 16396.0931 | 16983.0286 | 17298.4957 | 17923.2967 | 19868.9955 | 18214.0359 | 17869.53 | 18296.0143 | 19205.6487 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793 | 18591.6793
70% | 10695.2528 | 15011.3208 | 16131.7016 | 16356.3824 | 16523.7451 | 16798.5698 | 17418.8724 | 17833.73 | 18367.3865 | 18627.1169 | 18853.9085 | 18354.4376 | 18903.3639 | 19739.34 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 | 19104.1541 |  | 11583.1537 | 15837.6673 | 17007.5727 | 17219.9578 | 17348.158 | 17616.6854 | 18247.3148 | 18586.2666 | 19257.5803 | 21348.1249 | 19569.9633 | 19199.811 | 19658.0446 | 20635.3959 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201 | 19975.7201
65% | 11270.7458 | 15819.0539 | 16999.7204 | 17236.4909 | 17412.8591 | 17702.4716 | 18356.1517 | 18793.332 | 19355.7036 | 19629.4097 | 19868.4045 | 19342.0579 | 19920.521 | 20801.4795 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 | 20132.1154 |  | 12206.423 | 16689.8646 | 17922.7206 | 18146.5338 | 18281.6322 | 18564.6086 | 19229.1711 | 19586.3613 | 20293.7972 | 22496.8303 | 20622.989 | 20232.9194 | 20715.8098 | 21745.7507 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788 | 21050.5788
60% | 12407.7029 | 17414.8299 | 18714.5982 | 18975.2534 | 19169.4131 | 19488.2408 | 20207.862 | 20689.1437 | 21308.2456 | 21609.5623 | 21872.6662 | 21293.2234 | 21930.04 | 22899.8668 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 | 22162.9793 |  | 13437.7683 | 18373.4852 | 19730.7078 | 19977.0985 | 20125.8253 | 20437.3475 | 21168.9489 | 21562.1713 | 22340.9711 | 24766.2392 | 22703.3708 | 22273.9522 | 22805.555 | 23939.393 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945 | 23174.0945
55% | 13802.7901 | 19372.9044 | 20818.815 | 21108.7775 | 21324.768 | 21679.4438 | 22479.9772 | 23015.3728 | 23704.0848 | 24039.2806 | 24331.9672 | 23687.3735 | 24395.792 | 25474.6634 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 | 24654.9224 |  | 14948.6731 | 20439.3482 | 21949.1731 | 22223.2673 | 22388.7165 | 22735.2653 | 23549.1259 | 23986.5612 | 24852.927 | 27550.8855 | 25256.0739 | 24778.3727 | 25369.7474 | 26631.071 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244 | 25779.7244
50% | 13990.4644 | 19636.3146 | 21101.8851 | 21395.7902 | 21614.7174 | 21974.2157 | 22785.6338 | 23328.3091 | 24026.3854 | 24366.1388 | 24662.805 | 24009.4469 | 24727.4976 | 25821.0383 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 | 24990.1513 |  | 15151.9278 | 20717.2587 | 22247.6125 | 22525.4334 | 22693.1323 | 23044.3931 | 23869.3196 | 24312.7025 | 25190.8483 | 27925.4904 | 25599.4766 | 25115.2802 | 25714.6957 | 26993.1694 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472 | 26130.2472
45% | 10798.1308 | 15155.7151 | 16286.8728 | 16513.7149 | 16682.6875 | 16960.1557 | 17586.4251 | 18005.2732 | 18544.0629 | 18806.2917 | 19035.2648 | 18530.9894 | 19085.1959 | 19929.2132 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 | 19287.9175 |  | 11694.5724 | 15990.0102 | 17171.169 | 17385.597 | 17515.0305 | 17786.1408 | 18422.8362 | 18765.0484 | 19442.8195 | 21553.4731 | 19758.2074 | 19384.4945 | 19847.1359 | 20833.8883 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671 | 20167.8671
40% | 5305.0724 | 7445.9337 | 8001.6663 | 8113.1128 | 8196.1282 | 8332.4471 | 8640.1304 | 8845.9085 | 9110.6134 | 9239.4453 | 9351.9387 | 9104.1905 | 9376.4696 | 9791.1315 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 | 9476.0658 |  | 5745.49 | 7855.819 | 8436.117 | 8541.4645 | 8605.0545 | 8738.2498 | 9051.0554 | 9219.1826 | 9552.1685 | 10589.1229 | 9707.1171 | 9523.5137 | 9750.8073 | 10235.5942 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381 | 9908.381
35% | 1982.7385 | 2782.8723 | 2990.574 | 3032.2264 | 3063.2529 | 3114.2013 | 3229.196 | 3306.1044 | 3405.0362 | 3453.1863 | 3495.2301 | 3402.6357 | 3504.3984 | 3659.3757 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 | 3541.6218 |  | 2147.3419 | 2936.0645 | 3152.9473 | 3192.3203 | 3216.0867 | 3265.8676 | 3382.7768 | 3445.6133 | 3570.0647 | 3957.6201 | 3627.9758 | 3559.3552 | 3644.3048 | 3825.4909 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197 | 3703.197
30% | 988.8752 | 1387.9357 | 1491.5253 | 1512.2991 | 1527.7733 | 1553.1834 | 1610.5361 | 1648.8936 | 1698.2351 | 1722.2495 | 1743.2185 | 1697.0378 | 1747.7911 | 1825.0849 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 | 1766.356 |  | 1070.9699 | 1464.3391 | 1572.5077 | 1592.1446 | 1603.9979 | 1628.8258 | 1687.1333 | 1718.4725 | 1780.5417 | 1973.8319 | 1809.4244 | 1775.2004 | 1817.5683 | 1907.9335 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404 | 1846.9404
25% | 582.975 | 818.2345 | 879.304 | 891.5509 | 900.6734 | 915.6535 | 949.4649 | 972.0779 | 1001.1663 | 1015.3237 | 1027.6856 | 1000.4605 | 1030.3813 | 1075.9485 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 | 1041.3259 |  | 631.3725 | 863.2768 | 927.0458 | 938.6225 | 945.6104 | 960.2472 | 994.6215 | 1013.097 | 1049.6888 | 1163.6399 | 1066.7162 | 1046.54 | 1071.5173 | 1124.7906 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331 | 1088.8331
20% | 294.605 | 413.4928 | 444.3542 | 450.5431 | 455.1532 | 462.7233 | 479.8098 | 491.2372 | 505.937 | 513.0914 | 519.3384 | 505.5803 | 520.7007 | 543.728 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 | 526.2315 |  | 319.0626 | 436.2549 | 468.4804 | 474.3306 | 477.8619 | 485.2586 | 502.6296 | 511.9661 | 530.4577 | 588.0426 | 539.0624 | 528.8665 | 541.4887 | 568.4102 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392 | 550.2392
15% | 120.0243 | 168.46 | 181.0332 | 183.5546 | 185.4328 | 188.5169 | 195.4781 | 200.1337 | 206.1225 | 209.0372 | 211.5823 | 205.9772 | 212.1373 | 221.5188 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 | 214.3906 |  | 129.9885 | 177.7335 | 190.8624 | 193.2458 | 194.6845 | 197.698 | 204.775 | 208.5788 | 216.1124 | 239.5729 | 219.618 | 215.4641 | 220.6065 | 231.5745 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715 | 224.1715
10% | 48.3215 | 67.8216 | 72.8835 | 73.8986 | 74.6547 | 75.8964 | 78.699 | 80.5733 | 82.9844 | 84.1578 | 85.1825 | 82.9259 | 85.4059 | 89.1829 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 | 86.3131 |  | 52.333 | 71.555 | 76.8407 | 77.8003 | 78.3795 | 79.5927 | 82.4419 | 83.9733 | 87.0063 | 96.4514 | 88.4176 | 86.7453 | 88.8156 | 93.2313 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509 | 90.2509
5% | 41.1512 | 57.7577 | 62.0685 | 62.933 | 63.5769 | 64.6344 | 67.021 | 68.6173 | 70.6706 | 71.6699 | 72.5425 | 70.6207 | 72.7328 | 75.9493 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 | 73.5054 |  | 44.5675 | 60.9372 | 65.4385 | 66.2557 | 66.749 | 67.7822 | 70.2086 | 71.5127 | 74.0957 | 82.1393 | 75.2976 | 73.8734 | 75.6365 | 79.397 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588 | 76.8588
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 110199.0445 | 154669.8554 | 166213.7513 | 168528.761 | 170253.1907 | 173084.8598 | 179476.1774 | 183750.6821 | 189249.2367 | 191925.3816 | 194262.1395 | 189115.8171 | 194771.7054 | 203385.2247 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | 196840.5567 | E @ R (MWh) | 119347.5729 | 163184.1552 | 175238.3313 | 177426.6509 | 178747.5683 | 181514.3531 | 188012.0727 | 191504.4785 | 198421.3911 | 219961.4161 | 201640.0444 | 197826.1621 | 202547.5936 | 212617.7793 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781 | 205820.7781
Option 6 Winter POE50 W E @ R (MWh) N 2 | 77139.3311 | 108268.8988 | 116349.6259 | 117970.1327 | 119177.2335 | 121159.4019 | 125633.3242 | 128625.4775 | 132474.4657 | 134347.7671 | 135983.4976 | 132381.0719 | 136340.1938 | 142369.6573 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | 137788.3897 | Option 6 Winter POE10 W E @ R (MWh) N 2 | 35804.2719 | 48955.2466 | 52571.4994 | 53227.9953 | 53624.2705 | 54454.3059 | 56403.6218 | 57451.3435 | 59526.4173 | 65988.4248 | 60492.0133 | 59347.8486 | 60764.2781 | 63785.3338 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334 | 61746.2334
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 83.0141 | 107.4825 | 113.8862 | 113.5028 | 113.5314 | 114.1888 | 115.9231 | 117.084 | 118.2206 | 119.5499 | 120.7816 | 121.9774 | 122.114 | 123.5097 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516 | 122.4516
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 41.0899 | 53.2011 | 56.3708 | 56.1811 | 56.1952 | 56.5206 | 57.379 | 57.9536 | 58.5162 | 59.1742 | 59.7838 | 60.3758 | 60.4433 | 61.1342 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105 | 60.6105
97% | 17.9572 | 23.9377 | 25.5745 | 25.5337 | 25.5312 | 25.7204 | 25.8941 | 26.3308 | 26.6345 | 26.7756 | 26.9374 | 27.0831 | 27.4138 | 27.7832 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 | 27.7897 |  | 81.3455 | 105.322 | 111.597 | 111.2214 | 111.2494 | 111.8935 | 113.593 | 114.7306 | 115.8443 | 117.1469 | 118.3538 | 119.5256 | 119.6594 | 121.0271 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903 | 119.9903
95% | 88.4047 | 117.8471 | 125.9053 | 125.7044 | 125.6919 | 126.6233 | 127.4788 | 129.6287 | 131.1238 | 131.8183 | 132.6148 | 133.3322 | 134.9601 | 136.7789 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 | 136.811 |  | 120.141 | 155.5525 | 164.8202 | 164.2654 | 164.3068 | 165.2581 | 167.7681 | 169.4482 | 171.0931 | 173.0169 | 174.7995 | 176.5301 | 176.7277 | 178.7477 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164 | 177.2164
90% | 153.3269 | 204.3911 | 218.3671 | 218.0185 | 217.9968 | 219.6122 | 221.096 | 224.8247 | 227.4178 | 228.6223 | 230.0037 | 231.248 | 234.0715 | 237.2258 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 | 237.2815 |  | 520.9239 | 674.466 | 714.6501 | 712.2446 | 712.4239 | 716.5489 | 727.4318 | 734.7168 | 741.8491 | 750.1905 | 757.9195 | 765.4237 | 766.2804 | 775.0388 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992 | 768.3992
85% | 435.1168 | 580.0288 | 619.6904 | 618.7012 | 618.6397 | 623.2239 | 627.4345 | 638.016 | 645.3747 | 648.7931 | 652.7133 | 656.2444 | 664.2569 | 673.2085 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 | 673.3664 |  | 492.7658 | 638.0084 | 676.0203 | 673.7449 | 673.9145 | 677.8165 | 688.1112 | 695.0024 | 701.7491 | 709.6397 | 716.9509 | 724.0494 | 724.8598 | 733.1448 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641 | 726.8641
80% | 607.7821 | 810.199 | 865.5993 | 864.2176 | 864.1317 | 870.5349 | 876.4165 | 891.197 | 901.4758 | 906.2507 | 911.7265 | 916.6588 | 927.8508 | 940.3547 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 | 940.5754 |  | 344.1539 | 445.5932 | 472.1412 | 470.552 | 470.6705 | 473.3957 | 480.5856 | 485.3985 | 490.1105 | 495.6214 | 500.7276 | 505.6853 | 506.2513 | 512.0377 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511 | 507.6511
75% | 1584.3775 | 2112.0415 | 2256.4599 | 2252.8581 | 2252.6341 | 2269.3263 | 2284.6584 | 2323.1885 | 2349.9835 | 2362.4309 | 2376.7053 | 2389.5629 | 2418.7385 | 2451.3337 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 | 2451.9089 |  | 614.2626 | 795.3163 | 842.7005 | 839.864 | 840.0755 | 844.9396 | 857.7724 | 866.3627 | 874.773 | 884.6091 | 893.7229 | 902.5717 | 903.5819 | 913.9097 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803 | 906.0803
70% | 2737.3218 | 3648.9644 | 3898.4755 | 3892.2527 | 3891.8657 | 3920.7047 | 3947.1939 | 4013.7622 | 4060.0557 | 4081.5611 | 4106.223 | 4128.4369 | 4178.8434 | 4235.1581 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 | 4236.1519 |  | 1119.0216 | 1448.8529 | 1535.1742 | 1530.007 | 1530.3922 | 1539.2532 | 1562.6313 | 1578.2805 | 1593.6017 | 1611.5204 | 1628.1235 | 1644.2435 | 1646.0838 | 1664.8982 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353 | 1650.6353
65% | 6874.8447 | 9164.4555 | 9791.108 | 9775.4793 | 9774.5074 | 9846.9371 | 9913.4654 | 10080.6532 | 10196.9204 | 10250.9316 | 10312.8705 | 10368.6614 | 10495.2583 | 10636.6939 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 | 10639.1899 |  | 1407.9023 | 1822.8811 | 1931.4867 | 1924.9855 | 1925.4701 | 1936.6187 | 1966.0319 | 1985.7211 | 2004.9975 | 2027.542 | 2048.4312 | 2068.7126 | 2071.0281 | 2094.6996 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546 | 2076.7546
60% | 10049.1251 | 13395.9039 | 14311.8969 | 14289.052 | 14287.6313 | 14393.5037 | 14490.7497 | 14735.1321 | 14905.0826 | 14984.0321 | 15074.5696 | 15156.1205 | 15341.1702 | 15547.9101 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 | 15551.5584 |  | 2203.1064 | 2852.4713 | 3022.419 | 3012.2458 | 3013.0041 | 3030.4496 | 3076.4759 | 3107.2857 | 3137.4498 | 3172.7277 | 3205.4155 | 3237.1522 | 3240.7754 | 3277.8169 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363 | 3249.7363
55% | 11363.2237 | 15147.6523 | 16183.4274 | 16157.5952 | 16155.9887 | 16275.7057 | 16385.6683 | 16662.008 | 16854.1825 | 16943.456 | 17045.8329 | 17138.048 | 17347.2962 | 17581.0709 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 | 17585.1964 |  | 4233.6145 | 5481.4709 | 5808.052 | 5788.5027 | 5789.9599 | 5823.4841 | 5911.9308 | 5971.1368 | 6029.1017 | 6096.8938 | 6159.7085 | 6220.6955 | 6227.6582 | 6298.8391 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878 | 6244.878
50% | 14590.9152 | 19450.3 | 20780.2841 | 20747.1143 | 20745.0515 | 20898.7738 | 21039.971 | 21394.8041 | 21641.5653 | 21756.1967 | 21887.6534 | 22006.0619 | 22274.7466 | 22574.9243 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 | 22580.2216 |  | 9395.4016 | 12164.693 | 12889.4544 | 12846.0699 | 12849.3037 | 12923.7021 | 13119.9863 | 13251.3785 | 13380.0165 | 13530.4635 | 13669.8641 | 13805.209 | 13820.6608 | 13978.6283 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756 | 13858.8756
45% | 19430.1502 | 25901.2027 | 27672.2904 | 27628.1194 | 27625.3725 | 27830.0784 | 28018.1052 | 28490.6226 | 28819.2247 | 28971.8749 | 29146.9306 | 29304.6107 | 29662.4075 | 30062.1424 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 | 30069.1966 |  | 14237.0213 | 18433.3785 | 19531.6224 | 19465.8812 | 19470.7814 | 19583.5186 | 19880.9516 | 20080.0526 | 20274.98 | 20502.9551 | 20714.1914 | 20919.2819 | 20942.6962 | 21182.0673 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039 | 21000.6039
40% | 13627.6726 | 18166.2574 | 19408.4404 | 19377.4603 | 19375.5338 | 19519.1078 | 19650.9836 | 19982.3919 | 20212.8627 | 20319.9266 | 20442.705 | 20553.2966 | 20804.2436 | 21084.6045 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 | 21089.5521 |  | 14741.7803 | 19086.9151 | 20224.0962 | 20156.0242 | 20161.0981 | 20277.8323 | 20585.8105 | 20791.9704 | 20993.8088 | 21229.8664 | 21448.5919 | 21660.9537 | 21685.1981 | 21933.0559 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588 | 21745.1588
35% | 7065.4673 | 9418.5634 | 10062.5914 | 10046.5293 | 10045.5305 | 10119.9686 | 10188.3415 | 10360.165 | 10479.656 | 10535.1648 | 10598.8211 | 10656.1589 | 10786.2661 | 10931.6234 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 | 10934.1885 |  | 20078.2516 | 25996.3095 | 27545.146 | 27452.4322 | 27459.3429 | 27618.3344 | 28037.7996 | 28318.5887 | 28593.4918 | 28915.0015 | 29212.9048 | 29502.1407 | 29535.1616 | 29872.743 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279 | 29616.8279
30% | 3286.1675 | 4380.5987 | 4680.1378 | 4672.6673 | 4672.2027 | 4706.8241 | 4738.6245 | 4818.5401 | 4874.1157 | 4899.933 | 4929.5397 | 4956.2076 | 5016.7208 | 5084.3269 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 | 5085.5199 |  | 18553.5455 | 24022.1968 | 25453.4175 | 25367.7442 | 25374.1301 | 25521.0481 | 25908.6599 | 26168.1263 | 26422.1538 | 26719.2486 | 26994.5297 | 27261.8016 | 27292.3149 | 27604.261 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796 | 27367.7796
25% | 2243.729 | 2990.9846 | 3195.5039 | 3190.4032 | 3190.086 | 3213.7248 | 3235.4375 | 3290.0022 | 3327.9481 | 3345.5756 | 3365.7905 | 3383.9989 | 3425.316 | 3471.4761 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 | 3472.2907 |  | 5351.5932 | 6928.9735 | 7341.7954 | 7317.0838 | 7318.9257 | 7361.3028 | 7473.1058 | 7547.9464 | 7621.2182 | 7706.9124 | 7786.3146 | 7863.4066 | 7872.2079 | 7962.1857 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749 | 7893.9749
20% | 1359.2219 | 1811.8996 | 1935.7947 | 1932.7048 | 1932.5126 | 1946.8327 | 1959.9859 | 1993.0405 | 2016.0277 | 2026.7062 | 2038.9521 | 2049.9825 | 2075.0119 | 2102.9751 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 | 2103.4685 |  | 1436.0604 | 1859.3387 | 1970.1164 | 1963.4852 | 1963.9795 | 1975.3511 | 2005.3526 | 2025.4355 | 2045.0974 | 2068.0928 | 2089.3998 | 2110.0869 | 2112.4486 | 2136.5935 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897 | 2118.2897
15% | 870.2335 | 1160.0577 | 1239.3808 | 1237.4024 | 1237.2794 | 1246.4477 | 1254.869 | 1276.0321 | 1290.7494 | 1297.5863 | 1305.4266 | 1312.4888 | 1328.5137 | 1346.417 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 | 1346.7329 |  | 792.0754 | 1025.5394 | 1086.6401 | 1082.9826 | 1083.2552 | 1089.5273 | 1106.075 | 1117.152 | 1127.9967 | 1140.6801 | 1152.4322 | 1163.8424 | 1165.1451 | 1178.4625 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667 | 1168.3667
10% | 582.4579 | 776.4407 | 829.5326 | 828.2085 | 828.1262 | 834.2626 | 839.8991 | 854.0638 | 863.9143 | 868.4903 | 873.7379 | 878.4647 | 889.1904 | 901.1733 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 | 901.3847 |  | 185.1131 | 239.6751 | 253.9547 | 253.0999 | 253.1637 | 254.6295 | 258.4968 | 261.0855 | 263.62 | 266.5842 | 269.3308 | 271.9974 | 272.3018 | 275.4142 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548 | 273.0548
5% | 414.3969 | 552.4084 | 590.1813 | 589.2393 | 589.1807 | 593.5465 | 597.5567 | 607.6343 | 614.6426 | 617.8982 | 621.6317 | 624.9947 | 632.6256 | 641.1509 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 | 641.3014 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 36.3748 | 48.4892 | 51.8048 | 51.7221 | 51.717 | 52.1002 | 52.4522 | 53.3368 | 53.952 | 54.2377 | 54.5655 | 54.8606 | 55.5305 | 56.2788 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 | 56.292 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 97418.2674 | 129862.6237 | 138742.4466 | 138520.9835 | 138507.2114 | 139533.5592 | 140476.2819 | 142845.3746 | 144492.9097 | 145258.2621 | 146135.9511 | 146926.5221 | 148720.4324 | 150724.6103 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | 150759.9785 | E @ R (MWh) | 96032.1838 | 124337.6376 | 131745.5613 | 131302.1206 | 131335.1737 | 132095.6136 | 134101.872 | 135444.8567 | 136759.6897 | 138297.4372 | 139722.2775 | 141105.6629 | 141263.5984 | 142878.215 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995 | 141654.1995
Option 6 Summer POE50 W E @ R (MWh) N 2 | 68192.7872 | 90903.8366 | 97119.7126 | 96964.6884 | 96955.048 | 97673.4915 | 98333.3973 | 99991.7622 | 101145.0368 | 101680.7835 | 102295.1657 | 102848.5654 | 104104.3027 | 105507.2272 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | 105531.9849 | Option 6 Summer POE10 W E @ R (MWh) N 2 | 28809.6551 | 37301.2913 | 39523.6684 | 39390.6362 | 39400.5521 | 39628.6841 | 40230.5616 | 40633.457 | 41027.9069 | 41489.2312 | 41916.6832 | 42331.6989 | 42379.0795 | 42863.4645 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599 | 42496.2599
Option 7 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 110.3988 | 111.3674 | 113.0455 | 116.8717 | 119.4274 | 122.671 | 124.3515 | 125.8258 | 123.0846 | 126.2829 | 131.3148 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 |  | 78.6411 | 106.5944 | 114.2314 | 115.4081 | 116.1495 | 117.791 | 121.6771 | 123.7926 | 127.8346 | 140.1348 | 129.9793 | 127.9882 | 130.6605 | 136.5124 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403
98% | 87.3027 | 120.9335 | 129.6647 | 131.1472 | 132.2978 | 134.2912 | 138.8365 | 141.8726 | 145.7258 | 147.722 | 149.4734 | 146.2171 | 150.0165 | 155.9941 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 |  | 93.4209 | 126.6277 | 135.7001 | 137.0978 | 137.9786 | 139.9286 | 144.5451 | 147.0581 | 151.8598 | 166.4717 | 154.4076 | 152.0423 | 155.2168 | 162.1685 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499
97% | 172.8327 | 239.4116 | 256.6966 | 259.6314 | 261.9093 | 265.8557 | 274.854 | 280.8645 | 288.4926 | 292.4446 | 295.9119 | 289.4652 | 296.9869 | 308.8207 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 |  | 184.945 | 250.6842 | 268.6448 | 271.4119 | 273.1556 | 277.0161 | 286.1552 | 291.1302 | 300.6362 | 329.5634 | 305.68 | 300.9974 | 307.2819 | 321.0443 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028
95% | 510.5211 | 707.185 | 758.2422 | 766.9113 | 773.6398 | 785.297 | 811.8764 | 829.6304 | 852.1628 | 863.8365 | 874.0782 | 855.0358 | 877.2537 | 912.2089 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 |  | 546.299 | 740.4826 | 793.5354 | 801.7091 | 806.8595 | 818.2629 | 845.2585 | 859.9539 | 888.0332 | 973.4795 | 902.9316 | 889.1001 | 907.6635 | 948.3155 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222
90% | 2814.8088 | 3899.1347 | 4180.6436 | 4228.4418 | 4265.5399 | 4329.8131 | 4476.3615 | 4574.25 | 4698.4845 | 4762.8484 | 4819.3169 | 4714.3248 | 4836.8255 | 5029.5548 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 |  | 3012.0741 | 4082.7244 | 4375.2363 | 4420.3027 | 4448.7 | 4511.5741 | 4660.4169 | 4741.4413 | 4896.2592 | 5367.3759 | 4978.4031 | 4902.1418 | 5004.4932 | 5228.6319 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935
85% | 6876.3763 | 9525.3066 | 10213.0129 | 10329.7805 | 10420.4084 | 10577.4231 | 10935.4305 | 11174.565 | 11478.0609 | 11635.2975 | 11773.246 | 11516.7578 | 11816.0183 | 12286.8422 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 |  | 7358.2813 | 9973.8032 | 10688.3888 | 10798.4829 | 10867.8555 | 11021.4524 | 11385.0646 | 11583.0015 | 11961.2104 | 13112.1147 | 12161.8821 | 11975.5812 | 12225.6185 | 12773.1733 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51
80% | 10687.9274 | 14805.1503 | 15874.0497 | 16055.5412 | 16196.4038 | 16440.4513 | 16996.9008 | 17368.5868 | 17840.3094 | 18084.7017 | 18299.1145 | 17900.4559 | 18365.5953 | 19097.3952 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 |  | 11436.9506 | 15502.2469 | 16612.9248 | 16784.0437 | 16891.8693 | 17130.6044 | 17695.7655 | 18003.4182 | 18591.267 | 20380.1135 | 18903.1703 | 18613.6034 | 19002.2355 | 19853.298 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623
75% | 11791.7667 | 16334.2127 | 17513.507 | 17713.7428 | 17869.1536 | 18138.406 | 18752.3252 | 19162.3985 | 19682.8403 | 19952.4731 | 20189.0303 | 19749.1986 | 20262.3772 | 21069.7567 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 |  | 12618.1483 | 17103.3048 | 18328.6925 | 18517.4844 | 18636.4461 | 18899.8376 | 19523.368 | 19862.7948 | 20511.356 | 22484.9529 | 20855.4725 | 20535.9993 | 20964.769 | 21903.7284 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917
70% | 12669.5942 | 17550.1984 | 18817.2842 | 19032.4264 | 19199.4066 | 19488.7033 | 20148.3251 | 20588.926 | 21148.1115 | 21437.817 | 21691.9844 | 21219.4098 | 21770.7916 | 22638.2758 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 |  | 13557.495 | 18376.5449 | 19693.1554 | 19896.0018 | 20023.8195 | 20306.8189 | 20976.7675 | 21341.4626 | 22038.3054 | 24158.8249 | 22408.0393 | 22064.7832 | 22525.4722 | 23534.3317 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549
65% | 13351.323 | 18494.5441 | 19829.8096 | 20056.5282 | 20232.4932 | 20537.3565 | 21232.4714 | 21696.7803 | 22286.0546 | 22591.3486 | 22859.1924 | 22361.1894 | 22942.24 | 23856.402 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 |  | 14287.0002 | 19365.3548 | 20752.8099 | 20966.571 | 21101.2664 | 21399.4935 | 22105.4909 | 22489.8096 | 23224.1482 | 25458.7693 | 23613.7769 | 23252.0508 | 23737.5287 | 24800.6731 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435
60% | 14698.1621 | 20360.2151 | 21830.1779 | 22079.7671 | 22273.483 | 22609.0999 | 23374.3358 | 23885.4827 | 24534.2012 | 24870.2922 | 25165.1552 | 24616.9152 | 25256.5804 | 26262.9602 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 |  | 15728.2275 | 21318.8704 | 22846.2875 | 23081.6122 | 23229.8952 | 23558.2066 | 24335.4227 | 24758.5102 | 25566.9267 | 28026.9692 | 25995.8598 | 25597.644 | 26132.0954 | 27302.4864 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611
55% | 16350.7821 | 22649.4603 | 24284.7017 | 24562.354 | 24777.8508 | 25151.2035 | 26002.4804 | 26571.0991 | 27292.7577 | 27666.6379 | 27994.6544 | 27384.7719 | 28096.3592 | 29215.8935 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 |  | 17496.6651 | 23715.9042 | 25415.0598 | 25676.8438 | 25841.7993 | 26207.0251 | 27071.6291 | 27542.2874 | 28441.6 | 31178.2427 | 28918.7611 | 28475.7711 | 29070.3146 | 30372.3011 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529
50% | 16573.101 | 22957.4214 | 24614.8968 | 24896.3244 | 25114.7512 | 25493.1803 | 26356.0319 | 26932.3821 | 27663.8529 | 28042.8167 | 28375.2932 | 27757.1182 | 28478.3809 | 29613.1373 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 |  | 17734.5645 | 24038.3655 | 25760.6242 | 26025.9676 | 26193.1661 | 26563.3577 | 27439.7177 | 27916.7755 | 28828.3158 | 31602.1683 | 29311.9648 | 28862.9515 | 29465.579 | 30785.2684 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039
45% | 12791.4633 | 17719.0143 | 18998.2882 | 19215.4999 | 19384.0862 | 19676.1657 | 20342.1324 | 20786.9714 | 21351.5358 | 21644.0279 | 21900.6402 | 21423.5199 | 21980.2054 | 22856.034 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 |  | 13687.9049 | 18553.3094 | 19882.5844 | 20087.382 | 20216.4292 | 20502.1508 | 21178.5436 | 21546.7467 | 22250.2924 | 24391.2093 | 22623.5828 | 22277.025 | 22742.1454 | 23760.7091 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395
40% | 6284.3875 | 8705.2708 | 9333.7723 | 9440.4874 | 9523.3131 | 9666.8104 | 9993.9968 | 10212.5442 | 10489.9121 | 10633.6121 | 10759.6846 | 10525.2775 | 10798.7746 | 11229.0652 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 |  | 6724.8052 | 9115.1562 | 9768.223 | 9868.8391 | 9932.2394 | 10072.6131 | 10404.9218 | 10585.8183 | 10931.4671 | 11983.2898 | 11114.863 | 10944.6007 | 11173.1122 | 11673.5279 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612
35% | 2348.7515 | 3253.5419 | 3488.4405 | 3528.3246 | 3559.2802 | 3612.9114 | 3735.1954 | 3816.8761 | 3920.5407 | 3974.2477 | 4021.3665 | 3933.7583 | 4035.9762 | 4196.7946 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 |  | 2513.3549 | 3406.7341 | 3650.8138 | 3688.4184 | 3712.1139 | 3764.5777 | 3888.7761 | 3956.3851 | 4085.5692 | 4478.6815 | 4154.1123 | 4090.4778 | 4175.8826 | 4362.9099 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1759.7242 | 1775.163 | 1801.9112 | 1862.8993 | 1903.637 | 1955.3388 | 1982.1248 | 2005.6249 | 1961.931 | 2012.9114 | 2093.1183 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 |  | 1253.516 | 1699.0818 | 1820.8147 | 1839.5697 | 1851.3876 | 1877.5536 | 1939.4965 | 1973.2159 | 2037.6455 | 2233.7072 | 2071.8308 | 2040.0936 | 2082.6886 | 2175.967 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525
25% | 690.592 | 956.6232 | 1025.6893 | 1037.4162 | 1046.5179 | 1062.2869 | 1098.2414 | 1122.2576 | 1152.7376 | 1168.5288 | 1182.3829 | 1156.6239 | 1186.6785 | 1233.9632 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 |  | 738.9896 | 1001.6655 | 1073.4311 | 1084.4878 | 1091.4549 | 1106.8806 | 1143.398 | 1163.2767 | 1201.2601 | 1316.845 | 1221.4135 | 1202.7034 | 1227.8145 | 1282.8053 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793
20% | 348.989 | 483.4272 | 518.3296 | 524.2558 | 528.8553 | 536.8241 | 554.9937 | 567.1302 | 582.5332 | 590.5132 | 597.5144 | 584.4971 | 599.6851 | 623.5803 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 |  | 373.4466 | 506.1893 | 542.4558 | 548.0433 | 551.5641 | 559.3594 | 577.8134 | 587.8591 | 607.0539 | 665.4645 | 617.2384 | 607.7833 | 620.4731 | 648.2626 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999
15% | 142.1807 | 196.9518 | 211.1713 | 213.5857 | 215.4596 | 218.7061 | 226.1085 | 231.053 | 237.3283 | 240.5795 | 243.4318 | 238.1285 | 244.3162 | 254.0512 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 |  | 152.1449 | 206.2253 | 221.0005 | 223.2769 | 224.7113 | 227.8872 | 235.4055 | 239.4982 | 247.3183 | 271.1152 | 251.4675 | 247.6154 | 252.7853 | 264.107 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222
10% | 57.2416 | 79.2923 | 85.017 | 85.989 | 86.7435 | 88.0505 | 91.0307 | 93.0214 | 95.5478 | 96.8567 | 98.005 | 95.8699 | 98.3611 | 102.2804 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 |  | 61.2531 | 83.0258 | 88.9742 | 89.8907 | 90.4682 | 91.7468 | 94.7736 | 96.4213 | 99.5697 | 109.1503 | 101.2402 | 99.6893 | 101.7707 | 106.3288 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349
5% | 48.7477 | 67.5263 | 72.4016 | 73.2294 | 73.8719 | 74.985 | 77.5229 | 79.2182 | 81.3697 | 82.4844 | 83.4623 | 81.644 | 83.7655 | 87.1033 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 |  | 52.164 | 70.7058 | 75.7716 | 76.5521 | 77.0439 | 78.1327 | 80.7104 | 82.1137 | 84.7948 | 92.9538 | 86.2174 | 84.8967 | 86.6693 | 90.551 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 196101.5072 | 197821.9953 | 200802.7777 | 207599.2223 | 212138.9744 | 217900.5692 | 220885.5628 | 223504.3892 | 218635.1944 | 224316.3823 | 233254.5468 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 204999.3971 | 206316.373 | 209232.2711 | 216135.1177 | 219892.7708 | 227072.7236 | 248921.5973 | 230882.2942 | 227345.5395 | 232092.2705 | 242487.1014 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111
Option 7 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 137271.0551 | 138475.3967 | 140561.9444 | 145319.4556 | 148497.2821 | 152530.3985 | 154619.8939 | 156453.0725 | 153044.6361 | 157021.4676 | 163278.1828 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | Option 7 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 61499.8191 | 61894.9119 | 62769.6813 | 64840.5353 | 65967.8312 | 68121.8171 | 74676.4792 | 69264.6882 | 68203.6618 | 69627.6812 | 72746.1304 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 129.304 | 129.3303 | 130.0731 | 132.0395 | 133.3525 | 134.6398 | 136.1461 | 137.5394 | 138.8941 | 139.0451 | 140.6269 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 64.0022 | 64.0152 | 64.3829 | 65.3562 | 66.0061 | 66.6433 | 67.3889 | 68.0786 | 68.7491 | 68.8238 | 69.6068 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097
97% | 20.8131 | 27.6102 | 29.4592 | 29.4046 | 29.4015 | 29.6116 | 29.8423 | 30.3162 | 30.6568 | 30.8412 | 31.0426 | 31.2273 | 31.5615 | 31.9765 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 |  | 92.7689 | 120.0119 | 127.1357 | 126.7049 | 126.7307 | 127.4585 | 129.3855 | 130.672 | 131.9335 | 133.4095 | 134.7748 | 136.1022 | 136.2502 | 137.8002 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181
95% | 102.4643 | 135.9269 | 145.0299 | 144.761 | 144.7458 | 145.7802 | 146.9157 | 149.2489 | 150.9258 | 151.8338 | 152.8252 | 153.7342 | 155.3796 | 157.4227 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 |  | 137.0126 | 177.2483 | 187.7696 | 187.1334 | 187.1714 | 188.2465 | 191.0924 | 192.9925 | 194.8556 | 197.0355 | 199.052 | 201.0125 | 201.2311 | 203.5203 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745
90% | 177.7116 | 235.7483 | 251.5362 | 251.0698 | 251.0434 | 252.8375 | 254.8069 | 258.8536 | 261.762 | 263.3368 | 265.0563 | 266.6327 | 269.4865 | 273.03 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 |  | 594.078 | 768.5376 | 814.1574 | 811.3985 | 811.5637 | 816.2249 | 828.5646 | 836.8035 | 844.8817 | 854.3338 | 863.0771 | 871.5778 | 872.5255 | 882.4514 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815
85% | 504.3166 | 669.0154 | 713.8189 | 712.4955 | 712.4205 | 717.5119 | 723.1007 | 734.5845 | 742.838 | 747.307 | 752.1867 | 756.6605 | 764.759 | 774.815 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 |  | 561.9657 | 726.995 | 770.1489 | 767.5392 | 767.6954 | 772.1046 | 783.7774 | 791.5709 | 799.2124 | 808.1536 | 816.4243 | 824.4655 | 825.362 | 834.7513 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906
80% | 704.4422 | 934.4978 | 997.0804 | 995.2318 | 995.1271 | 1002.2389 | 1010.0454 | 1026.0863 | 1037.6149 | 1043.8574 | 1050.6735 | 1056.9226 | 1068.2348 | 1082.2812 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 |  | 392.484 | 507.7425 | 537.8818 | 536.0591 | 536.1682 | 539.2477 | 547.4001 | 552.8431 | 558.1801 | 564.4247 | 570.2011 | 575.8172 | 576.4433 | 583.0009 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998
75% | 1836.3528 | 2436.0657 | 2599.2074 | 2594.3882 | 2594.1154 | 2612.6546 | 2633.0048 | 2674.8204 | 2704.8735 | 2721.1465 | 2738.9148 | 2755.205 | 2784.6939 | 2821.3104 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 |  | 700.5244 | 906.2435 | 960.0375 | 956.7843 | 956.979 | 962.4754 | 977.0262 | 986.7412 | 996.2669 | 1007.4126 | 1017.7226 | 1027.7464 | 1028.8639 | 1040.5683 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421
70% | 3172.6584 | 4208.7797 | 4490.6388 | 4482.3127 | 4481.8414 | 4513.8714 | 4549.0304 | 4621.275 | 4673.1976 | 4701.3124 | 4732.0106 | 4760.1551 | 4811.103 | 4874.3651 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1743.0043 | 1743.359 | 1753.372 | 1779.8796 | 1797.5778 | 1814.931 | 1835.2355 | 1854.0175 | 1872.2783 | 1874.3141 | 1895.6364 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751
65% | 7968.2023 | 10570.444 | 11278.3393 | 11257.4282 | 11256.2445 | 11336.6886 | 11424.9912 | 11606.4352 | 11736.84 | 11807.4509 | 11884.55 | 11955.2357 | 12083.1924 | 12242.0767 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 |  | 1605.6162 | 2077.1285 | 2200.4254 | 2192.969 | 2193.4153 | 2206.0132 | 2239.3639 | 2261.631 | 2283.4639 | 2309.0102 | 2332.6409 | 2355.6158 | 2358.1771 | 2385.0038 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446
60% | 11647.312 | 15451.0709 | 16485.8185 | 16455.2522 | 16453.5219 | 16571.109 | 16700.1831 | 16965.4041 | 17156.0199 | 17259.2335 | 17371.9312 | 17475.2541 | 17662.2915 | 17894.5364 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 |  | 2512.492 | 3250.3215 | 3443.2583 | 3431.5904 | 3432.2888 | 3452.0021 | 3504.1898 | 3539.0337 | 3573.1982 | 3613.1734 | 3650.151 | 3686.1024 | 3690.1105 | 3732.0893 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745
55% | 13170.4015 | 17471.5683 | 18641.6273 | 18607.0639 | 18605.1073 | 18738.071 | 18884.0238 | 19183.9271 | 19399.4692 | 19516.1798 | 19643.6146 | 19760.4488 | 19971.9446 | 20234.5597 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 |  | 4828.1473 | 6246.0024 | 6616.7608 | 6594.3391 | 6595.6811 | 6633.5633 | 6733.8501 | 6800.8082 | 6866.4607 | 6943.2792 | 7014.3375 | 7083.4238 | 7091.1259 | 7171.7949 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733
50% | 16911.4168 | 22434.3178 | 23936.7286 | 23892.3477 | 23889.8353 | 24060.567 | 24247.9772 | 24633.0672 | 24909.8334 | 25059.6953 | 25223.3277 | 25373.3483 | 25644.9189 | 25982.129 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 |  | 10714.812 | 13861.3711 | 14684.1724 | 14634.4134 | 14637.3915 | 14721.4613 | 14944.0217 | 15092.6176 | 15238.3161 | 15408.7947 | 15566.4901 | 15719.8092 | 15736.9019 | 15915.9256 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945
45% | 22520.2713 | 29874.9022 | 31875.6039 | 31816.5035 | 31813.1579 | 32040.5146 | 32290.0814 | 32802.8907 | 33171.4494 | 33371.0147 | 33588.9175 | 33788.694 | 34150.3339 | 34599.3834 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 |  | 16236.3476 | 21004.3853 | 22251.1909 | 22175.7903 | 22180.3031 | 22307.6955 | 22644.9453 | 22870.1153 | 23090.8949 | 23349.2243 | 23588.1829 | 23820.5101 | 23846.4109 | 24117.6889 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008
40% | 15794.9825 | 20953.2804 | 22356.5072 | 22315.0562 | 22312.7097 | 22472.1702 | 22647.2082 | 23006.8759 | 23265.371 | 23405.3395 | 23558.1694 | 23698.2861 | 23951.9286 | 24266.8772 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 |  | 16811.9908 | 21749.0744 | 23040.0842 | 22962.0103 | 22966.6831 | 23098.592 | 23447.7987 | 23680.9519 | 23909.559 | 24177.0472 | 24424.4778 | 24665.0419 | 24691.8611 | 24972.7569 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339
35% | 8189.141 | 10863.5364 | 11591.06 | 11569.5691 | 11568.3525 | 11651.0272 | 11741.7782 | 11928.2532 | 12062.2738 | 12134.8425 | 12214.0795 | 12286.725 | 12418.2297 | 12581.5194 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 |  | 22897.8708 | 29622.1608 | 31380.5115 | 31274.1752 | 31280.5395 | 31460.199 | 31935.8172 | 32253.3711 | 32564.7331 | 32929.051 | 33266.0507 | 33593.6981 | 33630.2257 | 34012.8048 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338
30% | 3808.7911 | 5052.6595 | 5391.0326 | 5381.0371 | 5380.4713 | 5418.9235 | 5461.132 | 5547.8621 | 5610.1954 | 5643.9473 | 5680.8006 | 5714.5882 | 5775.7514 | 5851.6979 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 |  | 21159.0479 | 27372.7075 | 28997.5323 | 28899.2709 | 28905.152 | 29071.1685 | 29510.6691 | 29804.1085 | 30091.8262 | 30428.4785 | 30739.887 | 31042.6535 | 31076.4072 | 31429.934 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195
25% | 2600.5659 | 3449.8542 | 3680.8886 | 3674.0639 | 3673.6775 | 3699.9319 | 3728.7511 | 3787.9686 | 3830.5285 | 3853.5736 | 3878.7363 | 3901.8059 | 3943.5668 | 3995.4216 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 |  | 6103.1255 | 7895.3963 | 8364.0615 | 8335.719 | 8337.4153 | 8385.3012 | 8512.071 | 8596.7107 | 8679.7002 | 8776.8043 | 8866.6271 | 8953.9572 | 8963.6932 | 9065.6646 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969
20% | 1575.389 | 2089.8768 | 2229.8344 | 2225.7001 | 2225.4661 | 2241.3706 | 2258.8289 | 2294.7021 | 2320.4843 | 2334.4448 | 2349.688 | 2363.6632 | 2388.9615 | 2420.3744 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 |  | 1637.7285 | 2118.6711 | 2244.4339 | 2236.8284 | 2237.2836 | 2250.1334 | 2284.1512 | 2306.8636 | 2329.1332 | 2355.1904 | 2379.2937 | 2402.7281 | 2405.3406 | 2432.7039 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1424.9909 | 1424.8411 | 1435.0239 | 1446.2014 | 1469.169 | 1485.676 | 1494.614 | 1504.3734 | 1513.321 | 1529.518 | 1549.63 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 |  | 903.3078 | 1168.5771 | 1237.943 | 1233.7481 | 1233.9992 | 1241.0867 | 1259.8495 | 1272.3769 | 1284.6599 | 1299.032 | 1312.3265 | 1325.252 | 1326.693 | 1341.7855 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753
10% | 675.0905 | 895.5604 | 955.5354 | 953.7638 | 953.6635 | 960.4789 | 967.9602 | 983.3327 | 994.381 | 1000.3634 | 1006.8954 | 1012.8841 | 1023.725 | 1037.1862 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 |  | 211.1088 | 273.1039 | 289.3152 | 288.3348 | 288.3935 | 290.0499 | 294.4349 | 297.3626 | 300.2332 | 303.5921 | 306.6991 | 309.7199 | 310.0566 | 313.5838 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938
5% | 480.3015 | 637.1576 | 679.8276 | 678.5671 | 678.4957 | 683.3447 | 688.6673 | 699.6043 | 707.4647 | 711.721 | 716.3683 | 720.629 | 728.3419 | 737.919 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 59.5631 | 59.5568 | 59.9825 | 60.4497 | 61.4097 | 62.0997 | 62.4733 | 62.8812 | 63.2552 | 63.9322 | 64.7729 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 159520.5704 | 159503.7964 | 160643.7099 | 161894.98 | 164466.0868 | 166313.955 | 167314.5287 | 168407.043 | 169408.6762 | 171221.8548 | 173473.2847 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 149581.1188 | 149611.5589 | 150470.8515 | 152745.6837 | 154264.5107 | 155753.7228 | 157496.2176 | 159108.0516 | 160675.1553 | 160849.8627 | 162679.6988 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885
Option 7 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 111664.3993 | 111652.6574 | 112450.5969 | 113326.486 | 115126.2607 | 116419.7685 | 117120.1701 | 117884.9301 | 118586.0733 | 119855.2983 | 121431.2993 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | Option 7 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 44874.3356 | 44883.4677 | 45141.2555 | 45823.7051 | 46279.3532 | 46726.1168 | 47248.8653 | 47732.4155 | 48202.5466 | 48254.9588 | 48803.9096 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566
Option 8 -
Winter Season | [30 empty] | Winter Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
99% | 73.4908 | 101.8011 | 109.1509 | 110.3988 | 111.3674 | 113.0455 | 116.8717 | 119.4274 | 122.671 | 124.3515 | 125.8258 | 123.0846 | 126.2829 | 131.3148 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 | 127.4847 |  | 78.6411 | 106.5944 | 114.2314 | 115.4081 | 116.1495 | 117.791 | 121.6771 | 123.7926 | 127.8346 | 140.1348 | 129.9793 | 127.9882 | 130.6605 | 136.5124 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403 | 132.5403
98% | 87.3027 | 120.9335 | 129.6647 | 131.1472 | 132.2978 | 134.2912 | 138.8365 | 141.8726 | 145.7258 | 147.722 | 149.4734 | 146.2171 | 150.0165 | 155.9941 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 | 151.4442 |  | 93.4209 | 126.6277 | 135.7001 | 137.0978 | 137.9786 | 139.9286 | 144.5451 | 147.0581 | 151.8598 | 166.4717 | 154.4076 | 152.0423 | 155.2168 | 162.1685 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499 | 157.4499
97% | 172.8327 | 239.4116 | 256.6966 | 259.6314 | 261.9093 | 265.8557 | 274.854 | 280.8645 | 288.4926 | 292.4446 | 295.9119 | 289.4652 | 296.9869 | 308.8207 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 | 299.8133 |  | 184.945 | 250.6842 | 268.6448 | 271.4119 | 273.1556 | 277.0161 | 286.1552 | 291.1302 | 300.6362 | 329.5634 | 305.68 | 300.9974 | 307.2819 | 321.0443 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028 | 311.7028
95% | 510.5211 | 707.185 | 758.2422 | 766.9113 | 773.6398 | 785.297 | 811.8764 | 829.6304 | 852.1628 | 863.8365 | 874.0782 | 855.0358 | 877.2537 | 912.2089 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 | 885.6025 |  | 546.299 | 740.4826 | 793.5354 | 801.7091 | 806.8595 | 818.2629 | 845.2585 | 859.9539 | 888.0332 | 973.4795 | 902.9316 | 889.1001 | 907.6635 | 948.3155 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222 | 920.7222
90% | 2814.8088 | 3899.1347 | 4180.6436 | 4228.4418 | 4265.5399 | 4329.8131 | 4476.3615 | 4574.25 | 4698.4845 | 4762.8484 | 4819.3169 | 4714.3248 | 4836.8255 | 5029.5548 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 | 4882.8573 |  | 3012.0741 | 4082.7244 | 4375.2363 | 4420.3027 | 4448.7 | 4511.5741 | 4660.4169 | 4741.4413 | 4896.2592 | 5367.3759 | 4978.4031 | 4902.1418 | 5004.4932 | 5228.6319 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935 | 5076.4935
85% | 6876.3763 | 9525.3066 | 10213.0129 | 10329.7805 | 10420.4084 | 10577.4231 | 10935.4305 | 11174.565 | 11478.0609 | 11635.2975 | 11773.246 | 11516.7578 | 11816.0183 | 12286.8422 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 | 11928.4707 |  | 7358.2813 | 9973.8032 | 10688.3888 | 10798.4829 | 10867.8555 | 11021.4524 | 11385.0646 | 11583.0015 | 11961.2104 | 13112.1147 | 12161.8821 | 11975.5812 | 12225.6185 | 12773.1733 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51 | 12401.51
80% | 10687.9274 | 14805.1503 | 15874.0497 | 16055.5412 | 16196.4038 | 16440.4513 | 16996.9008 | 17368.5868 | 17840.3094 | 18084.7017 | 18299.1145 | 17900.4559 | 18365.5953 | 19097.3952 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 | 18540.3797 |  | 11436.9506 | 15502.2469 | 16612.9248 | 16784.0437 | 16891.8693 | 17130.6044 | 17695.7655 | 18003.4182 | 18591.267 | 20380.1135 | 18903.1703 | 18613.6034 | 19002.2355 | 19853.298 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623 | 19275.623
75% | 11791.7667 | 16334.2127 | 17513.507 | 17713.7428 | 17869.1536 | 18138.406 | 18752.3252 | 19162.3985 | 19682.8403 | 19952.4731 | 20189.0303 | 19749.1986 | 20262.3772 | 21069.7567 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 | 20455.2132 |  | 12618.1483 | 17103.3048 | 18328.6925 | 18517.4844 | 18636.4461 | 18899.8376 | 19523.368 | 19862.7948 | 20511.356 | 22484.9529 | 20855.4725 | 20535.9993 | 20964.769 | 21903.7284 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917 | 21266.3917
70% | 12669.5942 | 17550.1984 | 18817.2842 | 19032.4264 | 19199.4066 | 19488.7033 | 20148.3251 | 20588.926 | 21148.1115 | 21437.817 | 21691.9844 | 21219.4098 | 21770.7916 | 22638.2758 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 | 21977.983 |  | 13557.495 | 18376.5449 | 19693.1554 | 19896.0018 | 20023.8195 | 20306.8189 | 20976.7675 | 21341.4626 | 22038.3054 | 24158.8249 | 22408.0393 | 22064.7832 | 22525.4722 | 23534.3317 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549 | 22849.549
65% | 13351.323 | 18494.5441 | 19829.8096 | 20056.5282 | 20232.4932 | 20537.3565 | 21232.4714 | 21696.7803 | 22286.0546 | 22591.3486 | 22859.1924 | 22361.1894 | 22942.24 | 23856.402 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 | 23160.5801 |  | 14287.0002 | 19365.3548 | 20752.8099 | 20966.571 | 21101.2664 | 21399.4935 | 22105.4909 | 22489.8096 | 23224.1482 | 25458.7693 | 23613.7769 | 23252.0508 | 23737.5287 | 24800.6731 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435 | 24079.0435
60% | 14698.1621 | 20360.2151 | 21830.1779 | 22079.7671 | 22273.483 | 22609.0999 | 23374.3358 | 23885.4827 | 24534.2012 | 24870.2922 | 25165.1552 | 24616.9152 | 25256.5804 | 26262.9602 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 | 25496.946 |  | 15728.2275 | 21318.8704 | 22846.2875 | 23081.6122 | 23229.8952 | 23558.2066 | 24335.4227 | 24758.5102 | 25566.9267 | 28026.9692 | 25995.8598 | 25597.644 | 26132.0954 | 27302.4864 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611 | 26508.0611
55% | 16350.7821 | 22649.4603 | 24284.7017 | 24562.354 | 24777.8508 | 25151.2035 | 26002.4804 | 26571.0991 | 27292.7577 | 27666.6379 | 27994.6544 | 27384.7719 | 28096.3592 | 29215.8935 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 | 28363.7508 |  | 17496.6651 | 23715.9042 | 25415.0598 | 25676.8438 | 25841.7993 | 26207.0251 | 27071.6291 | 27542.2874 | 28441.6 | 31178.2427 | 28918.7611 | 28475.7711 | 29070.3146 | 30372.3011 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529 | 29488.5529
50% | 16573.101 | 22957.4214 | 24614.8968 | 24896.3244 | 25114.7512 | 25493.1803 | 26356.0319 | 26932.3821 | 27663.8529 | 28042.8167 | 28375.2932 | 27757.1182 | 28478.3809 | 29613.1373 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 | 28749.4081 |  | 17734.5645 | 24038.3655 | 25760.6242 | 26025.9676 | 26193.1661 | 26563.3577 | 27439.7177 | 27916.7755 | 28828.3158 | 31602.1683 | 29311.9648 | 28862.9515 | 29465.579 | 30785.2684 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039 | 29889.5039
45% | 12791.4633 | 17719.0143 | 18998.2882 | 19215.4999 | 19384.0862 | 19676.1657 | 20342.1324 | 20786.9714 | 21351.5358 | 21644.0279 | 21900.6402 | 21423.5199 | 21980.2054 | 22856.034 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 | 22189.3899 |  | 13687.9049 | 18553.3094 | 19882.5844 | 20087.382 | 20216.4292 | 20502.1508 | 21178.5436 | 21546.7467 | 22250.2924 | 24391.2093 | 22623.5828 | 22277.025 | 22742.1454 | 23760.7091 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395 | 23069.3395
40% | 6284.3875 | 8705.2708 | 9333.7723 | 9440.4874 | 9523.3131 | 9666.8104 | 9993.9968 | 10212.5442 | 10489.9121 | 10633.6121 | 10759.6846 | 10525.2775 | 10798.7746 | 11229.0652 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 | 10901.546 |  | 6724.8052 | 9115.1562 | 9768.223 | 9868.8391 | 9932.2394 | 10072.6131 | 10404.9218 | 10585.8183 | 10931.4671 | 11983.2898 | 11114.863 | 10944.6007 | 11173.1122 | 11673.5279 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612 | 11333.8612
35% | 2348.7515 | 3253.5419 | 3488.4405 | 3528.3246 | 3559.2802 | 3612.9114 | 3735.1954 | 3816.8761 | 3920.5407 | 3974.2477 | 4021.3665 | 3933.7583 | 4035.9762 | 4196.7946 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 | 4074.3863 |  | 2513.3549 | 3406.7341 | 3650.8138 | 3688.4184 | 3712.1139 | 3764.5777 | 3888.7761 | 3956.3851 | 4085.5692 | 4478.6815 | 4154.1123 | 4090.4778 | 4175.8826 | 4362.9099 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615 | 4235.9615
30% | 1171.4214 | 1622.6784 | 1739.8323 | 1759.7242 | 1775.163 | 1801.9112 | 1862.8993 | 1903.637 | 1955.3388 | 1982.1248 | 2005.6249 | 1961.931 | 2012.9114 | 2093.1183 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 | 2032.0682 |  | 1253.516 | 1699.0818 | 1820.8147 | 1839.5697 | 1851.3876 | 1877.5536 | 1939.4965 | 1973.2159 | 2037.6455 | 2233.7072 | 2071.8308 | 2040.0936 | 2082.6886 | 2175.967 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525 | 2112.6525
25% | 690.592 | 956.6232 | 1025.6893 | 1037.4162 | 1046.5179 | 1062.2869 | 1098.2414 | 1122.2576 | 1152.7376 | 1168.5288 | 1182.3829 | 1156.6239 | 1186.6785 | 1233.9632 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 | 1197.9721 |  | 738.9896 | 1001.6655 | 1073.4311 | 1084.4878 | 1091.4549 | 1106.8806 | 1143.398 | 1163.2767 | 1201.2601 | 1316.845 | 1221.4135 | 1202.7034 | 1227.8145 | 1282.8053 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793 | 1245.4793
20% | 348.989 | 483.4272 | 518.3296 | 524.2558 | 528.8553 | 536.8241 | 554.9937 | 567.1302 | 582.5332 | 590.5132 | 597.5144 | 584.4971 | 599.6851 | 623.5803 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 | 605.3923 |  | 373.4466 | 506.1893 | 542.4558 | 548.0433 | 551.5641 | 559.3594 | 577.8134 | 587.8591 | 607.0539 | 665.4645 | 617.2384 | 607.7833 | 620.4731 | 648.2626 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999 | 629.3999
15% | 142.1807 | 196.9518 | 211.1713 | 213.5857 | 215.4596 | 218.7061 | 226.1085 | 231.053 | 237.3283 | 240.5795 | 243.4318 | 238.1285 | 244.3162 | 254.0512 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 | 246.6413 |  | 152.1449 | 206.2253 | 221.0005 | 223.2769 | 224.7113 | 227.8872 | 235.4055 | 239.4982 | 247.3183 | 271.1152 | 251.4675 | 247.6154 | 252.7853 | 264.107 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222 | 256.4222
10% | 57.2416 | 79.2923 | 85.017 | 85.989 | 86.7435 | 88.0505 | 91.0307 | 93.0214 | 95.5478 | 96.8567 | 98.005 | 95.8699 | 98.3611 | 102.2804 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 | 99.2972 |  | 61.2531 | 83.0258 | 88.9742 | 89.8907 | 90.4682 | 91.7468 | 94.7736 | 96.4213 | 99.5697 | 109.1503 | 101.2402 | 99.6893 | 101.7707 | 106.3288 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349 | 103.2349
5% | 48.7477 | 67.5263 | 72.4016 | 73.2294 | 73.8719 | 74.985 | 77.5229 | 79.2182 | 81.3697 | 82.4844 | 83.4623 | 81.644 | 83.7655 | 87.1033 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 | 84.5627 |  | 52.164 | 70.7058 | 75.7716 | 76.5521 | 77.0439 | 78.1327 | 80.7104 | 82.1137 | 84.7948 | 92.9538 | 86.2174 | 84.8967 | 86.6693 | 90.551 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162 | 87.9162
9.992e-14% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 130541.7636 | 180829.3011 | 193884.7798 | 196101.5072 | 197821.9953 | 200802.7777 | 207599.2223 | 212138.9744 | 217900.5692 | 220885.5628 | 223504.3892 | 218635.1944 | 224316.3823 | 233254.5468 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | 226451.1896 | E @ R (MWh) | 139690.2921 | 189343.6009 | 202909.3599 | 204999.3971 | 206316.373 | 209232.2711 | 216135.1177 | 219892.7708 | 227072.7236 | 248921.5973 | 230882.2942 | 227345.5395 | 232092.2705 | 242487.1014 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111 | 235431.4111
Option 8 Winter POE50 W E @ R (MWh) N 2 | 91379.2345 | 126580.5108 | 135719.3459 | 137271.0551 | 138475.3967 | 140561.9444 | 145319.4556 | 148497.2821 | 152530.3985 | 154619.8939 | 156453.0725 | 153044.6361 | 157021.4676 | 163278.1828 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | 158515.8327 | Option 8 Winter POE10 W E @ R (MWh) N 2 | 41907.0876 | 56803.0803 | 60872.808 | 61499.8191 | 61894.9119 | 62769.6813 | 64840.5353 | 65967.8312 | 68121.8171 | 74676.4792 | 69264.6882 | 68203.6618 | 69627.6812 | 72746.1304 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233 | 70629.4233
Summer Season | [30 empty] | Summer Season
P50 | [30 empty] | P10
N | [30 empty] | N
| FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54 |  | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
1
0.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94.6719 | 122.4737 | 129.7436 | 129.304 | 129.3303 | 130.0731 | 132.0395 | 133.3525 | 134.6398 | 136.1461 | 137.5394 | 138.8941 | 139.0451 | 140.6269 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206 | 139.4206
98% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 46.8602 | 60.6214 | 64.2198 | 64.0022 | 64.0152 | 64.3829 | 65.3562 | 66.0061 | 66.6433 | 67.3889 | 68.0786 | 68.7491 | 68.8238 | 69.6068 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097 | 69.0097
97% | 20.8131 | 27.6102 | 29.4592 | 29.4046 | 29.4015 | 29.6116 | 29.8423 | 30.3162 | 30.6568 | 30.8412 | 31.0426 | 31.2273 | 31.5615 | 31.9765 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 | 31.9467 |  | 92.7689 | 120.0119 | 127.1357 | 126.7049 | 126.7307 | 127.4585 | 129.3855 | 130.672 | 131.9335 | 133.4095 | 134.7748 | 136.1022 | 136.2502 | 137.8002 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181 | 136.6181
95% | 102.4643 | 135.9269 | 145.0299 | 144.761 | 144.7458 | 145.7802 | 146.9157 | 149.2489 | 150.9258 | 151.8338 | 152.8252 | 153.7342 | 155.3796 | 157.4227 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 | 157.276 |  | 137.0126 | 177.2483 | 187.7696 | 187.1334 | 187.1714 | 188.2465 | 191.0924 | 192.9925 | 194.8556 | 197.0355 | 199.052 | 201.0125 | 201.2311 | 203.5203 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745 | 201.7745
90% | 177.7116 | 235.7483 | 251.5362 | 251.0698 | 251.0434 | 252.8375 | 254.8069 | 258.8536 | 261.762 | 263.3368 | 265.0563 | 266.6327 | 269.4865 | 273.03 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 | 272.7756 |  | 594.078 | 768.5376 | 814.1574 | 811.3985 | 811.5637 | 816.2249 | 828.5646 | 836.8035 | 844.8817 | 854.3338 | 863.0771 | 871.5778 | 872.5255 | 882.4514 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815 | 874.8815
85% | 504.3166 | 669.0154 | 713.8189 | 712.4955 | 712.4205 | 717.5119 | 723.1007 | 734.5845 | 742.838 | 747.307 | 752.1867 | 756.6605 | 764.759 | 774.815 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 | 774.093 |  | 561.9657 | 726.995 | 770.1489 | 767.5392 | 767.6954 | 772.1046 | 783.7774 | 791.5709 | 799.2124 | 808.1536 | 816.4243 | 824.4655 | 825.362 | 834.7513 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906 | 827.5906
80% | 704.4422 | 934.4978 | 997.0804 | 995.2318 | 995.1271 | 1002.2389 | 1010.0454 | 1026.0863 | 1037.6149 | 1043.8574 | 1050.6735 | 1056.9226 | 1068.2348 | 1082.2812 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 | 1081.2727 |  | 392.484 | 507.7425 | 537.8818 | 536.0591 | 536.1682 | 539.2477 | 547.4001 | 552.8431 | 558.1801 | 564.4247 | 570.2011 | 575.8172 | 576.4433 | 583.0009 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998 | 577.9998
75% | 1836.3528 | 2436.0657 | 2599.2074 | 2594.3882 | 2594.1154 | 2612.6546 | 2633.0048 | 2674.8204 | 2704.8735 | 2721.1465 | 2738.9148 | 2755.205 | 2784.6939 | 2821.3104 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 | 2818.6814 |  | 700.5244 | 906.2435 | 960.0375 | 956.7843 | 956.979 | 962.4754 | 977.0262 | 986.7412 | 996.2669 | 1007.4126 | 1017.7226 | 1027.7464 | 1028.8639 | 1040.5683 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421 | 1031.6421
70% | 3172.6584 | 4208.7797 | 4490.6388 | 4482.3127 | 4481.8414 | 4513.8714 | 4549.0304 | 4621.275 | 4673.1976 | 4701.3124 | 4732.0106 | 4760.1551 | 4811.103 | 4874.3651 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 | 4869.823 |  | 1276.1675 | 1650.9325 | 1748.9307 | 1743.0043 | 1743.359 | 1753.372 | 1779.8796 | 1797.5778 | 1814.931 | 1835.2355 | 1854.0175 | 1872.2783 | 1874.3141 | 1895.6364 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751 | 1879.3751
65% | 7968.2023 | 10570.444 | 11278.3393 | 11257.4282 | 11256.2445 | 11336.6886 | 11424.9912 | 11606.4352 | 11736.84 | 11807.4509 | 11884.55 | 11955.2357 | 12083.1924 | 12242.0767 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 | 12230.6689 |  | 1605.6162 | 2077.1285 | 2200.4254 | 2192.969 | 2193.4153 | 2206.0132 | 2239.3639 | 2261.631 | 2283.4639 | 2309.0102 | 2332.6409 | 2355.6158 | 2358.1771 | 2385.0038 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446 | 2364.5446
60% | 11647.312 | 15451.0709 | 16485.8185 | 16455.2522 | 16453.5219 | 16571.109 | 16700.1831 | 16965.4041 | 17156.0199 | 17259.2335 | 17371.9312 | 17475.2541 | 17662.2915 | 17894.5364 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 | 17877.8614 |  | 2512.492 | 3250.3215 | 3443.2583 | 3431.5904 | 3432.2888 | 3452.0021 | 3504.1898 | 3539.0337 | 3573.1982 | 3613.1734 | 3650.151 | 3686.1024 | 3690.1105 | 3732.0893 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745 | 3700.0745
55% | 13170.4015 | 17471.5683 | 18641.6273 | 18607.0639 | 18605.1073 | 18738.071 | 18884.0238 | 19183.9271 | 19399.4692 | 19516.1798 | 19643.6146 | 19760.4488 | 19971.9446 | 20234.5597 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 | 20215.7041 |  | 4828.1473 | 6246.0024 | 6616.7608 | 6594.3391 | 6595.6811 | 6633.5633 | 6733.8501 | 6800.8082 | 6866.4607 | 6943.2792 | 7014.3375 | 7083.4238 | 7091.1259 | 7171.7949 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733 | 7110.2733
50% | 16911.4168 | 22434.3178 | 23936.7286 | 23892.3477 | 23889.8353 | 24060.567 | 24247.9772 | 24633.0672 | 24909.8334 | 25059.6953 | 25223.3277 | 25373.3483 | 25644.9189 | 25982.129 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 | 25957.9175 |  | 10714.812 | 13861.3711 | 14684.1724 | 14634.4134 | 14637.3915 | 14721.4613 | 14944.0217 | 15092.6176 | 15238.3161 | 15408.7947 | 15566.4901 | 15719.8092 | 15736.9019 | 15915.9256 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945 | 15779.3945
45% | 22520.2713 | 29874.9022 | 31875.6039 | 31816.5035 | 31813.1579 | 32040.5146 | 32290.0814 | 32802.8907 | 33171.4494 | 33371.0147 | 33588.9175 | 33788.694 | 34150.3339 | 34599.3834 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 | 34567.1419 |  | 16236.3476 | 21004.3853 | 22251.1909 | 22175.7903 | 22180.3031 | 22307.6955 | 22644.9453 | 22870.1153 | 23090.8949 | 23349.2243 | 23588.1829 | 23820.5101 | 23846.4109 | 24117.6889 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008 | 23910.8008
40% | 15794.9825 | 20953.2804 | 22356.5072 | 22315.0562 | 22312.7097 | 22472.1702 | 22647.2082 | 23006.8759 | 23265.371 | 23405.3395 | 23558.1694 | 23698.2861 | 23951.9286 | 24266.8772 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 | 24244.2641 |  | 16811.9908 | 21749.0744 | 23040.0842 | 22962.0103 | 22966.6831 | 23098.592 | 23447.7987 | 23680.9519 | 23909.559 | 24177.0472 | 24424.4778 | 24665.0419 | 24691.8611 | 24972.7569 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339 | 24758.5339
35% | 8189.141 | 10863.5364 | 11591.06 | 11569.5691 | 11568.3525 | 11651.0272 | 11741.7782 | 11928.2532 | 12062.2738 | 12134.8425 | 12214.0795 | 12286.725 | 12418.2297 | 12581.5194 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 | 12569.7953 |  | 22897.8708 | 29622.1608 | 31380.5115 | 31274.1752 | 31280.5395 | 31460.199 | 31935.8172 | 32253.3711 | 32564.7331 | 32929.051 | 33266.0507 | 33593.6981 | 33630.2257 | 34012.8048 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338 | 33721.0338
30% | 3808.7911 | 5052.6595 | 5391.0326 | 5381.0371 | 5380.4713 | 5418.9235 | 5461.132 | 5547.8621 | 5610.1954 | 5643.9473 | 5680.8006 | 5714.5882 | 5775.7514 | 5851.6979 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 | 5846.245 |  | 21159.0479 | 27372.7075 | 28997.5323 | 28899.2709 | 28905.152 | 29071.1685 | 29510.6691 | 29804.1085 | 30091.8262 | 30428.4785 | 30739.887 | 31042.6535 | 31076.4072 | 31429.934 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195 | 31160.3195
25% | 2600.5659 | 3449.8542 | 3680.8886 | 3674.0639 | 3673.6775 | 3699.9319 | 3728.7511 | 3787.9686 | 3830.5285 | 3853.5736 | 3878.7363 | 3901.8059 | 3943.5668 | 3995.4216 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 | 3991.6984 |  | 6103.1255 | 7895.3963 | 8364.0615 | 8335.719 | 8337.4153 | 8385.3012 | 8512.071 | 8596.7107 | 8679.7002 | 8776.8043 | 8866.6271 | 8953.9572 | 8963.6932 | 9065.6646 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969 | 8987.8969
20% | 1575.389 | 2089.8768 | 2229.8344 | 2225.7001 | 2225.4661 | 2241.3706 | 2258.8289 | 2294.7021 | 2320.4843 | 2334.4448 | 2349.688 | 2363.6632 | 2388.9615 | 2420.3744 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 | 2418.119 |  | 1637.7285 | 2118.6711 | 2244.4339 | 2236.8284 | 2237.2836 | 2250.1334 | 2284.1512 | 2306.8636 | 2329.1332 | 2355.1904 | 2379.2937 | 2402.7281 | 2405.3406 | 2432.7039 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355 | 2411.8355
15% | 1008.6332 | 1338.0309 | 1427.6379 | 1424.9909 | 1424.8411 | 1435.0239 | 1446.2014 | 1469.169 | 1485.676 | 1494.614 | 1504.3734 | 1513.321 | 1529.518 | 1549.63 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 | 1548.1859 |  | 903.3078 | 1168.5771 | 1237.943 | 1233.7481 | 1233.9992 | 1241.0867 | 1259.8495 | 1272.3769 | 1284.6599 | 1299.032 | 1312.3265 | 1325.252 | 1326.693 | 1341.7855 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753 | 1330.2753
10% | 675.0905 | 895.5604 | 955.5354 | 953.7638 | 953.6635 | 960.4789 | 967.9602 | 983.3327 | 994.381 | 1000.3634 | 1006.8954 | 1012.8841 | 1023.725 | 1037.1862 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 | 1036.2197 |  | 211.1088 | 273.1039 | 289.3152 | 288.3348 | 288.3935 | 290.0499 | 294.4349 | 297.3626 | 300.2332 | 303.5921 | 306.6991 | 309.7199 | 310.0566 | 313.5838 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938 | 310.8938
5% | 480.3015 | 637.1576 | 679.8276 | 678.5671 | 678.4957 | 683.3447 | 688.6673 | 699.6043 | 707.4647 | 711.721 | 716.3683 | 720.629 | 728.3419 | 737.919 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 | 737.2314 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9.992e-14% | 42.1598 | 55.9283 | 59.6738 | 59.5631 | 59.5568 | 59.9825 | 60.4497 | 61.4097 | 62.0997 | 62.4733 | 62.8812 | 63.2552 | 63.9322 | 64.7729 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 | 64.7125 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E @ R (MWh) | 112911.4176 | 149785.8315 | 159816.886 | 159520.5704 | 159503.7964 | 160643.7099 | 161894.98 | 164466.0868 | 166313.955 | 167314.5287 | 168407.043 | 169408.6762 | 171221.8548 | 173473.2847 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | 173311.6334 | E @ R (MWh) | 109518.1284 | 141679.7064 | 150089.7144 | 149581.1188 | 149611.5589 | 150470.8515 | 152745.6837 | 154264.5107 | 155753.7228 | 157496.2176 | 159108.0516 | 160675.1553 | 160849.8627 | 162679.6988 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885 | 161284.1885
Option 8 Summer POE50 W E @ R (MWh) N 2 | 79037.9923 | 104850.082 | 111871.8202 | 111664.3993 | 111652.6574 | 112450.5969 | 113326.486 | 115126.2607 | 116419.7685 | 117120.1701 | 117884.9301 | 118586.0733 | 119855.2983 | 121431.2993 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | 121318.1434 | Option 8 Summer POE10 W E @ R (MWh) N 2 | 32855.4385 | 42503.9119 | 45026.9143 | 44874.3356 | 44883.4677 | 45141.2555 | 45823.7051 | 46279.3532 | 46726.1168 | 47248.8653 | 47732.4155 | 48202.5466 | 48254.9588 | 48803.9096 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566 | 48385.2566

## POF N,N-1 & N-2 Risk
N-2 Method 1
| Asset name | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Tx 1 Pof | DS-PHM-TRNFMR-9000004393 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378%
Tx 2 Pof | DS-PHM-TRNFMR-9000007050 | 0.01357% | 0.01357% | 0.01791% | 0.023% | 0.02887% | 0.03555% | 0.04308% | 0.0515% | 0.06084% | 0.07112% | 0.08238% | 0.09465% | 0.1079% | 0.1223% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378% | 0.1378%
Tx 3 Pof | bar: FY25 to FY54
Tx 4 Pof
Tx 5 Pof
Total Tx Pof |  | 0.02714% | 0.02714% | 0.03583% | 0.046% | 0.05773% | 0.0711% | 0.08616% | 0.103% | 0.1217% | 0.1422% | 0.1648% | 0.1893% | 0.2159% | 0.2446% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755% | 0.2755%
N-1 Risk |  | 0.01047% | 0.01047% | 0.01382% | 0.01775% | 0.02227% | 0.02743% | 0.03324% | 0.03974% | 0.04694% | 0.05488% | 0.06356% | 0.07303% | 0.08329% | 0.09438% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063% | 0.1063%
N-2 Risk |  | 4.318e-07% | 4.318e-07% | 7.523e-07% | 1.24e-06% | 1.953e-06% | 2.962e-06% | 4.351e-06% | 6.217e-06% | 8.675e-06% | 1.186e-05% | 1.591e-05% | 2.1e-05% | 2.731e-05% | 3.507e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05% | 4.449e-05%
N Risk |  | 99.99% | 99.99% | 99.99% | 99.98% | 99.98% | 99.97% | 99.97% | 99.96% | 99.95% | 99.95% | 99.94% | 99.93% | 99.92% | 99.91% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89% | 99.89%

## Summary
Involuntary load shedding (NER 5.17.1(c)(4)(ii))
Option 1 - Do Nothing / Base Case | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047852 | 0.076147 | 0.70127 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 4.0487 | 5.2651 | 7.0314 | 10.0174 | 13.4078 | 18.1148 | 25.1158 | 27.4427 | 29.628 | 37.5617 | 50.3309 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0053666 | 0.0084883 | 0.013014 | 0.019541 | 0.028413 | 0.040455 | 0.056638 | 0.075614 | 0.099076 | 0.13103 | 0.17292 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559
Total EUE (MWh) - Option 1 | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Cost of EUE ($) - Option 1 | 1320.0832 | 52250.2261 | 116638.2684 | 156512.078 | 203592.9757 | 271955.8559 | 387486.1996 | 518720.9803 | 700905.2416 | 971811.9987 | 1062374.4731 | 1149494.6633 | 1458110.3655 | 1976830.5821 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358
Hours at Risk pA. (Hrs) (N) | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 1.486 | 2.9986 | 2.9986 | 3.755 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986 | 2.9986
Option 2 - 1A New PHS ZSS + Four new feeders | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 0.017284 | 0.021753 | 0.030238 | 0.052809 | 0.092521 | 0.21841 | 0.99428 | 0.51227 | 0.42063 | 0.78725 | 2.1023 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.00338 | 0.0053591 | 0.0082684 | 0.01257 | 0.018452 | 0.026556 | 0.037643 | 0.050127 | 0.065434 | 0.087264 | 0.11674 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432
Total EUE (MWh) - Option 2 | 0.034194 | 1.3534 | 3.0212 | 0.020664 | 0.027112 | 0.038506 | 0.065379 | 0.11097 | 0.24497 | 1.0319 | 0.5624 | 0.48606 | 0.87452 | 2.219 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47
Cost of EUE ($) - Option 2 | 1320.0832 | 52250.2261 | 116638.2684 | 797.7574 | 1046.6889 | 1486.5837 | 2524.0333 | 4284.2482 | 9457.2332 | 39838.3701 | 21711.9982 | 18764.9736 | 33761.754 | 85667.3885 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917
Option 3 - 2A PHM 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0001052 | 0.00037821 | 0.0010464 | 0.0012944 | 0.0029852 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001 | 0.002001
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.00038758 | 0.00063093 | 0.0010283 | 0.0017479 | 0.0027597 | 0.0043468 | 0.0069231 | 0.0088106 | 0.010954 | 0.015688 | 0.023463 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917 | 0.026917
Total EUE (MWh) - Option 3 | 0.034194 | 1.3534 | 3.0212 | 0.00038758 | 0.00063093 | 0.0010283 | 0.0017479 | 0.0027597 | 0.0043468 | 0.0070283 | 0.0091888 | 0.012 | 0.016983 | 0.026449 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918 | 0.028918
Cost of EUE ($) - Option 3 | 1320.0832 | 52250.2261 | 116638.2684 | 14.9628 | 24.3577 | 39.6979 | 67.4814 | 106.5432 | 167.8132 | 271.3342 | 354.7438 | 463.2904 | 655.6296 | 1021.0799 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194 | 1116.4194
Option 4 - 3A OFR 3rd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 0.56278 | 0.77154 | 1.1477 | 2.0257 | 3.0536 | 4.7607 | 7.9704 | 7.9558 | 7.967 | 11.1441 | 17.2296 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934 | 15.7934
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0043733 | 0.0069237 | 0.010641 | 0.016056 | 0.023433 | 0.033505 | 0.04714 | 0.062871 | 0.082255 | 0.10915 | 0.14483 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996 | 0.17996
Total EUE (MWh) - Option 4 | 0.034194 | 1.3534 | 3.0212 | 0.56715 | 0.77847 | 1.1584 | 2.0418 | 3.077 | 4.7942 | 8.0175 | 8.0187 | 8.0493 | 11.2533 | 17.3744 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734 | 15.9734
Cost of EUE ($) - Option 4 | 1320.0832 | 52250.2261 | 116638.2684 | 21895.4636 | 30053.6762 | 44719.7826 | 78825.5457 | 118792.7016 | 185087.1566 | 309525.3397 | 309571.2941 | 310752.2884 | 434445.5896 | 670759.6627 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342 | 616671.342
Option 5 - 4A LLG 2nd Tx + Switchroom + Three new feeders + OFR12 New Feeder | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 0.017284 | 0.021753 | 0.030238 | 0.052809 | 0.092521 | 0.21841 | 0.99428 | 0.51227 | 0.42063 | 0.78725 | 2.1023 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257 | 1.3257
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.00338 | 0.0053591 | 0.0082684 | 0.01257 | 0.018452 | 0.026556 | 0.037643 | 0.050127 | 0.065434 | 0.087264 | 0.11674 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432 | 0.14432
Total EUE (MWh) - Option 5 | 0.034194 | 1.3534 | 3.0212 | 0.020664 | 0.027112 | 0.038506 | 0.065379 | 0.11097 | 0.24497 | 1.0319 | 0.5624 | 0.48606 | 0.87452 | 2.219 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47 | 1.47
Cost of EUE ($) - Option 5 | 1320.0832 | 52250.2261 | 116638.2684 | 797.7574 | 1046.6889 | 1486.5837 | 2524.0333 | 4284.2482 | 9457.2332 | 39838.3701 | 21711.9982 | 18764.9736 | 33761.754 | 85667.3885 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917 | 56751.6917
Option 6 - Non Network | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.0069141 | 0.26753 | 0.82414 | 1.1595 | 1.5561 | 2.1944 | 3.4694 | 4.9355 | 7.2051 | 11.1081 | 11.3691 | 11.5703 | 15.6421 | 22.8112 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847 | 21.7847
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0011081 | 0.0015033 | 0.0028031 | 0.0046474 | 0.0073556 | 0.011287 | 0.016967 | 0.024701 | 0.035226 | 0.049415 | 0.065829 | 0.086037 | 0.11405 | 0.15089 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788 | 0.18788
Total EUE (MWh) - Option 6 | 0.0080222 | 0.26904 | 0.82695 | 1.1641 | 1.5635 | 2.2057 | 3.4864 | 4.9602 | 7.2403 | 11.1575 | 11.4349 | 11.6563 | 15.7561 | 22.9621 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726 | 21.9726
Cost of EUE ($) - Option 6 | 309.7064 | 10386.4363 | 31925.2685 | 44942.0917 | 60360.6251 | 85154.6406 | 134596.9694 | 191492.3949 | 279520.2107 | 430749.6751 | 441457.0149 | 450005.3333 | 608282.673 | 886476.3956 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994 | 848278.5994
Option 7 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047852 | 0.076147 | 0.70127 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 4.0487 | 5.2651 | 7.0314 | 10.0174 | 13.4078 | 18.1148 | 25.1158 | 27.4427 | 29.628 | 37.5617 | 50.3309 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0053666 | 0.0084883 | 0.013014 | 0.019541 | 0.028413 | 0.040455 | 0.056638 | 0.075614 | 0.099076 | 0.13103 | 0.17292 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559
Total EUE (MWh) - Option 7 | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Cost of EUE ($) - Option 7 | 1320.0832 | 52250.2261 | 116638.2684 | 156512.078 | 203592.9757 | 271955.8559 | 387486.1996 | 518720.9803 | 700905.2416 | 971811.9987 | 1062374.4731 | 1149494.6633 | 1458110.3655 | 1976830.5821 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358
Option 8 - | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35 | FY36 | FY37 | FY38 | FY39 | FY40 | FY41 | FY42 | FY43 | FY44 | FY45 | FY46 | FY47 | FY48 | FY49 | FY50 | FY51 | FY52 | FY53 | FY54
Weighted Energy @ Risk (MWh) under N Conditions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047852 | 0.076147 | 0.70127 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746 | 0.1746
Weighted Energy @ Risk (MWh) under N-1 Conditions | 0.032901 | 1.3517 | 3.018 | 4.0487 | 5.2651 | 7.0314 | 10.0174 | 13.4078 | 18.1148 | 25.1158 | 27.4427 | 29.628 | 37.5617 | 50.3309 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438 | 50.8438
Weighted Energy @ Risk (MWh) under N-2 Conditions | 0.0012928 | 0.0017409 | 0.003241 | 0.0053666 | 0.0084883 | 0.013014 | 0.019541 | 0.028413 | 0.040455 | 0.056638 | 0.075614 | 0.099076 | 0.13103 | 0.17292 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559 | 0.21559
Total EUE (MWh) - Option 8 | 0.034194 | 1.3534 | 3.0212 | 4.0541 | 5.2736 | 7.0444 | 10.0369 | 13.4362 | 18.1553 | 25.1725 | 27.5183 | 29.7749 | 37.7689 | 51.2051 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234 | 51.234
Cost of EUE ($) - Option 8 | 1320.0832 | 52250.2261 | 116638.2684 | 156512.078 | 203592.9757 | 271955.8559 | 387486.1996 | 518720.9803 | 700905.2416 | 971811.9987 | 1062374.4731 | 1149494.6633 | 1458110.3655 | 1976830.5821 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358 | 1977946.3358